ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png | file://x:/photopub/docs/0000000583/ec1bedc2-2446-4934-898c-2959ac19bf77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
ELIN-786491-2017 | EL-451097-2016 | 4/6/2017 12:10:49 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unbonded_fixtures_-_factory_installed_bond_conductor_removed1.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed2.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed3.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed4.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed5.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed6.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed8.png,Unbonded_fixtures_-_factory_installed_bond_conductor_removed9.png Electrical equipment including light fixtures are required to be bonded to the grounded system conductor. This is required to provide a low impedance path for fault current back to the source and to provide an equipotential plane to minimize the possibility of a potential difference between metal parts. This installation at a newly constructed house had light fixtures that were not bonded. The bonding conductor that was supp | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unbonded_fixtures_-_factory_installed_bond_conductor_removed7.png | file://x:/photopub/docs/0000000583/5e7b0182-09c6-47bd-8747-f7aa10158601.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07da0b50_4c9e_43b0_947a_c38d747812ae
GAIN-770150-2017 | GA-507989-2017 | 3/9/2017 9:30:27 AM | ASSESS: GA: Rough-In | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent_certification.png Custom fireplace installation was found with venting material that was not certified for the application. The as found hazard is if uncertified vent materials are used for an appliance installation premature vent failure could occur leading to products of combustion entering the building envelope or clearances to combustible material being to close possibly leading to a fire. | 3 | Unapproved venting material | Vent_certification.png | file://x:/photopub/docs/0000000569/73bc977a-5479-47cb-b482-5e05dad32101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a27fa44a_00e7_461c_9093_55544b36e7c4
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property. Confirmed with voltage tester the voltage readings of outer luminaire enclosure or frames are anywhere from a fluctuating voltage reading of 3 volts up to 48 volts. The luminaire is live and is a fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors7.png | file://x:/photopub/docs/0000000579/f7c26c82-a74a-4b84-a31e-01b7a9ca751f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors9.png | file://x:/photopub/docs/0000000579/859f3dd8-c656-4eab-a54f-7333cbe7919b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors4.png | file://x:/photopub/docs/0000000579/d89fb5ae-b19e-482b-aea0-3f8a4c8e1678.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELIN-771417-2017 | EL-273981-2015 | 3/9/2017 11:42:23 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Inadequate_clearances.png At an existing single family dwelling, a 200amp 240volt service was found in an energized state with the consumer service conductors installed with inadequate clearances. This can lead to an "Equipment Damage" scenario. Pic attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Inadequate_clearances.png | file://x:/photopub/docs/0000000569/d3230909-5827-4c34-8d90-4c864c506692.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91f1fc7a_0292_4777_b585_7a3b69d169bd
GAUP-802514-2017 | UW-526487-2017 | 4/26/2017 3:22:43 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 | #Meter1.png,Meter2.png Meter not secured and improper swing joint on black iron piping. Meter to be secured and have swing joint to prevent breakage of piping or meter with snow loads and ground movement | 2 | Provision for expansion Incorrect swing joint | Meter1.png | file://x:/photopub/docs/0000000591/59bbd65b-a369-4f72-83fe-3d06b9196bfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d4618d7_88f0_4d52_b8b4_1d2283c84f9d
GAIN-802554-2017 | GA-490131-2017 | 4/26/2017 11:44:48 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | #Reg.png O.A.R.A. 2 psi to inches regulator equipped with a vent limiter installed on the vertical. Manufacture requires regulator to be mounted on the horizontal for proper operation of vent limiter | 2 | Not installed according to certified installation instructions | Reg.png | file://x:/photopub/docs/0000000591/00b4813d-3195-4c29-9530-742a57c910be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd058328_d5c6_43cd_9508_2b3e2fa73ba0
GAUP-802514-2017 | UW-526487-2017 | 4/26/2017 3:22:43 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA003 | Provision for expansion Incorrect swing joint | 2 | 2 | #Meter1.png,Meter2.png Meter not secured and improper swing joint on black iron piping. Meter to be secured and have swing joint to prevent breakage of piping or meter with snow loads and ground movement | 2 | Provision for expansion Incorrect swing joint | Meter2.png | file://x:/photopub/docs/0000000591/5514e3c4-7ed2-4278-b91e-7ec322ff73cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d4618d7_88f0_4d52_b8b4_1d2283c84f9d
EDMA-814611-2017 | ED-455641-2016 | 5/11/2017 | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #Sheave_wear1.png,Sheave_wear2.png Uneven wear on drive sheave must be regularly monitored for further wear | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Sheave_wear2.png | file://x:/photopub/docs/0000000600/01365fc6-c067-4cea-b755-e2a364d1edb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a13a11f8_0362_4ff1_86ac_d73892414b31
EDMA-814611-2017 | ED-455641-2016 | 5/11/2017 | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #Sheave_wear1.png,Sheave_wear2.png Uneven wear on drive sheave must be regularly monitored for further wear | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Sheave_wear1.png | file://x:/photopub/docs/0000000600/e5723c72-fbfb-42ad-a578-4456a64ea661.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a13a11f8_0362_4ff1_86ac_d73892414b31
ELIN-795490-2017 | EL-517665-2017 | 4/18/2017 1:20:27 PM | ASSESS: EL: Service Connection | png | #asFound Grounding conductor incorrectly terminated in electrical panel | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Grounding_conductor__grounding_conductor_incorrectly_terminated.png Grounding conductor incorrectly terminated on to the metal frame of the distribution equipment. Grounding conductor shall be terminated on the neutral bus bar | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_conductor__grounding_conductor_incorrectly_terminated.png | file://x:/photopub/docs/0000000587/29e518c7-9aae-4528-9784-f89512b7c530.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d604eb46_3f59_4eb3_9146_afc14e4d9ec1
AMOP-782202-2017 | 4708355 | 3/24/2017 2:55:40 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Safety_chain_not_attached.png Safety chain not installed, PCU could fall off if sweep/PCU connection were to fail | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Safety_chain_not_attached.png | file://x:/photopub/docs/0000000576/9914d955-dbc8-4e0b-84c1-b6d078e90f47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9444963c_4197_47f7_a8c0_86aabe64406f
BPVOP-794434-2017 | BPV-0000465848-2016 | 4/12/2017 8:25:35 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve_installation_1.png,Safety_valve_installation_2.png The safety valve on this unit needs to be serviced or replaced as it has gone beyond its maximum service interval which may result in the valve not operating when required. This could end up in a boiler becoming over pressurized. The valve has also been installed improperly as per the manufactures directions as these valves must be installed vertically. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_installation_2.png | file://x:/photopub/docs/0000000587/882262ae-f37c-41ca-9827-5e5b61c38f2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6fe1a85_c532_4353_b85c_88ee68cf3dc4
BPVOP-794434-2017 | BPV-0000465848-2016 | 4/12/2017 8:25:35 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve_installation_1.png,Safety_valve_installation_2.png The safety valve on this unit needs to be serviced or replaced as it has gone beyond its maximum service interval which may result in the valve not operating when required. This could end up in a boiler becoming over pressurized. The valve has also been installed improperly as per the manufactures directions as these valves must be installed vertically. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_installation_1.png | file://x:/photopub/docs/0000000587/924698b1-da32-442f-ab3c-00924b770064.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6fe1a85_c532_4353_b85c_88ee68cf3dc4
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-15_4238.JPG | file://x:/photopub/docs/0000000572/ec789635-0cd7-4e63-b922-48f6e2a644b5.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property. Confirmed with voltage tester the voltage readings of outer luminaire enclosure or frames are anywhere from a fluctuating voltage reading of 3 volts up to 48 volts. The luminaire is live and is a fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors5.png | file://x:/photopub/docs/0000000579/7fe3dcbc-936e-4d8d-9e97-3662ca859ce3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors6.png | file://x:/photopub/docs/0000000579/955d01bc-537b-4c47-af28-1b5ccee0c635.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors. | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png | file://x:/photopub/docs/0000000577/86f9062f-eab9-411d-8627-83cea95c8382.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors. | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png | file://x:/photopub/docs/0000000577/f9459ade-f386-430b-956d-8ad2682eb72d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
ELHE-780151-2017 | HE-514438-2017 | 3/21/2017 10:59:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Boards with nails on top of energized flexible extension cords and workers are stepping on cables that are damaged. NMD90 cable is used outdoors on grade and on floor of building where workers are stepping on exposed energized conductors that are connected to 240 volts | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers1.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers2.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers3.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers4.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers5.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers7.png,Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers8.png Found energized 240 volt 2 pole breaker connected to flexible extension cord that was open and exposed spliced to NMD90 cable without a junction box and cover to enclose energized conductors in a box. Evidence was found that workers were stepping on top of energized 240 volt connected conductors and these conductors were damaged and unsafe. When people are in direct contact with exposed energized conductors rated 240 volts, the electrical equipment is very unsafe and | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cables_open_spliced_are_damaged_energized_and_unsafe_to_workers6.png | file://x:/photopub/docs/0000000577/d1da8bf1-951b-4ddd-9c47-c10003bd001c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb9a0c7_5014_4e00_a904_3cd8cf7f6aec
GAIN-794675-2017 | GA-522366-2017 | 4/21/2017 3:01:02 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Vent.png The as-found-condition is that a unit heater is installed with the incorrect vent material for a horizontal venting application. The potential hazard is that the positive pressure in the vent will allow flue gas to escape into an occupied space, exposing people to harmful emissions such as carbon monoxide | 2 | Side wall vent termination not compliant with installation instructions | Vent.png | file://x:/photopub/docs/0000000592/14ed5ac0-b4dd-4a38-94c7-9425f4275136.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a10570be_81c7_4e11_b75f_9483f23f4a54
GAIN-775880-2017 | GA-494812-2017 | 3/23/2017 3:24:55 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Fran_kel9.png Special venting system leaking at rear of boiler. Possibility of flue gases entering occupied space. Carbon Monoxide risk. | 3 | Leaking or failing special venting system (Minor) | Fran_kel9.png | file://x:/photopub/docs/0000000576/6f344017-4fc2-4782-8b11-b5256473438c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf3c6ece_42a2_492b_8251_ff7e777ce346
GAIN-614994-2016 | GA-363615-2016 | 5/12/2017 1:20:14 PM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Coffee_roaster.png None CSA approved appliance, possible electrical and gas fire hazard | 3 | Uncertified appliance connected to gas supply but not in service | Coffee_roaster.png | file://x:/photopub/docs/0000000600/288801b9-4b09-43bd-9094-a10605a44369.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0e6c20f_6145_4ae6_93bd_f28747d714e4
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Penticton_Gateway_Casino_grand_opening_as_found2.png | file://x:/photopub/docs/0000000582/11bae447-7601-48ee-b3fe-e8f4e3481303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Ad_hoc_panel_covers.png | file://x:/photopub/docs/0000000582/b05014d1-8382-4d86-ba86-ff768d4d1ff4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Penticton_Gateway_Casino_grand_opening_as_found4.png | file://x:/photopub/docs/0000000582/cac31eca-3c7d-4825-8e4d-2f5b73a9d90b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Penticton_Gateway_Casino_grand_opening_as_found6.png | file://x:/photopub/docs/0000000582/a6a8660b-13b3-4f70-baa4-91dcee8df475.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Penticton_Gateway_Casino_grand_opening_as_found3.png | file://x:/photopub/docs/0000000582/6f770f30-2dfc-49cb-8f5c-04459cf3ac8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Penticton_Gateway_Casino_grand_opening_as_found5.png | file://x:/photopub/docs/0000000582/f60c5296-2157-48f0-bf18-6271f1269698.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound Ad how panel covers | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Ad_hoc_panel_covers.png | file://x:/photopub/docs/0000000582/0fd8e500-f4c5-4720-b3cf-5ce049bf1a12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELIN-773285-2017 | UW-510534-2017 | 3/8/2017 12:34:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Devices_and_Connectors_not_rated_for_Al1.png,Devices_and_Connectors_not_rated_for_Al2.png,Devices_and_Connectors_not_rated_for_Al3.png,Devices_and_Connectors_not_rated_for_Al4.png Electrical equipment must be approved for use when connected to aluminum electrical conductors. This is required because aluminum conductors expand more than copper conductors and a non-conductive oxide can form on the aluminum conductor when exposed to air. Loose connections and oxidization can create more resistance to the current flow which can cause the equipment to overheat and fail. During a hazard assessment in a single family dwelling, receptacles and switches rated for copper use only were found connected to aluminum conductors. Also, non-approved wire connectors were found for connecting copper and aluminum conductors together. The use of the non-approved devices and connectors at this dwelling has the potential to create equipment damage and a fire hazard to persons and property. | 3 | Conductors Equipment is not approved for the specific use. | Devices_and_Connectors_not_rated_for_Al2.png | file://x:/photopub/docs/0000000570/c7529990-d100-4086-9108-a00a649b90e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c9812dc_c5fc_4419_8357_ab16d5928365
ELIN-781144-2017 | EL-514147-2017 | 3/27/2017 4:08:19 PM | ASSESS: EL: Final | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | #Reverse_polarity.png A 15 amp 120 volt receptacle had the polarity reversed (white wire was hooked up to the brass coloured terminal and the black wire was hooked up to the silver coloured terminal). If a lamp were plugged into this receptacle the screw shell would be energized exposing occupants to a potential shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Reverse_polarity.png | file://x:/photopub/docs/0000000577/ecb9ca43-ee2f-475e-971b-ac0ff297bcab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d4bbb69_71fd_42c1_8e94_24003c57a3ca
ELIN-796496-2017 | EL-514467-2017 | 4/20/2017 9:43:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #5.png Temporary lighting was installed in smoke detector locations and energized via the lighting and smoke detector circuit. With the smoke detector and lighting circuit energized this allowes the accessible conductors in the open switch boxes to become energized as well. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 5.png | file://x:/photopub/docs/0000000588/45d39de5-ffe3-4b56-9cd5-2f5ff4067adf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a41426eb_2c58_47b6_b47d_029521c77f49
ELIN-794685-2017 | EL-375360-2016 | 4/20/2017 1:08:26 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #54.png Separate ground conductor was connected to seperate grounding electrode and installed in sub panel. Ground can only be connected on the Service Side of the Main Breaker at the main distribution panel or equivalent. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | 54.png | file://x:/photopub/docs/0000000588/3dd65654-b0d7-47cf-a4a7-8cc2202337f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b2aac9c_5f5b_4112_8b02_0f1fb5388eab
ELHE-810583-2017 | HE-530857-2017 | 5/5/2017 1:52:03 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Energized panel. | EL298 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #P5.png Exposed energized panel bus is capable of causing a shock, ark flash, injury or death. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | P5.png | file://x:/photopub/docs/0000000596/aa3f79eb-8a59-4959-a3f9-0ee0d73389b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa6854a1_cf38_4fd3_997c_7e572dc22ea3
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-43_4240.JPG | file://x:/photopub/docs/0000000572/7e0663d5-f877-49ee-9616-6c54fc6a7d01.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-55_4241.JPG | file://x:/photopub/docs/0000000572/3ebcff6f-a2af-4994-b135-c26b28267816.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-43_4240.JPG | file://x:/photopub/docs/0000000572/dbea086c-f116-4d0e-be1d-8b7c93b41447.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-15_4238.JPG | file://x:/photopub/docs/0000000572/5c8a850a-baba-4fe8-8a43-33687ae5a4f0.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound LWCO side of boiler | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-43_4240.JPG | file://x:/photopub/docs/0000000572/bb4055b4-9376-4764-9f18-e3de4224dd9f.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound Top view of LWCO no manual reset | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-15_4238.JPG | file://x:/photopub/docs/0000000572/ac24c9d1-d1c6-41dc-ad81-d5d70f3c81ef.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound LWCO no manual reset switch | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-55_4241.JPG | file://x:/photopub/docs/0000000572/d098d953-7950-4711-9508-005826491e0b.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-55_4241.JPG | file://x:/photopub/docs/0000000572/74eb46d0-c170-44c6-b5c9-e49b8792c22a.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
BPVOP-776256-2017 | 2291413 | 3/8/2017 1:16:36 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-09-15-42-43_4240.JPG,Photo-2017-03-09-15-42-15_4238.JPG,Photo-2017-03-09-15-42-55_4241.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-09-15-42-55_4241.JPG | file://x:/photopub/docs/0000000572/a0c2a473-f0f1-4388-87db-e2cc7abb76de.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b3fb386_2ffc_4d5b_8e8c_62f88c3e005b
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors3.png | file://x:/photopub/docs/0000000579/a4623681-6b49-4350-8bbd-911c0f3032cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors1.png | file://x:/photopub/docs/0000000579/684cae66-1995-40b9-816d-6d05a6e51c4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors8.png | file://x:/photopub/docs/0000000579/0f95c9f5-fd45-45a2-a9dd-4a2b61a0a219.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
GAIN-804600-2017 | GA-527662-2017 | 5/1/2017 10:29:45 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting.png The as found condition is standard PVC drain piping was used for the exhaust vent on a high efficient unit heater even though the manufacturer requires the material to meet the the ULC s636 standard. The as found hazard is the currently installed venting material could break down and leak products of combustion into the building envelope, potentially injuring occupants. | 3 | Unapproved venting material | Venting.png | file://x:/photopub/docs/0000000593/4c4c8735-7abd-4c6d-ac65-d577fdb44482.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c308bc28_96c6_496e_b9ba_2af377a7619b
ELOP-772528-2017 | 1540 | 3/27/2017 10:40:20 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Bonding conductor busbar removed from wall and bent over placing strain on the bonding conductors. | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Bonding_buss.png Electrical operating permit assessment of secondary school. Non-compliances from previous inspection. The grounding bus bar for all of the bonding conductors in the main electrical room has been removed from being fastened to the wall, for the installation of a new fire alarm panel, and the buss has been bent over placing strain on the bonding conductor's. Potential shock hazard as there is strain on the conductors and their continuity and integrity is in doubt. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Bonding_buss.png | file://x:/photopub/docs/0000000576/3105aef2-7386-4c3c-9cdc-689be885d85f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e28331a_e544_40d4_b6d2_3dd5dc2f1034
ELIN-790148-2017 | EL-427561-2016 | 4/6/2017 8:17:33 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Ad_hoc_panel_covers.png,Penticton_Gateway_Casino_grand_opening_as_found1.png,Penticton_Gateway_Casino_grand_opening_as_found2.png,Penticton_Gateway_Casino_grand_opening_as_found3.png,Penticton_Gateway_Casino_grand_opening_as_found4.png,Penticton_Gateway_Casino_grand_opening_as_found5.png,Penticton_Gateway_Casino_grand_opening_as_found6.png Opening day of new casino facility. Several panel boards found with exposed energized parts not locked, in areas not secured from general public access. Electrical rooms not secured. Apprentices found working on energized equipment in a common access area without supervision or personal protective equipment. No guards or barriers were in place to protect persons walking through the area. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Penticton_Gateway_Casino_grand_opening_as_found1.png | file://x:/photopub/docs/0000000582/a49b0ac2-9795-40d4-b89d-d0182e33489a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d78d92e_3364_42ff_9414_10be52948a9c
ELHE-696804-2016 | HE-461281-2016 | 3/13/2017 12:31:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Low_overhead_conductors.png Overhead conductors are lower than what has been determined as a safe height. When energized conductors are exposed to accidental contact there is risk of serious injury. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Low_overhead_conductors.png | file://x:/photopub/docs/0000000571/9b396626-870c-47dd-b146-3c36f05dc695.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd156d33_e7fe_4f7c_a4bc_160629f4726e
ELHE-785552-2017 | HE-517279-2017 | 3/29/2017 5:15:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound A few luminaires that are not approved and also not bonded are short circuited to energized conductors. The whole outer enclosure of the luminaire is live and is an electrical fire or shock hazard to people and property | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Luminaires_short_circuited_to_energized_conductors1.png,Luminaires_short_circuited_to_energized_conductors2.png,Luminaires_short_circuited_to_energized_conductors3.png,Luminaires_short_circuited_to_energized_conductors4.png,Luminaires_short_circuited_to_energized_conductors5.png,Luminaires_short_circuited_to_energized_conductors6.png,Luminaires_short_circuited_to_energized_conductors7.png,Luminaires_short_circuited_to_energized_conductors8.png,Luminaires_short_circuited_to_energized_conductors9.png Found energized exposed conductors and luminaires enclosures that are short circuited together with frames or enclosure of luminaires energized. When electrical equipment enclosures and energized circuit conductors are short circuited together, the outer electrical equipment enclosure could possibly be contacted by people and is an electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Luminaires_short_circuited_to_energized_conductors2.png | file://x:/photopub/docs/0000000579/13004e17-6e7c-4c6c-ba45-6a3f5129a25d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d797a9d7_52d7_4af8_917b_2ad9af691319
GAOP-623865-2016 | 2171032 | 4/26/2017 12:40:38 PM | ASSESS: GA OP: Periodic | png | #asFound | GA058 | Cathodic protection missing causing a hazard | 3 | 3 | #Risers1.png,Risers2.png | 3 | Cathodic protection missing causing a hazard | Risers2.png | file://x:/photopub/docs/0000000591/6bd008fd-1cfe-445c-8620-be07436ca804.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BF7C0517_B740_4772_8BCC_6D5F14EF955D
GAOP-623865-2016 | 2171032 | 4/26/2017 12:40:38 PM | ASSESS: GA OP: Periodic | png | #asFound No di-electric unions separating the underground piping system. | GA058 | Cathodic protection missing causing a hazard | 3 | 3 | #Risers1.png,Risers2.png | 3 | Cathodic protection missing causing a hazard | Risers1.png | file://x:/photopub/docs/0000000591/fac8cd51-5948-4273-9f9b-1b4d1d80b0f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BF7C0517_B740_4772_8BCC_6D5F14EF955D
ELIN-773621-2017 | EL-476622-2016 | 3/14/2017 2:13:38 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Breakers_need_Arc_fault_protection_.png This assessment found that Arc fault breakers were not installed for the washer and garage plugs. There is a fire hazard with the branch circuits not protected by this breaker. | 3 | Conductors Equipment is not approved for the specific use. | Breakers_need_Arc_fault_protection_.png | file://x:/photopub/docs/0000000571/6adc27bf-5eee-4e5c-85f0-3b356b29cf80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cb9e2475_0a39_4f23_a441_a0dc4fd09785
EDIN-779970-2017 | ED-379332-2016 | 3/22/2017 11:08:46 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED058 | Temp Slipping /Tripping Hazard | 1 | 1 | #Unfinished_and_uneven_pathway.png The paving stones for the pathway leading across the roof by the control room entrance are uneven and unfinished. | 1 | Temp Slipping /Tripping Hazard | Unfinished_and_uneven_pathway.png | file://x:/photopub/docs/0000000575/2289160e-c7ab-4f78-9408-da88213a26dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0952491_4125_44ef_bc81_2785644287be
GAIN-799580-2017 | GA-337475-2016 | 4/20/2017 1:31:51 PM | ASSESS: GA: Rough-In | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | #Piping.png The as found condition is corrugated stainless steel tubing (CSST) was found to be missing supports at the connection to the appliance. The as found hazard is poorly supported CSST can lead to premature damage, potentially causing the piping system to fail, releasing gas. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Piping.png | file://x:/photopub/docs/0000000588/dd242241-9196-4610-b308-76ef7a14efc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08a94b59_b072_47cf_ab56_4d5234bcbef9
ELOP-795342-2017 | EL-522813-2017 | 4/24/2017 2:10:41 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage21.png,Storage22.png,Storage23.png,Storage24.png,Storage25.png,Storage26.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage22.png | file://x:/photopub/docs/0000000591/1e5852e2-0ae8-4ab8-bec6-bcfd6d5c91df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9461D834_C68E_4F1A_9567_876D8BF04183
ELOP-795342-2017 | EL-522813-2017 | 4/24/2017 2:10:41 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage21.png,Storage22.png,Storage23.png,Storage24.png,Storage25.png,Storage26.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage26.png | file://x:/photopub/docs/0000000591/a7866fff-0289-4b7a-972d-622be63eba72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9461D834_C68E_4F1A_9567_876D8BF04183
ELOP-795342-2017 | EL-522813-2017 | 4/24/2017 2:10:41 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage21.png,Storage22.png,Storage23.png,Storage24.png,Storage25.png,Storage26.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage24.png | file://x:/photopub/docs/0000000591/bd37b17b-4f00-49ea-a8a7-401b20c1951b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9461D834_C68E_4F1A_9567_876D8BF04183
ELOP-795342-2017 | EL-522813-2017 | 4/24/2017 2:10:41 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage21.png,Storage22.png,Storage23.png,Storage24.png,Storage25.png,Storage26.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage25.png | file://x:/photopub/docs/0000000591/aeba85c1-3dad-4ef6-9177-06c7aef4580b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9461D834_C68E_4F1A_9567_876D8BF04183
ELOP-795342-2017 | EL-522813-2017 | 4/24/2017 2:10:41 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage21.png,Storage22.png,Storage23.png,Storage24.png,Storage25.png,Storage26.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage23.png | file://x:/photopub/docs/0000000591/28726637-1490-404e-8c50-387339fb0514.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9461D834_C68E_4F1A_9567_876D8BF04183
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker3.png | file://x:/photopub/docs/0000000591/9b9394e1-6950-4ed6-bec2-95b6957bf8a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
ELIN-793295-2017 | EL-513713-2017 | 4/11/2017 | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | #No_light_installed_at_entry.png No entry light was installed. This could be a hazard to person(s) at night due to inadequate lighting on the stairway. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | No_light_installed_at_entry.png | file://x:/photopub/docs/0000000585/48e8a6ce-06f7-44b6-93e9-994f4d8f053e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b74eea_1ddc_4611_a057_d75eb4ab3e27
BPVIN-785292-2017 | BPV-517094-2017 | 4/21/2017 10:28:19 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances_.png,Clearances_.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances_.png | file://x:/photopub/docs/0000000590/a132bbf6-c7ad-44d2-b140-91a0e1df6fed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ee63366_4f48_42ff_aa4a_bb47135175ab
GAIN-772759-2017 | GA-422014-2016 | 3/16/2017 1:09:44 PM | ASSESS: GA: Final | png | #asFound Water Booster | GA152 | Appliance installed and operating. Venting incomplete (example: venting into living space) | 5 | 5 | #Water_booster.png Venting for the gas water booster needs to terminate under the exhaust hood not into the kitchen area, the products of combustion are vented into the kitchen space which is interconnected to the dining space and could potentially lead to CO being dispersed if the appliance isn't burning properly, furthermore there was no interlocks in place to avoid the booster from firing when the exhaust fan was off. | 5 | Appliance installed and operating. Venting incomplete (example: venting into living space) | Water_booster.png | file://x:/photopub/docs/0000000572/46dcd3f3-f736-4801-bfcc-14b61482fb4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6058e650_778c_4c78_9ee7_e08ed955cfb2
ELIN-799074-2017 | EL-524585-2017 | 4/20/2017 10:45:03 AM | ASSESS: EL: Final | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | #Broken_Branch_Breaker.png A 2 pole 20 amp breaker handle is broken and the breaker is no longer in proper working condition, this poses a shock hazard to persons and possible mechanical damage to the electrical equipment. | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Broken_Branch_Breaker.png | file://x:/photopub/docs/0000000589/fea54e9a-8707-4f22-96fa-91613dd2684e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0a4b908_6381_412f_ba51_e7e3b197d005
GAHE-771411-2017 | HE-509420-2017 | 3/9/2017 7:43:59 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound 261 | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Vent_connector.png,261_.png At time of inspection venting of water heater was oversized, this inadequate venting of flue gases could causing carbon monoxide poisoning | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 261_.png | file://x:/photopub/docs/0000000569/52acb948-44b6-4c01-a01c-fbfa2e9f6964.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__694e1c44_4948_4577_926f_fe2092ed1041
GAIN-763477-2017 | GA-500364-2017 | 3/21/2017 8:09:00 AM | ASSESS: GA: Final | png | #asFound Oven corrugated gas connector | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Gas_connector.png Corrugated connector was found connecting ovens, they are not currently up to code standards, and can be more susceptible to wear and tear. Which could then lead to a gas leak, possibly causing injury or damage. | 2 | Certified appliance connector installed but not approved for application | Gas_connector.png | file://x:/photopub/docs/0000000574/932acb51-948d-4cec-b17e-6ae5361c8a18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a1c2390_b552_47c1_9313_ba73c3d9f7ad
ELIN-780006-2017 | EL-507332-2017 | 3/28/2017 11:57:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #15A_receptacles_installed_on_20A_branch_circuits_1.png,15A_receptacles_installed_on_20A_branch_circuits_2.png,15A_receptacles_installed_on_20A_branch_circuits_3.png,15A_receptacles_installed_on_20A_branch_circuits_4.png Receptacles are required to be properly rated when connected to branch circuits. This is required to prevent the receptacles from being over loaded and damaged during use. This installation has 15A receptacles installed on 20A branch circuits in a temporary construction service installed on a residential property. Left uncorrected the receptacles may be thermally damaged if the circuits are overload. This is a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 15A_receptacles_installed_on_20A_branch_circuits_2.png | file://x:/photopub/docs/0000000577/746d5904-bb38-46e7-86d4-fc9704159741.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f186264_530a_44b5_b002_c93bd46f981e
ELIN-780006-2017 | EL-507332-2017 | 3/28/2017 11:57:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #15A_receptacles_installed_on_20A_branch_circuits_1.png,15A_receptacles_installed_on_20A_branch_circuits_2.png,15A_receptacles_installed_on_20A_branch_circuits_3.png,15A_receptacles_installed_on_20A_branch_circuits_4.png Receptacles are required to be properly rated when connected to branch circuits. This is required to prevent the receptacles from being over loaded and damaged during use. This installation has 15A receptacles installed on 20A branch circuits in a temporary construction service installed on a residential property. Left uncorrected the receptacles may be thermally damaged if the circuits are overload. This is a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 15A_receptacles_installed_on_20A_branch_circuits_3.png | file://x:/photopub/docs/0000000577/8688aa0b-9dd1-4856-ade3-34c7b6c11ebf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f186264_530a_44b5_b002_c93bd46f981e
ELIN-780006-2017 | EL-507332-2017 | 3/28/2017 11:57:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #15A_receptacles_installed_on_20A_branch_circuits_1.png,15A_receptacles_installed_on_20A_branch_circuits_2.png,15A_receptacles_installed_on_20A_branch_circuits_3.png,15A_receptacles_installed_on_20A_branch_circuits_4.png Receptacles are required to be properly rated when connected to branch circuits. This is required to prevent the receptacles from being over loaded and damaged during use. This installation has 15A receptacles installed on 20A branch circuits in a temporary construction service installed on a residential property. Left uncorrected the receptacles may be thermally damaged if the circuits are overload. This is a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 15A_receptacles_installed_on_20A_branch_circuits_1.png | file://x:/photopub/docs/0000000577/21c37aab-c10c-45e9-bac0-737ef0b53254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f186264_530a_44b5_b002_c93bd46f981e
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A4.png | file://x:/photopub/docs/0000000573/f48e4ee6-837a-4520-89ac-8ee5ea569221.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELIN-777196-2017 | EL-512879-2017 | 3/20/2017 2:44:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png Indoor panel installed in a wet location. This is a shock hazard. 3" PVC conduit installed with in 35mm of the stud face. This is a shock and fire hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B2.png | file://x:/photopub/docs/0000000573/30be875c-2eb9-47a5-9ed5-2b23a2ae0e05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3aec9487_ac79_4e32_979b_8dc9deae2cc3
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A5.png | file://x:/photopub/docs/0000000573/3e0f205c-7d5c-4ac2-b3e0-73e6c671758b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELIN-777196-2017 | EL-512879-2017 | 3/20/2017 2:44:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png Indoor panel installed in a wet location. This is a shock hazard. 3" PVC conduit installed with in 35mm of the stud face. This is a shock and fire hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B1.png | file://x:/photopub/docs/0000000573/af5b39f8-ef49-4dad-8a78-e5ece90d7c1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3aec9487_ac79_4e32_979b_8dc9deae2cc3
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A2.png | file://x:/photopub/docs/0000000573/e95f7001-e02a-4b50-821a-2062e50ca21e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A6.png | file://x:/photopub/docs/0000000573/2ffb1fd1-8e97-4200-8ac3-9a0cf6d04d6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A1.png | file://x:/photopub/docs/0000000573/ee572179-61f9-422e-9395-dd387fbb46e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A3.png | file://x:/photopub/docs/0000000573/883846d3-53d1-479d-9172-13f454c4c5ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A8.png | file://x:/photopub/docs/0000000573/0ebc2ccb-1ca5-4c77-89f7-0890710f2497.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A7.png | file://x:/photopub/docs/0000000573/10b41130-e794-4848-af12-5289840d040b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
ELHE-778255-2017 | HE-513389-2017 | 3/20/2017 10:38:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL162 | Installation of electrical equipment Visible charring of combustibles. | 5 | 5 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Aluminum wire used to feed a gas furnace and connected with a copper only wire nut. This is a fire hazard. | 5 | Installation of electrical equipment Visible charring of combustibles. | A9.png | file://x:/photopub/docs/0000000573/8687587a-39aa-492b-b302-55dd355c4e86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ef51312_2b37_44bc_b66a_3b8a0d2331c9
AMOP-797621-2017 | 2053169 | 4/18/2017 3:20:09 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Missing_pin_retaining_clips.png Retaining clips were found to be missing on 2 sweep locations, connection pins could come out. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Missing_pin_retaining_clips.png | file://x:/photopub/docs/0000000588/8937e136-1263-49a2-b62b-a13c096d0223.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad22bba8_33f1_4f4b_b8d6_5f53149b5c29
ELIN-773396-2017 | EL-507485-2017 | 3/13/2017 2:41:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 2 | #A.png Gas line not bonded. | 3 | Equipment Gas line, cast or water pipe has not been bonded | A.png | file://x:/photopub/docs/0000000570/2cac486d-313c-4c44-b34f-a2fe725eed5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd19b08_30ee_47b3_b8ef_59b4cf94f148
ELOP-651848-2016 | 5316 | 2/28/2017 9:14:12 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Switch_cover.png In ski lift maintenance room, a 15amp 120volt light switch cover was found with all corners broken. This installation can lead to a shock hazard. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Switch_cover.png | file://x:/photopub/docs/0000000563/4a570033-7c01-44c5-92b8-e9dedbbb7828.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D9DCD4DA_5D47_4F86_908F_5931B7F67197
EDMA-786017-2017 | ED-336124-2016 | 3/30/2017 3:11:47 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | #Heat_detector.png The elevator homing function of the elevator works in conjunction with the building's fire panel. If there is a elevator related triggering device (such as a smoke detector), the elevator should automatically return to the appropriate designated floor. During a Major Alteration Acceptance inspection it was found the triggering of the pit heat detector failed to home the elevator. This would cause the elevator to not properly respond to a fire condition. It was found that the elevator contractor failed to pre-test the elevator. This 19 stop traction elevator is located in an existing residential building. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Heat_detector.png | file://x:/photopub/docs/0000000579/c7fa472a-bdca-4390-a42c-19a081380b2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e4974eb_1578_49f0_9c33_93886681fa01
ELIN-780006-2017 | EL-507332-2017 | 3/28/2017 11:57:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #15A_receptacles_installed_on_20A_branch_circuits_1.png,15A_receptacles_installed_on_20A_branch_circuits_2.png,15A_receptacles_installed_on_20A_branch_circuits_3.png,15A_receptacles_installed_on_20A_branch_circuits_4.png Receptacles are required to be properly rated when connected to branch circuits. This is required to prevent the receptacles from being over loaded and damaged during use. This installation has 15A receptacles installed on 20A branch circuits in a temporary construction service installed on a residential property. Left uncorrected the receptacles may be thermally damaged if the circuits are overload. This is a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 15A_receptacles_installed_on_20A_branch_circuits_4.png | file://x:/photopub/docs/0000000577/01e82cda-2fce-4c87-a181-23df86857035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f186264_530a_44b5_b002_c93bd46f981e
ELIN-787790-2017 | EL-398625-2016 | 4/3/2017 12:01:02 PM | ASSESS: EL: Final | png | #asFound Identified conductor fused in the streetlight pole. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Identified_conductor.png Respond to complaints from the city of Abbotsford on wiring for a street light service. Numerous code violations were present on a street light service that has not yet been connected for a new church. The wiring to the streetlight had its grounded conductor fused. This could result in a shock hazard. The grounding for the streetlight was improperly connected and may not clear a fault. Shock hazards if this service was to be connected. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Identified_conductor.png | file://x:/photopub/docs/0000000580/d5110db9-6c10-4c1e-8a05-4874661c7b48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7c619d8_2ddc_460a_a57f_177e7ac5f787
ELOP-628125-2016 | EL-411248-2016 | 3/30/2017 8:53:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Tran.png Conductors are exposed on the secondary of a transformer. The disconnect is off but the fuses are still in the disconnect. If this switch is turned on the conductors will be energized. There are no locks on the decommissioned disconnect. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Tran.png | file://x:/photopub/docs/0000000579/9e8e1415-03de-4fb6-bcfd-fa34b4cfbaea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B494732F_EC61_40E4_B8A5_2E3CBED22296
ELIN-763764-2017 | EL-504981-2017 | 2/27/2017 11:38:51 AM | ASSESS: EL: Service Connection | png | #asFound Screw in service attachment device is not acceptable. | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #P4.png Screw in attachment device may be pulled out if wood rots in future due to accidental moisture ingress. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | P4.png | file://x:/photopub/docs/0000000562/8a0eb8da-0c4f-4ed5-8e31-a7d6093a8f1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43a2363d_f441_47e7_b7d0_ae1885debc7f
BPVOP-764288-2017 | 4094386 | 2/27/2017 1:43:22 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2010 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_2.png | file://x:/photopub/docs/0000000562/cae235be-c760-4a05-a0fd-591b0ca0478c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__629858d0_2ba6_4334_903b_5cc551d0a1ff
BPVOP-764286-2017 | 4094372 | 2/27/2017 1:24:35 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_1.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2010 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_1.png | file://x:/photopub/docs/0000000562/f2a97a89-824c-467f-b79a-e16ef99045eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31982daa_d0fe_450e_8605_9c91cd7b3c96
GAIN-782063-2017 | GA-505911-2017 | 3/30/2017 | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Heater.png The as found hazard was a patio heater which did not have the appropriate clearances to the surrounding combustible material. This is a hazard because it creates a potential risk of fire. | 3 | Clearance to combustible not met | Heater.png | file://x:/photopub/docs/0000000579/603e02a7-bbce-4cf1-9186-eb2d0f26f053.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__841b2cea_c79f_4d01_bada_c0f7ba32d300
ELIN-773188-2017 | EL-508109-2017 | 3/13/2017 3:14:19 PM | ASSESS: EL: Final | png | #asFound Device located greater than 6 mm behind the surface of the wall | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Device_located__Device_located_greater_than_6_mm_behind_the_finished_surface.png Device box located greater than 6 mm behind the device. There's a likelihood of an arc that could cause combustible material to ignite and catch on fire. | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Device_located__Device_located_greater_than_6_mm_behind_the_finished_surface.png | file://x:/photopub/docs/0000000570/6e867bfc-2cd8-47f3-9ea8-9fe1a7292559.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4768744b_f7b4_4358_bc2a_aaab4ffc6c0b
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A3.png | file://x:/photopub/docs/0000000580/652a4d17-050f-43e4-a9f4-fac680b204a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A9.png | file://x:/photopub/docs/0000000580/f74d0f0b-298b-46c7-a086-22639ad30aff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A7.png | file://x:/photopub/docs/0000000580/73e86507-bcae-48db-ba72-490435908230.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A4.png | file://x:/photopub/docs/0000000580/c31def8d-0f93-4262-836a-baf2f98362dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A5.png | file://x:/photopub/docs/0000000580/e6de60a7-ade6-4899-b6a2-188d8e5bed3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A6.png | file://x:/photopub/docs/0000000580/50a28c2f-b10d-48b8-8729-6f4d4cd0fb24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A2.png | file://x:/photopub/docs/0000000580/b731db23-07a8-403b-9383-fc60119c4395.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A8.png | file://x:/photopub/docs/0000000580/1b5e84d2-3d8d-4451-a62b-44aefb1feeb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact1.png | file://x:/photopub/docs/0000000563/2bee127a-50d4-4427-8aef-5c897aab527d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact6.png | file://x:/photopub/docs/0000000563/b05437e7-2440-46a1-b7ec-70f969391035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact4.png | file://x:/photopub/docs/0000000563/de2ca61c-2a22-42c4-886c-a9b12e93eaef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact3.png | file://x:/photopub/docs/0000000563/cf258495-7e93-42a4-b99f-17d747e8ace5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact5.png | file://x:/photopub/docs/0000000563/517b67eb-4ef2-4089-a759-20f7e1ffd7b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
ELIN-787827-2017 | EL-515856-2017 | 4/4/2017 7:51:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Damaged_cable_jacket_with_tape_removed.png Damaged cable jackets may allow water to enter and rust aluminum armour creating additional damage | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Damaged_cable_jacket_with_tape_removed.png | file://x:/photopub/docs/0000000581/2ca8b79d-7a0f-4342-93d8-0b2f8bb98c1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c91be6da_1066_41b9_b0bb_6d65fb202e7f
ELIN-786720-2017 | EL-502525-2017 | 4/4/2017 12:03:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Service_cables_unsupported.png Service cables must be supported to prevent strain on terminations which could result in failure of the equipment | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Service_cables_unsupported.png | file://x:/photopub/docs/0000000581/3816fb7e-e22b-41a7-b698-846cf1b43976.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3243432b_5e4f_4774_8dd2_75c1f2d22d2c
AMOP-772187-2017 | 3730692 | 3/13/2017 4:03:04 PM | ASSESS: AM OP: Periodic | png | #asFound | AM022 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | 2 | 2 | #Missing_steering_wheel_pad.png Steering wheel protection was missing, potential for someone to hit their head on metal components | 2 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | Missing_steering_wheel_pad.png | file://x:/photopub/docs/0000000571/0830c117-2a2b-404c-bde4-8e69ea296258.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01963446_1246_42b1_8eda_5b530e753946
AMOP-772785-2017 | 2041913 | 3/13/2017 2:37:40 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Trip_hazard.png Ride decking was bent at the entrance to the loading area of the ride. The hole it created is a trip and/or fall hazard. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Trip_hazard.png | file://x:/photopub/docs/0000000571/0a8d2c08-aee1-402f-860e-5c276ebfe561.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86f47943_4050_4132_9fa7_066b1c23fdc9
AMOP-771939-2017 | 4490590 | 3/13/2017 12:56:07 PM | ASSESS: AM OP: Periodic | png | #asFound | AM032 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Passenger_restraint_indicator_lights.png Some lights used to indicate the state of passenger restraints not working, an unlocked restraint could me missed by the operator. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Passenger_restraint_indicator_lights.png | file://x:/photopub/docs/0000000571/2d557573-7bda-4802-94b4-f309a5126372.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56636522_56d7_4272_a243_24d7855fcf86
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property11.png | file://x:/photopub/docs/0000000588/3b10a0c2-0327-4844-84c0-6078a6222094.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png | file://x:/photopub/docs/0000000588/4e202831-1c29-441a-bd08-c9c97bb37342.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png | file://x:/photopub/docs/0000000588/74665dfc-24fc-4c53-ac2f-d382f7b0495b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELIN-793890-2017 | EL-500906-2017 | 4/18/2017 9:11:21 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #51.png,52.png I observed 3 C / 250 Kcmil ACWU feeder installed in the crawl space without protection as required by code. This is a potential shock hazard as this conductor is only fused back to the utilities main system fuse. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 52.png | file://x:/photopub/docs/0000000587/047fff4c-6a9a-46ac-96e4-cd5d4961f98e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbe3c723_3464_44a1_a95c_f8efb31d3f41
ELIN-793890-2017 | EL-500906-2017 | 4/18/2017 9:11:21 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #51.png,52.png I observed 3 C / 250 Kcmil ACWU feeder installed in the crawl space without protection as required by code. This is a potential shock hazard as this conductor is only fused back to the utilities main system fuse. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 51.png | file://x:/photopub/docs/0000000587/0c749099-3d61-4d54-bc49-088d12dccfda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbe3c723_3464_44a1_a95c_f8efb31d3f41
ELIN-787631-2017 | 5341843 | 4/3/2017 5:21:25 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png Panel cover missing. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | A10.png | file://x:/photopub/docs/0000000580/daf8d7ad-e5ac-4994-ad15-d7097c30a601.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8de635a_3914_41dd_8fec_73713ea369ec
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact2.png | file://x:/photopub/docs/0000000563/86737290-8680-43c6-9924-ff45ef83b576.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
ELHE-764770-2017 | HE-505584-2017 | 2/27/2017 10:32:34 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized__conductors_exposed_to_accidental_contact1.png,Energized__conductors_exposed_to_accidental_contact2.png,Energized__conductors_exposed_to_accidental_contact3.png,Energized__conductors_exposed_to_accidental_contact4.png,Energized__conductors_exposed_to_accidental_contact5.png,Energized__conductors_exposed_to_accidental_contact6.png,Energized__conductors_exposed_to_accidental_contact7.png Energized over head service supply cables are required to be located above grade on poles or structures where they can not be reached, walked on, or accidentally contacted when standing at grade level. This installation had two 120/240V overhead service supply cables that were energized, left hanging from a pole, and laying on the ground at the base of the pole. The cables had previously been disconnected from a house and a shop without being disconnected and made safe. This was an immediate shock, arc flash, and fire hazard that required the utilities attendance for disconnection prior to leaving the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized__conductors_exposed_to_accidental_contact7.png | file://x:/photopub/docs/0000000563/05669b51-2728-4839-8af6-5b4abde4ccfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f52200_89e3_460c_a653_82d6e16c03ae
AMOP-772907-2017 | 2044008 | 3/14/2017 3:27:59 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Passenger_walkway_blocking1.png,Passenger_walkway_blocking2.png,Passenger_walkway_blocking3.png,Passenger_walkway_blocking4.png Walkway platform blocking not set correctly, if the ride were to shift, the walkway could fail. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Passenger_walkway_blocking1.png | file://x:/photopub/docs/0000000571/498563fe-3fc1-4f78-948d-8e71586e6b66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__278fe84f_2791_402a_bc22_79bf329873fc
AMOP-772907-2017 | 2044008 | 3/14/2017 3:27:59 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Passenger_walkway_blocking1.png,Passenger_walkway_blocking2.png,Passenger_walkway_blocking3.png,Passenger_walkway_blocking4.png Walkway platform blocking not set correctly, if the ride were to shift, the walkway could fail. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Passenger_walkway_blocking3.png | file://x:/photopub/docs/0000000571/03daf347-9c99-475e-9bf3-cd302705811e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__278fe84f_2791_402a_bc22_79bf329873fc
AMOP-773763-2017 | 2040369 | 3/14/2017 7:43:56 PM | ASSESS: AM OP: Periodic | png | #asFound | AM043 | Wear or defects that are Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Wire_rope_indication.png Wire rope supporting structure of Ferris wheel shows signs of wear, wire rope could eventually fail. | 2 | Wear or defects that are Reasonably detectable by maintenance program Likely to propagate | Wire_rope_indication.png | file://x:/photopub/docs/0000000571/79bac117-ba10-4759-9b35-0c10b7f55023.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54ba0e86_4a7c_4ba9_9fc3_70cf88ed9e28
ELIN-788534-2017 | EL-486019-2017 | 4/11/2017 3:21:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Suite_panel_supplied_from_main_panel_.png Tenant power which depends on another tenant panel may be unreliable | 0 | No Created Hazard Identified | Suite_panel_supplied_from_main_panel_.png | file://x:/photopub/docs/0000000586/a2a1c058-20eb-4f22-a505-fa35089ca3df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd479fe4_b11e_4b9d_a2d6_29f0454c0925
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png | file://x:/photopub/docs/0000000588/1e9dc372-9bc0-4839-859b-e23f346bd86e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property10.png | file://x:/photopub/docs/0000000588/dbbf6441-6dbd-4370-a73b-10cb43558e32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property9.png | file://x:/photopub/docs/0000000588/82c91158-c61e-4f4d-aa26-28f492fb7a4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELIN-766231-2017 | EL-501188-2017 | 3/2/2017 2:00:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #ground_conductor_incorrectly_installed1.png,ground_conductor_incorrectly_installed2.png Service grounding conductor is installed under neutral lug in meter base. This lug is designed and approved for single cable only. Effective grounding of service is not achieved in this manner. Over current devices may not react as required in the case of an electrical fault if left installed in this manner. A risk of shock or fire to persons or property would exist. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | ground_conductor_incorrectly_installed1.png | file://x:/photopub/docs/0000000565/cbdc44d7-3d67-4912-8a83-1a5a88165079.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76d06191_7899_4546_a2fa_98c590ee9960
GAIN-772918-2017 | GA-349089-2016 | 3/10/2017 3:55:00 PM | ASSESS: GA: Rough-In | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent_clearance2.png The as found condition is single wall vent material was installed within the minimum 6 inch clearance from combustible material. The as found hazard is failure to maintain the minimum clearances from combustible material can lead to fire due to pyrolysis. | 3 | Non compliant Type C Vent clearance | Vent_clearance2.png | file://x:/photopub/docs/0000000569/57d0eba9-9e56-492d-b476-6c148f178ec5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b9bcf14_4082_48b6_a4bb_96761d8ed42d
ELIN-760076-2017 | EL-426735-2016 | 3/16/2017 12:07:25 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Westinghouse_breaker_installed_in_Siemens__panel.png 100 amp, 120/240 volt main distribution panel has branch circuit breaker installed not rated or type approved for main distribution. This is a thermal effect. | 3 | General Equipment is not approved for the specific use | Westinghouse_breaker_installed_in_Siemens__panel.png | file://x:/photopub/docs/0000000572/9456d06a-d43d-4dca-8762-8bd3e4864865.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de81d4e_7bc0_46cb_ba1c_1cce73629763
ELIN-786945-2017 | UW-518033-2017 | 3/31/2017 1:54:11 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Covers_or_protective_barriers_not_in_place.png Electrical wiring exiting the main distribution center is not properly protected. Covers on adjacent tubs and device boxes are not in place. The main distribution over-current devices are not labelled, accidentally turning on a breaker may provide a shock or arc flash hazard to persons and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Covers_or_protective_barriers_not_in_place.png | file://x:/photopub/docs/0000000579/29e474ee-73d3-434e-96a8-ebf8409ebb86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7737762_853f_434c_9478_4094c2c9673c
GAWP-762811-2017 | GA-469123-2016 | 3/6/2017 10:38:37 AM | ASSESS: GA Work In Progress | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open1.png,Open2.png Qty: 2 gas flanges 2" open and not capped, Qty: 1 gas line 3/8 not capped on gas skid with 168 working psi. If valve is open or does not seal tight gas will be released in a high risk area, causing a fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open1.png | file://x:/photopub/docs/0000000567/b890ff22-f408-4dcc-a460-c361f5a28f07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39a77629_3bcb_4ab4_a378_e5d2f863bb58
GAWP-762811-2017 | GA-469123-2016 | 3/6/2017 10:38:37 AM | ASSESS: GA Work In Progress | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open1.png,Open2.png Qty: 2 gas flanges 2" open and not capped, Qty: 1 gas line 3/8 not capped on gas skid with 168 working psi. If valve is open or does not seal tight gas will be released in a high risk area, causing a fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open2.png | file://x:/photopub/docs/0000000567/9f0a1670-4dfb-4414-8216-0b7e4b8d4beb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39a77629_3bcb_4ab4_a378_e5d2f863bb58
AMIN-804352-2017 | AM-511687-2017 | 4/28/2017 9:48:59 AM | ASSESS: AM IN: Acceptance | png | #asFound | AM032 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Hydraulic_tank_in_mechanical_room.png 570 litre oil capacity in the hydraulic tank situated in the mechanical room. The room has no fire monitoring. If a unmonitored fire were to ignite in the room, it could become a big fire. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Hydraulic_tank_in_mechanical_room.png | file://x:/photopub/docs/0000000595/b6d4e09d-53ad-4f7e-873d-75fab39a15dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54d0480e_b625_49b4_a648_c9a2c3922ab8
ELIN-798413-2017 | EL-465766-2016 | 5/1/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 | #5.png Surge Protection Device was mounted beside the panel with individual insulated conductors being terminated within the panel | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 5.png | file://x:/photopub/docs/0000000595/90a34599-75e9-435b-9817-b87f9f440973.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__584e565e_eea2_4ae8_9bc1_7a9c5752977e
GAIN-766512-2017 | GA-505730-2017 | 3/2/2017 12:22:09 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #StreetElbow.png Use of street elbow in a piping system is prohibited as they are more prone to failures as a result of stress on the line. A fracture could result in a uncontrolled gas leak | 3 | Code prohibited practices or materials | StreetElbow.png | file://x:/photopub/docs/0000000565/39390b62-5a5d-4343-8f13-d4bb7a132c95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__900b666f_d63b_455c_8ac7_fb31078718c7
AMOP-772783-2017 | AM-509969-2017 | 3/14/2017 2:09:24 PM | ASSESS: AM OP: Periodic | png | #asFound | AM037 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #No_step_sign_.png "No Step" signage has faded, a passenger could walk on the platform, collapse the section, and fall to the ground. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | No_step_sign_.png | file://x:/photopub/docs/0000000571/34112b95-8337-4027-bfab-312a05a19ed7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa38db4f_2ae2_4e89_a3db_414d6d99321c
AMOP-772907-2017 | 2044008 | 3/14/2017 3:27:59 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Passenger_walkway_blocking1.png,Passenger_walkway_blocking2.png,Passenger_walkway_blocking3.png,Passenger_walkway_blocking4.png Walkway platform blocking not set correctly, if the ride were to shift, the walkway could fail. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Passenger_walkway_blocking4.png | file://x:/photopub/docs/0000000571/ffc21982-e394-449c-af33-8398f84042f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__278fe84f_2791_402a_bc22_79bf329873fc
AMOP-772907-2017 | 2044008 | 3/14/2017 3:27:59 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Passenger_walkway_blocking1.png,Passenger_walkway_blocking2.png,Passenger_walkway_blocking3.png,Passenger_walkway_blocking4.png Walkway platform blocking not set correctly, if the ride were to shift, the walkway could fail. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Passenger_walkway_blocking2.png | file://x:/photopub/docs/0000000571/2cf0008d-a2c6-43b6-9561-92a8f386a6e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__278fe84f_2791_402a_bc22_79bf329873fc
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property12.png | file://x:/photopub/docs/0000000588/641416e0-25f0-4116-a7fd-34c1d6e95a1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png | file://x:/photopub/docs/0000000588/6fb9dd17-071d-488b-a343-6fdea7999317.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound This photo is in kitchen where people live and the conductor is energized and subject to possible shock or fire hazards. Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png | file://x:/photopub/docs/0000000588/223e9825-99d9-4a21-95aa-586dfb549ca2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELIN-766231-2017 | EL-501188-2017 | 3/2/2017 2:00:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #ground_conductor_incorrectly_installed1.png,ground_conductor_incorrectly_installed2.png Service grounding conductor is installed under neutral lug in meter base. This lug is designed and approved for single cable only. Effective grounding of service is not achieved in this manner. Over current devices may not react as required in the case of an electrical fault if left installed in this manner. A risk of shock or fire to persons or property would exist. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | ground_conductor_incorrectly_installed2.png | file://x:/photopub/docs/0000000565/a8bbf7b9-f7dd-4b49-a7d7-15aa2fe97425.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76d06191_7899_4546_a2fa_98c590ee9960
ELIN-767425-2017 | EL-506852-2017 | 3/3/2017 11:06:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | #1.png Main distribution not grounded. This is a shock hazard. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 1.png | file://x:/photopub/docs/0000000565/e8d8c302-b3a5-417b-9a10-e10d3ed912c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdf3f67_f833_4083_bdfd_76de1a2dce04
GAIN-771009-2017 | GA-479077-2016 | 3/22/2017 2:12:23 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Clearance_not_maintained.png Clearance between relief device termination and a mechanical air intake not maintained. Fire or explosion could occur if relieving gas was drawn into the combustion intake of an appliance. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Clearance_not_maintained.png | file://x:/photopub/docs/0000000575/03d67efc-d8c1-4d58-8687-2551dfa42a49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__419dce48_eafb_474c_baf7_ec0766386523
BPVOP-757661-2017 | UW-501416-2017 | 3/7/2017 1:49:47 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #T_and_P_1.png,T_and_P_2.png Upon the assessment of an Indirect DHW Heater with MAWP of 100 psig, was found that the Temperature and Pressure Relief valve had the set point at 150 psig. In case of an overpressure this relief will not protect the tank. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | T_and_P_1.png | file://x:/photopub/docs/0000000567/be92a71f-3400-419a-8647-7fc471127f40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41074ae3_1bd8_4031_b742_8b98edb4d473
BPVOP-757661-2017 | UW-501416-2017 | 3/7/2017 1:49:47 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #T_and_P_1.png,T_and_P_2.png Upon the assessment of an Indirect DHW Heater with MAWP of 100 psig, was found that the Temperature and Pressure Relief valve had the set point at 150 psig. In case of an overpressure this relief will not protect the tank. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | T_and_P_2.png | file://x:/photopub/docs/0000000567/46b67dfd-99e6-4307-b626-fa96124f4209.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41074ae3_1bd8_4031_b742_8b98edb4d473
ELIN-766894-2017 | EL-496695-2017 | 3/2/2017 3:53:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 3 | #B1.png,B2.png Uffer ground undersized. This is a fire hazard. | 4 | Installation Grounding; conductor is not properly sized. | B2.png | file://x:/photopub/docs/0000000565/b1a43720-3fad-4807-95f7-79a6b996f915.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea7a7cd3_48b6_47b9_97a5_bf90cfe0e581
ELIN-766894-2017 | EL-496695-2017 | 3/2/2017 3:53:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 3 | #B1.png,B2.png Uffer ground undersized. This is a fire hazard. | 4 | Installation Grounding; conductor is not properly sized. | B1.png | file://x:/photopub/docs/0000000565/84280fa1-5ecf-4c6d-bc98-b3fa7a2553fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea7a7cd3_48b6_47b9_97a5_bf90cfe0e581
ELIN-766307-2017 | EL-492097-2017 | 3/2/2017 3:29:21 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #A.png AFCI protection not provided. This is a fire hazard. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | A.png | file://x:/photopub/docs/0000000565/b256e96b-cf6d-489e-b3e4-c2a34a980e5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd2e117c_962e_444d_a225_ef4df8c9193e
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound This photo is in kitchen above sink where people children live and the conductor is energized and subject to possible shock or fire hazards. Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png | file://x:/photopub/docs/0000000588/72e28134-4216-4591-a0e2-ca58c0a8e3f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound This photo is in kitchen where people live and the conductor is energized and subject to possible shock or fire hazards. Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png | file://x:/photopub/docs/0000000588/82508eb2-8985-4a6b-9bd7-7a36351db036.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
ELHE-798030-2017 | HE-523971-2017 | 4/19/2017 2:45:17 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed energized conductors and bus bars subject to possible electrical fire or shock hazards to people and property | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property1.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property3.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property4.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property5.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property6.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property7.png,Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property8.png,Exposed_energized_conductor_na_dubs_bars_subject_to_pos | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_conductor_na_dubs_bars_subject_to_possible_electrical_fire_or_shock_hazard_to_people_and_property2.png | file://x:/photopub/docs/0000000588/38d9d86e-0fab-4c7c-961a-73b287c840b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23e2750c_abd5_4098_b6f4_03a73195aa50
GAIN-801443-2017 | GA-516993-2017 | 4/24/2017 1:50:44 PM | ASSESS: GA: Final | png | #asFound | GA053 | Non-certified appliance connector | 3 | 2 | #Csst.png | 3 | Non-certified appliance connector | Csst.png | file://x:/photopub/docs/0000000590/29fabfac-d5c6-4aed-8553-607cb9a958b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3fcc0b5_a223_449b_ac20_0079c50ed4e7
GAIN-797731-2017 | GA-523037-2017 | 4/26/2017 9:59:36 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Improper_coupling.png The as-found-condition is that an improper fitting has been installed on a black iron gas piping system. The potential hazard is that the fitting will be susceptible to damaged due to its lack of strength and integrity resulting in a gas leak in an occupied space. | 3 | Non-compliant material/fittings installed | Improper_coupling.png | file://x:/photopub/docs/0000000591/b3e456c2-2576-4794-b0cd-5f2fc5a076c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b690a15b_4949_4295_ad92_f1c93098b062
GAIN-768182-2017 | GA-507314-2017 | 4/20/2017 11:06:10 AM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Mcbride_food_stoore.png Underground copper gas line enters inside the building. Should rise before entering the building. A underground gas leak could fill the building with gas. | 3 | Underground piping entering a building below grade (unapproved) | Mcbride_food_stoore.png | file://x:/photopub/docs/0000000588/b1a91799-b883-4ac1-95a8-4dc99be65f31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__968db0f7_c02c_42c4_b3b3_aa162d474634
ELOP-800183-2017 | EL-512325-2017 | 4/21/2017 8:31:32 AM | ASSESS: EL OP: Acceptance | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Needs_a_weatherproof_enclosure.png This assessment found enclosure for dry use being used in a wet outdoor location that can creat a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Needs_a_weatherproof_enclosure.png | file://x:/photopub/docs/0000000589/8358b90a-91b0-4366-888c-02f1ff3a08f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec9ef35a_16d9_482d_a6ff_7cecafdfdea9
ELHE-767887-2017 | HE-507086-2017 | 1/6/2017 11:47:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_electrical_contacts_exposed_to_persons1.png,Energized_electrical_contacts_exposed_to_persons2.png Energized electrical terminals were left uncovered. If a person were to make contact with these terminals they would at least be shocked or could possibly have an electrical burn. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_electrical_contacts_exposed_to_persons1.png | file://x:/photopub/docs/0000000566/3cf8c8e4-0c2c-447f-b526-115ce5cee4d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78a5d4e1_9579_47d7_90f8_baf4a6c21dfc
ELHE-767887-2017 | HE-507086-2017 | 1/6/2017 11:47:56 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_electrical_contacts_exposed_to_persons1.png,Energized_electrical_contacts_exposed_to_persons2.png Energized electrical terminals were left uncovered. If a person were to make contact with these terminals they would at least be shocked or could possibly have an electrical burn. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_electrical_contacts_exposed_to_persons2.png | file://x:/photopub/docs/0000000566/f0710251-0410-4e84-8753-f01444f6175d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78a5d4e1_9579_47d7_90f8_baf4a6c21dfc
AMOP-790302-2017 | AM-101056-2014 | 4/6/2017 3:36:55 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Blocking_set_up1.png,Blocking_set_up2.png,Blocking_set_up3.png Blocking was inadequate for the size of jack stand feet, if the devices weight were to shift, it may have a chance to fall off the blocking. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking_set_up2.png | file://x:/photopub/docs/0000000583/c5c2e801-3714-4742-ba9e-4d851060457f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94d0b20c_1cdf_46df_a512_e0e6c2212e5e
AMOP-790302-2017 | AM-101056-2014 | 4/6/2017 3:36:55 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Blocking_set_up1.png,Blocking_set_up2.png,Blocking_set_up3.png Blocking was inadequate for the size of jack stand feet, if the devices weight were to shift, it may have a chance to fall off the blocking. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking_set_up3.png | file://x:/photopub/docs/0000000583/5a28f774-1ed4-445b-89e5-5e4924dff34c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94d0b20c_1cdf_46df_a512_e0e6c2212e5e
AMOP-790304-2017 | 2168294 | 4/6/2017 3:58:18 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Sweep_covers1.png,Sweep_covers2.png Sweep covers were not bolted down, covers could fall of and potentially hit someone. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Sweep_covers1.png | file://x:/photopub/docs/0000000583/9919ecd7-9dd8-434e-ba17-fc01e248c9c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd4c7582_30d1_4528_9958_0aba4313a3f0
AMOP-790304-2017 | 2168294 | 4/6/2017 3:58:18 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Sweep_covers1.png,Sweep_covers2.png Sweep covers were not bolted down, covers could fall of and potentially hit someone. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Sweep_covers2.png | file://x:/photopub/docs/0000000583/c20ff0c2-4727-41ae-aef6-7241250ab481.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd4c7582_30d1_4528_9958_0aba4313a3f0
EDRI-781182-2017 | ED-426308-2016 | 3/22/2017 10:54:50 AM | ASSESS: ED RI: Extension | png | #asFound Two layers of plywood were used as the landing floor. At the edge of the plywood no tapered edge was installed creating an abrupt 1" change in elevation, creating a trip hazard. | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | #Tripping_hazard.png Two layers of plywood were used as the landing floor. At the edge of the plywood no tapered edge was installed creating an abrupt 1" change in elevation, creating a trip hazard. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Tripping_hazard.png | file://x:/photopub/docs/0000000576/444741f9-cd81-4676-9237-8d2aa7c47952.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8377a730_7b88_4863_a01d_9d2498516d9f
ELIN-767075-2017 | EL-506661-2017 | 3/3/2017 1:00:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #weather_exposure.png This assessment found moisture can enter panel create a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | weather_exposure.png | file://x:/photopub/docs/0000000566/2a6fa6c4-5552-4476-b1f9-003b5c73766f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1b4c34d_9632_4571_82c4_e81aa498e2a5
GAIN-768122-2017 | GA-495464-2017 | 3/6/2017 12:38:41 PM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Generator.png Contractor ran new gas line from Fortis meter set directly to new generator installed on property. Regulator on Fortis meter set is set at 2psi, while the max inlet pressure of the generator is 1/2 psi. Incorrect gas pressures could potentially damage appliance and create a fire hazard. More pictures added in attachments. | 4 | Appliance regulator not installed, incorrect delivery pressure | Generator.png | file://x:/photopub/docs/0000000566/3aaa1e62-e3e7-4ef9-b6a0-93fd37b2c152.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f493fd8_65d0_4214_ac4e_211af3cb4f97
ELIN-776141-2017 | EL-512157-2017 | 3/17/2017 11:09:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound One end of the unfused service conductors. | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_cond.png,Panel.png Complete re-wire of existing single family dwelling. The Service conductors extend into the building approximately 3.3 m without concrete encasement. These are unfused service conductors and any mechanical damage to them from the re-building of this dwelling could result in shock or fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cond.png | file://x:/photopub/docs/0000000572/b8650946-48bf-4995-8968-171d1bcc5e18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56289df0_4b18_4566_b122_c91b2c285c5d
ELIN-776141-2017 | EL-512157-2017 | 3/17/2017 11:09:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Service conductors entering panel | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_cond.png,Panel.png Complete re-wire of existing single family dwelling. The Service conductors extend into the building approximately 3.3 m without concrete encasement. These are unfused service conductors and any mechanical damage to them from the re-building of this dwelling could result in shock or fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Panel.png | file://x:/photopub/docs/0000000572/5ace1bac-c744-4c03-b96b-801d77054adf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56289df0_4b18_4566_b122_c91b2c285c5d
AMOP-790302-2017 | AM-101056-2014 | 4/6/2017 3:36:55 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Blocking_set_up1.png,Blocking_set_up2.png,Blocking_set_up3.png Blocking was inadequate for the size of jack stand feet, if the devices weight were to shift, it may have a chance to fall off the blocking. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking_set_up1.png | file://x:/photopub/docs/0000000583/b072fd2e-1b36-4b79-9fa9-55d9d28e61cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94d0b20c_1cdf_46df_a512_e0e6c2212e5e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box4.png | file://x:/photopub/docs/0000000593/3dc7a282-9d9e-449d-aed0-66104cd1beb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box1.png | file://x:/photopub/docs/0000000593/5ec693dc-b7c7-4705-a6b8-5fd3295fde7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box2.png | file://x:/photopub/docs/0000000593/aba921bf-3a2a-45a1-b29b-536d3c1cb034.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box8.png | file://x:/photopub/docs/0000000593/12ee8d8b-a065-4497-8900-374253dc1982.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box3.png | file://x:/photopub/docs/0000000593/e7d44715-e69f-4f49-83a9-e753b72c9c91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box6.png | file://x:/photopub/docs/0000000593/c655df11-33b2-4513-9270-285fd7cab22c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-792450-2017 | EL-518677-2017 | 4/11/2017 2:10:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Solar system conductors located inside a building. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #4.png 3 C/ #12 AWG Non-metallic sheathed cable is feeding a solar system. When these cables are located inside a building they are required to be protected by metal armour. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 4.png | file://x:/photopub/docs/0000000585/d2d92de5-5c3d-42ff-b490-56e4da052fec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8d95348_4954_49af_8d80_b8d79ff897f2
ELIN-766465-2017 | EL-397092-2016 | 3/2/2017 10:59:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | #Typical_15_amp_2c_cabling.png The 15 amp 120 volt wiring for the kitchen counter receptacles are neither split circuits or 20 amp rated, this can create a thermal issue with the use of appliances and lack of power available as required for the counter space | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | Typical_15_amp_2c_cabling.png | file://x:/photopub/docs/0000000565/f4087fce-93ca-4e40-a8fc-8de9ad97cd1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cde625b5_3416_429c_bc86_59c4157a6c70
ELIN-756394-2017 | EL-222060-2015 | 3/2/2017 4:55:54 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Missing_filler_plates1.png,Missing_filler_plates2.png The 2x 125 amp 120/240 volt consumer service panels have missing breaker filler plates, this can expose personnel to accidental contact and is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Missing_filler_plates2.png | file://x:/photopub/docs/0000000565/c296b60a-1089-42f2-9104-b92f44a26900.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31d69367_94d3_400c_8ecb_e935c2fb2a33
ELIN-756394-2017 | EL-222060-2015 | 3/2/2017 4:55:54 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Missing_filler_plates1.png,Missing_filler_plates2.png The 2x 125 amp 120/240 volt consumer service panels have missing breaker filler plates, this can expose personnel to accidental contact and is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Missing_filler_plates1.png | file://x:/photopub/docs/0000000565/ef6d2efb-f9f1-4728-9ec5-f4b4855a9c8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31d69367_94d3_400c_8ecb_e935c2fb2a33
ELIN-771324-2017 | EL-321324-2015 | 3/8/2017 3:49:38 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_conductors.png Expose energized conductors in areas where unqualified persons are working. Should anyone make contact with the exposed conductors they would be shocked. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_conductors.png | file://x:/photopub/docs/0000000568/64b28923-dd61-4f19-b0fb-bc263e897b10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99690ef8_dc4f_451e_b5a8_1285d97db4a0
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power1.png | file://x:/photopub/docs/0000000573/6a8573e1-c4f5-4036-abbd-1f1ed4340d16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box9.png | file://x:/photopub/docs/0000000593/adf1c026-5d5e-4cf5-a017-dcfc04db31ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box5.png | file://x:/photopub/docs/0000000593/20ef78a5-f686-4e07-aa09-692f81a39461.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box10.png | file://x:/photopub/docs/0000000593/6a37f695-ae33-4d85-acba-0a16ec6edbd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
ELIN-798680-2017 | EL-433646-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_receptacle_without_an_outlet_box1.png,Microwave_receptacle_without_an_outlet_box2.png,Microwave_receptacle_without_an_outlet_box3.png,Microwave_receptacle_without_an_outlet_box4.png,Microwave_receptacle_without_an_outlet_box5.png,Microwave_receptacle_without_an_outlet_box6.png,Microwave_receptacle_without_an_outlet_box7.png,Microwave_receptacle_without_an_outlet_box8.png,Microwave_receptacle_without_an_outlet_box9.png,Microwave_receptacle_without_an_outlet_box10.png Branch circuit wiring for receptacles and lights is required to be installed in outlet boxes where they connect to equipment that is intended to be mounted to outlet boxes. This is required so that the wiring connections and energized terminals are contained within boxes and are not subject to accidental contact or mechanical damage and any thermal energy created by the wiring, connections, or device/fixture is contained within the box. This installation for a new house has a microwave receptacle that is installed without an outlet box. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_receptacle_without_an_outlet_box7.png | file://x:/photopub/docs/0000000593/0adad665-bb8b-48b0-9147-11e38943a483.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0782a77_2c83_4a9d_8d3c_86df62f3c28e
GAHE-808366-2017 | HE-529594-2017 | 5/3/2017 9:24:18 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Mount_baker4.png Propane cylinders installed with less than the minimum required distance ( 10 feet)to a source of ignition. Risk of a release of fuel occurring during tank change out or relief valve spillage. Fuel could be inadvertently Ignited due to arc producing device installed in close proximity. Fire risk. | 4 | Ignition sources present with-in minimum distance required | Mount_baker4.png | file://x:/photopub/docs/0000000595/8abc95fa-f761-4ceb-9e9f-c1512de724cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f80920d2_78bd_47b1_a3d6_778527d5ab1a
GAIN-782195-2017 | GA-471397-2016 | 3/29/2017 9:25:55 AM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 | #Non_compliant_outlet_placement.png Electrical outlet not compliant with canadian electrical code. Outlet mounted to supply air plenum will exceed temperature rating for the outlet. | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Non_compliant_outlet_placement.png | file://x:/photopub/docs/0000000578/8092653f-2fe9-4450-805c-35bd08a9b6c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f289274d_1c97_4871_bc5d_dd3698cf1e6f
GAIN-768057-2017 | GA-388645-2016 | 3/6/2017 10:01:40 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_termination.png Unit heater vent installed at a commercial location is too close to supply air intake (mechanical air-supply). This will result in some of the products of combustion re-circulating back into the building, being drawn in via the supply air fan. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination.png | file://x:/photopub/docs/0000000567/01601602-bf3c-401a-b89c-b6046e6a05d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e04e383_8f2c_4142_b7a4_d9413be33757
GAIN-768101-2017 | GA-430938-2016 | 3/6/2017 2:26:25 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_terminations.png On demand water heater air intakes are terminated directly above relief style gas pressure regulator. In the even that the regulator begins to vent gas because of an over pressure situation, gas could be drawn into the water heater combustion chamber causing a potential over fire or explosion scenario. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_terminations.png | file://x:/photopub/docs/0000000567/5d1aa7d6-5fe4-4988-96ff-6ff7e11af847.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa7b0539_e330_4871_a98d_6ccdfe8568c4
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power3.png | file://x:/photopub/docs/0000000573/d2e8c320-6a3d-457f-8716-5bda9446ad7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power5.png | file://x:/photopub/docs/0000000573/67b01305-6ee8-4336-bc13-32ecf12220ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-775112-2017 | EL-506685-2017 | 3/16/2017 11:02:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_energized_panel_and_temporary_wiring1.png,Open_energized_panel_and_temporary_wiring2.png,Open_energized_panel_and_temporary_wiring3.png,Open_energized_panel_and_temporary_wiring4.png,Open_energized_panel_and_temporary_wiring5.png,Open_energized_panel_and_temporary_wiring6.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed from a temporary power panel on the exterio | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_energized_panel_and_temporary_wiring5.png | file://x:/photopub/docs/0000000573/4aa48342-b937-437e-a40d-1cd47a947294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bff735f_76d4_4f01_9f2b_6cbaba4c812d
ELIN-775112-2017 | EL-506685-2017 | 3/16/2017 11:02:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_energized_panel_and_temporary_wiring1.png,Open_energized_panel_and_temporary_wiring2.png,Open_energized_panel_and_temporary_wiring3.png,Open_energized_panel_and_temporary_wiring4.png,Open_energized_panel_and_temporary_wiring5.png,Open_energized_panel_and_temporary_wiring6.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed from a temporary power panel on the exterio | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_energized_panel_and_temporary_wiring6.png | file://x:/photopub/docs/0000000573/c20ad31b-3f80-4b13-8670-d8d261723957.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bff735f_76d4_4f01_9f2b_6cbaba4c812d
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power2.png | file://x:/photopub/docs/0000000573/0928b6b9-d6f6-41e6-b8a6-86068d5970d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power6.png | file://x:/photopub/docs/0000000573/b0b66b80-9fe6-4a4f-8a52-4d26d9b02860.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-775112-2017 | EL-506685-2017 | 3/16/2017 11:02:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_energized_panel_and_temporary_wiring1.png,Open_energized_panel_and_temporary_wiring2.png,Open_energized_panel_and_temporary_wiring3.png,Open_energized_panel_and_temporary_wiring4.png,Open_energized_panel_and_temporary_wiring5.png,Open_energized_panel_and_temporary_wiring6.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed from a temporary power panel on the exterio | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_energized_panel_and_temporary_wiring3.png | file://x:/photopub/docs/0000000573/6f3ad287-ba8d-4c9f-9de4-05bb4bea3585.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bff735f_76d4_4f01_9f2b_6cbaba4c812d
ELIN-775112-2017 | EL-506685-2017 | 3/16/2017 11:02:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_energized_panel_and_temporary_wiring1.png,Open_energized_panel_and_temporary_wiring2.png,Open_energized_panel_and_temporary_wiring3.png,Open_energized_panel_and_temporary_wiring4.png,Open_energized_panel_and_temporary_wiring5.png,Open_energized_panel_and_temporary_wiring6.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed from a temporary power panel on the exterio | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_energized_panel_and_temporary_wiring1.png | file://x:/photopub/docs/0000000573/a8b8cd3d-7f89-49ef-bd54-851d200d702c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bff735f_76d4_4f01_9f2b_6cbaba4c812d
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power7.png | file://x:/photopub/docs/0000000573/55135879-6505-4993-ab58-6c2ade356c28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-775112-2017 | EL-506685-2017 | 3/16/2017 11:02:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_energized_panel_and_temporary_wiring1.png,Open_energized_panel_and_temporary_wiring2.png,Open_energized_panel_and_temporary_wiring3.png,Open_energized_panel_and_temporary_wiring4.png,Open_energized_panel_and_temporary_wiring5.png,Open_energized_panel_and_temporary_wiring6.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed from a temporary power panel on the exterio | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_energized_panel_and_temporary_wiring2.png | file://x:/photopub/docs/0000000573/21026af4-cbcc-45ea-8a4c-fb5b2f46fbd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bff735f_76d4_4f01_9f2b_6cbaba4c812d
ELIN-775112-2017 | EL-506685-2017 | 3/16/2017 11:02:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_energized_panel_and_temporary_wiring1.png,Open_energized_panel_and_temporary_wiring2.png,Open_energized_panel_and_temporary_wiring3.png,Open_energized_panel_and_temporary_wiring4.png,Open_energized_panel_and_temporary_wiring5.png,Open_energized_panel_and_temporary_wiring6.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed from a temporary power panel on the exterio | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_energized_panel_and_temporary_wiring4.png | file://x:/photopub/docs/0000000573/0c24457a-dd13-4d22-ad0a-d82de633f26a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bff735f_76d4_4f01_9f2b_6cbaba4c812d
ELIN-775111-2017 | EL-506685-2017 | 3/16/2017 6:14:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Open_Energized_panel_and_temporary_power1.png,Open_Energized_panel_and_temporary_power2.png,Open_Energized_panel_and_temporary_power3.png,Open_Energized_panel_and_temporary_power4.png,Open_Energized_panel_and_temporary_power5.png,Open_Energized_panel_and_temporary_power6.png,Open_Energized_panel_and_temporary_power7.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. An armoured cable was entered through the face of the panel and was connected to a 50 amp, 2 pole branch circuit breaker. This permanent electrical panel was being feed fro | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_Energized_panel_and_temporary_power4.png | file://x:/photopub/docs/0000000573/a16b14a8-3c10-4a34-ba29-2464792331b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91766dc9_5039_4979_ae79_d8923d391847
ELIN-793626-2017 | EL-502214-2017 | 4/11/2017 4:35:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Masts1.png,Masts2.png Over head conductor attachment point attach to 2" EMT/RW90 for 400A service. FSR declaration submitted by FSR without a physical inspection, declaration submitted by FSR before correction were completed (false declaration submitted). | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Masts2.png | file://x:/photopub/docs/0000000585/39ab147f-8432-4107-9303-4fc65ad46cde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e6344df_f354_4aa2_879a_d27fd6cf6077
ELIN-793626-2017 | EL-502214-2017 | 4/11/2017 4:35:41 PM | ASSESS: EL: Service Connection | png | #asFound Over head conductor attachment point attach to 2" EMT/RW90 for 400A service | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Masts1.png,Masts2.png Over head conductor attachment point attach to 2" EMT/RW90 for 400A service. FSR declaration submitted by FSR without a physical inspection, declaration submitted by FSR before correction were completed (false declaration submitted). | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Masts1.png | file://x:/photopub/docs/0000000585/27b463b2-95ce-41af-99cc-b22882366f65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e6344df_f354_4aa2_879a_d27fd6cf6077
BPVIN-780613-2017 | BPV-359320-2016 | 3/21/2017 12:00:00 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Teck_gwtp.png Hot water boiler, maximum allowable working pressure 160 PSI. An emergency shut shutdown switch for the boiler was not located at the exit. The inability to shut down the boiler in the event of an emergency may result in damage to equipment and personal injury. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Teck_gwtp.png | file://x:/photopub/docs/0000000575/f699c482-1423-4beb-904c-446a4907f412.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b3d77ab_340a_45f5_987f_5540bf93bf05
ELIN-782886-2017 | EL-474981-2016 | 3/27/2017 10:41:43 AM | ASSESS: EL: Final | png | #asFound Large panel cover gap between breakers exposing energized terminals for accidental contact. | EL294 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #P4.png A person can accidentally contact energized parts of the service panel through the large gap left between the panel cover and face of breakers. Accidental contact may result in electrical shock, injury or death. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | P4.png | file://x:/photopub/docs/0000000576/f6cc943a-e449-4dc3-9969-4a3cf2f7381f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dd70ca4_4df0_43f2_85c3_684cc4c16b16
ELIN-795616-2017 | EL-523041-2017 | 4/26/2017 10:37:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #Under_sized_service_conductors1.png,Under_sized_service_conductors2.png,Under_sized_service_conductors3.png,Under_sized_service_conductors4.png,Under_sized_service_conductors5.png Service conductors are required to be properly rated and sized so that they are protected by the service over current devices. This is required to prevent the conductor, conductor insulation, termination, and over current device from being thermally damaged by an overheated conductor. This installation for a service upgrade from 100A to 200A for a house has a service conductors that are rated at 180A installed for service equipment and over current devices rated at 200A. This is a potential fire hazard if the service conductors are over loaded and thermally damaged causing an electrical fault. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Under_sized_service_conductors1.png | file://x:/photopub/docs/0000000591/d2d65f54-56dd-4c42-a7de-24dbbc458b59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bab52e4e_39a5_49ac_aa36_6470705db1c6
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker2.png | file://x:/photopub/docs/0000000591/74c0da0e-a48d-43d6-9329-542fee8cdc09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
EDMA-771138-2017 | ED-445627-2016 | 3/8/2017 12:15:25 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Dialler.png The emergency 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found the 2-way emergency communication was not functioning with the loss of the 110VAC cab power. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevator. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This 2 stop elevator is located in a 4 stop existing school. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Dialler.png | file://x:/photopub/docs/0000000568/d811191c-e806-49cb-9ad3-58fcfd182fab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c500756_1819_4731_a4be_4387038a517d
ELOP-766997-2017 | EL-500775-2017 | 3/3/2017 11:24:50 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Extension ring hanging loose. | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Box.png Initial Operating permit assessment on furniture store. An electrical outlet box housing a receptacle and switch is not fastened to the wall in an area only accessible to employees. It has no back on it and It is hanging loose and therefore, could be a shock hazard if employees use one hand to hold the box in place and the other to unplug a cord thereby contacting energized conductors. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Box.png | file://x:/photopub/docs/0000000566/f59e01ed-fe1c-4e6b-83d2-b8c48d2475a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0BE0CAFB_09A5_4127_B084_F7F8D5C238C0
ELIN-766238-2017 | EL-501187-2017 | 3/3/2017 12:41:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Length of unfused service conductor inside crawlspace. | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Unfused_conductor.png Rough wire of new single family dwelling. The length of service conductor, which is not fused, exceeds the maximum permissible length inside the dwelling. If this cable gets damaged then there is a great possibility of fire or shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Unfused_conductor.png | file://x:/photopub/docs/0000000566/7bfb6b11-8a32-4627-8afb-593cb0587b6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6848d5fc_293a_41e8_b8c4_a390f13e5a2f
ELIN-774784-2017 | EL-511444-2017 | 3/15/2017 11:35:07 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #No_bond_screw_in_place.png 100 amp, 120/240 volt main distribution panel has no bonding between the metal enclosure and the grounded conductor bus. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_screw_in_place.png | file://x:/photopub/docs/0000000572/9a30ef85-1fa1-4d9e-87b1-88a5afa3e3e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e11897c_7d9a_48bf_9e28_b33982d8f8b4
ELIN-774174-2017 | EL-511126-2017 | 3/15/2017 2:08:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Siemens_breaker_installed_in_Cutler_Hammer_Panel.png 100 amp, 120/240 volt main distribution panel has a main breaker installed in panel that is not type approved to be installed in panel. This could cause a thermal effect. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Siemens_breaker_installed_in_Cutler_Hammer_Panel.png | file://x:/photopub/docs/0000000572/a9d50416-6a31-4cfe-9214-89fa49aaed3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b47a1c1e_1488_4de6_92b6_353803f316a6
ELIN-770832-2017 | EL-498408-2017 | 3/15/2017 12:02:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Overloaded_light_switch_box.png The 15 amp 120 volt NMSC entering the lighting switch box is overloaded with conductors and presents the possibility of both a thermal and equipment/conductor damage issue | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Overloaded_light_switch_box.png | file://x:/photopub/docs/0000000572/7bd4db9f-355d-4b3d-8564-e26c21df3869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f6da2ed_ebd0_4e44_b5ce_f160ab8f1339
GAIN-804373-2017 | GA-508247-2017 | 4/28/2017 | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #M.png Copper tubing at meter A and B not secured to wall, physical damage could break or kink gas lines | 2 | Physical protection of piping and tubing absent. | M.png | file://x:/photopub/docs/0000000593/2048ec0c-27f6-4035-9994-531d25488dde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca5465e_72d7_4884_9274_6094c1a9c291
ELIN-783163-2017 | EL-384259-2016 | 4/28/2017 3:01:17 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Panel_with_cab_tire.png Flexible cord wedged under panel cover for support. Cable could be starained and create arcing. also panel cover is not sitting flush leaving a space for access to live parts. | 4 | Conductors, Misuse of flexible cords. | Panel_with_cab_tire.png | file://x:/photopub/docs/0000000593/62afbaa3-2cfe-4908-967c-4d64c2ef00dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf0063ce_8b82_4d01_b172_d6dffc3fd0c9
AMOP-781326-2017 | 2048342 | 3/23/2017 2:30:46 PM | ASSESS: AM OP: Periodic | png | #asFound Connected to round stock with key and keyways | AM023 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | 3 | 3 | #Lap_bar_connection1.png,Lap_bar_connection2.png Worn out connection at lap bar, it could worsen and cause a failure of the lap bar during ride operation. | 3 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | Lap_bar_connection1.png | file://x:/photopub/docs/0000000575/c29e918a-b4ef-4242-86cd-063aae1df630.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__706c87e3_c1f6_42b8_9726_0f4a21582550
AMOP-781326-2017 | 2048342 | 3/23/2017 2:30:46 PM | ASSESS: AM OP: Periodic | png | #asFound | AM023 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | 3 | 3 | #Lap_bar_connection1.png,Lap_bar_connection2.png Worn out connection at lap bar, it could worsen and cause a failure of the lap bar during ride operation. | 3 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | Lap_bar_connection2.png | file://x:/photopub/docs/0000000575/d2d3f7ad-9908-40eb-b649-0fc67f600c42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__706c87e3_c1f6_42b8_9726_0f4a21582550
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker6.png | file://x:/photopub/docs/0000000591/f66e6a81-03f6-4f76-92d9-ecfff682602c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
ELIN-795616-2017 | EL-523041-2017 | 4/26/2017 10:37:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #Under_sized_service_conductors1.png,Under_sized_service_conductors2.png,Under_sized_service_conductors3.png,Under_sized_service_conductors4.png,Under_sized_service_conductors5.png Service conductors are required to be properly rated and sized so that they are protected by the service over current devices. This is required to prevent the conductor, conductor insulation, termination, and over current device from being thermally damaged by an overheated conductor. This installation for a service upgrade from 100A to 200A for a house has a service conductors that are rated at 180A installed for service equipment and over current devices rated at 200A. This is a potential fire hazard if the service conductors are over loaded and thermally damaged causing an electrical fault. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Under_sized_service_conductors5.png | file://x:/photopub/docs/0000000591/306dc0f6-5e1d-40bb-ac3a-e88b72b03a89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bab52e4e_39a5_49ac_aa36_6470705db1c6
ELIN-795616-2017 | EL-523041-2017 | 4/26/2017 10:37:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #Under_sized_service_conductors1.png,Under_sized_service_conductors2.png,Under_sized_service_conductors3.png,Under_sized_service_conductors4.png,Under_sized_service_conductors5.png Service conductors are required to be properly rated and sized so that they are protected by the service over current devices. This is required to prevent the conductor, conductor insulation, termination, and over current device from being thermally damaged by an overheated conductor. This installation for a service upgrade from 100A to 200A for a house has a service conductors that are rated at 180A installed for service equipment and over current devices rated at 200A. This is a potential fire hazard if the service conductors are over loaded and thermally damaged causing an electrical fault. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Under_sized_service_conductors4.png | file://x:/photopub/docs/0000000591/0dcea854-cfa6-4e29-8339-e725260a8687.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bab52e4e_39a5_49ac_aa36_6470705db1c6
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker4.png | file://x:/photopub/docs/0000000591/755d9fc5-4217-4cd9-b163-de2eba385c25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
ELIN-795616-2017 | EL-523041-2017 | 4/26/2017 10:37:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #Under_sized_service_conductors1.png,Under_sized_service_conductors2.png,Under_sized_service_conductors3.png,Under_sized_service_conductors4.png,Under_sized_service_conductors5.png Service conductors are required to be properly rated and sized so that they are protected by the service over current devices. This is required to prevent the conductor, conductor insulation, termination, and over current device from being thermally damaged by an overheated conductor. This installation for a service upgrade from 100A to 200A for a house has a service conductors that are rated at 180A installed for service equipment and over current devices rated at 200A. This is a potential fire hazard if the service conductors are over loaded and thermally damaged causing an electrical fault. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Under_sized_service_conductors3.png | file://x:/photopub/docs/0000000591/7a6f22a0-0448-42bf-8f1f-310082f65e5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bab52e4e_39a5_49ac_aa36_6470705db1c6
AMOP-795454-2017 | 2053200 | 4/12/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 2 | #Undersized_blocking.png Blocking not supporting 100% of the stabilizer pad surface area. It is industry standard that blocking surface provides a minimum of 100% support of the stabilizer pad surface area at all locations. Insufficient support of the entire pad surface area could result in excessive compression of the blocking | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Undersized_blocking.png | file://x:/photopub/docs/0000000589/9d2f29f7-4efd-4a5b-8e48-b2dfb1688fb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__496a3b40_a733_4b51_87dc_14d898cc037f
GAIN-766255-2017 | GA-500108-2017 | 3/10/2017 9:58:08 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Abs_clearance_.png The as-found-condition is that a single wall vent serving a water heater is in close proximity to combustible material. The potential hazard is that the combustible material will catch fire due to the high temperature of the vent pipe. | 3 | Non compliant Type C Vent clearance | Abs_clearance_.png | file://x:/photopub/docs/0000000569/8241934e-bc53-40c8-9356-4b75cd782721.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49083d0c_4772_4d28_a72e_d5d73fb4df2b
BPVOP-771330-2017 | 4579808 | 3/8/2017 4:00:23 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD_1_.png Upon the assessment of a Freon Accumulator with MAWP of 400 psig, was found that the Pressure Relief Device was installed in 2011 and was overdue as per CSA B52. This can contribute to the failure of the pressure vessel. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_1_.png | file://x:/photopub/docs/0000000569/06ffd147-809c-408b-b594-a0c959fc2ffd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e44a3b08_e79c_4fb3_9667_513c37c762f6
BPVOP-771328-2017 | 4579816 | 3/8/2017 4:25:21 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD_2_.png Upon the assessment of a Freon Accumulator with MAWP of 400 psig, was found that the Pressure Relief Device was installed in 2011 and was overdue as per CSA B52. This can contribute to the failure of the pressure vessel. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_2_.png | file://x:/photopub/docs/0000000569/8bf29d48-ebde-4705-9792-17d5e5bcea89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6499623_cd10_4a4b_813f_a64b229d46bc
BPVOP-771329-2017 | 4579821 | 3/8/2017 4:36:18 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD_3.png Upon the assessment of a Freon Accumulator with MAWP of 400 psig, was found that the Pressure Relief Device was installed in 2011 and was overdue as per CSA B52. This can contribute to the failure of the pressure vessel. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_3.png | file://x:/photopub/docs/0000000569/fa56f08d-2128-4b5d-9436-458fca090a99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77c31332_1d64_4e99_bd16_3fde6e60347b
ELIN-770634-2017 | EL-501998-2017 | 3/13/2017 11:23:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 5 | #Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor1.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor2.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor3.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor4.png Electrical equipment is required to be de-energized prior to working on it and is required to have protective covers installed after working on it and prior to re-energizing it. This is required to prevent workers from shock and arc flash hazards during the installation and to protect persons and property from shock, arc flash and fire hazards after the installation is completed. During installation for a service upgrade from 100A 120/240V to 200A 120/240V an electrical contractor completed work on the energized conductors of the existing 100A service by terminating the conductors to the new 200A service panel without de-energizing them. After the work was completed the panel cover for the new panel wa | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor4.png | file://x:/photopub/docs/0000000571/6a340eec-fa59-466a-a2b0-3ef6beb47f45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07068aa7_3a0a_46b9_a8e5_75e3eca91045
ELIN-770634-2017 | EL-501998-2017 | 3/13/2017 11:23:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 5 | #Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor1.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor2.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor3.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor4.png Electrical equipment is required to be de-energized prior to working on it and is required to have protective covers installed after working on it and prior to re-energizing it. This is required to prevent workers from shock and arc flash hazards during the installation and to protect persons and property from shock, arc flash and fire hazards after the installation is completed. During installation for a service upgrade from 100A 120/240V to 200A 120/240V an electrical contractor completed work on the energized conductors of the existing 100A service by terminating the conductors to the new 200A service panel without de-energizing them. After the work was completed the panel cover for the new panel wa | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor2.png | file://x:/photopub/docs/0000000571/13a4de9e-795e-4ad7-9936-09de5641ba1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07068aa7_3a0a_46b9_a8e5_75e3eca91045
ELIN-770634-2017 | EL-501998-2017 | 3/13/2017 11:23:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 5 | #Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor1.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor2.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor3.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor4.png Electrical equipment is required to be de-energized prior to working on it and is required to have protective covers installed after working on it and prior to re-energizing it. This is required to prevent workers from shock and arc flash hazards during the installation and to protect persons and property from shock, arc flash and fire hazards after the installation is completed. During installation for a service upgrade from 100A 120/240V to 200A 120/240V an electrical contractor completed work on the energized conductors of the existing 100A service by terminating the conductors to the new 200A service panel without de-energizing them. After the work was completed the panel cover for the new panel wa | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor1.png | file://x:/photopub/docs/0000000571/d86ead66-b4ed-437f-9dcc-f4ebf209a640.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07068aa7_3a0a_46b9_a8e5_75e3eca91045
ELIN-770634-2017 | EL-501998-2017 | 3/13/2017 11:23:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 5 | #Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor1.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor2.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor3.png,Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor4.png Electrical equipment is required to be de-energized prior to working on it and is required to have protective covers installed after working on it and prior to re-energizing it. This is required to prevent workers from shock and arc flash hazards during the installation and to protect persons and property from shock, arc flash and fire hazards after the installation is completed. During installation for a service upgrade from 100A 120/240V to 200A 120/240V an electrical contractor completed work on the energized conductors of the existing 100A service by terminating the conductors to the new 200A service panel without de-energizing them. After the work was completed the panel cover for the new panel wa | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_equipment_worked_on_and_left_open_by_electrical_the_contractor3.png | file://x:/photopub/docs/0000000571/b2e11108-4631-4557-b15b-0a29e7d61671.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07068aa7_3a0a_46b9_a8e5_75e3eca91045
ELOP-795342-2017 | EL-522813-2017 | 4/24/2017 2:10:41 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Storage21.png,Storage22.png,Storage23.png,Storage24.png,Storage25.png,Storage26.png Electrical rooms used for storage limiting safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Storage21.png | file://x:/photopub/docs/0000000591/cd7824da-bf04-4655-9785-83c6aa8c3522.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9461D834_C68E_4F1A_9567_876D8BF04183
ELOP-789583-2017 | EL-515241-2017 | 4/24/2017 11:03:08 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel.png Panel breaker spaces open on energized panels leaving exposed electrical parts and a potential shock hazard. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel.png | file://x:/photopub/docs/0000000591/2a56b113-d666-495d-b713-b67ed43f88db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56D41DAD_639C_4E17_A334_E03F0C22ACC8
ELHE-792848-2017 | HE-521235-2017 | 4/12/2017 12:40:36 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL046 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | 5 | 5 | #Lead_acid_batteries_between_bed_and_bathtub3.png Storage batteries are located beside the bathtub with unprotected terminals. There is no method provided for venting the gas produced by charging the batteries to the outdoors. There is shock hazard created by the situation as well as the hazard created if the gas were to build up to explosive levels. | 5 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | Lead_acid_batteries_between_bed_and_bathtub3.png | file://x:/photopub/docs/0000000592/72d62755-55f4-4fbf-b899-f1f932b3e311.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e26aa12_7af5_4e0c_9215_48d3f27bc8be
ELHE-792848-2017 | HE-521235-2017 | 4/12/2017 12:40:36 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL046 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | 5 | 5 | #Lead_acid_batteries_between_bed_and_bathtub3.png Storage batteries are located beside the bathtub with unprotected terminals. There is no method provided for venting the gas produced by charging the batteries to the outdoors. There is shock hazard created by the situation as well as the hazard created if the gas were to build up to explosive levels. | 5 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | Lead_acid_batteries_between_bed_and_bathtub3.png | file://x:/photopub/docs/0000000592/ee264e9b-da8a-4a12-ae26-462889bcd903.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e26aa12_7af5_4e0c_9215_48d3f27bc8be
ELHE-792836-2017 | HE-521228-2017 | 4/11/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Battery_storage.png Lead acid batteries are stored in an area that is not secured from the rest of the house. Accidental contact could occur resulting in shock injury. The batteries have not been vented to the outdoors. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Battery_storage.png | file://x:/photopub/docs/0000000592/c74c1436-a2ce-4bb8-8a33-11e092879407.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc37135c_0134_48c0_81f0_0f0b5e67e111
ELIN-760610-2017 | EL-400683-2016 | 3/22/2017 12:00:48 PM | ASSESS: EL: Final | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | #Poor_photo_of_isolated_electrode_for_comm_system_not_interconnected_as_required.png A new residence with a 200 amp 240 volt service had a communication wiring system installed both to the residence and inside the residence. The communication wiring system ground was not properly interconnected with the main service ground as required to protect interior wiring from hazardous conditions experienced during electrical storms. When improperly grounded or interconnected damage to structures or injury to persons can occur. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Poor_photo_of_isolated_electrode_for_comm_system_not_interconnected_as_required.png | file://x:/photopub/docs/0000000578/9655998e-6042-4305-ad42-1a3998d2f0f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78b8a6a8_9509_4f3e_886a_9b65a2c934ef
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker7.png | file://x:/photopub/docs/0000000591/295e526f-6ca1-459e-a244-09723c4bc6d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker1.png | file://x:/photopub/docs/0000000591/d7404734-0f58-46b9-a2ea-a96a4b1da28a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
ELIN-795616-2017 | EL-523041-2017 | 4/26/2017 10:37:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #Under_sized_service_conductors1.png,Under_sized_service_conductors2.png,Under_sized_service_conductors3.png,Under_sized_service_conductors4.png,Under_sized_service_conductors5.png Service conductors are required to be properly rated and sized so that they are protected by the service over current devices. This is required to prevent the conductor, conductor insulation, termination, and over current device from being thermally damaged by an overheated conductor. This installation for a service upgrade from 100A to 200A for a house has a service conductors that are rated at 180A installed for service equipment and over current devices rated at 200A. This is a potential fire hazard if the service conductors are over loaded and thermally damaged causing an electrical fault. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Under_sized_service_conductors2.png | file://x:/photopub/docs/0000000591/b90a4ab8-0ff4-40af-a3f1-749247e0a096.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bab52e4e_39a5_49ac_aa36_6470705db1c6
ELIN-791244-2017 | EL-435503-2016 | 4/25/2017 4:49:06 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_conductor_no_terminated_properly_at_main_breaker1.png,Service_conductor_no_terminated_properly_at_main_breaker2.png,Service_conductor_no_terminated_properly_at_main_breaker3.png,Service_conductor_no_terminated_properly_at_main_breaker4.png,Service_conductor_no_terminated_properly_at_main_breaker5.png,Service_conductor_no_terminated_properly_at_main_breaker6.png,Service_conductor_no_terminated_properly_at_main_breaker7.png Stranded conductors are required to be installed into solderless termination lugs so that there are no stray strands and inserted into the lug properly so that the conductor is terminated securely. This is required to prevent stray conductor strands from causing short-circuits and grounds and to provide a solid low impedance conductor connection. This installation for a new house has a 200A 120/240V service conductor that is terminated a breaker in the service panel. The conductor termination has a stray strand and is not properly inserted into the termination lug to provide a solid | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_conductor_no_terminated_properly_at_main_breaker5.png | file://x:/photopub/docs/0000000591/cc16611e-90c3-4ea2-8304-5dd48daebdf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d9a4a_734a_44a6_ba89_44857d3662ec
ELIN-723090-2016 | EL-163863-2014 | 3/9/2017 12:43:01 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_near_sink_not_GFCI_protected_.png Kitchen receptacle within 1.5 meter of sink must be ground fault protected to prevent shock when electrical equipment is used near water. If cord connected electric appliances fall into or contact water there is serious potential for shock injury. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_near_sink_not_GFCI_protected_.png | file://x:/photopub/docs/0000000569/0238fda1-82d1-4fdc-a418-b2f387fff9fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f10fb04_7110_44d4_8d1c_c58ebdbeb64b
ELOP-777117-2017 | 5407878 | 3/22/2017 8:27:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Broken grounding conductor between service and grounding electrode | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Broken_grounding__broken_grounding_conductor.png Grounding conductor is broken between the service and grounding electrode. There was no equal potential between the electrical equipment and ground. Should someone be standing in front of the electrical equipment during a ground fault The operator may receive an electrical shock. | 4 | Installation Grounding; conductor is not continuous. | Broken_grounding__broken_grounding_conductor.png | file://x:/photopub/docs/0000000574/d5621c6b-84fb-4c2a-b978-a735bf831907.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45A56C57_4BE5_40A1_A948_DB867452A592
ELHE-777525-2017 | HE-513107-2017 | 3/17/2017 3:33:48 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Open temporary construction service. | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Open.png Hazard elimination. Abandoned temporary construction service mounted on a pole found with door removed. This exposed the electrical panel and equipment to rain. The equipment is not rated to withstand water and is located near a busy street. Shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Open.png | file://x:/photopub/docs/0000000573/7d5b0165-0e2c-42d0-9d5e-61ac9b3e22de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f78f74c_829f_4a0c_bb26_7a5956279438
BPVOP-784082-2017 | 3891938 | 3/28/2017 12:53:13 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound Stand is not anchored and easily moved | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 3 | #Base.png The pressure vessel is not properly anchored and can be moved easily placing stress on the attached piping. In a seismic event or if bumped by Mobil equipment this could cause failure of the piping or pressure vessel. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | Base.png | file://x:/photopub/docs/0000000577/668b7809-d25d-4760-993e-79d07f9114a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65685584_312a_4554_afdf_236326949cc3
ELIN-791565-2017 | EL-508053-2017 | 4/11/2017 12:54:17 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Detached_shed1.png,Detached_shed2.png,Detached_shed3.png,Detached_shed4.png The 15 amp 120 volt wiring to the detached shed uses wiring methods not approved that include NMSC in wet locations, male cord connector attached to teck cable, this method is both a shock and thermal hazard | 3 | Conductors Equipment is not approved for the specific use. | Detached_shed1.png | file://x:/photopub/docs/0000000585/34dcc0a4-b1f5-46fb-b87e-feb2a1993f08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0a05628_028d_459a_9c7f_568e2e6199d1
ELHE-769347-2017 | HE-508080-2017 | 2/28/2017 12:24:48 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Pic4.png -Panel boards located in locked electrical room , electrical panel cover have been installed with some branch circuit breaker spaces being open to accidental contact with energized bussing within panel. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Pic4.png | file://x:/photopub/docs/0000000570/940d3cac-d3be-4632-96f2-21f6970712a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad434135_93bd_4adf_b79c_bd7dbf6c38aa
GAIN-808966-2017 | GA-527662-2017 | 5/5/2017 1:24:24 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent.png Venting material found to be constructed of PVC plastic material contrary to manufacturer required s636 material. Incorrect venting material can fail prematurely leading products of combustion to leak into occupied spaces potentially leading to physical harm. | 3 | Unapproved venting material | Vent.png | file://x:/photopub/docs/0000000596/f862ff52-6453-48fc-8d2d-f133476c9d58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3fa5e75_eb4d_45fd_b344_d049934c8716
ELIN-760767-2017 | EL-442163-2016 | 2/24/2017 3:48:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_service_cable1.png,Consumer_service_cable2.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service in an existing commercial building, the cable was installed a total length of 12 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service_cable2.png | file://x:/photopub/docs/0000000562/b59418f6-b8f8-4807-956d-3afb19ef8a3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b590ba1_2c46_4425_b60e_4e747a3e5b9c
ELIN-760767-2017 | EL-442163-2016 | 2/24/2017 3:48:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Consumer_service_cable1.png,Consumer_service_cable2.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service in an existing commercial building, the cable was installed a total length of 12 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Consumer_service_cable1.png | file://x:/photopub/docs/0000000562/4bc9bf01-9668-4c61-8295-ee6559e9cb6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b590ba1_2c46_4425_b60e_4e747a3e5b9c
ELIN-770667-2017 | EL-497147-2017 | 3/13/2017 1:44:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_too_close_to_edge_of_framing1.png,NMSC_too_close_to_edge_of_framing2.png When non-metallic sheathed cable is located too close to the edge of the framing there is risk of damage to the cable. If the screw intended to support the drywall pierces the cable there is risk of short circuit and potentially a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_too_close_to_edge_of_framing1.png | file://x:/photopub/docs/0000000570/6f603a46-c14e-40a1-9d14-30e83e65da64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49463b0f_2f55_4b47_868e_a8bc64fd108d
BPVOP-779379-2017 | 2277712 | 3/21/2017 10:03:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 150 psig, I found a Pressure Relief Device not replaced within the last 3 years and no NDE was performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD.png | file://x:/photopub/docs/0000000575/61aa6931-f4fb-4dcf-beac-4b5b36be43f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8a10002_0085_4626_88de_3d5032f05293
EDMA-784512-2017 | ED-491698-2017 | 3/28/2017 | ASSESS: ED MA: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Encased_jack_in_a_parkade1.png,Encased_jack_in_a_parkade2.png The jack of a hydraulic elevator is part of the supporting means of the elevator. During a modernization inspection it was found that the jack which is typically buried in the ground was exposed in a parkade area encased in cinder blocks. Rupturing of the jack will cause the elevator to crash to the bottom of the elevator hoistway. There is a hazard of possible damage to the jack from a vehicle in the parkade as the jack is located between 2 parking stalls with no protection. It was found the building engineer did not recognize the hazard of the jack being located in a parkade area. This 2 stop hydraulic elevator is located in an existing college cafeteria area. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Encased_jack_in_a_parkade2.png | file://x:/photopub/docs/0000000578/e067ed8b-13af-4ea1-811a-e405814fa995.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f51f0012_b439_49cf_a0c5_511e885d6c75
EDMA-784512-2017 | ED-491698-2017 | 3/28/2017 | ASSESS: ED MA: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Encased_jack_in_a_parkade1.png,Encased_jack_in_a_parkade2.png The jack of a hydraulic elevator is part of the supporting means of the elevator. During a modernization inspection it was found that the jack which is typically buried in the ground was exposed in a parkade area encased in cinder blocks. Rupturing of the jack will cause the elevator to crash to the bottom of the elevator hoistway. There is a hazard of possible damage to the jack from a vehicle in the parkade as the jack is located between 2 parking stalls with no protection. It was found the building engineer did not recognize the hazard of the jack being located in a parkade area. This 2 stop hydraulic elevator is located in an existing college cafeteria area. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Encased_jack_in_a_parkade1.png | file://x:/photopub/docs/0000000578/8b421dc3-91f1-42a3-8629-b4ba4243cc7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f51f0012_b439_49cf_a0c5_511e885d6c75
GAIN-802842-2017 | GA-472972-2016 | 4/28/2017 9:27:24 AM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Furnace_air_intake_piping.png The air intake piping for a furnace was installed to close to the gas regulator vent on the gas meter. If the regulator failed and relieved gas there is a possibility that the air intake for the furnace could draw in the combustible gas causing a fire or explosion. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Furnace_air_intake_piping.png | file://x:/photopub/docs/0000000593/565e4d65-9acc-49a7-9849-b67d48b2cfb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4918d52_7df9_438e_b6c5_298a4e09cf29
GAHE-778347-2017 | HE-513449-2017 | 3/20/2017 10:40:51 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #ISC.png ISC found in the open position unattended, P650 device found in the open position with the door closed on bottle filling cabinet. In the event of a propane release the ISC will be in the open position allowing uncontrollable release of propane | 4 | Incorrect use of safety controls (Example: bypass limit) | ISC.png | file://x:/photopub/docs/0000000573/fe2939dd-f1c5-4853-9c45-116db6f7203c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1b64283_815e_4439_b5a5_0ed0e8f3b3da
ELIN-807297-2017 | EL-494511-2017 | 5/4/2017 10:04:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Gang_operated_load_break_does_not_show_approval_for_use.png Gang operated load break switch installed does not bear approval markings. Use of unapproved equipment may not satisfy the requirements for the application in which it is being used. Failure of equipment may result in damage to persons or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Gang_operated_load_break_does_not_show_approval_for_use.png | file://x:/photopub/docs/0000000595/a1314b5a-8353-4fe2-a834-04c8baddacdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1db01ff_2414_466f_83ad_e0fad2abe437
BPVIN-759401-2017 | BPV-502441-2017 | 2/17/2017 7:27:49 AM | ASSESS: BPV IN: Piping | pdf | #asFound Inspection photos of Tie Point 30 | BP182 | 5.1.0 In service proc/process - Welding procedures not in compliance with code. | 3 | 3 | #PG_Pulp_NCGH_Piping_TP30_Inspection_Photos.pdf Welding groove to attach Tie Point weldolet to run pipe only partially filled. Piping Code has specific requirements for minimum weld finish. | 3 | 5.1.0 In service proc/process - Welding procedures not in compliance with code. | PG_Pulp_NCGH_Piping_TP30_Inspection_Photos.pdf | file://x:/photopub/docs/0000000563/adc5d2f7-00f9-4f68-909e-ce97e4e8e0af.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12534513_9b8f_44bd_b6e2_64a265ffb6f3
ELHE-781159-2017 | HE-515171-2017 | 3/23/2017 2:39:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | #Directory.png The main service panel is not accessible. This could create a fire and shock hazard due to the breaker identification on the directory is very hard to read. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Directory.png | file://x:/photopub/docs/0000000575/b7f736a9-8a01-4e58-92a8-918de56eefdf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f96b3f83_cc40_4753_99e2_baff70daaf5f
GAIN-790557-2017 | GA-511155-2017 | 4/13/2017 10:56:53 AM | ASSESS: GA: Final | png | #asFound | GA100 | Hazards created by exhaust fans | 3 | 3 | #Regulator_vent.png The as found condition is commercial kitchen equipment relying on a commercial exhaust hood for removing products of combustion from the building are not interlocked together. The as found hazard is should the exhaust fan not be turned on, the appliances can still be operated, allowing products of combustion to enter the building placing occupants at risk for carbon monoxide poisoning. | 3 | Hazards created by exhaust fans | Regulator_vent.png | file://x:/photopub/docs/0000000586/520199fc-1c54-42aa-bf06-8657c43889ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28cca992_0666_4e54_b7b2_9184560a735c
ELIN-806486-2017 | EL-496355-2017 | 5/1/2017 1:07:17 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #ACWU_to_TA_in_PVC_pipe.png At an existing single family dwelling, a new 100amp 120/240volt sub-distribution feeder cable in the new outbuilding was observed without the use of the approved connectors. This can lead to a "Shock Hazard" condition. Pic attached. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | ACWU_to_TA_in_PVC_pipe.png | file://x:/photopub/docs/0000000593/c0b38bfa-ed02-456e-8e5d-c3e470f46014.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbae3218_bec1_4738_b75c_bc0a3a33c062
ELIN-800098-2017 | EL-522814-2017 | 4/24/2017 11:13:00 AM | ASSESS: EL: Service Connection | png | #asFound Panel fillers missing | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #System_is__System_is_not_energized1.png,System_is__System_is_not_energized2.png Knock out and panel filler covers missing. There is a possibility that someone could be injured if they accidentally insert their hand inside the panel board or if an arc fault should occur inside the distribution equipment. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | System_is__System_is_not_energized2.png | file://x:/photopub/docs/0000000590/4ad722d0-4ea8-4db5-84d3-fca4020ffe40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20ab32b2_4e71_4e20_af81_37881cf96b89
ELIN-800098-2017 | EL-522814-2017 | 4/24/2017 11:13:00 AM | ASSESS: EL: Service Connection | png | #asFound Knock out feelers missing | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #System_is__System_is_not_energized1.png,System_is__System_is_not_energized2.png Knock out and panel filler covers missing. There is a possibility that someone could be injured if they accidentally insert their hand inside the panel board or if an arc fault should occur inside the distribution equipment. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | System_is__System_is_not_energized1.png | file://x:/photopub/docs/0000000590/cb3812e1-2283-4bf9-8465-cc8c6de6ffca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20ab32b2_4e71_4e20_af81_37881cf96b89
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A2.png | file://x:/photopub/docs/0000000591/ba7646cb-e016-4fd3-b9c1-5ebf8ae7f2f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A11.png | file://x:/photopub/docs/0000000591/aa36a943-411f-4dde-b416-99b85ae774bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A4.png | file://x:/photopub/docs/0000000591/40264884-6a59-41c5-a2e4-954f6bdf7fda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A9.png | file://x:/photopub/docs/0000000591/49969bad-51de-44b3-9b20-8990efcad4cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELIN-759805-2017 | EL-494199-2017 | 2/27/2017 2:51:19 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #No_receptacles_either_side_sink_with_counters_in_excess_of_300_mm_on_both_sides.png A new dwelling kitchen has not been provided receptacles on 2 isolated counter spaces over 30 centimetres wide where typically cord connected appliances may be used and are required to have receptacles as a minimum requirement of the code. Owners may resort to the use of extension cords that may go over sinks or cooking appliances where receptacles have not been installed as required. this can lead to damage to property or injury to persons. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | No_receptacles_either_side_sink_with_counters_in_excess_of_300_mm_on_both_sides.png | file://x:/photopub/docs/0000000563/345ebd5c-6015-4c30-8667-967735250f26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d494aa90_3f8e_451b_b371_25cf6c93b621
ELOP-740806-2017 | 4235219 | 2/27/2017 11:02:30 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | #No_gradient_mat_of_visible_grounding_to_handle_of_switch.png An existing privately owned 25000 volt power line, pole mounted disconnects, and an assortment of other equipment was assessed. It was found that the main disconnecting means for this private line was lacking all indications that it was safe to operate, grounding incomplete to protect operators. Operators of high voltage equipment can be mortally injured when operating equipment of this type without the necessary grounding and protection it provides | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | No_gradient_mat_of_visible_grounding_to_handle_of_switch.png | file://x:/photopub/docs/0000000563/4e3cf1cf-a708-477e-8ec3-eeb03ee623a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C2B51E13_21E9_4EEF_A6A2_A3687E7575A4
ELIN-773751-2017 | EL-510549-2017 | 3/22/2017 4:57:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_not_installed__also_service_conductors_incomplete.png A new residential service rated 200 amps and 240 volts has been authorized for connection to the utility without a main system ground. A main system ground is provided on a service to ensure that in the event of a fault on the system the building or persons in the building are provided protection against injury and the building is protected from potential damage. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_not_installed__also_service_conductors_incomplete.png | file://x:/photopub/docs/0000000576/09fefd58-8b29-4ae2-a5d9-e0d98d8d5a5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49c518f7_4fff_48b8_bfb5_d9f59c2acb47
AMOP-799678-2017 | 2723352 | 4/20/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Pin_partially_backed_out_of_light_fixture.png Overhead decorative light fixtures attached to the diagonal support columns of the device are not secured by retaining clips and at one location the attachment pin has backed out. There is a risk in which a decorative light fixture could become detached. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Pin_partially_backed_out_of_light_fixture.png | file://x:/photopub/docs/0000000590/137ea85a-5d67-4e9f-ad89-5412fe9f0be1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3353e2c8_7b64_46e7_9eb0_69c831d0b2dd
ELIN-780773-2017 | EL-513928-2017 | 3/29/2017 3:06:37 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #No8_Cabtyre.png At a modular silver label inspection,a trailer was found with the main feeder cable sized smaller than than the over-current protection ahead of it. This can lead to a "thermal effect" condition. Pic attached. | 3 | Protection and control Loading of distribution equipment exceeded | No8_Cabtyre.png | file://x:/photopub/docs/0000000578/8890938f-cae6-49d4-9bfa-c7a8efe2e47d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c136469_60c6_4b29_b7be_39cb94a2050d
GAHE-772091-2017 | HE-509728-2017 | 3/9/2017 12:29:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Relief_opening_indoors.png Construction heaters have been placed in operation but has not been installed correctly. Second stage relief regulators have not been vented to the outdoors and if the regulators were to fail propane gas would escape into the confined space and the potential would be a gas explosion which would cause significant damage and injuries or death if people were in the buildings | 5 | Relief style regulator/device allowed to vent within building/confined space | Relief_opening_indoors.png | file://x:/photopub/docs/0000000569/de7c56db-4238-41a9-a863-239e9a91a3da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b828cdf5_576a_4bcc_8847_49c528c36f0b
GAHE-776799-2017 | HE-512694-2017 | 3/17/2017 8:16:02 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #Piping1.png,Piping2.png An Emergency shut down valve is required when dispensing propane, an emergency shut down valve should be incorporated with closure of the cabinet door and the remote dispenser to shut off supply line when propane is not being dispensed, if this emergency valve is not shut when not dispensing propane, in event of failure of the dispensing system, propane has the potential of having a uncontrolled release. | 4 | Incorrect use of safety controls (Example: bypass limit) | Piping2.png | file://x:/photopub/docs/0000000572/31a146ab-4de0-40c0-acd0-fbe951cd905f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71137663_09ed_4f80_8e36_2e1519ae1568
GAHE-776799-2017 | HE-512694-2017 | 3/17/2017 8:16:02 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #Piping1.png,Piping2.png An Emergency shut down valve is required when dispensing propane, an emergency shut down valve should be incorporated with closure of the cabinet door and the remote dispenser to shut off supply line when propane is not being dispensed, if this emergency valve is not shut when not dispensing propane, in event of failure of the dispensing system, propane has the potential of having a uncontrolled release. | 4 | Incorrect use of safety controls (Example: bypass limit) | Piping1.png | file://x:/photopub/docs/0000000572/df811505-3f63-416b-9e00-877ba6e4156e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71137663_09ed_4f80_8e36_2e1519ae1568
GAHE-776793-2017 | HE-512690-2017 | 3/17/2017 7:48:11 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound ISC emergency shut down handle mounted on side of cabinet | GA054 | Code prohibited practices or materials | 3 | 3 | #ISC.png Emergency shut down is in place mounted on outside of cabinet, when dispensing propane this emergency shut down should be incorporated with closure of the cabinet door to shut off when propane is not being dispensed, if this emergency valve is not shut when not in operation and in the event of failure of the system propane has the potential of having a uncontrolled release of propane. | 3 | Code prohibited practices or materials | ISC.png | file://x:/photopub/docs/0000000572/8bdda19a-a79d-4fba-a22f-84d1bca0753e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfbf0476_b854_4cae_b12c_07e45ba86c7e
GAUP-776825-2017 | UW-512697-2017 | 3/17/2017 8:30:04 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Open gas line was found in bottle shed and was capped before inspection was complete by the service technician. | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open_gas_line.png Open gas lines was found in bottle fill shed but had manual valves installed and in the closed position to prevent the escape of gas if valves were to fail or if personnel were to turn these valves to the on position there potentially could have been a uncontrolled escape of gas causing injury or damage to property. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000572/3dddb74c-ee53-40a0-8643-8ccd918eeeff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e6d3431_8c07_4d2a_8887_e41f5bdc1878
ELIN-775727-2017 | EL-510377-2017 | 3/15/2017 1:28:21 PM | ASSESS: EL: Service Connection | png | #asFound Improper termination at meter base. Leaving service conductors exposed and subject to damage. | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #4.png Exposed service conductors at meter base due to improper termination of ACWU in a wet location. This is a shock hazard as the service conductors can be damaged, moisture can also enter the service cable. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4.png | file://x:/photopub/docs/0000000572/f44f958d-d061-46b5-aecc-b9968a4b120d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5909f74_a895_4934_beb3_ffed83631d49
ELIN-774489-2017 | EL-507690-2017 | 3/15/2017 3:45:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound NMD 90 branch circuits run in attic where there is greater then 1M of headroom requires running board for protection. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #7.png NMD 90 branch circuits run in the attic where there is greater than 1 m of headspace. This requires protection in the form of a running board. This is a shock hazard as an individual may step on the conductors and damage the outer sheath creating potential arc hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 7.png | file://x:/photopub/docs/0000000572/d2bee404-e0ce-4570-baa2-3f8dccbc49c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4639be12_f22b_4b60_9b5d_b0fe7f99fed5
ELIN-783045-2017 | EL-456032-2016 | 3/29/2017 10:51:55 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Panel_Location.png A new 200 amp 120/240 volt Panel is located in a home under construction but has not been provided with weather and mechanical protection. This poses a hazard to the equipment but also to persons using the panel. The panel is also not protected from unauthorized persons, and this could pose a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Panel_Location.png | file://x:/photopub/docs/0000000578/4e383a8e-419d-40c9-bb3f-f43522fa39a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dd8a891_1b11_4040_8376_f38069e3d204
ELOP-806501-2017 | 1540 | 5/1/2017 12:40:23 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound Photo of grounding and bonding bar removed from the wall and hanging down under the fire alarm panel. | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Bar.png Reinspection of noncompliance on operating permit assessment for secondary school. Noncompliance not corrected in the time allocated. Bar used for grounding in electrical room has been removed from the wall and is therefore, not secured. This places strain on the conductors used for grounding and bonding. Therefore, they are subject to mechanical damage and may not operate if required to trip overcurrent devices. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Bar.png | file://x:/photopub/docs/0000000593/0d0236e7-179c-4277-8178-b2854d49bbc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__634068bc_fd5f_4a29_b66a_97a08ecfd910
ELOP-738146-2017 | EL-484666-2016 | 3/6/2017 10:13:15 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 3 | #45kva_xfmr_inadequate_separation.png An open ventilated dry core transformer converting 125 amps 208 to 50 amps at 480 volts 3 phase was found installed lacking the minimum separation from combustible surfaces in a commercial wood processing facility. When a transformer of this type is subjected to certain fault conditions the transformer can react in way that will ignite adjacent combustible surfaces that would be a potential for damage to structures or injury to persons | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | 45kva_xfmr_inadequate_separation.png | file://x:/photopub/docs/0000000574/59579ffb-cdc4-4092-af62-eebe2a260c99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74514BAC_5CFA_4167_8A73_2692A716C378
ELIN-776958-2017 | EL-512547-2017 | 3/21/2017 12:50:38 PM | ASSESS: EL: Final | png | #asFound | EL169 | Protection and control Disconnect is not of proper type or rating. | 3 | 3 | #No_disconnect_compresso_relocatable_structure.png A heat pump split. Air compressor has been installed operating at 15 amps and 240 volts without a remote disconnect. Technicians servicing this equipment can be injured if the circuits are not clearly labeled for use and within site of the units. | 3 | Protection and control Disconnect is not of proper type or rating. | No_disconnect_compresso_relocatable_structure.png | file://x:/photopub/docs/0000000574/398ae402-cee5-4b97-82a5-1a2062c5f9cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2f7358a_6e14_4b86_94bd_b9df90822fe8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A5.png | file://x:/photopub/docs/0000000591/39da4055-2af7-4f81-807a-9620ae539025.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A6.png | file://x:/photopub/docs/0000000591/94a9f595-35aa-481d-8fe6-856e99417ff0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELHE-802564-2017 | HE-526541-2017 | 4/25/2017 3:42:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png,A10.png,A11.png 100A service overloaded with the addition of an electric furnace. This resulted in weakening and overheating of the meter base jaws. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A7.png | file://x:/photopub/docs/0000000591/b43b300e-e62e-4ca2-9df6-c9c6cfd9874e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c3ca0fe_133d_4511_a2b7_f66e0052a5a8
ELIN-804661-2017 | EL-527702-2017 | 5/2/2017 11:55:16 AM | ASSESS: EL: Service Connection | png | #asFound XO of transformer | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Transformer.png XO of transformer attached to system ground | 4 | Installation Grounding; conductor is not continuous. | Transformer.png | file://x:/photopub/docs/0000000594/70056cd9-0cf7-4aec-8565-856530b43155.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f130435_524d_4a08_9db6_1d3237a1f7e3
ELIN-774506-2017 | EL-511222-2017 | 3/16/2017 3:19:42 PM | ASSESS: EL: Service Connection | pdf | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Certificate_of_Inspection_Permit_EL-510912-2017_Insp_ELIN-775244-2017.pdf,Weather_proof_cover_has_not_been_provided_.png When electrical equipment is exposed to a wet environment there is risk of equipment rusting causing poor contact for electrical components. Loose or poor connections can cause an arcing hazard with the potential to result in improper operation or fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Certificate_of_Inspection_Permit_EL-510912-2017_Insp_ELIN-775244-2017.pdf | file://x:/photopub/docs/0000000572/385b806d-cf42-45bf-8016-dd5b5b0ccffd.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbfac8f1_3e09_4d22_a866_b9bba4ff36d9
ELIN-774506-2017 | EL-511222-2017 | 3/16/2017 3:19:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Certificate_of_Inspection_Permit_EL-510912-2017_Insp_ELIN-775244-2017.pdf,Weather_proof_cover_has_not_been_provided_.png When electrical equipment is exposed to a wet environment there is risk of equipment rusting causing poor contact for electrical components. Loose or poor connections can cause an arcing hazard with the potential to result in improper operation or fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Weather_proof_cover_has_not_been_provided_.png | file://x:/photopub/docs/0000000572/43736f8d-d7bc-4942-bad5-4ec9625940c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbfac8f1_3e09_4d22_a866_b9bba4ff36d9
ELIN-762640-2017 | EL-450364-2016 | 2/24/2017 12:26:53 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Non-GFCI_receptacle.png Receptacle within 1.5 m of a sink is not GFCI. Possibility for shock. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Non-GFCI_receptacle.png | file://x:/photopub/docs/0000000562/22a6dc8e-173b-4f33-98b5-acfb21632893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca4c7581_6355_46d8_95e7_1d43019cbc8a
GAHE-767307-2017 | HE-506799-2017 | 3/2/2017 3:40:24 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | #Tank.png Propane dispenser installed on edge of bank, dirt has been deteriorating from underneath skid, fill point of tank at edge of bank. | 2 | Appliance installed in a proposed hazardous location | Tank.png | file://x:/photopub/docs/0000000565/855a76a2-0cf4-4646-a295-d4dedbc3fd48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a98c8dfe_aa74_45c8_8c34_b78958851d87
ELIN-769518-2017 | EL-506546-2017 | 3/15/2017 1:26:42 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound NMD90 Cable too close to edge of wood stud and no protection plate. All roughwire is covered and could not see if this was done in other parts of roughwire and so not authorized to cover anything until all roughwire is exposed for inspection | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #NMD90_Cable_too_close_to_edge_of_wood_stud_and_no_protection_plate.png Found NMD90 120/240 volt branch circuit cables located less than 32mm from edges of wood stud members while there are no protection plates and so cable is not protected from possible mechanical damage. When NMD90 non-metallic sheathed cable is not protected from possible mechanical damage the conductors could get damaged by drywall screws and could be an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | NMD90_Cable_too_close_to_edge_of_wood_stud_and_no_protection_plate.png | file://x:/photopub/docs/0000000571/ce8aad22-0fa6-47f7-a903-af48b3fd4e5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__444ea028_efcb_46a9_ab4a_3b5411361abd
ELIN-783465-2017 | EL-449253-2016 | 3/29/2017 5:09:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_live_panel.png Energized 100 amp 120/240 volt electrical panels are open with no protective covers in place, this poses a shock hazard to person and potential mechanical damage to the electrical panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_live_panel.png | file://x:/photopub/docs/0000000578/c155b97d-9c5d-4835-bb5e-59fd77d56bb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1996188_99d6_4e74_af3f_227902ae393a
ELIN-803527-2017 | EL-518560-2017 | 4/27/2017 1:35:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | #Bond_screw_not_removed_in_sub_panel.png Neutral bond screws have been left in place in sub distribution panel. Leaving bond screw in place would cause neutral currents to circulate throughout the service equipment. In this situation over current devices may be affected in the case of a fault, and provide a risk of shock or equipment damage to persons and property. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Bond_screw_not_removed_in_sub_panel.png | file://x:/photopub/docs/0000000592/17cbb936-0258-45a3-afe8-0f5055812a15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4338d7bd_46be_4616_837e_5fea6d4306ab
ELIN-803525-2017 | EL-518560-2017 | 4/27/2017 2:14:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #System_ground_connected_to_enclosure.png Currently grounding conductor is terminated to lug on duplex meter base enclosure. Neutral grounded system requires ground connection at service neutral. If a fault were to occur overcurrent devices may not act as required to clear the fault. Risk of shock or fire would be present to persons and property. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | System_ground_connected_to_enclosure.png | file://x:/photopub/docs/0000000592/0c29901b-6c50-4d96-a559-ecb671e7d73d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ee24224_9127_4d00_90c3_c27b17b3ad0d
ELIN-803527-2017 | EL-518560-2017 | 4/27/2017 1:35:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | #Bond_screw_not_removed_in_sub_panel.png Neutral bond screws have been left in place in sub distribution panel. Leaving bond screw in place would cause neutral currents to circulate throughout the service equipment. In this situation over current devices may be affected in the case of a fault, and provide a risk of shock or equipment damage to persons and property. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Bond_screw_not_removed_in_sub_panel.png | file://x:/photopub/docs/0000000592/ffb2afa0-a6fc-49b9-8571-d6806117513c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4338d7bd_46be_4616_837e_5fea6d4306ab
ELOP-759891-2017 | EL-060119-2013 | 3/2/2017 10:57:42 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_spaces1.png,Panel_spaces2.png,Panel_spaces3.png,Panel_spaces4.png Open breaker spaces and cover pieces removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_spaces4.png | file://x:/photopub/docs/0000000566/b77d0a13-3072-45e5-8ce0-621aab08f310.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ccfe70b_ac46_44e6_99b5_179774d6ee2f
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz12.png | file://x:/photopub/docs/0000000566/8b3e0463-c172-4a48-b4d8-948891361116.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-759891-2017 | EL-060119-2013 | 3/2/2017 10:57:42 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_spaces1.png,Panel_spaces2.png,Panel_spaces3.png,Panel_spaces4.png Open breaker spaces and cover pieces removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_spaces2.png | file://x:/photopub/docs/0000000566/a8c6fbd8-a2bc-4019-ac8d-ee8ec0929c7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ccfe70b_ac46_44e6_99b5_179774d6ee2f
ELOP-759891-2017 | EL-060119-2013 | 3/2/2017 10:57:42 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_spaces1.png,Panel_spaces2.png,Panel_spaces3.png,Panel_spaces4.png Open breaker spaces and cover pieces removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_spaces3.png | file://x:/photopub/docs/0000000566/aeffc76b-c194-46a4-a814-b248da789a47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ccfe70b_ac46_44e6_99b5_179774d6ee2f
ELOP-759891-2017 | EL-060119-2013 | 3/2/2017 10:57:42 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_spaces1.png,Panel_spaces2.png,Panel_spaces3.png,Panel_spaces4.png Open breaker spaces and cover pieces removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_spaces1.png | file://x:/photopub/docs/0000000566/071e9274-b72e-4b20-a8bd-f4b7a939a82a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ccfe70b_ac46_44e6_99b5_179774d6ee2f
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz10.png | file://x:/photopub/docs/0000000566/96743029-e022-49b0-ada2-edd4a1948082.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz1.png | file://x:/photopub/docs/0000000566/511a2e85-92cb-4e83-bc8a-ffc3364829a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz2.png | file://x:/photopub/docs/0000000566/98f85920-b2d0-43a2-bc1e-dce12518c11b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz4.png | file://x:/photopub/docs/0000000566/91338863-0b17-4ef3-bb14-28b6b1d5a0b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound 1 of 9 structures that are approved and certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png | file://x:/photopub/docs/0000000564/d45585c6-4cf9-4e67-813c-cc33bf593599.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound Some structures of the 9 assembled and attached relocatable structures do not bear evidence of approved certification mark or label on structure and is considered unapproved electrical equipment. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png | file://x:/photopub/docs/0000000564/19f0b04a-ba0d-4d90-b9b7-a4520480db67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound Some structures of the 9 assembled and attached relocatable structures do not bear evidence of approved certification mark or label on structure and is considered unapproved electrical equipment. This structure is missing label/mark from CSA. CSA rep Bill Cook was on site and agreed the structure must be marked or labeled if CSA approved | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png | file://x:/photopub/docs/0000000564/035d1812-9315-41b8-9799-884b9a459575.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound 1 of 9 structures that are approved and certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png | file://x:/photopub/docs/0000000564/da6a7a83-7605-4d6d-a455-2eaef9ebacb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
BPVOP-756590-2017 | 2267134 | 2/14/2017 2:00:10 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP072 | 1.2.3 Boiler construction - Stains on insulation indicating corrosion under insulation. | 2 | 2 | #Water_mark_underneath_vessel.png Stain on floor underneath vessel indicates leakage. Any leakage of vessel's pressure boundary will be hard to detect if source of stain is not detected and rectified. | 2 | 1.2.3 Boiler construction - Stains on insulation indicating corrosion under insulation. | Water_mark_underneath_vessel.png | file://x:/photopub/docs/0000000565/6e908387-0ae0-4426-aa4b-b806ca858b8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7e47552_294a_40cc_bf15_61e08cad9216
ELIN-795948-2017 | EL-503891-2017 | 4/19/2017 4:15:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Coupling_has_opened1.png,Coupling_has_opened2.png At a new pump house installation, the 200amp 240volt 1phase service conduit was found in an unsupported and opened condition. This will lead to an "Equipment Damage" condition. Pic attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Coupling_has_opened1.png | file://x:/photopub/docs/0000000588/ec1b7313-c61d-4aa8-96c8-8aa827c66953.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0fd6b9a_ed62_4da9_9a23_36ead80503e9
ELIN-795948-2017 | EL-503891-2017 | 4/19/2017 4:15:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Coupling_has_opened1.png,Coupling_has_opened2.png At a new pump house installation, the 200amp 240volt 1phase service conduit was found in an unsupported and opened condition. This will lead to an "Equipment Damage" condition. Pic attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Coupling_has_opened2.png | file://x:/photopub/docs/0000000588/e1d4a068-a503-44c9-8cc8-5cbfd46d7e2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0fd6b9a_ed62_4da9_9a23_36ead80503e9
ELIN-801323-2017 | EL-524207-2017 | 5/1/2017 1:43:44 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Outside_receptacles_1.png,Outside_receptacles_2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for exterior receptacles within 2.5m of a finished grade. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they were using cord connected equipment outdoors during wet or damp conditions.. During an assessment for a modular home silver label inspection, No GFCI protection was found for the exterior receptacles. This is a potential shock hazard for any persons working with cord connected outside of the modular home during damp or wet conditions. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Outside_receptacles_2.png | file://x:/photopub/docs/0000000594/52b9325a-6b16-4def-a0bc-81bebbd5c9e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b3ffb26_7623_4bf1_b032_8dafb0742d90
ELIN-801323-2017 | EL-524207-2017 | 5/1/2017 1:43:44 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Outside_receptacles_1.png,Outside_receptacles_2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for exterior receptacles within 2.5m of a finished grade. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they were using cord connected equipment outdoors during wet or damp conditions.. During an assessment for a modular home silver label inspection, No GFCI protection was found for the exterior receptacles. This is a potential shock hazard for any persons working with cord connected outside of the modular home during damp or wet conditions. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Outside_receptacles_1.png | file://x:/photopub/docs/0000000594/71a4a5d9-4fcc-430b-820d-65e7c5074e58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b3ffb26_7623_4bf1_b032_8dafb0742d90
ELIN-803525-2017 | EL-518560-2017 | 4/27/2017 2:14:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #System_ground_connected_to_enclosure.png Currently grounding conductor is terminated to lug on duplex meter base enclosure. Neutral grounded system requires ground connection at service neutral. If a fault were to occur overcurrent devices may not act as required to clear the fault. Risk of shock or fire would be present to persons and property. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | System_ground_connected_to_enclosure.png | file://x:/photopub/docs/0000000592/00e2a5dc-f89e-4f58-a04c-d64cc1084f21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ee24224_9127_4d00_90c3_c27b17b3ad0d
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz3.png | file://x:/photopub/docs/0000000566/e7f99189-7945-454d-828d-8c4c9cd25761.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz9.png | file://x:/photopub/docs/0000000566/ce2babf7-df65-4268-ad58-64723f0b3a77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz11.png | file://x:/photopub/docs/0000000566/41616197-45bf-46e4-a5f0-f040b469d746.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz5.png | file://x:/photopub/docs/0000000566/a7283b1d-8b0b-489f-b04e-ecc89d8f3bd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz6.png | file://x:/photopub/docs/0000000566/5d398377-38be-452e-9648-12040f5b504e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz7.png | file://x:/photopub/docs/0000000566/984bc0f4-52ae-41f8-a984-1ef63aa4df23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
ELOP-765829-2017 | EL-445887-2016 | 3/2/2017 10:00:04 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Annunciator_haz1.png,Annunciator_haz2.png,Annunciator_haz3.png,Annunciator_haz4.png,Annunciator_haz5.png,Annunciator_haz6.png,Annunciator_haz7.png,Annunciator_haz8.png,Annunciator_haz9.png,Annunciator_haz10.png,Annunciator_haz11.png,Annunciator_haz12.png Fire alarm annunciator panel without evidence of approval and moisture ingress issue. Annunciator is used by the fire department in case of a fire to identify the area of concern and with the fogged screen it could limit there ability to address a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Annunciator_haz8.png | file://x:/photopub/docs/0000000566/d8d77d6e-a39f-4a1d-8936-b45427398a7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__083e42cb_837b_417c_9b91_29f94bc2c1a7
GAUP-791587-2017 | UW-520611-2017 | 4/10/2017 9:01:17 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #Garnett.png,Garnett.png Non bonded gas line. Shock hazard could exist if piping were to be inadvertently energized. This material is also susceptible to lighting strikes causing perforation of the tubing wall resulting in leaks and or risk of fire. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Garnett.png | file://x:/photopub/docs/0000000584/252a80e9-1396-4cff-9fec-d045b4dd8b8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12f3c013_ed4d_4c10_b7ac_342cf0114a5a
ELIN-804391-2017 | EL-520247-2017 | 4/26/2017 | ASSESS: EL: Final | png | #asFound Luminaire not bonded as required for approved electrical equipment | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Luminaire_not_bonded_properly1.png,Luminaire_not_bonded_properly2.png,Luminaire_not_bonded_properly3.png Found luminaire support bracket has bonding screw which is not bonded in two locations as required by approved luminaires. When electrical equipment is not bonded back to ground the electrical equipment could become a possible electrical shock hazard to people. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Luminaire_not_bonded_properly3.png | file://x:/photopub/docs/0000000592/131e692c-2b6d-4c6a-bd19-675397307a6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8f6f0f4_7890_492d_a718_d8a5ecd7ddd2
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound Some structures of the 9 assembled and attached relocatable structures do not bear evidence of approved certification mark or label on structure and is considered unapproved electrical equipment. This structure is missing label/mark from CSA. CSA rep Bill Cook was on site and agreed the structure must be marked or labeled if CSA approved | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png | file://x:/photopub/docs/0000000564/a6593c6d-bd14-477f-ab83-568b8e7f1e72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound Some structures of the 9 assembled and attached relocatable structures do not bear evidence of approved certification mark or label on structure and is considered unapproved electrical equipment. This structure is missing label/mark from CSA. CSA rep Bill Cook was on site and agreed the structure must be marked or labeled if CSA approved | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png | file://x:/photopub/docs/0000000564/af161320-3e1b-4728-8b40-c7dbde45c7f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-792501-2017 | EL-475430-2016 | 4/19/2017 2:47:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Switches_installed_within_1M_of_a_tub1.png,Switches_installed_within_1M_of_a_tub2.png Switches and receptacles are required to be installed at least 1M from a tub or shower stall. This is required to prevent occupants of the tub or shower from operating or using electrical equipment while in the tub or shower in an effort to protect persons from electrical shock hazards. This installation in a bathroom of a house renovation has light and fan switches that are installed approximately 300mm from a tub. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Switches_installed_within_1M_of_a_tub1.png | file://x:/photopub/docs/0000000588/738b62b2-f4b7-47c0-97b1-8be6d26383cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7a567b4_6c46_4174_b478_43d67e2b46b9
GAIN-772994-2017 | GA-413994-2016 | 3/27/2017 11:00:59 AM | ASSESS: GA: Final | png | #asFound Range without anti trip bracket | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Range_salmon_arm.png At time of inspection anti trip bracket wasn't installed .This condition could cause personnel operating appliance to be injured from appliance tipping forward. | 3 | Appliance not installed according to installation instructions | Range_salmon_arm.png | file://x:/photopub/docs/0000000577/dd854c28-9ea6-4d11-a415-6f4f7d7533fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0176599_a230_4958_94db_b8da4126edd9
ELIN-790072-2017 | EL-519710-2017 | 4/7/2017 1:58:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service1.png,Service2.png,Service3.png,Service4.png Protection or relocation of service conductors required to prevent accidental contact by persons | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service2.png | file://x:/photopub/docs/0000000583/570398f4-4899-4f49-9ea1-76298d2ead93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd4e610_57cb_47e5_993e_4c4ac36cb101
ELIN-790072-2017 | EL-519710-2017 | 4/7/2017 1:58:44 PM | ASSESS: EL: Service Connection | png | #asFound Service conductors ar | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service1.png,Service2.png,Service3.png,Service4.png Protection or relocation of service conductors required to prevent accidental contact by persons | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service1.png | file://x:/photopub/docs/0000000583/ce4b167d-a3ca-4e3e-829e-8eb52f447bcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd4e610_57cb_47e5_993e_4c4ac36cb101
ELIN-790072-2017 | EL-519710-2017 | 4/7/2017 1:58:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service1.png,Service2.png,Service3.png,Service4.png Protection or relocation of service conductors required to prevent accidental contact by persons | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service4.png | file://x:/photopub/docs/0000000583/4cb328a8-57e3-4756-a9b0-79cfd757c05f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd4e610_57cb_47e5_993e_4c4ac36cb101
ELIN-790074-2017 | EL-519710-2017 | 4/7/2017 12:57:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Lockable door/enclosure required for panel to be energized. | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Panel_.png Panel in unsecured dwelling unit is without lockable door/enclosure. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_.png | file://x:/photopub/docs/0000000583/8b34ce6b-8394-4ad6-bfad-dcd4f3a6e8e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f3b5d43_98bb_4360_ab8e_4b6c3dd3f6b5
ELIN-790072-2017 | EL-519710-2017 | 4/7/2017 1:58:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Service1.png,Service2.png,Service3.png,Service4.png Protection or relocation of service conductors required to prevent accidental contact by persons | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service3.png | file://x:/photopub/docs/0000000583/5af9e56a-d58f-4d57-a736-85ecd6b28d79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd4e610_57cb_47e5_993e_4c4ac36cb101
ELIN-764682-2017 | EL-500672-2017 | 3/3/2017 2:34:17 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Unprotected_ans_energized_1.png,Unprotected_ans_energized_2.png Cover plates have not been installed on energized receptacles and switches. This could expose occupants to a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unprotected_ans_energized_2.png | file://x:/photopub/docs/0000000566/d0f4031a-6bda-4b15-9f7d-8260adfe6bdf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d36b5448_98d3_4528_9510_697a816ba46f
ELIN-764682-2017 | EL-500672-2017 | 3/3/2017 2:34:17 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Unprotected_ans_energized_1.png,Unprotected_ans_energized_2.png Cover plates have not been installed on energized receptacles and switches. This could expose occupants to a potential shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Unprotected_ans_energized_1.png | file://x:/photopub/docs/0000000566/d9c655d5-2ccf-48c0-a316-4ad883007999.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d36b5448_98d3_4528_9510_697a816ba46f
GAIN-755502-2017 | GA-446471-2016 | 3/3/2017 1:55:00 PM | ASSESS: GA: Final | png | #asFound Combustion air supply | GA124 | Blocked combustion air supply | 4 | 4 | #Combustion_air_.png At time of inspection combustion air opening was not large enough to provide proper combustion of propane gas to pool boilers, this could cause incomplete or poor combustion. | 4 | Blocked combustion air supply | Combustion_air_.png | file://x:/photopub/docs/0000000566/19f6da42-41de-49b8-8fa0-942dc9b39abf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdd87e44_6e8a_4bdc_ab59_6dafe43d99e0
GAIN-806593-2017 | GA-527433-2017 | 5/3/2017 12:51:56 PM | ASSESS: GA: Final | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #Frayne_2.png Corrugated stainless steel tubing with bond connection missing. Corrugated stainless steel tubing is highly susceptible to electrical fault damage which could lead to an uncontrolled release of gas resulting in a possible fire and or explosion. Fire risk. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Frayne_2.png | file://x:/photopub/docs/0000000595/9a18e70c-4eea-4a2c-ad18-fb1335708360.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c1c701_fc04_44c9_ae35_c20174c65d1e
ELIN-804391-2017 | EL-520247-2017 | 4/26/2017 | ASSESS: EL: Final | png | #asFound Luminaire not bonded as required for approved electrical equipment | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Luminaire_not_bonded_properly1.png,Luminaire_not_bonded_properly2.png,Luminaire_not_bonded_properly3.png Found luminaire support bracket has bonding screw which is not bonded in two locations as required by approved luminaires. When electrical equipment is not bonded back to ground the electrical equipment could become a possible electrical shock hazard to people. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Luminaire_not_bonded_properly1.png | file://x:/photopub/docs/0000000592/0d8386dd-7073-48bf-83d4-ff2bc502ae41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8f6f0f4_7890_492d_a718_d8a5ecd7ddd2
ELIN-804391-2017 | EL-520247-2017 | 4/26/2017 | ASSESS: EL: Final | png | #asFound Luminaire not bonded as required for approved electrical equipment | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Luminaire_not_bonded_properly1.png,Luminaire_not_bonded_properly2.png,Luminaire_not_bonded_properly3.png Found luminaire support bracket has bonding screw which is not bonded in two locations as required by approved luminaires. When electrical equipment is not bonded back to ground the electrical equipment could become a possible electrical shock hazard to people. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Luminaire_not_bonded_properly2.png | file://x:/photopub/docs/0000000592/5b59ae2e-6234-482b-b1c5-7137dd5030ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8f6f0f4_7890_492d_a718_d8a5ecd7ddd2
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound 1 of 9 structures that are approved and certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png | file://x:/photopub/docs/0000000564/9c1439d6-7df0-4f73-9e18-3d1181c17ae6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound 1 of 9 structures that are approved and certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png | file://x:/photopub/docs/0000000564/9412534f-d736-4ef0-8a97-ad693bb772d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound 1 of 9 structures that are approved and certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png | file://x:/photopub/docs/0000000564/9b5f2ea4-b3cc-4d37-bf5c-25be84c1890d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-770288-2017 | EL-497607-2017 | 4/5/2017 1:48:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_circuits_energized_no_arc_fault_breakers_.png In a new multi family dwelling with a 200 amp 240 volt service branch circuits feeding 15 amp and 20 amp receptacles in the dwelling have been energized using standard overcurrent devices rather than Combination Arc Fault interrupter breakers. Additionally the branch circuit wiring was found incomplete and energized. With these conditions both person and property are at risk for an incident involving electrical technology. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_circuits_energized_no_arc_fault_breakers_.png | file://x:/photopub/docs/0000000582/8bbcda3c-fc59-40ed-b8b2-c22757dec95e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c291c92_d76c_43fe_aba8_2b3472b94a2a
ELIN-792177-2017 | EL-518853-2017 | 4/11/2017 10:48:23 AM | ASSESS: EL: Service Connection | png | #asFound Panels are mounted too low and are in danger of mechanical damage due to location in shop. | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 2 | #Panels_1.png,Panels_2.png Panel location. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Panels_1.png | file://x:/photopub/docs/0000000585/89fa0f69-1105-401f-b864-009f27908bb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d880d75_b1cc_41e5_b326_3b2c0b4e4cc3
ELIN-792177-2017 | EL-518853-2017 | 4/11/2017 10:48:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 2 | #Panels_1.png,Panels_2.png Panel location. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Panels_2.png | file://x:/photopub/docs/0000000585/3bf5fb4c-830c-4003-91be-407a8715cff3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d880d75_b1cc_41e5_b326_3b2c0b4e4cc3
ELIN-792891-2017 | EL-331378-2016 | 4/11/2017 11:29:08 AM | ASSESS: EL: Final | png | #asFound Live conductors in box without a cover | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #5.png A outlet box was without a cover leaving the conductors exposed. This is a shock hazard as someone may accidentally come into contact with live conductors. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 5.png | file://x:/photopub/docs/0000000585/73ad8830-b904-4f9e-b5fa-842da20ce0eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d730395c_3c55_4e3b_99aa_a3ab8928cca2
ELIN-790943-2017 | EL-510658-2017 | 4/10/2017 1:49:24 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Non_gfci_receptacle_beside_sink.png Standard type receptacle has been installed within 1.5 meters of a sink. Ground fault circuit protection is required for receptacles located within this measurement. Ground fault protected circuits detect leakage currents associated with electrical equipment coming into contact with water. Ground fault protection would de-energize this situation and protect persons and equipment from shock and fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Non_gfci_receptacle_beside_sink.png | file://x:/photopub/docs/0000000584/37f19ff5-866b-4024-b208-558e2b71579f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e19706c_f4ad_40a6_8b8c_38a0192e3797
ELIN-767838-2017 | EL-467066-2016 | 3/7/2017 1:41:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_in_contact_with_heating_ducts1.png,Wiring_in_contact_with_heating_ducts2.png,Wiring_in_contact_with_heating_ducts3.png,Wiring_in_contact_with_heating_ducts4.png,Wiring_in_contact_with_heating_ducts5.png,Wiring_in_contact_with_heating_ducts6.png Non-metallic sheathed cables are required to be installed 25mm away from metal heating ducts or to have thermal insulation installed between the wring and the ducts when 25mm separation can not be achieved. This is required to prevent mechanical and thermal damage to the cable sheathing and conductor insulation. This installation for 15A 120V wiring installed in the basement of a house has wiring that has been installed in contact with the metal heating ducts in multiple locations. Left uncorrected this is a shock and fire hazard if the cable sheathing and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts3.png | file://x:/photopub/docs/0000000567/b4d7c669-3ee8-47de-b228-936335e14304.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ab129ec_6a78_46b8_b3ea_d79ff2aa25fe
ELIN-767838-2017 | EL-467066-2016 | 3/7/2017 1:41:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_in_contact_with_heating_ducts1.png,Wiring_in_contact_with_heating_ducts2.png,Wiring_in_contact_with_heating_ducts3.png,Wiring_in_contact_with_heating_ducts4.png,Wiring_in_contact_with_heating_ducts5.png,Wiring_in_contact_with_heating_ducts6.png Non-metallic sheathed cables are required to be installed 25mm away from metal heating ducts or to have thermal insulation installed between the wring and the ducts when 25mm separation can not be achieved. This is required to prevent mechanical and thermal damage to the cable sheathing and conductor insulation. This installation for 15A 120V wiring installed in the basement of a house has wiring that has been installed in contact with the metal heating ducts in multiple locations. Left uncorrected this is a shock and fire hazard if the cable sheathing and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts1.png | file://x:/photopub/docs/0000000567/8947b370-5a5a-4d53-9d15-8640415d29e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ab129ec_6a78_46b8_b3ea_d79ff2aa25fe
ELIN-767838-2017 | EL-467066-2016 | 3/7/2017 1:41:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_in_contact_with_heating_ducts1.png,Wiring_in_contact_with_heating_ducts2.png,Wiring_in_contact_with_heating_ducts3.png,Wiring_in_contact_with_heating_ducts4.png,Wiring_in_contact_with_heating_ducts5.png,Wiring_in_contact_with_heating_ducts6.png Non-metallic sheathed cables are required to be installed 25mm away from metal heating ducts or to have thermal insulation installed between the wring and the ducts when 25mm separation can not be achieved. This is required to prevent mechanical and thermal damage to the cable sheathing and conductor insulation. This installation for 15A 120V wiring installed in the basement of a house has wiring that has been installed in contact with the metal heating ducts in multiple locations. Left uncorrected this is a shock and fire hazard if the cable sheathing and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts2.png | file://x:/photopub/docs/0000000567/0c88c346-2248-438d-acb2-fa78adf4fee8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ab129ec_6a78_46b8_b3ea_d79ff2aa25fe
EDIN-806844-2017 | ED-398597-2016 | 5/2/2017 3:42:26 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED048 | Wear or defects that are: Likely to progress Contractor is aware of condition | 2 | 2 | #Hoistway_wiring_hanger_system.png The hoisway wiring hanger system is not installed as required by the elevator contractor engineer. There is a requirement of at least one hanger every 100 feet. It was found that there is only 2 hangers in total for a length of almost 400 feet. This lack of hangers for strain relief poses a risk of the hoistway wiring being stressed under its own weight and breaking. | 2 | Wear or defects that are: Likely to progress Contractor is aware of condition | Hoistway_wiring_hanger_system.png | file://x:/photopub/docs/0000000596/5a334d2a-12d8-4a73-891b-61a90c8a0be9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94a29028_6b1c_45d6_8222_da11ccc2419c
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound Some structures of the 9 assembled and attached relocatable structures do not bear evidence of approved certification mark or label on structure and is considered unapproved electrical equipment. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png | file://x:/photopub/docs/0000000564/5d413993-20b9-40bd-b330-921c0257600a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-762750-2017 | EL-419298-2016 | 3/1/2017 1:39:53 PM | ASSESS: EL: Final | png | #asFound 1 of 9 structures that are approved and certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Some_parts_of_structure_are_certified_while_other_parts_are_not_certified1.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified2.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified3.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified4.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified5.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified6.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified7.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified8.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified9.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified10.png,Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png Found electrical equipment which does not bear evidence of approved certification mark or label on equipment as required. When electrical equipment is n | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Some_parts_of_structure_are_certified_while_other_parts_are_not_certified11.png | file://x:/photopub/docs/0000000564/cc797e56-54ba-4015-87ba-18f8ee8d378a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94aa5ced_438b_458b_abc4_58e2f92a5282
ELIN-792501-2017 | EL-475430-2016 | 4/19/2017 2:47:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Switches_installed_within_1M_of_a_tub1.png,Switches_installed_within_1M_of_a_tub2.png Switches and receptacles are required to be installed at least 1M from a tub or shower stall. This is required to prevent occupants of the tub or shower from operating or using electrical equipment while in the tub or shower in an effort to protect persons from electrical shock hazards. This installation in a bathroom of a house renovation has light and fan switches that are installed approximately 300mm from a tub. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Switches_installed_within_1M_of_a_tub2.png | file://x:/photopub/docs/0000000588/d110466a-4b7e-4003-947c-e7d7b9b3dace.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7a567b4_6c46_4174_b478_43d67e2b46b9
ELIN-790943-2017 | EL-510658-2017 | 4/10/2017 1:49:24 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Non_gfci_receptacle_beside_sink.png Standard type receptacle has been installed within 1.5 meters of a sink. Ground fault circuit protection is required for receptacles located within this measurement. Ground fault protected circuits detect leakage currents associated with electrical equipment coming into contact with water. Ground fault protection would de-energize this situation and protect persons and equipment from shock and fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Non_gfci_receptacle_beside_sink.png | file://x:/photopub/docs/0000000584/d1caa259-9079-4c34-994e-75f283987c1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e19706c_f4ad_40a6_8b8c_38a0192e3797
ELHE-792336-2017 | HE-520955-2017 | 4/10/2017 2:31:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Thermostat i living room controls two baseboard heaters. | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | #Thermostat.png Respond to tenant complaints about baseboard heating in an existing unit of town housing. The existing wall-mounted thermostats are not effectively controlling the baseboard heaters in the living room area. Temperatures of over 30Â° C have been observed within a two minute period on a cold baseboard heater. Possible thermal damage to surrounding combustibles. Fire hazard. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Thermostat.png | file://x:/photopub/docs/0000000584/b4a10b2b-a549-44d7-bdce-355391e5d6b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ae086f4_02da_479b_b573_38c8b720b405
GAHE-792820-2017 | HE-521223-2017 | 4/24/2017 2:05:49 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Bosch tankless water heaters with out vent installed in occupied gathering area. Units Red Tagged. | GA152 | Appliance installed and operating. Venting incomplete (example: venting into living space) | 5 | 4 | #Tankless_water_heaters_.png 1) All gas appliances are required to be connected to an effective vent. 2) Multiple tankless natural draft water heaters installed with out connection to a vent. 3) An appliance installed and operating in an occupied space with out a vent may result in toxic levels of Carbon Monoxide. | 5 | Appliance installed and operating. Venting incomplete (example: venting into living space) | Tankless_water_heaters_.png | file://x:/photopub/docs/0000000590/6131bae1-8c88-4aa9-a022-c457905f478b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f62edcd4_075b_430c_8324_9a03523ab8be
ELIN-767838-2017 | EL-467066-2016 | 3/7/2017 1:41:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_in_contact_with_heating_ducts1.png,Wiring_in_contact_with_heating_ducts2.png,Wiring_in_contact_with_heating_ducts3.png,Wiring_in_contact_with_heating_ducts4.png,Wiring_in_contact_with_heating_ducts5.png,Wiring_in_contact_with_heating_ducts6.png Non-metallic sheathed cables are required to be installed 25mm away from metal heating ducts or to have thermal insulation installed between the wring and the ducts when 25mm separation can not be achieved. This is required to prevent mechanical and thermal damage to the cable sheathing and conductor insulation. This installation for 15A 120V wiring installed in the basement of a house has wiring that has been installed in contact with the metal heating ducts in multiple locations. Left uncorrected this is a shock and fire hazard if the cable sheathing and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts4.png | file://x:/photopub/docs/0000000567/73b34ed4-c2cb-442e-b9ce-977afd62f134.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ab129ec_6a78_46b8_b3ea_d79ff2aa25fe
ELIN-767838-2017 | EL-467066-2016 | 3/7/2017 1:41:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_in_contact_with_heating_ducts1.png,Wiring_in_contact_with_heating_ducts2.png,Wiring_in_contact_with_heating_ducts3.png,Wiring_in_contact_with_heating_ducts4.png,Wiring_in_contact_with_heating_ducts5.png,Wiring_in_contact_with_heating_ducts6.png Non-metallic sheathed cables are required to be installed 25mm away from metal heating ducts or to have thermal insulation installed between the wring and the ducts when 25mm separation can not be achieved. This is required to prevent mechanical and thermal damage to the cable sheathing and conductor insulation. This installation for 15A 120V wiring installed in the basement of a house has wiring that has been installed in contact with the metal heating ducts in multiple locations. Left uncorrected this is a shock and fire hazard if the cable sheathing and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts5.png | file://x:/photopub/docs/0000000567/f1775bb3-32ef-4829-8738-8fbc81e82fc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ab129ec_6a78_46b8_b3ea_d79ff2aa25fe
ELIN-767838-2017 | EL-467066-2016 | 3/7/2017 1:41:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_in_contact_with_heating_ducts1.png,Wiring_in_contact_with_heating_ducts2.png,Wiring_in_contact_with_heating_ducts3.png,Wiring_in_contact_with_heating_ducts4.png,Wiring_in_contact_with_heating_ducts5.png,Wiring_in_contact_with_heating_ducts6.png Non-metallic sheathed cables are required to be installed 25mm away from metal heating ducts or to have thermal insulation installed between the wring and the ducts when 25mm separation can not be achieved. This is required to prevent mechanical and thermal damage to the cable sheathing and conductor insulation. This installation for 15A 120V wiring installed in the basement of a house has wiring that has been installed in contact with the metal heating ducts in multiple locations. Left uncorrected this is a shock and fire hazard if the cable sheathing and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts6.png | file://x:/photopub/docs/0000000567/d55a9115-2edc-4ed9-bb1e-ec2a6f64d7ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ab129ec_6a78_46b8_b3ea_d79ff2aa25fe
GAIN-789976-2017 | GA-265398-2015 | 4/6/2017 8:51:54 AM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #1.png Observed a uncapped active gas line installed directly below Navien boiler in mechanical room. Jarring or bumping of the gas valve would release natural gas into the mechanical room with a source of ignition only feet away creating a serious fire and injury hazard. More pictures in attachments. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 1.png | file://x:/photopub/docs/0000000582/fc1b230a-8fdb-49c3-86ea-3a8dca5f2b24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c0d9bf2_06a0_4250_8da1_32f5fcc39bdf
GAIN-798651-2017 | GA-509909-2017 | 5/1/2017 7:35:58 AM | ASSESS: GA: Final | png | #asFound | GA139 | Incorrect appliance type installed for application | 3 | 3 | #REB_BLUE_2.png Unapproved furnace for application. No approved base where furnace outlet meets combustible floor. Possible fire risk due to lack of separation from heating surface to combustible material. | 3 | Incorrect appliance type installed for application | REB_BLUE_2.png | file://x:/photopub/docs/0000000594/afe3f558-915b-4e8e-9844-c059eb328882.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20345685_1e19_4275_a716_4f9c53cfbddc
ELIN-789571-2017 | EL-518554-2017 | 5/9/2017 5:52:23 AM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #70amp_breaker.png In an existing modular home, A 60amp 120/240volt sub-feed cable was found with a 70amp breaker in place for over-current protection. This can lead to a "Thermal Effect" condition. Pic attached. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 70amp_breaker.png | file://x:/photopub/docs/0000000598/18d512b3-025f-4b8d-9e03-5e753d585b3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09d25f00_678d_44f2_af98_3c12ff90464c
ELIN-769056-2017 | UW-507782-2017 | 3/7/2017 1:28:41 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #P41.png,P42.png Reduction or elimination of working clearance creates hazards for maintenance and repair Electrical personnel. | 1 | General Working space or dedicated space is being used for storage | P42.png | file://x:/photopub/docs/0000000568/bc7476d4-9b54-40a8-950b-341c35220a91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8163edaa_bd14_4568_b6b1_8d51b625574b
ELIN-769056-2017 | UW-507782-2017 | 3/7/2017 1:28:41 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Electrical room is being used as storage space. | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #P41.png,P42.png Reduction or elimination of working clearance creates hazards for maintenance and repair Electrical personnel. | 1 | General Working space or dedicated space is being used for storage | P41.png | file://x:/photopub/docs/0000000568/e344db43-011e-437e-8f0d-9048245b4fa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8163edaa_bd14_4568_b6b1_8d51b625574b
GAHE-778777-2017 | HE-513634-2017 | 3/21/2017 8:36:38 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA138 | Equipment unserviceable due to lack of clearance. | 3 | 3 | #Boiler.png Insufficient clearance for servicing of boiler. Boiler seems to never have had a proper servicing due to lack of work space around boiler. Jammed between hot water tank and drywall. CO was present in house and could have led to a fatality. | 3 | Equipment unserviceable due to lack of clearance. | Boiler.png | file://x:/photopub/docs/0000000574/e39bc118-4d7a-464d-9094-4ef069ce840f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e7eaee4_6ff0_4398_abb8_c0ab1386759e
ELIN-794264-2017 | EL-519636-2017 | 4/12/2017 12:27:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_and_bondin__grounding_and_bonding1.png,Grounding_and_bondin__grounding_and_bonding2.png,Grounding_and_bondin__grounding_and_bonding3.png The grounding and bonding for a service supply connection is not correct. The possibility is that equal potential will not be established in the event of fault current on the system or service. This creates the high possibility for shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_and_bondin__grounding_and_bonding2.png | file://x:/photopub/docs/0000000586/11764e05-184c-437c-9583-407a5ac930fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6990e594_ba04_45b0_8e6a_f5bae6f63333
ELIN-794264-2017 | EL-519636-2017 | 4/12/2017 12:27:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_and_bondin__grounding_and_bonding1.png,Grounding_and_bondin__grounding_and_bonding2.png,Grounding_and_bondin__grounding_and_bonding3.png The grounding and bonding for a service supply connection is not correct. The possibility is that equal potential will not be established in the event of fault current on the system or service. This creates the high possibility for shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_and_bondin__grounding_and_bonding1.png | file://x:/photopub/docs/0000000586/0feddfcf-7753-46a1-84ba-a07d0cc1e5c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6990e594_ba04_45b0_8e6a_f5bae6f63333
ELIN-794264-2017 | EL-519636-2017 | 4/12/2017 12:27:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_and_bondin__grounding_and_bonding1.png,Grounding_and_bondin__grounding_and_bonding2.png,Grounding_and_bondin__grounding_and_bonding3.png The grounding and bonding for a service supply connection is not correct. The possibility is that equal potential will not be established in the event of fault current on the system or service. This creates the high possibility for shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_and_bondin__grounding_and_bonding3.png | file://x:/photopub/docs/0000000586/64d5fa0a-39bd-479f-a0be-076852c0c281.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6990e594_ba04_45b0_8e6a_f5bae6f63333
EDIN-771499-2017 | ED-427056-2016 | 3/8/2017 6:28:42 PM | ASSESS: ED IN: Acceptance | png | #asFound elevator lobby without fire alarm initiating device | ED031 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | 4 | 4 | #Elevator_Lobby.png If there was a fire located at the elevator lobby there will not be any indication to the occupants of the elevator which could result in the elevator bringing passengers to the fire. | 4 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | Elevator_Lobby.png | file://x:/photopub/docs/0000000568/74ee6f00-203d-4e55-80c6-a98a35ce206d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e246c68_3dad_4d80_8974_774378df57f1
ELIN-810760-2017 | EL-523390-2017 | 5/8/2017 11:13:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_unsafe1.png,Exposed_energized_conductors_unsafe2.png,Exposed_energized_conductors_unsafe3.png,Exposed_conductors_connected_to_power_supply_system1.png,Exposed_conductors_connected_to_power_supply_system2.png,Exposed_conductors_connected_to_power_supply_system3.png Found exposed branch circuit conductors and bus bars and other electrical equipment while feeders and branch circuit conductors are connected to energized power supply system. When electrical equipment is not fully covered or is not fully completed and conductors are connected to energized power supply system, the exposed conductors are a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors_connected_to_power_supply_system2.png | file://x:/photopub/docs/0000000597/3499f2d2-7dd3-44da-90d0-4a92d8840ce1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627767a_36c8_4559_a2ab_5f8699fef503
ELIN-810760-2017 | EL-523390-2017 | 5/8/2017 11:13:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_unsafe1.png,Exposed_energized_conductors_unsafe2.png,Exposed_energized_conductors_unsafe3.png,Exposed_conductors_connected_to_power_supply_system1.png,Exposed_conductors_connected_to_power_supply_system2.png,Exposed_conductors_connected_to_power_supply_system3.png Found exposed branch circuit conductors and bus bars and other electrical equipment while feeders and branch circuit conductors are connected to energized power supply system. When electrical equipment is not fully covered or is not fully completed and conductors are connected to energized power supply system, the exposed conductors are a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors_connected_to_power_supply_system1.png | file://x:/photopub/docs/0000000597/2f25cd31-e32c-4b0d-a9af-329f9b14bf7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627767a_36c8_4559_a2ab_5f8699fef503
ELIN-810760-2017 | EL-523390-2017 | 5/8/2017 11:13:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_unsafe1.png,Exposed_energized_conductors_unsafe2.png,Exposed_energized_conductors_unsafe3.png,Exposed_conductors_connected_to_power_supply_system1.png,Exposed_conductors_connected_to_power_supply_system2.png,Exposed_conductors_connected_to_power_supply_system3.png Found exposed branch circuit conductors and bus bars and other electrical equipment while feeders and branch circuit conductors are connected to energized power supply system. When electrical equipment is not fully covered or is not fully completed and conductors are connected to energized power supply system, the exposed conductors are a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_unsafe2.png | file://x:/photopub/docs/0000000597/3232442a-24e8-455f-ab6f-4d43c45f6ee8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627767a_36c8_4559_a2ab_5f8699fef503
ELIN-810760-2017 | EL-523390-2017 | 5/8/2017 11:13:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_unsafe1.png,Exposed_energized_conductors_unsafe2.png,Exposed_energized_conductors_unsafe3.png,Exposed_conductors_connected_to_power_supply_system1.png,Exposed_conductors_connected_to_power_supply_system2.png,Exposed_conductors_connected_to_power_supply_system3.png Found exposed branch circuit conductors and bus bars and other electrical equipment while feeders and branch circuit conductors are connected to energized power supply system. When electrical equipment is not fully covered or is not fully completed and conductors are connected to energized power supply system, the exposed conductors are a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_unsafe1.png | file://x:/photopub/docs/0000000597/67a786b0-df52-435f-81cb-97510ab025a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627767a_36c8_4559_a2ab_5f8699fef503
ELIN-810760-2017 | EL-523390-2017 | 5/8/2017 11:13:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_unsafe1.png,Exposed_energized_conductors_unsafe2.png,Exposed_energized_conductors_unsafe3.png,Exposed_conductors_connected_to_power_supply_system1.png,Exposed_conductors_connected_to_power_supply_system2.png,Exposed_conductors_connected_to_power_supply_system3.png Found exposed branch circuit conductors and bus bars and other electrical equipment while feeders and branch circuit conductors are connected to energized power supply system. When electrical equipment is not fully covered or is not fully completed and conductors are connected to energized power supply system, the exposed conductors are a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors_connected_to_power_supply_system3.png | file://x:/photopub/docs/0000000597/6306638a-9287-42fd-b4c5-39c6f371efe9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627767a_36c8_4559_a2ab_5f8699fef503
ELIN-810760-2017 | EL-523390-2017 | 5/8/2017 11:13:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_unsafe1.png,Exposed_energized_conductors_unsafe2.png,Exposed_energized_conductors_unsafe3.png,Exposed_conductors_connected_to_power_supply_system1.png,Exposed_conductors_connected_to_power_supply_system2.png,Exposed_conductors_connected_to_power_supply_system3.png Found exposed branch circuit conductors and bus bars and other electrical equipment while feeders and branch circuit conductors are connected to energized power supply system. When electrical equipment is not fully covered or is not fully completed and conductors are connected to energized power supply system, the exposed conductors are a possible electrical fire or shock hazard to people and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_unsafe3.png | file://x:/photopub/docs/0000000597/67428c1b-5f07-4e5d-be91-1601018019f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627767a_36c8_4559_a2ab_5f8699fef503
BPVOP-809355-2017 | 5047790 | 5/4/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_HE110.png Upon the assessment of a plate Heat Exchanger with MAWP of 125 psig, was found that the Safety Relief Valve was installed in 2011 and was overdue as per CSA B51. This can contribute to the failure of the pressure vessel in case of overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_HE110.png | file://x:/photopub/docs/0000000597/69fbb2e3-ff15-4d16-9018-aba22c5347e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a327f03_d31c_4860_91ad_ef7be43fba70
ELIN-793675-2017 | UW-521807-2017 | 4/11/2017 3:05:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #P41.png,P42.png,P43.png,P44.png Shock and fire hazards with potential to cause serious injury or death. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | P42.png | file://x:/photopub/docs/0000000585/addf40b3-6d4e-4595-81ce-654b3cc4ba6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff25f14b_9147_4824_a983_4054da5f4391
ELIN-793675-2017 | UW-521807-2017 | 4/11/2017 3:05:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound L.E.D. Lamp manufacturer's warning label prohibits energizing these lamp with 347 volts without a ballast but lamp are directly energized with 347 Volts. New electrical characteristics label is not placed on the fixture. Only original label is present. Burn marks are shown on the lamp pins and black marks on the fixture from ark. This alteration was done without a permit. | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #P41.png,P42.png,P43.png,P44.png Shock and fire hazards with potential to cause serious injury or death. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | P41.png | file://x:/photopub/docs/0000000585/af0355b3-47dd-4d54-8a3d-e9a9abee7e4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff25f14b_9147_4824_a983_4054da5f4391
BPVOP-803284-2017 | 2263966 | 4/26/2017 9:33:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Non 200 psi steam working pressure valves for bottom blow off | BP009 | 1.0.1 Temp/Pressure ratings not met - Operating pressures above Maximum Allowable Working Pressure | 3 | 3 | #Valves_bottom_blow_off.png Review of existing boiler isolation valves for both the bottom blow off and feed water do not have the temperature or pressure service ratings for this high pressure steam boiler for application and use. Valves operated above their expected temperature and pressure ratings may fail when used and cause significant equipment damage or injury to personnel in close proximity. | 3 | 1.0.1 Temp/Pressure ratings not met - Operating pressures above Maximum Allowable Working Pressure | Valves_bottom_blow_off.png | file://x:/photopub/docs/0000000591/190eda92-a968-4e81-bbac-c24a723889c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47f6fd41_b63d_4eb7_9388_c488243328df
GAIN-801319-2017 | GA-507346-2017 | 4/27/2017 3:09:16 PM | ASSESS: GA: Final | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | #Approved_flex_undersized1.png,Approved_flex_undersized2.png Gas appliances are sometimes connected by means of an approved gas flex connector that must be made to a certain standard and have the correct load rating, in this instance the gas connector load rating was undersized to match the load of the appliance. This could potentially cause a under firing of the appliance and or improper operation. | 3 | Undersized hose or appliance connector | Approved_flex_undersized1.png | file://x:/photopub/docs/0000000592/002e9901-1e78-4364-a043-d1819aba2d1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00a865d0_9f2b_4d27_8a95_4638c5c49d66
GAIN-801319-2017 | GA-507346-2017 | 4/27/2017 3:09:16 PM | ASSESS: GA: Final | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | #Approved_flex_undersized1.png,Approved_flex_undersized2.png Gas appliances are sometimes connected by means of an approved gas flex connector that must be made to a certain standard and have the correct load rating, in this instance the gas connector load rating was undersized to match the load of the appliance. This could potentially cause a under firing of the appliance and or improper operation. | 3 | Undersized hose or appliance connector | Approved_flex_undersized2.png | file://x:/photopub/docs/0000000592/efdd617b-c57c-49bf-883f-7fb0495663e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00a865d0_9f2b_4d27_8a95_4638c5c49d66
ELIN-780190-2017 | EL-509790-2017 | 3/23/2017 1:01:42 PM | ASSESS: EL: Final | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | #Bathroom_receptacl__bathroom_receptacle.png Receptacle within 1.5 m of bathroom sink is not bonded to ground and not GFI protected. Possibility for shock. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Bathroom_receptacl__bathroom_receptacle.png | file://x:/photopub/docs/0000000575/bf7cced1-5756-4e48-9a88-2192c8f33d5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c46a792_7223_4f3e_9b9d_44c1efb28e7d
ELIN-767135-2017 | EL-506667-2017 | 4/18/2017 4:00:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members1.png,Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members2.png,Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members3.png Cables are required to be installed 32mm from the face of the structural members that they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation at a new house under construction had a 3c#250 ACWU service cable installed under a concrete slab from the meter base to the service panel. The service cable passed through the wall plates at each end closer than 32mm from the face of the wall plates to the service cable. This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members1.png | file://x:/photopub/docs/0000000587/d25d2aad-77dc-4518-9764-e7711702d7a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2510402_e39a_4afe_aca5_df51635a9fd1
ELIN-767135-2017 | EL-506667-2017 | 4/18/2017 4:00:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members1.png,Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members2.png,Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members3.png Cables are required to be installed 32mm from the face of the structural members that they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation at a new house under construction had a 3c#250 ACWU service cable installed under a concrete slab from the meter base to the service panel. The service cable passed through the wall plates at each end closer than 32mm from the face of the wall plates to the service cable. This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members3.png | file://x:/photopub/docs/0000000587/b350355d-c707-4504-a805-5babe3576569.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2510402_e39a_4afe_aca5_df51635a9fd1
ELIN-767135-2017 | EL-506667-2017 | 4/18/2017 4:00:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members1.png,Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members2.png,Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members3.png Cables are required to be installed 32mm from the face of the structural members that they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation at a new house under construction had a 3c#250 ACWU service cable installed under a concrete slab from the meter base to the service panel. The service cable passed through the wall plates at each end closer than 32mm from the face of the wall plates to the service cable. This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_passes_through_wall_plates_closer_then_32mm_from_face_of_structural_members2.png | file://x:/photopub/docs/0000000587/1bf530c0-cc98-435d-b761-ee7fbffc75b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2510402_e39a_4afe_aca5_df51635a9fd1
BPVIN-762712-2017 | BPV-500086-2017 | 3/3/2017 1:45:05 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound Boiler shutdown switches are mounted on boiler rather than remote for easy access during an emergency | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_shut_down_switch.png No remote boiler emergency shutdown switch provided. Lack of emergency shut down provision may have boiler to run longer in an unsafe condition. Lack of remote shutdown switch will have operators using the boiler mounted shut down switches in emergency which maybe unsafe for the operator due to fire or steam leakage. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_shut_down_switch.png | file://x:/photopub/docs/0000000567/c7a2eb3e-14bc-47b1-8d54-03c02572e55a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f043dba_0daf_47b7_b79e_e71daba1c92d
ELIN-793675-2017 | UW-521807-2017 | 4/11/2017 3:05:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #P41.png,P42.png,P43.png,P44.png Shock and fire hazards with potential to cause serious injury or death. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | P44.png | file://x:/photopub/docs/0000000585/3fc9452c-937c-42d2-be13-04f86035c14d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff25f14b_9147_4824_a983_4054da5f4391
ELIN-793675-2017 | UW-521807-2017 | 4/11/2017 3:05:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #P41.png,P42.png,P43.png,P44.png Shock and fire hazards with potential to cause serious injury or death. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | P43.png | file://x:/photopub/docs/0000000585/184a2000-04d5-42cb-87dc-131f553477ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff25f14b_9147_4824_a983_4054da5f4391
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A7.png | file://x:/photopub/docs/0000000591/affa0583-1e2d-41dc-a974-817b9bb5346a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
AMOP-781836-2017 | 2046680 | 3/24/2017 2:25:13 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Missing_nut_on_connecting_rod_bolt.png Missing nut on the bolt used in the connecting rod between train cars. Bolt could work its way out and drop, could cause an abrupt stop of train car. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Missing_nut_on_connecting_rod_bolt.png | file://x:/photopub/docs/0000000576/2178a0ef-e5ff-409a-b9a8-2bcc0cd463ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2532bce0_6955_405f_ad8c_7270ff2dc214
ELIN-809035-2017 | EL-523590-2017 | 5/3/2017 6:37:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #4_0_ACWU_for_service1.png,4_0_ACWU_for_service2.png,4_0_ACWU_for_service3.png,4_0_ACWU_for_service4.png Conductors are required to be sized to carry the maximum ampacity of the load. Correctly sized conductors prevents overheating and the breakdown of the conductor insulation under maximum load. During an assessment for an new 200 amp, 120/240V, single phase electrical service for a commercial building, the safety office found 4/0 aluminum conductors installed for the service conductors. 4/0 aluminum conductors are rated for 180 amps at a 75 deg. C temperature termination rating. Maximum loading of the 200 amp electrical service could break down the insulation of the 4/0 Al conductor which could lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4_0_ACWU_for_service4.png | file://x:/photopub/docs/0000000596/6da83abd-388f-4760-aa35-398ff31f39bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96612b41_ca4d_4c3f_a70d_fa9da11ad6b1
ELIN-807188-2017 | EL-404194-2016 | 5/3/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_Arc-fault_protection.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, a new 15 amp circuits for a receptacle in a laundry area of the lower floor was installed without arc-fault protection. If a series or parallel arc was to occur in the branch circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_Arc-fault_protection.png | file://x:/photopub/docs/0000000596/76e9dcc1-288a-43dd-8385-46e9420829ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9aa483a_213c_4f4d_a7eb_42cdcb7df841
ELIN-809035-2017 | EL-523590-2017 | 5/3/2017 6:37:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #4_0_ACWU_for_service1.png,4_0_ACWU_for_service2.png,4_0_ACWU_for_service3.png,4_0_ACWU_for_service4.png Conductors are required to be sized to carry the maximum ampacity of the load. Correctly sized conductors prevents overheating and the breakdown of the conductor insulation under maximum load. During an assessment for an new 200 amp, 120/240V, single phase electrical service for a commercial building, the safety office found 4/0 aluminum conductors installed for the service conductors. 4/0 aluminum conductors are rated for 180 amps at a 75 deg. C temperature termination rating. Maximum loading of the 200 amp electrical service could break down the insulation of the 4/0 Al conductor which could lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4_0_ACWU_for_service1.png | file://x:/photopub/docs/0000000596/f082ece8-4b46-47a7-acea-7a1708cd3d21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96612b41_ca4d_4c3f_a70d_fa9da11ad6b1
ELIN-809035-2017 | EL-523590-2017 | 5/3/2017 6:37:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #4_0_ACWU_for_service1.png,4_0_ACWU_for_service2.png,4_0_ACWU_for_service3.png,4_0_ACWU_for_service4.png Conductors are required to be sized to carry the maximum ampacity of the load. Correctly sized conductors prevents overheating and the breakdown of the conductor insulation under maximum load. During an assessment for an new 200 amp, 120/240V, single phase electrical service for a commercial building, the safety office found 4/0 aluminum conductors installed for the service conductors. 4/0 aluminum conductors are rated for 180 amps at a 75 deg. C temperature termination rating. Maximum loading of the 200 amp electrical service could break down the insulation of the 4/0 Al conductor which could lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4_0_ACWU_for_service3.png | file://x:/photopub/docs/0000000596/13efce25-9532-4a06-9745-e653d71c20a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96612b41_ca4d_4c3f_a70d_fa9da11ad6b1
ELIN-809035-2017 | EL-523590-2017 | 5/3/2017 6:37:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #4_0_ACWU_for_service1.png,4_0_ACWU_for_service2.png,4_0_ACWU_for_service3.png,4_0_ACWU_for_service4.png Conductors are required to be sized to carry the maximum ampacity of the load. Correctly sized conductors prevents overheating and the breakdown of the conductor insulation under maximum load. During an assessment for an new 200 amp, 120/240V, single phase electrical service for a commercial building, the safety office found 4/0 aluminum conductors installed for the service conductors. 4/0 aluminum conductors are rated for 180 amps at a 75 deg. C temperature termination rating. Maximum loading of the 200 amp electrical service could break down the insulation of the 4/0 Al conductor which could lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4_0_ACWU_for_service2.png | file://x:/photopub/docs/0000000596/90398de9-14b1-4f36-9a49-50c0e21e7b5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96612b41_ca4d_4c3f_a70d_fa9da11ad6b1
BPVIN-669295-2016 | BPV-420954-2016 | 3/10/2017 2:50:27 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Lockable_switch.png Hot water boiler, maximum allowable working pressure 75 PSI. A lockable disconnect is not present at each boiler. The inability to shut down the boiler and lock out the power source at the boiler may result in unintentional operation and personal injury during maintenance. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Lockable_switch.png | file://x:/photopub/docs/0000000570/adc56368-18b1-4c2f-99d7-a2c599ceeb16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bbc7d02_9471_468a_95c1_9d59af8a2377
ELIN-791412-2017 | EL-520465-2017 | 4/11/2017 10:59:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 3 | #Service_Pole.png A new 200 amp 120/240 volt overhead pole service has been installed on a wood pole that as no approval markings. This poses a hazard to persons and the Equipment as the depth and integrity of the pole can not be verified, this could result in a failure of the pole over time. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Service_Pole.png | file://x:/photopub/docs/0000000585/24dce520-6d6f-4af1-a74e-1388a6cdc437.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6abea988_cdec_44e9_8507_ec930032b03e
GAWP-777288-2017 | GA-423401-2016 | 3/17/2017 2:11:30 PM | ASSESS: GA Work In Progress | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | #Venting.png Venting for boiler running though the furnace return air duct. If ever there was a failure of the venting, flue gases would recirculate through the furnace and get distributed through the living space. | 3 | Power vent not installed according to installation instruction. | Venting.png | file://x:/photopub/docs/0000000573/cb1687aa-5b27-4af8-8171-dd3d6bd44f1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52c90246_e4bb_49ae_bdc1_80c22a01dff4
ELIN-791565-2017 | EL-508053-2017 | 4/11/2017 12:54:17 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Detached_shed1.png,Detached_shed2.png,Detached_shed3.png,Detached_shed4.png The 15 amp 120 volt wiring to the detached shed uses wiring methods not approved that include NMSC in wet locations, male cord connector attached to teck cable, this method is both a shock and thermal hazard | 3 | Conductors Equipment is not approved for the specific use. | Detached_shed3.png | file://x:/photopub/docs/0000000585/f675b89e-2293-436f-a113-0fced10ddb73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0a05628_028d_459a_9c7f_568e2e6199d1
ELIN-791565-2017 | EL-508053-2017 | 4/11/2017 12:54:17 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Detached_shed1.png,Detached_shed2.png,Detached_shed3.png,Detached_shed4.png The 15 amp 120 volt wiring to the detached shed uses wiring methods not approved that include NMSC in wet locations, male cord connector attached to teck cable, this method is both a shock and thermal hazard | 3 | Conductors Equipment is not approved for the specific use. | Detached_shed2.png | file://x:/photopub/docs/0000000585/0f08fe23-078a-4921-92c0-e0d68d731aeb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0a05628_028d_459a_9c7f_568e2e6199d1
ELIN-791565-2017 | EL-508053-2017 | 4/11/2017 12:54:17 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Detached_shed1.png,Detached_shed2.png,Detached_shed3.png,Detached_shed4.png The 15 amp 120 volt wiring to the detached shed uses wiring methods not approved that include NMSC in wet locations, male cord connector attached to teck cable, this method is both a shock and thermal hazard | 3 | Conductors Equipment is not approved for the specific use. | Detached_shed4.png | file://x:/photopub/docs/0000000585/ef2bdbf0-f4c2-4fa8-a29a-b64d364b0d7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0a05628_028d_459a_9c7f_568e2e6199d1
ELIN-772330-2017 | EL-493647-2017 | 3/13/2017 11:45:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Not_weatherpr__not_weatherproof_and_not_accessible1.png,Not_weatherpr__not_weatherproof_and_not_accessible2.png This assessment found a new residential service installed without adequate protection from the weather. The equipment was at a height making it inaccessible. There is the potential for the panel to be exposed to the elements, presenting a shock hazard if the main breaker didn't operate properly because it had become wet. The height of the equipment also presents a shock hazard as anyone working on the equipment would be doing so off of a ladder. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Not_weatherpr__not_weatherproof_and_not_accessible2.png | file://x:/photopub/docs/0000000570/cd48379b-f164-4d52-9805-f2ea454dfe33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2fa4bb_e770_4291_a957_d60d8543f67e
ELIN-772330-2017 | EL-493647-2017 | 3/13/2017 11:45:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Not_weatherpr__not_weatherproof_and_not_accessible1.png,Not_weatherpr__not_weatherproof_and_not_accessible2.png This assessment found a new residential service installed without adequate protection from the weather. The equipment was at a height making it inaccessible. There is the potential for the panel to be exposed to the elements, presenting a shock hazard if the main breaker didn't operate properly because it had become wet. The height of the equipment also presents a shock hazard as anyone working on the equipment would be doing so off of a ladder. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Not_weatherpr__not_weatherproof_and_not_accessible1.png | file://x:/photopub/docs/0000000570/949e403d-0cd6-4716-b0ea-c6dcd7a17e45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2fa4bb_e770_4291_a957_d60d8543f67e
BPVOP-782097-2017 | 3828562 | 3/24/2017 11:24:28 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances_.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances_.png | file://x:/photopub/docs/0000000576/94a40907-a3b9-46d7-bbbb-2656e54a23c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1bf35c5_6f95_4b54_9563_ec275843c3f9
ELIN-778376-2017 | EL-454586-2016 | 3/21/2017 3:43:28 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL294 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_live_parts.png Panel covers were missing on panels in multiple units. Panels were energized with live bus bars exposed to accidental contact. Construction site was active with multiple trades working that would not understand the full safety/shock risk | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_live_parts.png | file://x:/photopub/docs/0000000574/4fb25db4-c764-4884-971a-32e8a6b071d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__090b513c_e270_4375_a05f_e2f1e70f8add
ELIN-779389-2017 | EL-504709-2017 | 3/22/2017 12:51:09 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Size of staples used for support of NMD90 cables is not approved for the use as installed. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples1.png,Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples2.png,Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples3.png Size of staples used for support of non-metallic sheathed NMD90 cables is not approved for the use as installed. When electrical equipment is not approved for the use as installed and is not used as specified by manufacturer's installation instructions and specifications, the electrical equipment could get damaged and cause a possible electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples3.png | file://x:/photopub/docs/0000000576/20338405-ebdd-471b-9d6b-8dea4fb31fca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d93fc8e1_1045_465f_bf2a_3d91dddda7d4
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 1000W_HPS_fixture.png | file://x:/photopub/docs/0000000577/fd22d26d-13aa-47ab-af79-b771e7aaee28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Capacitor_.png | file://x:/photopub/docs/0000000577/8839ae4c-ea4f-4436-9b3f-b8ec8e6bd0db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Capacitor_.png | file://x:/photopub/docs/0000000577/e247b61c-a29f-4ee2-a383-5f8261f506bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Burnt_wall.png | file://x:/photopub/docs/0000000577/60d1d619-f162-4224-ba24-fe8c45641711.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Burnt_wall.png | file://x:/photopub/docs/0000000577/7e6ecb0d-0711-4b65-9fd8-32c0dbdf483c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Ballasts.png | file://x:/photopub/docs/0000000577/4adaa345-0b23-49d8-a167-5dce70ec4b46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Ballasts.png | file://x:/photopub/docs/0000000577/4a614301-229c-4f96-8bea-0729873dc304.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
ELHE-781139-2017 | HE-515152-2017 | 3/22/2017 6:38:37 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #1000W_HPS_fixture.png,Ballasts.png,Capacitor_.png,Burnt_wall.png Reactors, capacitors and other auxiliary equipment for electric-discharge lighting systems are to be enclosed within the luminaire or a metal cabinet. This requirement is so the thermal energy from a fault in the auxiliary equipment will be contained within the fixture or cabinet. At a fire investigation for a horticultural operation inside a steel shipping container at a commercial unit, the safety officer found site built, non approved 1000 watt high pressure sodium light fixtures. The ballasts for the light fixtures were mounted inside open junction boxes and the capacitors were hung by wire outside the junction boxes. When one of the capacitors failed, sparks from the capacitor dropped to the floor and ignited combustible materials. The combustible material ignited the wood on the wall of the shipping container and created large amounts of smoke. This created a fire and smoke hazard to persons within this commercial unit and the other uni | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 1000W_HPS_fixture.png | file://x:/photopub/docs/0000000577/7495f665-930f-4371-9ad1-f6378256d769.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce612588_3aa7_4422_b12b_9e68ebfa21cb
BPVIN-791726-2017 | UW-520752-2017 | 4/7/2017 4:13:16 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV.png Upon the assessment of a Potable Hot Water Heater with MAWP of 160 psig, was found that the Safety Relief Valve was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV.png | file://x:/photopub/docs/0000000583/c574072a-25ad-4896-8dfa-e58aafe58672.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__669656b5_1c96_477c_87d7_b67ef3e45607
BPVOP-791697-2017 | 4149140 | 4/7/2017 3:28:06 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Safety_Relief_Valve.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2007 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 0 | No Created Hazard Identified | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000583/5294fd56-84d6-43d9-ba15-0c2b8272e7d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88a10a7e_8fc6_4643_8c9b_66435bb55703
ELIN-766709-2017 | EL-504901-2017 | 3/3/2017 7:58:29 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Range_not_130mm_off_floor.png This assessment found that the Range box is mounted to high. When the range is pushed back to the wall, damage can occur to the cord, causing a potential shock and fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Range_not_130mm_off_floor.png | file://x:/photopub/docs/0000000565/49ff9b75-bd9e-4fef-8551-4dd22e85e9b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7271b00d_0ea4_48ad_97ab_be923761bafb
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator10.png | file://x:/photopub/docs/0000000575/aa844f22-0821-46e9-ba00-e9f025219ecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELIN-760634-2017 | EL-500704-2017 | 2/24/2017 11:15:39 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Incomplete_installation_.png Outside light fixtures were not installed and wiring to fixtures was installed. This condition could lead to a potential shock or fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Incomplete_installation_.png | file://x:/photopub/docs/0000000562/d3abaa11-e605-42b3-aff1-767ec13484e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d5aa2db_94b5_4641_97be_9d5334313e1d
BPVOP-764259-2017 | 2267695 | 2/27/2017 9:55:18 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 | #scale.png | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | scale.png | file://x:/photopub/docs/0000000563/06b5a747-07fc-4f3c-a38b-9286dd39e210.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4d3f999_fc5a_4dc4_8044_b810bc60ce00
ELIN-792348-2017 | UW-520962-2017 | 4/7/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Receptacle_no_cover.png Receptacle was installed and energized at front of new mobile home. Receptacle was installed at a height of approximately 24" leaving a large opening that a child's fingers could fit and come contact with energized portion of wiring. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Receptacle_no_cover.png | file://x:/photopub/docs/0000000585/08ef80b5-cb99-48f4-bf88-010145c4ab3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07e333ec_c032_4353_9781_ff5558efd2c0
GAUP-766311-2017 | UW-506301-2017 | 3/1/2017 11:34:04 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Fireplace.png Combustible materials installed to close to fireplace. Combustible material must be installed above metal tabs installed on top of the fireplace for clearance. Potential for fire if combustible materials were to ignite. | 3 | Clearance to combustible not met | Fireplace.png | file://x:/photopub/docs/0000000564/9707c54c-745b-4f75-8ad2-0545a0ede8c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d4186c9_969e_46d9_b3f0_24b1f4aa3c91
ELHE-806262-2017 | HE-528368-2017 | 5/4/2017 4:26:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Lead_acid_batteries_not_vented.png Lead acid batteries are stored in an area that is not sealed and vented from the rest of the house. Accidental contact could occur resulting in shock injury. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Lead_acid_batteries_not_vented.png | file://x:/photopub/docs/0000000596/d1d951ed-0819-4d24-ada1-0af624225f1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5f0e36b_0239_4e67_8ddd_50a7f3ded5b8
ELIN-764949-2017 | EL-504618-2017 | 2/28/2017 2:16:16 PM | ASSESS: EL: Service Connection | png | #asFound Thin wall conduit type DB2 and fitting is unprotected through foundation wall. Approximately 300mm exposed plus the DB2 fitting. | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Thin_wall.png Service connection and rough wire of new single family dwelling. The conduit that contains the unfused service conductors from BC Hydro is a thin wall conduit for underground use that has been installed above grade inside the garage wall. It is subject to mechanical damage because it has not been provided with concrete for mechanical protection. Damage to this thinwall conduit could expose the service conductors to damage. It would then be a shock and fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Thin_wall.png | file://x:/photopub/docs/0000000563/d9278404-344a-4692-853c-e968f6281801.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bfc3e4f_d58a_48a1_8d15_ac279e0ddb91
BPVOP-758947-2017 | 2253822 | 2/24/2017 9:57:03 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | #corrosion.png | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | corrosion.png | file://x:/photopub/docs/0000000562/61a7bc1d-ad47-42c9-93ac-ec2c92147a80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7257062f_46c4_484f_b47c_df89ab79e23e
EDIN-787310-2017 | ED-478612-2016 | 3/31/2017 9:32:07 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Missing_cotter_pin.png The Pin that secures the governor rope to the governor activating rod eyelet is used to ensure that governor rope is mechanically fastened to the governor rod. During the acceptance assessment it was found that a cotter used to secure the Pin from falling out was not installed. Without the cotter pin installed it is likely that the Pin will work itself free. This will occur over time when the elevator is in operation from the movement and vibration of the governor rope. Losing the Pin will cause the governor rope to fall and cause damage to the elevator and to safety components in the hoistway. In addition, if the elevator mechanical safeties needed to be engaged, without the governor rope in place, the elevator mechanical safety would not engage. The loss of the governor may cause damage and possibly injury to the occupants if ever the safeties needed to be engaged in an emergency. This 13 stop traction elevator is newly installed in a residential building. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Missing_cotter_pin.png | file://x:/photopub/docs/0000000579/fc7fa222-39a8-4a84-8299-e45fb3f76f13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63f1a8d4_5a87_45b1_bfa7_93ff2d4a7eaf
BPVIN-790018-2017 | BPV-514510-2017 | 4/4/2017 | ASSESS: BPV IN: Installation Boiler | JPG | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | #Photo-2017-04-04-09-50-07_4582.JPG The manufacturer specifications require a flow switch to be installed in the event that the boiler fluid stops flowing. This may contribute to an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Photo-2017-04-04-09-50-07_4582.JPG | file://x:/photopub/docs/0000000582/2cea8a2e-ced3-4a6c-bf7c-6ca2dcd65283.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4043606f_81a0_4bac_96b4_17f3775ebc9e
BPVIN-790018-2017 | BPV-514510-2017 | 4/4/2017 | ASSESS: BPV IN: Installation Boiler | JPG | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | #Photo-2017-04-04-09-50-07_4582.JPG The manufacturer specifications require a flow switch to be installed in the event that the boiler fluid stops flowing. This may contribute to an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Photo-2017-04-04-09-50-07_4582.JPG | file://x:/photopub/docs/0000000582/9c3bb03c-26cc-4e19-9eda-1438d7173040.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4043606f_81a0_4bac_96b4_17f3775ebc9e
ELIN-756444-2017 | EL-499325-2017 | 2/28/2017 9:18:19 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Use_of_flexible_cord1.png,Use_of_flexible_cord2.png The use of a 2 wire ungrounded flexible cord with a 15 amp 120 volt circuit installed permanently in the carport area above the soffiting material from an existing exterior light to a motion light is subject to damage and is a thermal hazard | 4 | Conductors, Misuse of flexible cords. | Use_of_flexible_cord1.png | file://x:/photopub/docs/0000000564/eecd7c1c-899f-4920-b6e3-304ff04c2f9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a681e096_ac5d_47a3_9215_89b835225bb6
ELIN-756444-2017 | EL-499325-2017 | 2/28/2017 9:18:19 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Use_of_flexible_cord1.png,Use_of_flexible_cord2.png The use of a 2 wire ungrounded flexible cord with a 15 amp 120 volt circuit installed permanently in the carport area above the soffiting material from an existing exterior light to a motion light is subject to damage and is a thermal hazard | 4 | Conductors, Misuse of flexible cords. | Use_of_flexible_cord2.png | file://x:/photopub/docs/0000000564/6ee20301-9dc7-4a42-b516-122617d04560.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a681e096_ac5d_47a3_9215_89b835225bb6
GAIN-784508-2017 | GA-316814-2015 | 4/27/2017 11:51:17 AM | ASSESS: GA: Final | png | #asFound OPD (correction) | GA031 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | 3 | 3 | #Ops_and_reg_no_relief_piping.png Regulators and Over protection DEvices and measure to protect downstream piping from over pressurization. This over pressure is vented to a relief port. When this equipment is put inside a building these ports need to be piped to the outside. The relief ports are not vented outside, in an over pressure scenario these ports could fill up building with gas causing an explosion | 3 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | Ops_and_reg_no_relief_piping.png | file://x:/photopub/docs/0000000592/decb346e-96d4-435d-94e3-678944925bf9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c453b969_5f62_43b1_8734_57a0dd244b43
ELIN-712984-2016 | EL-403209-2016 | 3/24/2017 4:11:11 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_Breakers1.png,No_AFCI_Breakers2.png,No_AFCI_Breakers3.png,No_AFCI_Breakers4.png Arc-fault protection is required for bedrooms on branch circuits 20 amps or less installed in residential dwellings under the previous 2012 BC Electrical Code. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. During an inspection for a safety check of an existing single family dwelling, the safety officer found no AFCI breakers installed in the electrical panel even though the panel directory showed that the AFCI breakers had previously been installed. If a series or parallel arc-fault was to occur in the bedroom branch circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire and/or smoke hazard to persons and property inside this dwelling. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_Breakers4.png | file://x:/photopub/docs/0000000577/30d87342-56c1-4a78-87e7-76baaf0fd9a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc011ca_01b9_48f9_89a9_a08cba3e7121
ELIN-712984-2016 | EL-403209-2016 | 3/24/2017 4:11:11 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_Breakers1.png,No_AFCI_Breakers2.png,No_AFCI_Breakers3.png,No_AFCI_Breakers4.png Arc-fault protection is required for bedrooms on branch circuits 20 amps or less installed in residential dwellings under the previous 2012 BC Electrical Code. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. During an inspection for a safety check of an existing single family dwelling, the safety officer found no AFCI breakers installed in the electrical panel even though the panel directory showed that the AFCI breakers had previously been installed. If a series or parallel arc-fault was to occur in the bedroom branch circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire and/or smoke hazard to persons and property inside this dwelling. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_Breakers2.png | file://x:/photopub/docs/0000000577/6216e101-2b16-4dd5-b8c9-90667cbde983.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc011ca_01b9_48f9_89a9_a08cba3e7121
ELIN-793848-2017 | EL-512220-2017 | 4/12/2017 5:17:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Temp_to_permanent_with_open_panel1.png,Temp_to_permanent_with_open_panel2.png,Temp_to_permanent_with_open_panel3.png,Temp_to_permanent_with_open_panel4.png,Temp_to_permanent_with_open_panel5.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. This permanent electrical panel was being feed from a temporary power panel mounted on a pole outside the dwelling. A flexible cord was installed from the permanent meter base on the pole to a 60A, 2 Pole breaker in the temporary panel. Branch circuits from the permanent electrical panel inside wer | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_to_permanent_with_open_panel3.png | file://x:/photopub/docs/0000000586/fa176c3a-0c89-40c9-a2d0-977645c36a3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fbfafc9_7d38_44a0_b365_affd1c3e9100
ELIN-793848-2017 | EL-512220-2017 | 4/12/2017 5:17:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Temp_to_permanent_with_open_panel1.png,Temp_to_permanent_with_open_panel2.png,Temp_to_permanent_with_open_panel3.png,Temp_to_permanent_with_open_panel4.png,Temp_to_permanent_with_open_panel5.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. This permanent electrical panel was being feed from a temporary power panel mounted on a pole outside the dwelling. A flexible cord was installed from the permanent meter base on the pole to a 60A, 2 Pole breaker in the temporary panel. Branch circuits from the permanent electrical panel inside wer | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_to_permanent_with_open_panel4.png | file://x:/photopub/docs/0000000586/b641d5a6-1730-408b-a1a1-2b95f9789ce4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fbfafc9_7d38_44a0_b365_affd1c3e9100
ELIN-793848-2017 | EL-512220-2017 | 4/12/2017 5:17:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Temp_to_permanent_with_open_panel1.png,Temp_to_permanent_with_open_panel2.png,Temp_to_permanent_with_open_panel3.png,Temp_to_permanent_with_open_panel4.png,Temp_to_permanent_with_open_panel5.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. This permanent electrical panel was being feed from a temporary power panel mounted on a pole outside the dwelling. A flexible cord was installed from the permanent meter base on the pole to a 60A, 2 Pole breaker in the temporary panel. Branch circuits from the permanent electrical panel inside wer | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_to_permanent_with_open_panel5.png | file://x:/photopub/docs/0000000586/c6654643-9539-457d-959a-91c8227bc20e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fbfafc9_7d38_44a0_b365_affd1c3e9100
ELIN-793848-2017 | EL-512220-2017 | 4/12/2017 5:17:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Temp_to_permanent_with_open_panel1.png,Temp_to_permanent_with_open_panel2.png,Temp_to_permanent_with_open_panel3.png,Temp_to_permanent_with_open_panel4.png,Temp_to_permanent_with_open_panel5.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. This permanent electrical panel was being feed from a temporary power panel mounted on a pole outside the dwelling. A flexible cord was installed from the permanent meter base on the pole to a 60A, 2 Pole breaker in the temporary panel. Branch circuits from the permanent electrical panel inside wer | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_to_permanent_with_open_panel1.png | file://x:/photopub/docs/0000000586/f3354a98-abf8-47b6-b99a-cf8060f94fd6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fbfafc9_7d38_44a0_b365_affd1c3e9100
ELIN-807602-2017 | EL-496405-2017 | 5/2/2017 3:07:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | #No_bonding_bushings.png In a new agricultural facility, a 400amp 120/240volt 1phase main service was found with the main supply feeders not bonded to ground. This can lead to a "Shock Hazard" condition. Pic attached. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | No_bonding_bushings.png | file://x:/photopub/docs/0000000595/dc73788d-d620-455b-aa4b-4b6878d93d83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72cc0c30_a3b4_483f_9f27_b56fe87f0e2c
GAHE-769418-2017 | HE-508098-2017 | 3/6/2017 2:37:54 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Regulator.png Incorrect pressure being delivered to appliances installed in house. 2psi gas pressure connected to appliances with max inlet pressures of 7" WC (1/2 psi). Potential for over firing of appliances creating a fire hazard | 4 | Appliance regulator not installed, incorrect delivery pressure | Regulator.png | file://x:/photopub/docs/0000000567/8abc7ee2-da53-44be-82fd-3fc0fb551473.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8126a45e_b848_4546_8009_dc31c9d58f5a
BPVIN-790018-2017 | BPV-514510-2017 | 4/4/2017 | ASSESS: BPV IN: Installation Boiler | JPG | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | #Photo-2017-04-04-09-50-07_4582.JPG The manufacturer specifications require a flow switch to be installed in the event that the boiler fluid stops flowing. This may contribute to an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Photo-2017-04-04-09-50-07_4582.JPG | file://x:/photopub/docs/0000000582/226b7516-14cf-4ce6-b32c-f4a096917482.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4043606f_81a0_4bac_96b4_17f3775ebc9e
BPVIN-790018-2017 | BPV-514510-2017 | 4/4/2017 | ASSESS: BPV IN: Installation Boiler | JPG | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | #Photo-2017-04-04-09-50-07_4582.JPG The manufacturer specifications require a flow switch to be installed in the event that the boiler fluid stops flowing. This may contribute to an incident. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Photo-2017-04-04-09-50-07_4582.JPG | file://x:/photopub/docs/0000000582/00e2a6ad-dca8-437b-84a9-5c3ccae7d4d1.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4043606f_81a0_4bac_96b4_17f3775ebc9e
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure9.png | file://x:/photopub/docs/0000000586/b56f1732-3e77-4fbe-b189-38b4b2116268.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure4.png | file://x:/photopub/docs/0000000586/57de7277-463f-432e-8bd3-e753ed611dc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795927-2017 | EL-519636-2017 | 4/13/2017 5:08:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding.png Grounding electrode conductor is terminated to a bonding lug for service entrance equipment. Identified conductor/neutral has not been grounded. Possibility to have fault current carried on a bond conductor terminated to a ground electrode not interconnected with the main system grounding. This creates a possibility for circulating currents or circulating fault currents and the potential for shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding.png | file://x:/photopub/docs/0000000586/cf556db5-1a82-4321-8a5c-eaee101b53bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d758f1d_0f2d_4ea3_b7b3_5cfe39bf00dd
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure5.png | file://x:/photopub/docs/0000000586/2d001f68-209e-410a-948b-e294b24db58f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure2.png | file://x:/photopub/docs/0000000586/bcae7327-3440-44e1-adbc-cc7d446553fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure8.png | file://x:/photopub/docs/0000000586/900394fd-b888-4167-a78f-73b8cf3f2c30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure3.png | file://x:/photopub/docs/0000000586/159a6972-ac3f-4120-b31d-3e307a249da0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure7.png | file://x:/photopub/docs/0000000586/99fae770-d5c1-4872-ae80-83faeee53b36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure1.png | file://x:/photopub/docs/0000000586/ccda30f6-fade-45ac-ba84-144122842dc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELIN-795694-2017 | UW-523103-2017 | 4/13/2017 5:28:52 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Electrical_infrastru__electrical_infrastructure1.png,Electrical_infrastru__electrical_infrastructure2.png,Electrical_infrastru__electrical_infrastructure3.png,Electrical_infrastru__electrical_infrastructure4.png,Electrical_infrastru__electrical_infrastructure5.png,Electrical_infrastru__electrical_infrastructure6.png,Electrical_infrastru__electrical_infrastructure7.png,Electrical_infrastru__electrical_infrastructure8.png,Electrical_infrastru__electrical_infrastructure9.png Regulated electrical infrastructure has been installed without a permit. Branch circuits are not supported and are not installed in junction boxes. Main service circuit breakers have been manipulated and not identified. There is potential for shock and fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Electrical_infrastru__electrical_infrastructure6.png | file://x:/photopub/docs/0000000586/ac54fe0f-9a83-43b2-bcf0-d2f5314be819.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed03b29e_e201_4877_96f1_979c006a6e35
ELHE-774021-2017 | HE-511038-2017 | 3/7/2017 6:50:25 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #open_air_splice.png 15 amp, 120 volt branch circuit wiring not installed within an outlet box and splice made for lighting fixture exposed to persons and property. This is a thermal issue. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | open_air_splice.png | file://x:/photopub/docs/0000000571/bb494794-e695-48bf-8420-5b30db537b96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a27fea_663a_4698_94f6_81559db7f5ec
ELIN-712984-2016 | EL-403209-2016 | 3/24/2017 4:11:11 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_Breakers1.png,No_AFCI_Breakers2.png,No_AFCI_Breakers3.png,No_AFCI_Breakers4.png Arc-fault protection is required for bedrooms on branch circuits 20 amps or less installed in residential dwellings under the previous 2012 BC Electrical Code. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. During an inspection for a safety check of an existing single family dwelling, the safety officer found no AFCI breakers installed in the electrical panel even though the panel directory showed that the AFCI breakers had previously been installed. If a series or parallel arc-fault was to occur in the bedroom branch circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire and/or smoke hazard to persons and property inside this dwelling. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_Breakers1.png | file://x:/photopub/docs/0000000577/d5166751-e3bf-44d2-b8a6-9b1581753950.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc011ca_01b9_48f9_89a9_a08cba3e7121
ELIN-712984-2016 | EL-403209-2016 | 3/24/2017 4:11:11 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_Breakers1.png,No_AFCI_Breakers2.png,No_AFCI_Breakers3.png,No_AFCI_Breakers4.png Arc-fault protection is required for bedrooms on branch circuits 20 amps or less installed in residential dwellings under the previous 2012 BC Electrical Code. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. During an inspection for a safety check of an existing single family dwelling, the safety officer found no AFCI breakers installed in the electrical panel even though the panel directory showed that the AFCI breakers had previously been installed. If a series or parallel arc-fault was to occur in the bedroom branch circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire and/or smoke hazard to persons and property inside this dwelling. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_Breakers3.png | file://x:/photopub/docs/0000000577/ca93293d-e31c-457b-8d6b-c6c2d6143e07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc011ca_01b9_48f9_89a9_a08cba3e7121
ELIN-783316-2017 | EL-502760-2017 | 3/28/2017 10:07:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #No_electrode_installed.png 200 amp, 120/240 volt dual socket meter base installed on outside of dwelling. Ground conductor installed and terminated at meter base on neutral conductor. Ground conductor then is installed to ground electrode location but no electrode in place. This is a thermal issue. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_electrode_installed.png | file://x:/photopub/docs/0000000577/6d95f03d-d545-46d5-91b1-0030476ab30a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4180316d_10ba_44bb_9d7d_6e5aa94e5015
ELIN-793848-2017 | EL-512220-2017 | 4/12/2017 5:17:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Temp_to_permanent_with_open_panel1.png,Temp_to_permanent_with_open_panel2.png,Temp_to_permanent_with_open_panel3.png,Temp_to_permanent_with_open_panel4.png,Temp_to_permanent_with_open_panel5.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. Also, temporary electrical installations must not be connected to the permanent circuits of a building to ensure that a circuit cannot be energized by two separate power sources (the temporary and the permanent source). During an electrical assessment of a new residential dwelling under construction, an energized 120/240 volt permanent electrical panel was found with no panel cover installed. This permanent electrical panel was being feed from a temporary power panel mounted on a pole outside the dwelling. A flexible cord was installed from the permanent meter base on the pole to a 60A, 2 Pole breaker in the temporary panel. Branch circuits from the permanent electrical panel inside wer | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_to_permanent_with_open_panel2.png | file://x:/photopub/docs/0000000586/91abeb74-cfe7-4f3c-95fe-a7f460632a14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fbfafc9_7d38_44a0_b365_affd1c3e9100
ELHE-798816-2017 | HE-524411-2017 | 4/19/2017 1:21:40 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Tagged_main_breaker_in_on_position_.png Branch circuits were identified on April 18 to be unsafe and energized. Circuits on main panel have not been identified and are all energized. Main disconnect on panel was De-energized and tagged in the off position. On April 19 an assessment was made due to observation of power supply being used at the residence. Electrical contractor has not submitted a declaration of compliance and the power was re-energized. Access was denied, by building contractor, to assess any corrections. Conditions remain for energized exposed branch circuits. Potential for shock and fire hazard. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Tagged_main_breaker_in_on_position_.png | file://x:/photopub/docs/0000000588/50718d48-969d-42b5-8e79-7d0b3eae8522.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb790c4c_f3df_417f_a155_777a77d40c2f
ELIN-790189-2017 | EL-504141-2017 | 4/6/2017 1:05:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound No receptacle provided for basement bathroom. The photograph shows that the plumbing has been roughed in for the sink. | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | #No_recept.png Rough wire of new single family dwelling. The basement bathroom has been roughed in for the plumbing. No receptacle has been installed for the sink in the bathroom. Therefore, anyone wishing to use electrical hair drying or grooming equipment would be required to run an extension cord through the doorway. This would become a tripping hazard and possibly lead to a shock hazard if the cord was connected to a non-GFCI protected receptacle. | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | No_recept.png | file://x:/photopub/docs/0000000582/a80a541e-c54a-43e1-8eb2-fff524348484.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__255a950d_65d3_4ca0_a1b6_e832e987fd4e
ELHE-795766-2017 | HE-522077-2017 | 4/13/2017 3:40:21 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings1.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings2.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings3.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings4.png Found voltage readings from voltage tests of panelboard feeder line side conductors for 120/240 volt system have readings that are between 0 to 75 volts between line conductors to ground and 0 to 75 volts from line conductors to neutral conductor of panelboard. The feeder conductors are installed in underground and are inaccessible to inspect and could be damaged. When power supply system conductors do not have proper voltage readings between line conductor to ground or line conductor to neutral, the electrical equipment and conductors might possibly be damaged and could be an electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings4.png | file://x:/photopub/docs/0000000587/69da9ee4-b526-49ed-b365-e951223d6434.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3406e06_52f0_48b2_aa8f_5a2824dfa3d9
ELHE-795766-2017 | HE-522077-2017 | 4/13/2017 3:40:21 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings1.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings2.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings3.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings4.png Found voltage readings from voltage tests of panelboard feeder line side conductors for 120/240 volt system have readings that are between 0 to 75 volts between line conductors to ground and 0 to 75 volts from line conductors to neutral conductor of panelboard. The feeder conductors are installed in underground and are inaccessible to inspect and could be damaged. When power supply system conductors do not have proper voltage readings between line conductor to ground or line conductor to neutral, the electrical equipment and conductors might possibly be damaged and could be an electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings1.png | file://x:/photopub/docs/0000000587/584e1221-bfe9-4810-914d-164288844640.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3406e06_52f0_48b2_aa8f_5a2824dfa3d9
ELHE-795766-2017 | HE-522077-2017 | 4/13/2017 3:40:21 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings1.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings2.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings3.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings4.png Found voltage readings from voltage tests of panelboard feeder line side conductors for 120/240 volt system have readings that are between 0 to 75 volts between line conductors to ground and 0 to 75 volts from line conductors to neutral conductor of panelboard. The feeder conductors are installed in underground and are inaccessible to inspect and could be damaged. When power supply system conductors do not have proper voltage readings between line conductor to ground or line conductor to neutral, the electrical equipment and conductors might possibly be damaged and could be an electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings3.png | file://x:/photopub/docs/0000000587/e8b06b18-f9f8-48d7-b437-209d74d894fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3406e06_52f0_48b2_aa8f_5a2824dfa3d9
ELHE-795766-2017 | HE-522077-2017 | 4/13/2017 3:40:21 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings1.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings2.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings3.png,Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings4.png Found voltage readings from voltage tests of panelboard feeder line side conductors for 120/240 volt system have readings that are between 0 to 75 volts between line conductors to ground and 0 to 75 volts from line conductors to neutral conductor of panelboard. The feeder conductors are installed in underground and are inaccessible to inspect and could be damaged. When power supply system conductors do not have proper voltage readings between line conductor to ground or line conductor to neutral, the electrical equipment and conductors might possibly be damaged and could be an electrical fire or shock hazard to people and property. | 3 | General Equipment is not approved for the specific use | Damaged_feeder_conductors_possible_resulted_in_unacceptable_and_improper_voltage_readings2.png | file://x:/photopub/docs/0000000587/ad8e899a-d2fb-4b90-b2b3-0903aede4d7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3406e06_52f0_48b2_aa8f_5a2824dfa3d9
ELIN-787887-2017 | EL-507062-2017 | 4/6/2017 9:05:01 AM | ASSESS: EL: Final | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | #Patient_areas_1.png,Patient_areas_2.png,Patient_areas_3.png,Patient_areas_4.png,Patient_areas_5.png,Patient_areas_6.png - patient care area of clinic receptacles installed without additional bonding required for the use of medical equipment that will be in direct contact with patients. Additional bonding to ground is required because of frequent contact between equipment and direct cont to persons to prevent shock | 4 | Medical Bonding is not adequate. | Patient_areas_5.png | file://x:/photopub/docs/0000000582/9b5eed8e-fde8-4c7e-a95a-ca094c5b3632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f723e3e8_577d_4edf_a6d8_04ed222535f2
ELIN-787887-2017 | EL-507062-2017 | 4/6/2017 9:05:01 AM | ASSESS: EL: Final | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | #Patient_areas_1.png,Patient_areas_2.png,Patient_areas_3.png,Patient_areas_4.png,Patient_areas_5.png,Patient_areas_6.png - patient care area of clinic receptacles installed without additional bonding required for the use of medical equipment that will be in direct contact with patients. Additional bonding to ground is required because of frequent contact between equipment and direct cont to persons to prevent shock | 4 | Medical Bonding is not adequate. | Patient_areas_6.png | file://x:/photopub/docs/0000000582/7652681f-5c4c-4be4-a773-6add965d8ce7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f723e3e8_577d_4edf_a6d8_04ed222535f2
ELIN-787887-2017 | EL-507062-2017 | 4/6/2017 9:05:01 AM | ASSESS: EL: Final | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | #Patient_areas_1.png,Patient_areas_2.png,Patient_areas_3.png,Patient_areas_4.png,Patient_areas_5.png,Patient_areas_6.png - patient care area of clinic receptacles installed without additional bonding required for the use of medical equipment that will be in direct contact with patients. Additional bonding to ground is required because of frequent contact between equipment and direct cont to persons to prevent shock | 4 | Medical Bonding is not adequate. | Patient_areas_1.png | file://x:/photopub/docs/0000000582/ee9a3188-0960-4abe-a9e7-5c14001dd46b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f723e3e8_577d_4edf_a6d8_04ed222535f2
ELIN-787887-2017 | EL-507062-2017 | 4/6/2017 9:05:01 AM | ASSESS: EL: Final | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | #Patient_areas_1.png,Patient_areas_2.png,Patient_areas_3.png,Patient_areas_4.png,Patient_areas_5.png,Patient_areas_6.png - patient care area of clinic receptacles installed without additional bonding required for the use of medical equipment that will be in direct contact with patients. Additional bonding to ground is required because of frequent contact between equipment and direct cont to persons to prevent shock | 4 | Medical Bonding is not adequate. | Patient_areas_3.png | file://x:/photopub/docs/0000000582/e609219e-8b79-427f-a061-c2b1a1394f51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f723e3e8_577d_4edf_a6d8_04ed222535f2
GAIN-790668-2017 | GA-476784-2016 | 4/24/2017 9:16:28 AM | ASSESS: GA: Final | png | #asFound No dedicated air supply provided in structure for burners | GA122 | Combustion air supply missing | 4 | 4 | #No_combustion_air.png A burner installed in a structure requires combustion air (dedicated air supply) to sufficiently burn. Structure does not have a dedicated air supply. A negative air scenario could happen in structure which can cause flames to leave burner compartment of appliance searching for sufficient air to burn. | 4 | Combustion air supply missing | No_combustion_air.png | file://x:/photopub/docs/0000000590/0f0ab0d4-fe59-4352-9f42-731fcee7e687.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c90fc0a_ae5f_49e5_a14d_d5773bcee8f0
ELIN-769755-2017 | EL-508354-2017 | 3/7/2017 1:22:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_supply_flat_roof.png Overhead supply conductors are within reach of the flat roof. Potential for shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_supply_flat_roof.png | file://x:/photopub/docs/0000000567/0fe37b09-0a2b-4eb0-9e81-f6e158dce358.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5be7ac2e_9373_4fb8_9c57_c1f352fcb446
AMOP-775756-2017 | 3251949 | 3/20/2017 12:24:08 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Light_pane_missing_bolts.png Light panels above PCU's were missing bolts at time of inspection. Covers of the panels could fall and hit passengers | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Light_pane_missing_bolts.png | file://x:/photopub/docs/0000000574/66e3803e-2f4e-4f7f-825a-8fe7380315d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__214ef8dd_d879_4ce3_951a_3375e3b9f716
AMOP-775464-2017 | 5055822 | 3/20/2017 9:33:41 AM | ASSESS: AM OP: Periodic | png | #asFound | AM032 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Smoke_alarm_dust_covers.png Dust covers on the smoke alarms had not been removed, detectors may fail to annunciate in the event of fire. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Smoke_alarm_dust_covers.png | file://x:/photopub/docs/0000000574/da8acf6a-4183-4e54-a69c-2729545254ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c830bb2_5002_4e0b_a75f_242bc956ff9c
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | B.png | file://x:/photopub/docs/0000000591/9a2e82b3-7245-4bfe-9a70-069d8893b68c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A4.png | file://x:/photopub/docs/0000000591/114f50a3-0bd4-49a5-a900-f396bc7b1b69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A2.png | file://x:/photopub/docs/0000000591/e1139d16-c3c1-439b-bfb5-2767ddadddef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A5.png | file://x:/photopub/docs/0000000591/dce33fdd-72e1-40b9-80cd-d84fdd0771ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A6.png | file://x:/photopub/docs/0000000591/c7c5a583-34f5-4127-bc66-0ef3d1e0af35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A1.png | file://x:/photopub/docs/0000000591/f14ad547-bc64-4653-866d-4c367c23bd5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELIN-802235-2017 | EL-515484-2017 | 4/26/2017 12:11:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,B.png 600V system not grounded installed in a dwelling too close to combustible material. This is a shock hazard and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | A3.png | file://x:/photopub/docs/0000000591/ffdf7e1c-d57c-4c19-8692-2ddc682afe1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73c7c3d8_445a_446d_aa2c_9012f3de7695
ELHE-792848-2017 | HE-521235-2017 | 4/12/2017 12:40:36 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL046 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | 5 | 5 | #Lead_acid_batteries_between_bed_and_bathtub3.png Storage batteries are located beside the bathtub with unprotected terminals. There is no method provided for venting the gas produced by charging the batteries to the outdoors. There is shock hazard created by the situation as well as the hazard created if the gas were to build up to explosive levels. | 5 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | Lead_acid_batteries_between_bed_and_bathtub3.png | file://x:/photopub/docs/0000000592/db37b015-ebfb-4f6f-a3e9-03c00a7d793f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e26aa12_7af5_4e0c_9215_48d3f27bc8be
ELHE-792848-2017 | HE-521235-2017 | 4/12/2017 12:40:36 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL046 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | 5 | 5 | #Lead_acid_batteries_between_bed_and_bathtub3.png Storage batteries are located beside the bathtub with unprotected terminals. There is no method provided for venting the gas produced by charging the batteries to the outdoors. There is shock hazard created by the situation as well as the hazard created if the gas were to build up to explosive levels. | 5 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to general public. | Lead_acid_batteries_between_bed_and_bathtub3.png | file://x:/photopub/docs/0000000592/7cb9219f-f9a4-4c36-b087-851747a026fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e26aa12_7af5_4e0c_9215_48d3f27bc8be
ELIN-776295-2017 | EL-467733-2016 | 3/17/2017 12:21:43 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #No_receptacle.png Kitchen counter receptacle is required on the work surface. This is a hazard as an individual might use an extension cord or plug an appliance into the island receptacle and have a cord in a walkway. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | No_receptacle.png | file://x:/photopub/docs/0000000572/a8834a2c-979f-4771-a064-7f4931cdd1b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7cb540a_52f1_425c_8101_16dfee769970
GAIN-770268-2017 | GA-480548-2016 | 3/29/2017 1:12:00 PM | ASSESS: GA: Final | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | #Csst.png The as found condition is a length of Corregated Stainless Steel Tubing (CSST) used for gas delivery was found without piping supports as required but he manufacturer. The as found hazard is failure to support a gas tubing system according to manufacturer instructions could allow for the system to be damaged or impinged leading to gas leakage. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Csst.png | file://x:/photopub/docs/0000000578/ad060fb6-237c-452f-8771-c6a708f7411e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__baa535b0_3216_4028_965c_ceaeac8d6965
ELIN-787887-2017 | EL-507062-2017 | 4/6/2017 9:05:01 AM | ASSESS: EL: Final | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | #Patient_areas_1.png,Patient_areas_2.png,Patient_areas_3.png,Patient_areas_4.png,Patient_areas_5.png,Patient_areas_6.png - patient care area of clinic receptacles installed without additional bonding required for the use of medical equipment that will be in direct contact with patients. Additional bonding to ground is required because of frequent contact between equipment and direct cont to persons to prevent shock | 4 | Medical Bonding is not adequate. | Patient_areas_4.png | file://x:/photopub/docs/0000000582/0685523a-e11a-4583-92f2-03443b122d71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f723e3e8_577d_4edf_a6d8_04ed222535f2
ELIN-787887-2017 | EL-507062-2017 | 4/6/2017 9:05:01 AM | ASSESS: EL: Final | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | #Patient_areas_1.png,Patient_areas_2.png,Patient_areas_3.png,Patient_areas_4.png,Patient_areas_5.png,Patient_areas_6.png - patient care area of clinic receptacles installed without additional bonding required for the use of medical equipment that will be in direct contact with patients. Additional bonding to ground is required because of frequent contact between equipment and direct cont to persons to prevent shock | 4 | Medical Bonding is not adequate. | Patient_areas_2.png | file://x:/photopub/docs/0000000582/9323f31c-d655-4404-8911-7533482358bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f723e3e8_577d_4edf_a6d8_04ed222535f2
BPVOP-790682-2017 | 2302113 | 4/6/2017 4:48:04 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_1.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Temperature and Pressure relief valve was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_1.png | file://x:/photopub/docs/0000000583/25593c01-e5af-423a-9dfb-fd0123b9c740.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b4710e6_ac8e_4980_9d44_d707d1615f92
BPVOP-790684-2017 | 2260337 | 4/6/2017 4:57:16 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Temperature and Pressure relief valve was overdue as per CSA B51. This can contribute to the failure of the pressure vessel safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_.png | file://x:/photopub/docs/0000000583/e8fed091-faec-46da-a180-ca2725d16530.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__388e0f27_ab86_46f6_ae4c_76b7dd37eff2
ELIN-767858-2017 | EL-445827-2016 | 3/7/2017 8:54:06 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_dishwasher_feed_not_terminated_in_a_box.png Dishwasher non metallic sheathed cable is energized and not terminated in a box. Conductors have wire nuts installed on them to protect from shock or accidental contact. If wire nuts become loose or fall of there is potential for shock and fire to persons and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_dishwasher_feed_not_terminated_in_a_box.png | file://x:/photopub/docs/0000000567/c117941f-b9d2-4d55-a32e-8ba27e2a058a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4eaf1798_8eeb_47b5_ad65_d478a1851865
BPVOP-798041-2017 | 2908169 | 4/20/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve2.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement of the safety valve on a high pressure steam boiler with a maximum allowable working pressure of 150psig. If left in this condition, the safety valve could malfunction in a critical situation. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve2.png | file://x:/photopub/docs/0000000590/ccf86609-384d-4a55-88dd-24b1ad4527b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61d255b5_5f71_435c_980e_583e1cd0e069
GAHE-793898-2017 | HE-521974-2017 | 4/13/2017 10:16:45 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting1.png,Venting2.png Gas furnace and 2 gas water heaters vented into masonry chimney that has no liner or clay lined. Products of combustion could be introduced into building | 3 | Unapproved venting material | Venting2.png | file://x:/photopub/docs/0000000586/72708005-7d78-4264-a551-a24769cb0255.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbb088df_2324_429b_8935_4ce7ce4a6471
GAHE-793898-2017 | HE-521974-2017 | 4/13/2017 10:16:45 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting1.png,Venting2.png Gas furnace and 2 gas water heaters vented into masonry chimney that has no liner or clay lined. Products of combustion could be introduced into building | 3 | Unapproved venting material | Venting1.png | file://x:/photopub/docs/0000000586/9ac6de52-5116-42d3-a6f9-6bdfb16005c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbb088df_2324_429b_8935_4ce7ce4a6471
ELIN-798550-2017 | EL-429589-2016 | 4/24/2017 10:39:56 AM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Switches_and_thermostat__and_thermostats1.png,Switches_and_thermostat__and_thermostats2.png Switch is in thermostat are within 1 m of shower and not GFI protected. Possibility for shock. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Switches_and_thermostat__and_thermostats2.png | file://x:/photopub/docs/0000000590/749563bc-a672-45e2-83ca-81cdac53a732.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8e31515_4c6d_433d_8d33_f48b129ee668
ELIN-798550-2017 | EL-429589-2016 | 4/24/2017 10:39:56 AM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Switches_and_thermostat__and_thermostats1.png,Switches_and_thermostat__and_thermostats2.png Switch is in thermostat are within 1 m of shower and not GFI protected. Possibility for shock. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Switches_and_thermostat__and_thermostats1.png | file://x:/photopub/docs/0000000590/a02b9b4b-38bb-4a45-b550-03c7cfb14eff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8e31515_4c6d_433d_8d33_f48b129ee668
ELIN-795591-2017 | EL-439602-2016 | 4/13/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized21.png,Energized22.png,Energized23.png Panel Cover was removed allowing access to bare energized parts. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized22.png | file://x:/photopub/docs/0000000587/3ae4316f-0b0e-47f9-b510-bf8f2ddecd0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88877309_417e_43d0_a24f_9787ccac7c01
ELIN-795591-2017 | EL-439602-2016 | 4/13/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized21.png,Energized22.png,Energized23.png Panel Cover was removed allowing access to bare energized parts. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized21.png | file://x:/photopub/docs/0000000587/2248d71f-bf63-4a09-9d3f-dffe350a67b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88877309_417e_43d0_a24f_9787ccac7c01
ELIN-795591-2017 | EL-439602-2016 | 4/13/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized21.png,Energized22.png,Energized23.png Panel Cover was removed allowing access to bare energized parts. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized23.png | file://x:/photopub/docs/0000000587/00cd3c4e-1457-41ad-88c9-5df118f32cbf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88877309_417e_43d0_a24f_9787ccac7c01
BPVOP-777202-2017 | 2291414 | 3/9/2017 1:47:45 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-08-13-39-33_4174.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-08-13-39-33_4174.JPG | file://x:/photopub/docs/0000000573/8be4fb47-55f2-4e3f-9975-a74072dc3e65.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d11c5b27_8c18_42df_8f11_391c8d1fb9e0
BPVOP-777202-2017 | 2291414 | 3/9/2017 1:47:45 PM | ASSESS: BPV OP: Re-Certification Boiler | JPG | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | #Photo-2017-03-08-13-39-33_4174.JPG Low water cut out manual reset switch missing. This may contribute to an incident if low water condition occurs in boiler system. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Photo-2017-03-08-13-39-33_4174.JPG | file://x:/photopub/docs/0000000573/7c9fbfc0-703f-40d1-a263-efdd4939c213.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d11c5b27_8c18_42df_8f11_391c8d1fb9e0
GAIN-779702-2017 | GA-513547-2017 | 3/23/2017 9:38:57 AM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Underground_entry1.png,Underground_entry2.png The as found hazard was two underground gas lines which entered a building below grade. This is a hazard because it creates a risk of damage to the piping through building settling. | 3 | Underground piping entering a building below grade (unapproved) | Underground_entry1.png | file://x:/photopub/docs/0000000575/fe2a4864-a2c6-49ab-8469-b64da7eadbd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a711d1_4fe1_4da3_969c_01bd55656067
GAIN-779702-2017 | GA-513547-2017 | 3/23/2017 9:38:57 AM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Underground_entry1.png,Underground_entry2.png The as found hazard was two underground gas lines which entered a building below grade. This is a hazard because it creates a risk of damage to the piping through building settling. | 3 | Underground piping entering a building below grade (unapproved) | Underground_entry2.png | file://x:/photopub/docs/0000000575/60e9fd0f-ce19-4519-97a9-d166cafe6555.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01a711d1_4fe1_4da3_969c_01bd55656067
ELOP-790032-2017 | EL-458854-2016 | 4/5/2017 3:11:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Extensioncord.png There is a feed to the roof out of a damaged Junction box where the bond conductor is not connected due to the wiring method used. This would allow a fault to energize the metal parts of the equipment it feeds, without tripping the over current device. | 3 | Continuity Bonding; method for equipment is not adequate. | Extensioncord.png | file://x:/photopub/docs/0000000582/29be7bac-3fa1-411a-b494-f902f99b4bce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17f1b9e7_4e16_4ed3_91de_f75fee6c0a72
ELOP-790032-2017 | EL-458854-2016 | 4/5/2017 3:11:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Extensioncord.png There is a feed to the roof out of a damaged Junction box where the bond conductor is not connected due to the wiring method used. This would allow a fault to energize the metal parts of the equipment it feeds, without tripping the over current device. | 3 | Continuity Bonding; method for equipment is not adequate. | Extensioncord.png | file://x:/photopub/docs/0000000582/88b419a2-90c9-4d80-bed5-3c0b63fabdd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17f1b9e7_4e16_4ed3_91de_f75fee6c0a72
GAUP-770208-2017 | UW-508632-2017 | 3/7/2017 11:30:59 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound To existing unused appliances | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Venting.png,Common_Vent.png,Venting2.png Common venting for 2 new appliances is still connected to 2 other appliances not in use. Common vent is 20" diameter to vent exhaust gases of 4 appliances. With the 2 appliances firing the common vent should be approx 10" diameter. Product of Combustion could back draft and spill into mechanical room in certain temperate conditions and possibly CO poising could occur. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Venting.png | file://x:/photopub/docs/0000000567/af04dce5-9abb-48da-afb5-df133281d40f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08e67e91_27b2_4791_a2dd_2f9399322574
GAUP-770208-2017 | UW-508632-2017 | 3/7/2017 11:30:59 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Venting.png,Common_Vent.png,Venting2.png Common venting for 2 new appliances is still connected to 2 other appliances not in use. Common vent is 20" diameter to vent exhaust gases of 4 appliances. With the 2 appliances firing the common vent should be approx 10" diameter. Product of Combustion could back draft and spill into mechanical room in certain temperate conditions and possibly CO poising could occur. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Common_Vent.png | file://x:/photopub/docs/0000000567/d693758a-9def-4ecc-a1af-a12a73f438e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08e67e91_27b2_4791_a2dd_2f9399322574
GAUP-770208-2017 | UW-508632-2017 | 3/7/2017 11:30:59 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Connected to 20 inch common vent | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Venting.png,Common_Vent.png,Venting2.png Common venting for 2 new appliances is still connected to 2 other appliances not in use. Common vent is 20" diameter to vent exhaust gases of 4 appliances. With the 2 appliances firing the common vent should be approx 10" diameter. Product of Combustion could back draft and spill into mechanical room in certain temperate conditions and possibly CO poising could occur. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Venting2.png | file://x:/photopub/docs/0000000567/26bace40-09d5-4f0a-ae57-ec15f1638caa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08e67e91_27b2_4791_a2dd_2f9399322574
GAIN-791651-2017 | GA-518141-2017 | 4/10/2017 2:52:20 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Return_air_opening.png Newly installed atmospheric style water heater has been installed in a location where the furnace return air opening will affect the safe operation of said water heater during normal operation of furnace and water heater when furnace fan is on products of combustion will be drawn from water heater and circulated through the occupied space potentially causing occupants to become sick from carbon monoxide poisoning | 3 | Appliance not installed according to installation instructions | Return_air_opening.png | file://x:/photopub/docs/0000000584/07270c67-567a-4b58-8aa3-e0159c836e66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f3d2fae_5807_4608_abd9_4efcaf22a73c
ELIN-796913-2017 | EL-352383-2016 | 4/18/2017 3:01:11 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Exposed_energized__exposed_energized_wiring1.png,Exposed_energized__exposed_energized_wiring2.png,Exposed_energized__exposed_energized_wiring3.png,Exposed_energized__exposed_energized_wiring4.png Wiring is not terminated. Circuits were energized. Potential for shock to other trades working in the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized__exposed_energized_wiring1.png | file://x:/photopub/docs/0000000587/46594645-7416-44fd-aa54-d6f5912f3d83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076a554c_0036_4f9e_8712_0cccb9eb6ef3
ELIN-796913-2017 | EL-352383-2016 | 4/18/2017 3:01:11 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Exposed_energized__exposed_energized_wiring1.png,Exposed_energized__exposed_energized_wiring2.png,Exposed_energized__exposed_energized_wiring3.png,Exposed_energized__exposed_energized_wiring4.png Wiring is not terminated. Circuits were energized. Potential for shock to other trades working in the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized__exposed_energized_wiring3.png | file://x:/photopub/docs/0000000587/ffd66bf5-1825-427a-be0c-ecd54fb08b1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076a554c_0036_4f9e_8712_0cccb9eb6ef3
ELIN-796913-2017 | EL-352383-2016 | 4/18/2017 3:01:11 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Exposed_energized__exposed_energized_wiring1.png,Exposed_energized__exposed_energized_wiring2.png,Exposed_energized__exposed_energized_wiring3.png,Exposed_energized__exposed_energized_wiring4.png Wiring is not terminated. Circuits were energized. Potential for shock to other trades working in the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized__exposed_energized_wiring4.png | file://x:/photopub/docs/0000000587/b3d37892-162d-480c-8dff-d000f4f6ea67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076a554c_0036_4f9e_8712_0cccb9eb6ef3
ELIN-796913-2017 | EL-352383-2016 | 4/18/2017 3:01:11 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Exposed_energized__exposed_energized_wiring1.png,Exposed_energized__exposed_energized_wiring2.png,Exposed_energized__exposed_energized_wiring3.png,Exposed_energized__exposed_energized_wiring4.png Wiring is not terminated. Circuits were energized. Potential for shock to other trades working in the building. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized__exposed_energized_wiring2.png | file://x:/photopub/docs/0000000587/d1509c30-0cd1-4377-b453-42e26c855f91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076a554c_0036_4f9e_8712_0cccb9eb6ef3
ELIN-794866-2017 | EL-453141-2016 | 4/18/2017 9:20:18 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_cover_plate.png Missing cover plates on outlet boxes with energized devices could result in accidental contact with energized device terminals and likelihood of electrical shock. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_cover_plate.png | file://x:/photopub/docs/0000000587/ff072395-1df8-470f-a972-7fa782fda307.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8601e0f0_164d_48ac_a122_2a7d1d7092e8
ELIN-789850-2017 | EL-308283-2015 | 4/21/2017 10:12:43 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #NMD_No_Fittings1.png,NMD_No_Fittings2.png 120 volt 15 amp 14/2 NMD90 has been entered into a metal box without a fitting, this poses a shock hazard persons and possible mechanical damage to the wire and equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | NMD_No_Fittings1.png | file://x:/photopub/docs/0000000589/8c61bb52-718b-45d3-9ac7-eb9e0d729a1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4492cf1_5bf4_4c64_8687_437e8b846b6c
GAIN-781737-2017 | GA-444176-2016 | 3/27/2017 2:08:58 PM | ASSESS: GA: Final | png | #asFound | GA168 | Appliance not installed according to installation instructions (Not In Service) | 2 | 2 | #Brass_fittings_in_condensate_drain_.png Appliance not installed as per manufacturers installation instructions. Condensate drain piping must be of plastic piping material, not brass. | 2 | Appliance not installed according to installation instructions (Not In Service) | Brass_fittings_in_condensate_drain_.png | file://x:/photopub/docs/0000000577/520f9e5d-ad75-4aa2-a78e-40b06707c02d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__899296b1_d262_4b85_b69d_97f957c5974f
GAIN-781736-2017 | GA-444170-2016 | 3/27/2017 2:17:06 PM | ASSESS: GA: Final | png | #asFound | GA168 | Appliance not installed according to installation instructions (Not In Service) | 2 | 2 | #Brass_fittings_in_condensate_drain-2.png Appliance not installed as per manufacturers installation instructions. Condensate drain piping must be of plastic piping materials. | 2 | Appliance not installed according to installation instructions (Not In Service) | Brass_fittings_in_condensate_drain-2.png | file://x:/photopub/docs/0000000577/ba74136d-8ff0-4847-acce-a8dbb83ddb65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__daf06e24_302b_4a01_bbcc_d09078739bbd
GAIN-781561-2017 | GA-515272-2017 | 3/27/2017 10:09:07 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | #Regulator_not_installed_as_per_manufacturers_installation_instructions.png Certified regulator not installed as per manufacturers installation instructions. Vent limiter must be installed in the vertical position for operation as designed. | 2 | Not installed according to certified installation instructions | Regulator_not_installed_as_per_manufacturers_installation_instructions.png | file://x:/photopub/docs/0000000577/5f2c05c3-4f35-4817-992d-553d072c0143.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4de6aadc_cfd0_4811_98d9_c3bc34106ecd
BPVIN-762971-2017 | BPV-503460-2017 | 3/27/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound The remote switches shown are for 2 of the 3 boilers installed in the Boiler Room. The 3rd boiler is missing the remote shutdown switch | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Remote_Shutdown_Switches.png The remote shutdown switch provides a means of shutting off the boiler fuel supply should an emergency situation arise. The remote shutdown switch allows the operator to shut the unit down from a safe distance. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_Shutdown_Switches.png | file://x:/photopub/docs/0000000577/57915da6-d8ad-46d6-9c0b-d39e4e90fa76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__323b2bba_ec36_4ab1_8912_431a8b6e491a
GAHE-798596-2017 | HE-498752-2017 | 4/20/2017 8:25:03 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #1st_stage_reg_below_liquid_level.png When installing a first stage regulator it is common practice to do so by installing the regulator above the liquid level of the propane tank. This practice is commonly done because typically the first stage regulator is for vapour service only, the regulators in question are installed below the liquid level which may cause liquid propane to be trapped inside these regulators causing potential failure of regulator and system. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 1st_stage_reg_below_liquid_level.png | file://x:/photopub/docs/0000000588/bd67daa8-3b62-482a-9e0e-90693fb1d443.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fc7abde_4230_4d2d_8ec6_5fa6a4fdbef6
GAUP-798586-2017 | UW-469877-2016 | 4/19/2017 8:11:32 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Regulators1.png,Regulators2.png For a gas system to function properly the components installed must provide proper flow and be of proper size, the gas piping for the system and the regulators at the unit heaters do not match the second stage regulator delivery pressure possibly causing underfiring of the unit heaters. The system piping is undersized and the 2psi-inches regulators are redundant. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Regulators2.png | file://x:/photopub/docs/0000000588/2eb66b33-9d12-48e0-bef5-8ee131c33969.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0597bd11_5dc6_4f41_aaff_a7b3b5bf8ef1
GAUP-798586-2017 | UW-469877-2016 | 4/19/2017 8:11:32 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound 2psi - inches reg with 2nd stage regulator stamped 6-16"wc low pressure | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Regulators1.png,Regulators2.png For a gas system to function properly the components installed must provide proper flow and be of proper size, the gas piping for the system and the regulators at the unit heaters do not match the second stage regulator delivery pressure possibly causing underfiring of the unit heaters. The system piping is undersized and the 2psi-inches regulators are redundant. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Regulators1.png | file://x:/photopub/docs/0000000588/7239a140-f882-432d-95bb-60cdd27dd48d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0597bd11_5dc6_4f41_aaff_a7b3b5bf8ef1
GAHE-798641-2017 | HE-524298-2017 | 4/20/2017 7:44:03 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Incorrect orientation of swing joint and no vehicular protection | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Improper_swing_joint2.png When a gas pipe laid underground and comes up with a riser above grade must have a swing joint installed to prevent damage to piping in case of movement and settling of ground, also when this riser comes above grade and enters the building and is in an area of traffic from moving equipment or vehicles protection must be provided. | 2 | Physical protection of piping and tubing absent. | Improper_swing_joint2.png | file://x:/photopub/docs/0000000588/29187e7e-92db-40af-b1b5-df7a79ab3b03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cd357c4_64ca_4057_93bd_1553d41dafe2
BPVOP-809690-2017 | 2290982 | 5/4/2017 3:05:58 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that machine mounted vertical air receiver (1.5m long and 0.60m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000596/56cbad82-991a-4434-98d1-4fbf32a8d94c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a0b41c3_f3a7_4c1f_b27e_b773b2950c38
BPVOP-809691-2017 | 2290983 | 5/4/2017 3:12:11 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRESSURE_RELIEF_VALVE.png Upon assessment it is determined that machine mounted vertical air receiver (1.5m long and 0.60m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRESSURE_RELIEF_VALVE.png | file://x:/photopub/docs/0000000596/7cf6dd19-02d0-4c85-9420-cd01875be744.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b23b90bf_a2c3_42a4_b33c_5d4dc7a8835c
ELIN-788520-2017 | EL-444138-2016 | 4/6/2017 12:11:36 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #No_in_use_covers_1.png,No_in_use_covers_2.png The exterior receptacles located under roof canopy in wet location area does not include extra duty in use covers. This can lead to a shock issue and possible thermal issue | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_in_use_covers_2.png | file://x:/photopub/docs/0000000583/a92d0979-a0dd-4f56-89c7-cd0c384a8ac8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21e9dc32_3419_4899_aaee_09f2bf1c6e4c
ELIN-788520-2017 | EL-444138-2016 | 4/6/2017 12:11:36 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #No_in_use_covers_1.png,No_in_use_covers_2.png The exterior receptacles located under roof canopy in wet location area does not include extra duty in use covers. This can lead to a shock issue and possible thermal issue | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_in_use_covers_1.png | file://x:/photopub/docs/0000000583/134446be-89a5-4c63-aba3-840bc36505d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21e9dc32_3419_4899_aaee_09f2bf1c6e4c
ELIN-789850-2017 | EL-308283-2015 | 4/21/2017 10:12:43 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #NMD_No_Fittings1.png,NMD_No_Fittings2.png 120 volt 15 amp 14/2 NMD90 has been entered into a metal box without a fitting, this poses a shock hazard persons and possible mechanical damage to the wire and equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | NMD_No_Fittings2.png | file://x:/photopub/docs/0000000589/93ae40de-b4b5-4346-ae1e-df34b004d4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4492cf1_5bf4_4c64_8687_437e8b846b6c
ELIN-799913-2017 | EL-524647-2017 | 4/21/2017 11:58:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Ground_Wire.png The ground wire for a 200 amp 240 volt electrical service runs exposed on the exterior of the home without mechanical protection, this could result in damage to the ground wire. Loss of the ground wire could result in a shock hazard and damage to the other electrical components. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_Wire.png | file://x:/photopub/docs/0000000589/3d8d6566-bf67-4e0b-88e9-47b91c84d898.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ab91297_2d69_4e27_83b0_0792ed204fb4
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png | file://x:/photopub/docs/0000000590/32d6f75e-48cf-4758-ae42-654a9ab3ee43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png | file://x:/photopub/docs/0000000590/96b06c86-00e7-487b-be0e-2c699e2461f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures14.png | file://x:/photopub/docs/0000000590/5ae0a6a0-bf53-4d4f-9c89-930162866f98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-781669-2017 | EL-352243-2016 | 3/24/2017 11:31:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_bonding.png Service conduit not bonded. Possibility for high fault current unable to return to over current protection. High possibility for fire or shock in event of a fault. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_bonding.png | file://x:/photopub/docs/0000000576/9d267ee1-0262-4c09-beda-4e292df90dd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__349c71f4_8957_445d_9a23_8e30026dd6df
ELIN-781668-2017 | EL-352243-2016 | 3/24/2017 11:14:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Switches_.png Switches are located within 1 m of the bathtub and are not going to be GFCI protected. Possibility for shock. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Switches_.png | file://x:/photopub/docs/0000000576/e6f8a1cd-9aa5-49f1-9d6e-d9f46af0aa38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50055587_76fd_4301_abc9_008eb1c36ae5
ELIN-772359-2017 | EL-505090-2017 | 3/10/2017 10:18:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Electrode_not_installed.png The 200 amp 120/240 volt consumer service is installed and energized, the grounding electrode is not installed and is laying on top of grade. This creates the possibility of a potential difference between ground and the identified neutral conductor and can interfere with the proper operation of overcurrent devices. This can lead to both a thermal and shock hazard | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Electrode_not_installed.png | file://x:/photopub/docs/0000000570/e54a76b5-4b22-4712-8df2-9c32ab5b27ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3aee895e_3e3b_4ba2_94d0_1ead8d5d3566
ELIN-770667-2017 | EL-497147-2017 | 3/13/2017 1:44:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_too_close_to_edge_of_framing1.png,NMSC_too_close_to_edge_of_framing2.png When non-metallic sheathed cable is located too close to the edge of the framing there is risk of damage to the cable. If the screw intended to support the drywall pierces the cable there is risk of short circuit and potentially a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_too_close_to_edge_of_framing2.png | file://x:/photopub/docs/0000000570/1f7b5925-b4c1-4ca9-80d8-6301dc478636.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49463b0f_2f55_4b47_868e_a8bc64fd108d
ELIN-770667-2017 | EL-497147-2017 | 3/13/2017 1:44:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_too_close_to_edge_of_framing1.png,NMSC_too_close_to_edge_of_framing2.png When non-metallic sheathed cable is located too close to the edge of the framing there is risk of damage to the cable. If the screw intended to support the drywall pierces the cable there is risk of short circuit and potentially a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_too_close_to_edge_of_framing2.png | file://x:/photopub/docs/0000000570/3df02256-3f60-412c-9e50-e6ea27919e76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49463b0f_2f55_4b47_868e_a8bc64fd108d
ELIN-765252-2017 | EL-499279-2017 | 3/3/2017 2:02:16 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Outlet_location_missed.png Not enough 120 volt 15 amp receptacle locations have been provided in the roughwire of basement area of a home. This could pose a shock and fire hazard as extension cords and splitters may be used to power equipment in areas of the basement that proper spacing and density of installed receptacles has not been followed. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Outlet_location_missed.png | file://x:/photopub/docs/0000000566/f267f273-d94f-4b4c-a2ee-c917ae1ecc3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31ded5c3_159e_4bcf_a895_c73ea75c38a3
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png | file://x:/photopub/docs/0000000590/18820f4d-2bde-49b2-8b59-5065a71bed94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures12.png | file://x:/photopub/docs/0000000590/30c2e822-494c-4965-acaa-4b87c720c603.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png | file://x:/photopub/docs/0000000590/0295725b-d1fc-4cd8-8b09-387bb9ce80de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png | file://x:/photopub/docs/0000000590/e9ae17f5-990e-405d-bb83-683727f32c83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png | file://x:/photopub/docs/0000000590/850bb9de-261a-4dcd-b145-f51d2766f42b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png | file://x:/photopub/docs/0000000590/10c8306c-8d17-455d-8a27-d0122abb54b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png | file://x:/photopub/docs/0000000590/f24cf4a4-fd38-4902-a217-dd00ca56358f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
GAUP-791587-2017 | UW-520611-2017 | 4/10/2017 9:01:17 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #Garnett.png,Garnett.png Non bonded gas line. Shock hazard could exist if piping were to be inadvertently energized. This material is also susceptible to lighting strikes causing perforation of the tubing wall resulting in leaks and or risk of fire. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Garnett.png | file://x:/photopub/docs/0000000584/f8b87c6b-be31-416c-9750-b539cf34911b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12f3c013_ed4d_4c10_b7ac_342cf0114a5a
GAUP-792659-2017 | UW-521081-2017 | 4/10/2017 11:30:14 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Gibbons2.png Appliance certified for indoor use only installed outdoors below sun deck. Risk of water damage to safety controls resulting in unsafe condition. Contacts in safety controls could corrode closed preventing limits from activating in upset condition. Fire risk from overheating or dry firing due to non operating low water cut off. | 3 | Appliance not installed according to installation instructions | Gibbons2.png | file://x:/photopub/docs/0000000584/391a3e6e-6523-42b3-b959-68c1c7e6717b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314c2436_d609_4567_9e82_a4df59837d9c
ELIN-770667-2017 | EL-497147-2017 | 3/13/2017 1:44:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_too_close_to_edge_of_framing1.png,NMSC_too_close_to_edge_of_framing2.png When non-metallic sheathed cable is located too close to the edge of the framing there is risk of damage to the cable. If the screw intended to support the drywall pierces the cable there is risk of short circuit and potentially a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_too_close_to_edge_of_framing1.png | file://x:/photopub/docs/0000000570/5f873316-a357-47b2-ae48-5f3ddcd50b8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49463b0f_2f55_4b47_868e_a8bc64fd108d
ELIN-797711-2017 | EL-522873-2017 | 4/21/2017 8:36:19 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_covers.png At a stand alone 100amp 120/240volt single family dwelling modular home re-certification, the back mudroom was found in demolition state with all outlets found uncovered and energized. This can lead to a "Shock Hazard" condition. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_covers.png | file://x:/photopub/docs/0000000589/387d0345-71dd-4534-b913-4ddc085a1981.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4dfe0ea_54cd_4d1d_8bfa_e2f02662e79d
ELIN-782364-2017 | EL-457869-2016 | 3/27/2017 3:21:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Location_of_fused_disconnect.png 300 amp, 120/240 volt service rated fused disconnect switch installed in a location that does not provide 1 meter clearance in front of switch to provide safe operation. This is a thermal issue. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Location_of_fused_disconnect.png | file://x:/photopub/docs/0000000577/e099d50c-e60b-426e-a759-18d55ae8a5c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2989ae6f_a2f9_431d_846c_612ea882caf5
BPVIN-799845-2017 | UW-474302-2016 | 5/1/2017 10:06:10 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Remote_Shutdown_Lockout_Switch.png The remote shutdown switches must have a means of being locked in the "OPEN" position during times of boiler shutdown for maintenance or servicing. The lockout feature allows the switch to be locked in the "OFF" position and prevents the switch from being inadvertently turned back on. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_Shutdown_Lockout_Switch.png | file://x:/photopub/docs/0000000594/78ee1ab8-e0f5-4ee4-abb7-39bacb68a02a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b711a11_43ea_4c13_9e2e_0410a2a6a0f5
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png | file://x:/photopub/docs/0000000590/58671bc9-84f1-46b2-baf9-bdf8cb59766d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png | file://x:/photopub/docs/0000000590/1e2f9250-5bc2-4a07-aa12-9d182fe926d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png | file://x:/photopub/docs/0000000590/78d3bfd9-41bd-4e18-a86a-e186a064e543.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
GAIN-782160-2017 | GA-514659-2017 | 4/4/2017 9:50:47 AM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #1.png Underground gas lines running to back yard under a 20psi pressure test with air while tied into the main gas system of a residence. Only a ball valve was separating the 20psi air and the 1/2psi natural gas. If ball valve was opened it would introduce high pressure air into the gas piping system in the residence creating a dangerous air/fuel ratio inside the piping which has a potential to ignite. More pictures in attachments. | 3 | Code prohibited practices or materials | 1.png | file://x:/photopub/docs/0000000581/b085f980-460b-4b75-add7-f4b1939eecc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53815d1e_ff18_44b6_a75e_4088258389c8
ELIN-807582-2017 | EL-324686-2015 | 5/2/2017 2:37:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Panel_Openings1.png,Energized_Panel_Openings2.png,Panel_De-energized_.png A 200 amp 120/240 volt electrical panel has large openings in the cover where the interior energized bus is accessible. This poses a shock hazard to persons and potential mechanical damage to the electrical panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Panel_Openings2.png | file://x:/photopub/docs/0000000595/17379dda-cf20-4ced-9b49-7478a1792c05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2964c7a2_41dd_4233_8bc0_2d3ec0dd85d5
ELIN-807582-2017 | EL-324686-2015 | 5/2/2017 2:37:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Panel_Openings1.png,Energized_Panel_Openings2.png,Panel_De-energized_.png A 200 amp 120/240 volt electrical panel has large openings in the cover where the interior energized bus is accessible. This poses a shock hazard to persons and potential mechanical damage to the electrical panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Panel_Openings1.png | file://x:/photopub/docs/0000000595/cc0cc93b-37dc-4cfb-82f8-c1c556d1cf53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2964c7a2_41dd_4233_8bc0_2d3ec0dd85d5
ELIN-807582-2017 | EL-324686-2015 | 5/2/2017 2:37:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Panel_Openings1.png,Energized_Panel_Openings2.png,Panel_De-energized_.png A 200 amp 120/240 volt electrical panel has large openings in the cover where the interior energized bus is accessible. This poses a shock hazard to persons and potential mechanical damage to the electrical panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_De-energized_.png | file://x:/photopub/docs/0000000595/6e100161-a731-458d-9f78-e81f028eed1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2964c7a2_41dd_4233_8bc0_2d3ec0dd85d5
ELIN-787907-2017 | EL-518489-2017 | 4/6/2017 1:05:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Gas_line_in_contavt_with_electric_lin_e_only_8_inches_below_grade.png An underground installation of armoured cable operating at 60 amps and 240volts was found in direct contact with an underground gas line no separation. The underground installation was also not buried to a minimum depots and in this case less than a 1/3n of the minimum cover for the cable and gas line were provided. Either of these two conditions are hazardous but the combined hazards of this installation for future damage or injury to persons is possible. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Gas_line_in_contavt_with_electric_lin_e_only_8_inches_below_grade.png | file://x:/photopub/docs/0000000584/c703b946-2e24-45e3-8d75-c5326ee22e70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293358cc_eaaf_4c2d_837a_59451b571726
ELIN-798980-2017 | EL-457590-2016 | 4/21/2017 2:49:00 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures1.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures2.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures3.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures4.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures5.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures6.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures7.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures8.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures9.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures10.png,Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures11.png,Ineffective_bonding_repair_after_original_ | 3 | Continuity Bonding; method for equipment is not adequate. | Ineffective_bonding_repair_after_original_bond_conductors_were_cut_off_the_fixtures13.png | file://x:/photopub/docs/0000000590/da266361-51df-4938-a247-a4715a168bd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__075fba9c_d469_41da_b881_67aee96e1526
ELIN-797729-2017 | EL-473747-2016 | 4/19/2017 12:20:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Bonding.png The 200 amp 120/240 volt service installation upgrade did not include the bonding requirements for the existing water or gas lines, bonding these lines eliminates any potential difference from being applied to the system, without this- it can become a shock hazard | 3 | Equipment Gas line, cast or water pipe has not been bonded | Bonding.png | file://x:/photopub/docs/0000000588/5923f62a-3f62-4036-9288-823eab5d409c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2999884f_0c61_4b69_a4cd_ffe690ce0049
ELIN-804792-2017 | EL-474758-2016 | 4/28/2017 3:36:29 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Hazard1.png,Hazard2.png The 100 amp 120/240 volt panelboard is not securely attached, does not have the cover installed and is fed through a 'branch breaker' for the mobile home service. This is a shock hazard | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Hazard1.png | file://x:/photopub/docs/0000000593/13c58871-7e75-49bb-bced-5c684797ca34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__801c8fdf_e446_4c79_a610_5ac5e515be4d
ELIN-770789-2017 | EL-407854-2016 | 3/14/2017 9:17:08 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #122122.png 15 amp rated receptacles were protected by a 20 amp circuit. Possible fire hazard as plug was underrated for over current protection | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 122122.png | file://x:/photopub/docs/0000000571/abc2cb52-6c7c-4bad-8078-43ac220be010.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4eb2885b_c1e3_4148_be5b_5f91753c4aae
ELIN-782481-2017 | EL-514894-2017 | 3/30/2017 7:02:46 PM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | #Water_in_panel.png The 100 amp 120/240 volt temporary service during or after installation had moisture accumulate on the overcurrent devices in the panelboard, this is an equipment damage issue and could lead to additional shock or thermal issues as well. The service is not energized at this time. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Water_in_panel.png | file://x:/photopub/docs/0000000579/2dfe994a-1fa9-46fd-ac74-0369e606bdb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74bdda2c_d091_4fa5_a693_669d523b747e
ELIN-734240-2017 | EL-263654-2015 | 3/30/2017 11:09:05 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Mai_residence_panel.png The 15 amp 120 volt receptacles located in the bedrooms of the residence do not include AFCI protection, this is a thermal hazard | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Mai_residence_panel.png | file://x:/photopub/docs/0000000579/c686bf5e-344c-4261-bb08-0704ffd82a54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea6747d3_7a52_4a69_b854_6dd68f3cbfa7
ELIN-783336-2017 | EL-293890-2015 | 3/30/2017 10:30:45 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Thermostat.png The 15 amp 120 volt branch circuit for the electric in-floor heat in the washroom is not installed due to box fill issues, is energized and single occupant in residence. This is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Thermostat.png | file://x:/photopub/docs/0000000579/8ec7cf4f-11d5-4abf-8872-82ab38875ca4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e5ce19c_8639_4b3b_b780_a2eea5403525
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png | file://x:/photopub/docs/0000000584/6286cd38-2378-4df5-ac27-16bde53922f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png | file://x:/photopub/docs/0000000584/5337b4c8-32c8-44ce-b901-8e2488db9b99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public8.png | file://x:/photopub/docs/0000000584/2296c75b-6939-405d-b8c4-2c65036869e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public9.png | file://x:/photopub/docs/0000000584/93344f95-40a3-488f-bac7-18232967917a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public7.png | file://x:/photopub/docs/0000000584/947feed5-1f1b-421d-b4f3-b1b624816040.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELIN-804792-2017 | EL-474758-2016 | 4/28/2017 3:36:29 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Hazard1.png,Hazard2.png The 100 amp 120/240 volt panelboard is not securely attached, does not have the cover installed and is fed through a 'branch breaker' for the mobile home service. This is a shock hazard | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Hazard2.png | file://x:/photopub/docs/0000000593/3e8cbe5d-0f28-42db-8c0f-d6e072486773.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__801c8fdf_e446_4c79_a610_5ac5e515be4d
EDIN-808882-2017 | ED-435064-2016 | 5/3/2017 2:48:11 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | #Trip_hazard.png | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Trip_hazard.png | file://x:/photopub/docs/0000000595/fb6aa336-b6eb-4dcb-8af1-3c1a92b73d46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad93b498_f54a_4025_b46e_3421f5142367
GAIN-778839-2017 | GA-509923-2017 | 4/3/2017 9:30:28 AM | ASSESS: GA: Rough-In | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Venting.png Appliance vent located to close to air supply inlet for the mechanical room. Potential for flue gases exiting furnace vent to enter the air supply inlet allowing the products of combustion to enter the living space. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Venting.png | file://x:/photopub/docs/0000000580/98e7cf2a-a813-48bf-b1e2-288a9970bdcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91590b55_3319_4086_9422_558364e3d774
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator11.png | file://x:/photopub/docs/0000000575/ee73ae65-0ca8-412b-9097-36b6fef10271.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator3.png | file://x:/photopub/docs/0000000575/642c88fe-4f39-49de-8819-cef5d5ef536c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator2.png | file://x:/photopub/docs/0000000575/4f89aa68-def3-43fc-bea4-75e9c7f25e60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator4.png | file://x:/photopub/docs/0000000575/3dda31ba-71e1-4222-a31a-d2f8aab80864.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public10.png | file://x:/photopub/docs/0000000584/30b3db58-3fff-4c08-860f-cbd6fbdc701e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png | file://x:/photopub/docs/0000000584/07ba1dc0-00ce-42fb-bbbc-2516c2f0ad60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png | file://x:/photopub/docs/0000000584/9600b1bc-c052-4209-8b31-f68abf34b1b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png | file://x:/photopub/docs/0000000584/5c1506de-d0d9-4fdb-97f3-0650a704876f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-791843-2017 | HE-517279-2017 | 4/7/2017 6:46:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unapproved electrical equipment and products are still being displayed and offered for sale with store display areas accessible to general public | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public1.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public2.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public3.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public4.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public5.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png,Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_with | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_is_still_being_displayed_or_offered_for_sale_within__to_general_public_store_display_areas_accessible_to_general_public6.png | file://x:/photopub/docs/0000000584/232fde55-036f-4df2-9bd8-d9cf118f90a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__174dec4d_56a0_458a_8e8a_da0a5a1d0401
ELHE-774924-2017 | HE-511595-2017 | 3/14/2017 3:55:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #P31.png,P32.png,P33.png,P34.png,P35.png Electrical service equipment is exposed to weather elements because wooden box housing this equipment is not weatherproofed. Water is seeping in through roof and other openings that can enter into distribution panel parts causing corrosion at electrical metal parts and within circuit breakers. Moisture in electrical equipment can cause failure of the distribution system and sometimes fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | P34.png | file://x:/photopub/docs/0000000572/d324be45-cc22-42f1-a68d-6790785249d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5673e2_440d_42e4_8b08_b40ce44416e5
ELHE-774924-2017 | HE-511595-2017 | 3/14/2017 3:55:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #P31.png,P32.png,P33.png,P34.png,P35.png Electrical service equipment is exposed to weather elements because wooden box housing this equipment is not weatherproofed. Water is seeping in through roof and other openings that can enter into distribution panel parts causing corrosion at electrical metal parts and within circuit breakers. Moisture in electrical equipment can cause failure of the distribution system and sometimes fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | P33.png | file://x:/photopub/docs/0000000572/b73dd10f-ab93-40d8-b790-4bf5502eeafb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5673e2_440d_42e4_8b08_b40ce44416e5
ELHE-774924-2017 | HE-511595-2017 | 3/14/2017 3:55:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #P31.png,P32.png,P33.png,P34.png,P35.png Electrical service equipment is exposed to weather elements because wooden box housing this equipment is not weatherproofed. Water is seeping in through roof and other openings that can enter into distribution panel parts causing corrosion at electrical metal parts and within circuit breakers. Moisture in electrical equipment can cause failure of the distribution system and sometimes fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | P32.png | file://x:/photopub/docs/0000000572/faac7ecc-51a4-4ec2-a55a-cff232ef168a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5673e2_440d_42e4_8b08_b40ce44416e5
ELHE-774924-2017 | HE-511595-2017 | 3/14/2017 3:55:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Box housing service equipment is not weatherproofed and moisture is damaging the service equipment. | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #P31.png,P32.png,P33.png,P34.png,P35.png Electrical service equipment is exposed to weather elements because wooden box housing this equipment is not weatherproofed. Water is seeping in through roof and other openings that can enter into distribution panel parts causing corrosion at electrical metal parts and within circuit breakers. Moisture in electrical equipment can cause failure of the distribution system and sometimes fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | P31.png | file://x:/photopub/docs/0000000572/7f340d7a-d622-4972-8864-600f990550b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5673e2_440d_42e4_8b08_b40ce44416e5
ELHE-774924-2017 | HE-511595-2017 | 3/14/2017 3:55:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #P31.png,P32.png,P33.png,P34.png,P35.png Electrical service equipment is exposed to weather elements because wooden box housing this equipment is not weatherproofed. Water is seeping in through roof and other openings that can enter into distribution panel parts causing corrosion at electrical metal parts and within circuit breakers. Moisture in electrical equipment can cause failure of the distribution system and sometimes fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | P35.png | file://x:/photopub/docs/0000000572/80fd02bb-75ec-41c0-909b-5e6c4bc94abc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5673e2_440d_42e4_8b08_b40ce44416e5
GAIN-772250-2017 | GA-372515-2016 | 3/10/2017 5:35:12 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #Propane_regulator.png 2 stage propane regulator was installed below the maximum liquid level inside tank. This could result in liquid entering regulator which it is not designed to handle Liquefaction of propane can create a hazard. First-stage and integral two-stage propane vapour regulators that are not installed directly on a propane container can be subjected to liquid propane due to no-flow conditions and/or changes in ambient temperatures if they are installed below the liquid level of the supply container. Vapour service regulators are not designed to regulate propane liquid, and may be damaged by it, or may pass liquid leading to hazardous conditions downstream. These regulators must be installed above the maximum liquid level of the supply container(s), and have the supply connection oriented to allow for any liquid to drain back to the container. Second-stage regulators installed in areas of the province where the ambient temperature may permit reliquification at the supplied intermediate pressur | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Propane_regulator.png | file://x:/photopub/docs/0000000569/df21321d-d619-437c-b0ee-da55b8d945e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1048d7cb_776e_40b3_89f1_0f1a571f4fa6
ELIN-779389-2017 | EL-504709-2017 | 3/22/2017 12:51:09 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Size of staples used for support of NMD90 cables is not approved for the use as installed. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples1.png,Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples2.png,Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples3.png Size of staples used for support of non-metallic sheathed NMD90 cables is not approved for the use as installed. When electrical equipment is not approved for the use as installed and is not used as specified by manufacturer's installation instructions and specifications, the electrical equipment could get damaged and cause a possible electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples1.png | file://x:/photopub/docs/0000000576/57035efb-6a28-4e24-ad3f-edad77e9c015.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d93fc8e1_1045_465f_bf2a_3d91dddda7d4
ELIN-779389-2017 | EL-504709-2017 | 3/22/2017 12:51:09 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Size of staples used for support of NMD90 cables is not approved for the use as installed. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples1.png,Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples2.png,Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples3.png Size of staples used for support of non-metallic sheathed NMD90 cables is not approved for the use as installed. When electrical equipment is not approved for the use as installed and is not used as specified by manufacturer's installation instructions and specifications, the electrical equipment could get damaged and cause a possible electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | Staples_on_NMD90_cable_not_used_as_per_approved_use_of_staples2.png | file://x:/photopub/docs/0000000576/b4b74f59-2123-4bd4-8aba-720d5c1a8868.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d93fc8e1_1045_465f_bf2a_3d91dddda7d4
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator5.png | file://x:/photopub/docs/0000000575/f9a3fec6-af1f-4b63-96af-fbf8b5a30fc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator16.png | file://x:/photopub/docs/0000000575/d17eb52d-93d9-442f-bee2-b137ba39bd21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator1.png | file://x:/photopub/docs/0000000575/019ea4e2-908e-4b4f-93ba-4fb8699b5469.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator14.png | file://x:/photopub/docs/0000000575/72f9a747-dac6-4564-aded-bf670abcddf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator15.png | file://x:/photopub/docs/0000000575/5534c672-1736-4c00-b9aa-5166689847d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator7.png | file://x:/photopub/docs/0000000575/42ab22d0-24fe-40fb-99e1-3a63c7abd586.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator9.png | file://x:/photopub/docs/0000000575/a6520793-a5d1-434e-be3c-b85f3eb82416.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator6.png | file://x:/photopub/docs/0000000575/c32dfa31-8866-4507-bd8e-0d49eae5522f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator13.png | file://x:/photopub/docs/0000000575/940e7e77-db48-4c79-9f5a-ac40aec1b2f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator8.png | file://x:/photopub/docs/0000000575/88c2653d-d7b9-449a-af95-c9e75b6c1787.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELHE-781436-2017 | HE-515307-2017 | 3/23/2017 3:38:47 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL278 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | 4 | 4 | #Fire_alarm_annunciator1.png,Fire_alarm_annunciator2.png,Fire_alarm_annunciator3.png,Fire_alarm_annunciator4.png,Fire_alarm_annunciator5.png,Fire_alarm_annunciator6.png,Fire_alarm_annunciator7.png,Fire_alarm_annunciator8.png,Fire_alarm_annunciator9.png,Fire_alarm_annunciator10.png,Fire_alarm_annunciator11.png,Fire_alarm_annunciator12.png,Fire_alarm_annunciator13.png,Fire_alarm_annunciator14.png,Fire_alarm_annunciator15.png,Fire_alarm_annunciator16.png Life safety system - Fire alarm annunciator panel in trouble condition with signs of moisture ingress and no evidence of approval. | 4 | Life Safety System, Fire Alarm, Emergency systems, Life safety is not observed or has failed | Fire_alarm_annunciator12.png | file://x:/photopub/docs/0000000575/1a207257-4009-48a9-8faf-eb137e88c8f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e07ce59_8614_4f4f_a3c8_69c8cf36368f
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png | file://x:/photopub/docs/0000000596/11a33465-6c21-427f-8abf-69acbce3611d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELIN-775769-2017 | EL-458781-2016 | 3/16/2017 9:52:41 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #15_amp_receptacle_on_20_amp_circuit_.png Receptacles rated for 15 amps were installed on a circuit with overcurrent protection and wiring rated at 20 amps. This could lead to overheating of the 15 amp receptacle and a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 15_amp_receptacle_on_20_amp_circuit_.png | file://x:/photopub/docs/0000000572/ba604a39-9fe2-4262-9380-a57264f87f55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14a2a87c_42a2_4970_9f8d_e1bd79df1322
ELHE-793027-2017 | HE-521306-2017 | 4/12/2017 4:49:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Main_distribution_no_cover_access_impeded.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_distribution_no_cover_access_impeded.png | file://x:/photopub/docs/0000000596/d13b5f95-46f1-4473-aef0-fd6c2cf3c5f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f786b35a_00bb_4859_a52a_34ca3318e964
ELHE-793027-2017 | HE-521306-2017 | 4/12/2017 4:49:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Main_distribution_no_cover_access_impeded.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_distribution_no_cover_access_impeded.png | file://x:/photopub/docs/0000000596/deaf525e-3b30-426c-9d86-f86ca1732881.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f786b35a_00bb_4859_a52a_34ca3318e964
GAUP-779977-2017 | UW-514344-2017 | 3/22/2017 7:01:54 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Overheated_boiler1.png,Overheated_boiler2.png,Overheated_boiler3.png Boiler shows signs of overheating, original spark igniter was melted, new igniter was installed but not grounded properly, can lead to fire and improper arcing. | 3 | Appliance not installed according to installation instructions | Overheated_boiler2.png | file://x:/photopub/docs/0000000576/de1df6d1-3cff-457b-aa35-dc7106166bb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__196ee435_9c2f_49ea_9d09_82eaff8c4ed9
GAIN-770797-2017 | GA-506313-2017 | 3/17/2017 8:29:26 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Venting.png Venting oversized, can cause condensation and poor drafting of appliance which can result in damage that the appliance and possible sooting. Creation of carbon monoxide as well | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Venting.png | file://x:/photopub/docs/0000000576/d0e00ed5-589b-4fe6-8de7-5477defb7098.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2566243b_fea9_4961_8398_8ede92920e93
GAUP-779977-2017 | UW-514344-2017 | 3/22/2017 7:01:54 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Overheated_boiler1.png,Overheated_boiler2.png,Overheated_boiler3.png Boiler shows signs of overheating, original spark igniter was melted, new igniter was installed but not grounded properly, can lead to fire and improper arcing. | 3 | Appliance not installed according to installation instructions | Overheated_boiler1.png | file://x:/photopub/docs/0000000576/a539c314-cb45-48ff-9014-71f5dd77a7e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__196ee435_9c2f_49ea_9d09_82eaff8c4ed9
GAUP-779977-2017 | UW-514344-2017 | 3/22/2017 7:01:54 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Overheated_boiler1.png,Overheated_boiler2.png,Overheated_boiler3.png Boiler shows signs of overheating, original spark igniter was melted, new igniter was installed but not grounded properly, can lead to fire and improper arcing. | 3 | Appliance not installed according to installation instructions | Overheated_boiler3.png | file://x:/photopub/docs/0000000576/6bd6a89d-17d2-4c51-b802-61bf4341a60c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__196ee435_9c2f_49ea_9d09_82eaff8c4ed9
ELIN-772530-2017 | EL-469338-2016 | 3/14/2017 12:57:52 PM | ASSESS: EL: Service Connection | png | #asFound More than 1.5 m of service conductors in side dwelling | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 2 | #11.png,12.png Service conductors enter house for greater than 1.5 m this is a shock and fire hazard as the service conductors could be damaged. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 12.png | file://x:/photopub/docs/0000000571/5cd0a24a-684c-4848-91dc-f3503fffec29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff94a2b7_2bb3_4e49_b3cb_289d636be314
ELIN-772530-2017 | EL-469338-2016 | 3/14/2017 12:57:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 2 | #11.png,12.png Service conductors enter house for greater than 1.5 m this is a shock and fire hazard as the service conductors could be damaged. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 11.png | file://x:/photopub/docs/0000000571/9f6d96f4-7ef3-4f5d-a8bb-a4e9e5f4ee46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff94a2b7_2bb3_4e49_b3cb_289d636be314
BPVIN-772077-2017 | BPV-509712-2017 | 3/9/2017 12:16:04 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRV_.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 200psi air receiver mounted with machine. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRV_.png | file://x:/photopub/docs/0000000572/fb119e18-449b-40ea-83d9-c1451a112d03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73cefdba_6e98_4da6_a197_a3276a9f0f2f
ELIN-770753-2017 | EL-473182-2016 | 3/9/2017 3:30:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png Cables run along open faces of rafters with a greater than 1 meter vertical distance to the roof. This is a shock and fire hazard as an individual could step on the cables and damage the insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A2.png | file://x:/photopub/docs/0000000569/80d48dd7-19ba-4d7a-9021-1ebbcc166ed8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4064b025_6231_4760_9a03_5dc6a4900ef0
ELIN-770753-2017 | EL-473182-2016 | 3/9/2017 3:30:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png Cables run along open faces of rafters with a greater than 1 meter vertical distance to the roof. This is a shock and fire hazard as an individual could step on the cables and damage the insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A4.png | file://x:/photopub/docs/0000000569/f0dfc6e6-7ebe-42ad-bd4e-93bea0c63986.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4064b025_6231_4760_9a03_5dc6a4900ef0
ELIN-770753-2017 | EL-473182-2016 | 3/9/2017 3:30:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png Cables run along open faces of rafters with a greater than 1 meter vertical distance to the roof. This is a shock and fire hazard as an individual could step on the cables and damage the insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A3.png | file://x:/photopub/docs/0000000569/470c056e-8cf4-4864-b7ab-0828615f2f0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4064b025_6231_4760_9a03_5dc6a4900ef0
ELIN-770753-2017 | EL-473182-2016 | 3/9/2017 3:30:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png Cables run along open faces of rafters with a greater than 1 meter vertical distance to the roof. This is a shock and fire hazard as an individual could step on the cables and damage the insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A1.png | file://x:/photopub/docs/0000000569/1370e2bd-6344-47bc-b85a-8ae437f67c1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4064b025_6231_4760_9a03_5dc6a4900ef0
ELIN-770753-2017 | EL-473182-2016 | 3/9/2017 3:30:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png Cables run along open faces of rafters with a greater than 1 meter vertical distance to the roof. This is a shock and fire hazard as an individual could step on the cables and damage the insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A5.png | file://x:/photopub/docs/0000000569/11eb76c4-3b48-474c-a199-e55f1e056bb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4064b025_6231_4760_9a03_5dc6a4900ef0
GAIN-760425-2017 | GA-467083-2016 | 2/27/2017 12:16:41 PM | ASSESS: GA: Final | png | #asFound No 2psi-inches regulator installed | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #2psi_system.png Pressure regulators are installed to deliver a certain gas pressure as required by the gas piping system or appliance if these pressures are not regulated to appliance specifications then it could cause damage to the gas system or components in turn causing pre-mature failure or immediate failure of the appliance or piping system. | 4 | Appliance regulator not installed, incorrect delivery pressure | 2psi_system.png | file://x:/photopub/docs/0000000563/0428369f-c460-4853-bcc9-91835a17e0ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a19996a7_ed9a_4324_bd08_a789ecfe2635
BPVOP-812533-2017 | 2295987 | 5/9/2017 10:39:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | #Scale.png,Scale.png | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale.png | file://x:/photopub/docs/0000000599/0b8ca976-49aa-42f8-b6aa-f853e488dfeb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f83efa9_ac91_443b_adb2_44c18431ae6c
ELIN-798807-2017 | EL-520816-2017 | 4/21/2017 2:55:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #No_bond_screw_in_panel1.png,No_bond_screw_in_panel2.png In a grounded alternating current system for consumer service electrical panel, the neutral (grounded conductor) is required to be connected to the bonding system of the electrical installation. This interconnection provides a path to ground for an electrical fault between an ungrounded conductor and the bonding system. The interconnection inside the the electrical panel is usually accomplished by installing a neutral bonding screw or strap between the neutral buss and the metal enclosure of the electrical panel. In this installation of a new electrical service installed in a new single family dwelling, the neutral bonding screw was not installed in the electrical panel. Once the electrical panel is energized, there is a potential shock hazard to persons if an electrical fault was to occur. Any persons touching metal connected to the bonding system could now provide the electrical path to ground during an electrical fault. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | No_bond_screw_in_panel2.png | file://x:/photopub/docs/0000000589/5b3ad068-0fbc-4bbf-b7e5-42b69092d7d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__152073de_3873_4cdc_9533_f284b54933dd
ELIN-798807-2017 | EL-520816-2017 | 4/21/2017 2:55:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #No_bond_screw_in_panel1.png,No_bond_screw_in_panel2.png In a grounded alternating current system for consumer service electrical panel, the neutral (grounded conductor) is required to be connected to the bonding system of the electrical installation. This interconnection provides a path to ground for an electrical fault between an ungrounded conductor and the bonding system. The interconnection inside the the electrical panel is usually accomplished by installing a neutral bonding screw or strap between the neutral buss and the metal enclosure of the electrical panel. In this installation of a new electrical service installed in a new single family dwelling, the neutral bonding screw was not installed in the electrical panel. Once the electrical panel is energized, there is a potential shock hazard to persons if an electrical fault was to occur. Any persons touching metal connected to the bonding system could now provide the electrical path to ground during an electrical fault. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | No_bond_screw_in_panel1.png | file://x:/photopub/docs/0000000589/62c8ad4c-7687-428a-9f3f-8c4f6f4272a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__152073de_3873_4cdc_9533_f284b54933dd
ELIN-781025-2017 | EL-503345-2017 | 3/24/2017 9:25:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Device fox requires additional support from two sides | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Device_box__Device_box_requires_additional_support.png Device boxes greater than 4 inches require additional support on two sides | 4 | Installation of electrical equipment Fixtures without suitable support. | Device_box__Device_box_requires_additional_support.png | file://x:/photopub/docs/0000000576/0f9720e8-5668-4370-8814-99f0a8be030d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64312cc3_82b2_4db3_91c3_6afd4b9fb027
ELIN-793233-2017 | UW-521465-2017 | 4/10/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Coverplate_missing.png A cover plate was not installed on an energized receptacle. This could lead to accidental contact of the energized terminals resulting in a shock or electrocution hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Coverplate_missing.png | file://x:/photopub/docs/0000000586/fdc6bf64-4fd2-476a-97a6-0d9ece5cdf7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6190186_963f_44d3_8994_4b2d573c6b9f
ELHE-793242-2017 | HE-521471-2017 | 4/10/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_in_disrepair.png The overhead service conductors are not adequately supported and the panel below is in disrepair. This condition could lead to the conductors separating and potentially causing a fire hazard to nearby structures or a shock and electrocution hazard to persons in the area. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_in_disrepair.png | file://x:/photopub/docs/0000000586/28b0b399-e716-48bf-b09a-5521ebb04880.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7cc68200_1ebc_4d52_8c8d_899d3ae3c766
ELHE-793236-2017 | HE-521466-2017 | 4/12/2017 2:56:02 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Unattached_conductors_over_roof.png Energized conductors are within reach of a person on the roof and are not attached to an approved attachment device. This condition could lead to a potential shock and fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Unattached_conductors_over_roof.png | file://x:/photopub/docs/0000000586/5ffe6a1b-6331-4a03-800f-4160a644bb68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b29c0f8_2408_487f_8bf6_90f9c04414e4
GAOP-792743-2017 | 2170214 | 4/10/2017 11:37:17 AM | ASSESS: GA OP: Periodic | png | #asFound | GA031 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | 3 | 3 | #Propane_shack1.png,Propane_shack2.png,Propane_shack3.png,Propane_shack4.png Propane cylinder fill station is a fully enclosed structure with no ventilation grilles to allow any propane leakage or seepage to escape to outside when door is closed. Allows for buildup of propane which could lead to fire or explosion if door is opened and sources of ignition are present. | 3 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | Propane_shack2.png | file://x:/photopub/docs/0000000584/0e352a14-8e65-4500-8e82-7507dec62138.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5945a903_7a75_403d_8bc2_086ea64969a5
GAOP-792743-2017 | 2170214 | 4/10/2017 11:37:17 AM | ASSESS: GA OP: Periodic | png | #asFound | GA031 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | 3 | 3 | #Propane_shack1.png,Propane_shack2.png,Propane_shack3.png,Propane_shack4.png Propane cylinder fill station is a fully enclosed structure with no ventilation grilles to allow any propane leakage or seepage to escape to outside when door is closed. Allows for buildup of propane which could lead to fire or explosion if door is opened and sources of ignition are present. | 3 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | Propane_shack1.png | file://x:/photopub/docs/0000000584/b64d21e7-9767-4cde-909b-869548001063.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5945a903_7a75_403d_8bc2_086ea64969a5
GAOP-792743-2017 | 2170214 | 4/10/2017 11:37:17 AM | ASSESS: GA OP: Periodic | png | #asFound | GA031 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | 3 | 3 | #Propane_shack1.png,Propane_shack2.png,Propane_shack3.png,Propane_shack4.png Propane cylinder fill station is a fully enclosed structure with no ventilation grilles to allow any propane leakage or seepage to escape to outside when door is closed. Allows for buildup of propane which could lead to fire or explosion if door is opened and sources of ignition are present. | 3 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | Propane_shack3.png | file://x:/photopub/docs/0000000584/d263722a-92bb-4446-bab1-df7cf78d547d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5945a903_7a75_403d_8bc2_086ea64969a5
GAOP-792743-2017 | 2170214 | 4/10/2017 11:37:17 AM | ASSESS: GA OP: Periodic | png | #asFound | GA031 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | 3 | 3 | #Propane_shack1.png,Propane_shack2.png,Propane_shack3.png,Propane_shack4.png Propane cylinder fill station is a fully enclosed structure with no ventilation grilles to allow any propane leakage or seepage to escape to outside when door is closed. Allows for buildup of propane which could lead to fire or explosion if door is opened and sources of ignition are present. | 3 | Gas meter regulator not vented to the outdoors (fully enclosed with-in a structure). No source of ignition present | Propane_shack4.png | file://x:/photopub/docs/0000000584/beefb285-5fa5-4052-86aa-62ce8948054b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5945a903_7a75_403d_8bc2_086ea64969a5
ELIN-795738-2017 | EL-523131-2017 | 4/18/2017 | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_conductor_terminated_on_metal_enclosure.png 100 amp, 120/240 volt main distribution panel has an existing ground wire installed to the metal enclosure and not to the neutral conductor. This is a thermal issue. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_terminated_on_metal_enclosure.png | file://x:/photopub/docs/0000000588/378c8cb5-da80-44e6-9ac3-e38ee81de65b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fce3eaba_9881_4642_a89e_c8c06b16ca22
BPVIN-767059-2017 | BPV-199342-2015 | 3/1/2017 8:37:26 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP022 | 1.0.2 Clearances/Maintenance - Insufficient clearance for operation, maintenance and inspection. | 2 | 2 | #CLEARANCE_AROUND_BOILER_NOT_AS_PER_CODE.png Upon assessment it is found that clearance around boiler is not to code. It will be difficult to perform maintenance. | 2 | 1.0.2 Clearances/Maintenance - Insufficient clearance for operation, maintenance and inspection. | CLEARANCE_AROUND_BOILER_NOT_AS_PER_CODE.png | file://x:/photopub/docs/0000000565/2552bfe5-151e-49c5-bb4f-091b70fd2559.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95b6ad97_94b8_4af9_858e_30892af5965b
ELIN-802150-2017 | EL-506611-2017 | 4/26/2017 4:09:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90.png A 20KW 240 volt electric Furnace has been temporarily connected with a piece of #2 non metallic sheathed cable, the cable is laying loose on a concrete floor without support or protection. This poses a shock hazard to persons and potential damage to the electrical equipment as this cable is not rated to be used exposed without mechanical protection and proper support. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90.png | file://x:/photopub/docs/0000000591/d70a28fa-7bcf-4d74-b24b-acb2050252cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8244916_70b7_4e04_afc7_20f37760d26b
BPVOP-809302-2017 | 3940749 | 5/4/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV.png Upon the assessment of a Hot Water Boiler with MAWP of 30 psig, was found that the Safety Relief Valve was installed in 2010 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV.png | file://x:/photopub/docs/0000000599/3888f99c-d9f2-4c51-95d9-d50734fd5eb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18ccde7b_64c6_4ee1_9f46_c8a0f02d3282
BPVOP-809300-2017 | 3940751 | 5/4/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve.png Upon the assessment of a Hot Water Boiler with MAWP of 30 psig, was found that the Safety Relief Valve was installed in 2010 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000599/15a8a3fd-f1c3-4ce9-805b-e7b312f0d87c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33b78421_1280_4744_8724_d05a66cb52a8
ELIN-773094-2017 | UW-510463-2017 | 3/10/2017 3:55:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png Service conductors are under sized. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A2.png | file://x:/photopub/docs/0000000569/2d89e26d-6ddc-4d28-a538-62847dd305c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbffa098_ff9b_471c_9908_ac543b350aaf
ELIN-773094-2017 | UW-510463-2017 | 3/10/2017 3:55:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png Service conductors are under sized. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A3.png | file://x:/photopub/docs/0000000569/9e961f37-f448-44e9-9afb-e7cc0ab1f726.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbffa098_ff9b_471c_9908_ac543b350aaf
ELIN-773094-2017 | UW-510463-2017 | 3/10/2017 3:55:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #A1.png,A2.png,A3.png Service conductors are under sized. This is a fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A1.png | file://x:/photopub/docs/0000000569/f461d372-32c9-448c-a2de-f0050b4e843b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbffa098_ff9b_471c_9908_ac543b350aaf
GAIN-790154-2017 | GA-491995-2017 | 4/6/2017 2:34:55 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | #Vent_limiter_wrong_postion.png The regulator in question is installed to reduce from high pressure (2psi) to low pressure (1/4 psi). This regulator comes with a vent limiter which allows for the regulator to function properly allowing air in and out, but more importantly in an event of failure allow only a certain amount of gas to escape safely. If not installed in the correct position it limits the functionality of this device and could cause more gas to escape or an overpressure situation to occur. This could lead to equipment failure. | 2 | Not installed according to certified installation instructions | Vent_limiter_wrong_postion.png | file://x:/photopub/docs/0000000582/e79e159d-ff02-42fe-8b93-e5c665bcda3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdfb2429_aa66_4efd_a837_16f759f6f8a7
GAIN-790912-2017 | GA-438888-2016 | 4/6/2017 2:25:39 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Venting.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting.png | file://x:/photopub/docs/0000000582/de1e3102-723e-4d84-857c-275ca6d466ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__905674f1_c361_4aaa_88cc_e2f4d11a6801
ELIN-768148-2017 | EL-506692-2017 | 3/9/2017 1:43:26 PM | ASSESS: EL: Final | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #Panel_location_.png - Panel located behind water tank would cause a greater risk of shock during maintenance work. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_location_.png | file://x:/photopub/docs/0000000569/66630d49-89b7-470a-ae1a-386649fdf306.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f08d46e4_2e06_4414_86a8_87ad92ef2c5f
GAIN-755253-2017 | GA-322182-2015 | 4/10/2017 10:17:43 AM | ASSESS: GA: Final | png | #asFound Commercial Kitchen exhaust hood, running with MUA turned off. | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Kitchenexhaust_MUA1.png,Kitchenexhaust_MUA2.png Commercial kitchen in work camp trailer was running without replacing the exhausted air from the exhaust hood. This was causing a negative pressure inside the building. This could lead to natural draft water heater vent reversing and spilling flue gases into the work camp trailer, exposing occupants to carbon monoxide. | 3 | Appliance not installed according to installation instructions | Kitchenexhaust_MUA1.png | file://x:/photopub/docs/0000000584/7378ca6f-9e59-4bf5-8cbe-6ce372b07c6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd60a962_4855_4326_8649_83596832c06c
GAIN-755253-2017 | GA-322182-2015 | 4/10/2017 10:17:43 AM | ASSESS: GA: Final | png | #asFound Engineered Air make up fair fan. | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Kitchenexhaust_MUA1.png,Kitchenexhaust_MUA2.png Commercial kitchen in work camp trailer was running without replacing the exhausted air from the exhaust hood. This was causing a negative pressure inside the building. This could lead to natural draft water heater vent reversing and spilling flue gases into the work camp trailer, exposing occupants to carbon monoxide. | 3 | Appliance not installed according to installation instructions | Kitchenexhaust_MUA2.png | file://x:/photopub/docs/0000000584/b866400a-3367-48d2-acf2-dc22db158763.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd60a962_4855_4326_8649_83596832c06c
BPVOP-771418-2017 | 3551961 | 3/8/2017 4:26:36 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Venting corroded | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Corroded_vent_piping1.png,Corroded_vent_piping2.png,Corroded_vent_piping3.png Boiler combustion gases were found directly venting into the boiler room. (carbon Monoxide) Owner was instructed not to operate this boiler until the boiler venting has been replaced. Gas fitter shut off gas supply to the boiler and turned off the electric supply. Serious injury may have resulted if was not de-energized. | 4 | 5.1.0 In service proc/process - Casing leakage | Corroded_vent_piping3.png | file://x:/photopub/docs/0000000568/daad9719-93fd-484e-a8f5-edd83b090df4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7392aeda_eb7a_404b_8e1b_30d0277e670b
BPVOP-771418-2017 | 3551961 | 3/8/2017 4:26:36 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Corroded boiler vent piping | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Corroded_vent_piping1.png,Corroded_vent_piping2.png,Corroded_vent_piping3.png Boiler combustion gases were found directly venting into the boiler room. (carbon Monoxide) Owner was instructed not to operate this boiler until the boiler venting has been replaced. Gas fitter shut off gas supply to the boiler and turned off the electric supply. Serious injury may have resulted if was not de-energized. | 4 | 5.1.0 In service proc/process - Casing leakage | Corroded_vent_piping1.png | file://x:/photopub/docs/0000000568/51312862-7054-414c-afef-3b58ce7322c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7392aeda_eb7a_404b_8e1b_30d0277e670b
ELIN-787598-2017 | EL-508458-2017 | 4/5/2017 11:16:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL014 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | 2 | 2 | #Suite_panel_supplied_from_main_panel.png Tenant panels shall be independently supplied to prevent inadvertent disconnection when service is required. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | Suite_panel_supplied_from_main_panel.png | file://x:/photopub/docs/0000000582/35296e5d-f5c2-4f92-8324-16b33af4c648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb298de1_10c1_4f75_84d8_d359feb8ea57
ELIN-772320-2017 | EL-446398-2016 | 3/16/2017 12:13:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Meter_base_location_and_door_swing.png Service meter base is in location where swing of door may break meter and create shock or fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Meter_base_location_and_door_swing.png | file://x:/photopub/docs/0000000572/cbcfa84b-62ab-4303-ad2b-3d91e475f7c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d0359d_2d4f_4e8a_8521_1dbaf509a6d7
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars1.png | file://x:/photopub/docs/0000000592/6262f123-3805-481c-b4d9-3edaf0a37c87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars7.png | file://x:/photopub/docs/0000000592/f8250792-0f91-463c-98df-1eeaab1ac776.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars6.png | file://x:/photopub/docs/0000000592/b90ffc48-27e1-4987-915b-a494e9040068.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars5.png | file://x:/photopub/docs/0000000592/26f4eb58-97f4-49a4-bd4f-1ebf3f903d5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
EDIN-794039-2017 | ED-434994-2016 | 4/11/2017 3:48:17 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED025 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | 3 | 3 | #No_hoistway_separaton_barrier.png The hoistway protective barrier to separate the adjacent elevator hoistway is to ensure the safety of the elevator workers. The barrier is meant to protect the workers from falling tools or debris from the adjacent hoistway. As well, the barrier protects the workers from the moving elevator in the adjacent hoistway. During an an acceptance assessment it was found that the elevator contractor failed to have enough time to install the protective barrier. Without the barrier, there is a higher probability of elevator workers getting hurt from falling debris or tools or being hit by a moving elevator from the adjacent hoistway. The hoistway is for a 16 stop traction elevator in a new residential building. | 3 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | No_hoistway_separaton_barrier.png | file://x:/photopub/docs/0000000585/b96573ba-c674-4598-8172-0b5a4e1bf4f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5066c466_19cf_46d7_be5a_8fd1f8ba6896
BPVOP-771418-2017 | 3551961 | 3/8/2017 4:26:36 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Venting at first elbow corroded through | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Corroded_vent_piping1.png,Corroded_vent_piping2.png,Corroded_vent_piping3.png Boiler combustion gases were found directly venting into the boiler room. (carbon Monoxide) Owner was instructed not to operate this boiler until the boiler venting has been replaced. Gas fitter shut off gas supply to the boiler and turned off the electric supply. Serious injury may have resulted if was not de-energized. | 4 | 5.1.0 In service proc/process - Casing leakage | Corroded_vent_piping2.png | file://x:/photopub/docs/0000000568/eb30f8e3-87b5-4abf-804a-6c043ab9e7d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7392aeda_eb7a_404b_8e1b_30d0277e670b
GAIN-756629-2017 | GA-500864-2017 | 3/9/2017 9:56:34 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Gas_leak.png The as found hazard was a small natural gas leak on the piping connection between the black iron piping and the corrugated stainless steel tubing. This is hazardous if gas reached a source of ignition it could catch fire and create a potential explosion situation. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Gas_leak.png | file://x:/photopub/docs/0000000569/c367a7f0-8fbe-4e27-931f-e0e0c0443d64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51cfc9fb_c7bb_4f8f_b840_69234b3afe0e
ELIN-786811-2017 | EL-471433-2016 | 4/3/2017 3:25:53 PM | ASSESS: EL: Final | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 2 | #1.png Communications duct used above grade. This is a potential shock hazard as this type of duct becomes brittle when exposed to the effects of UV rays. Breakage of this duct could lead to damage of the conductors inside. | 3 | Conductors, No expansion joint or not installed correctly. | 1.png | file://x:/photopub/docs/0000000580/9fbac898-7c68-4ae6-8948-8c02e0b80db1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f3c3501_a9d2_462d_a5f3_34181980304e
BPVOP-800378-2017 | 2292550 | 4/21/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #17.png All pressure relief devices require periodic inspection, testing and service. I found no record of testing for the last year for Safety valve on this Steam Boiler. Potential exists for a Safety Valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 17.png | file://x:/photopub/docs/0000000590/f4b610d3-2122-4e6c-9ae3-f3b87f41fc5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce458abc_3152_4cd9_9ee8_71cf22df92ae
ELIN-765289-2017 | EL-468000-2016 | 3/1/2017 7:58:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Typical_temporary_power1.png,Typical_temporary_power2.png The 20 amp fed 120 volt temporary power receptacles (rated 15 amps) do not include cover plates or adequate protection to prevent accidental contact by persons, this is a shock and thermal hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Typical_temporary_power2.png | file://x:/photopub/docs/0000000565/372a2de5-3eb7-4f57-9a19-5db1a1e943e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0122e29f_4bee_4673_b4d5_8be260f7c51b
ELIN-765289-2017 | EL-468000-2016 | 3/1/2017 7:58:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Typical_temporary_power1.png,Typical_temporary_power2.png The 20 amp fed 120 volt temporary power receptacles (rated 15 amps) do not include cover plates or adequate protection to prevent accidental contact by persons, this is a shock and thermal hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Typical_temporary_power1.png | file://x:/photopub/docs/0000000565/3722e01e-a3db-47b0-a768-6082f3008027.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0122e29f_4bee_4673_b4d5_8be260f7c51b
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars2.png | file://x:/photopub/docs/0000000592/3c7493bf-08fb-44b8-9ef0-6fdfbd55c393.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars4.png | file://x:/photopub/docs/0000000592/50cddeb0-af22-44de-b8e5-5a012399faf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
ELHE-804743-2017 | HE-527739-2017 | 4/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exposed_energized_conductors_and_bus_bars1.png,Exposed_energized_conductors_and_bus_bars2.png,Exposed_energized_conductors_and_bus_bars3.png,Exposed_energized_conductors_and_bus_bars4.png,Exposed_energized_conductors_and_bus_bars5.png,Exposed_energized_conductors_and_bus_bars6.png,Exposed_energized_conductors_and_bus_bars7.png Found exposed and energized bus bars and conductors hanging out of a panelboard that is missing panel cover on 120/208 volt 3 phase 200 amp panel. When electrical equipment is energized and exposed on a panelboard, the electrical equipment is a possible electrical fire or shock hazard to people or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_and_bus_bars3.png | file://x:/photopub/docs/0000000592/74cd131d-3572-450c-8e31-278e2f929a6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39995bd4_8e68_4413_98e7_c4f55196b156
BPVOP-767194-2017 | 3233516 | 2/10/2017 12:35:25 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRV_of_vessel_exceeded_replacement_or_recertification_interval.png Upon assessment of pressure vessel (length-1.8m and diameter-0.30m) in refrigeration system with Maximum Allowable Working Pressure (MAWP) of 450psig and Maximum Allowable Temperature (MAT) of 300*Fahrenheit, it was determined that pressure relief valve has exceeded the required 5year interval for servicing/replacement. Failure to have pressure valve serviced or replaced as required may subject vessel to pressure above MAWP if control fails to shut down compressor. This could result in failure of pressure-boundary with rapid uncontrolled release of refrigerant and may cause a severe incident (asphyxiation of personnel in the vicinity due oxygen deficiency or injury due to shooting effect of flying object etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRV_of_vessel_exceeded_replacement_or_recertification_interval.png | file://x:/photopub/docs/0000000565/1cc38e05-dd9a-457b-ae8f-b83ea78d5e62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06bb59fc_ef96_440e_88ad_d01d99da033c
BPVOP-767198-2017 | 3233515 | 2/10/2017 1:27:32 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRV_OF_VESSEL_EXCEEDED_REPLACEMENT_OR_SERVICING_INTERVAL.png Upon assessment of pressure vessel (length-1.8m and diameter-0.30m) in refrigeration system with Maximum Allowable Working Pressure (MAWP) of 450psig and Maximum Allowable Temperature (MAT) of 300*Fahrenheit, it was determined that pressure relief valve has exceeded the required 5year interval for servicing/replacement. Failure to have pressure valve serviced or replaced as required may subject vessel to pressure above MAWP if control fails to shut down compressor. This could result in failure of pressure-boundary with rapid uncontrolled release of refrigerant and may cause a severe incident (asphyxiation of personnel in the vicinity due oxygen deficiency or injury due to shooting effect of flying object etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRV_OF_VESSEL_EXCEEDED_REPLACEMENT_OR_SERVICING_INTERVAL.png | file://x:/photopub/docs/0000000565/7807125f-fd2c-4b76-81e3-63138db73f52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cdbf47f_13b1_4d65_8519_4b8924806a0a
ELIN-766916-2017 | EL-504618-2017 | 3/2/2017 1:49:55 PM | ASSESS: EL: Service Connection | png | #asFound DB2 conduit used above grade | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Db2.png Thin wall conduit used below grade for a new service on a single family dwelling has been installed above grade without mechanical protection. If this conduit or it's fitting is fractured the service conductors would be exposed leading to shock and fire if the unfused conductors are damaged. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Db2.png | file://x:/photopub/docs/0000000565/9c069989-d3f3-4f33-adc9-ef5574fa5bb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f1d9d73_a95b_4a7d_9d28_2c8f99fb15a1
ELOP-806904-2017 | EL-487473-2017 | 5/1/2017 1:49:49 PM | ASSESS: EL OP: Acceptance | png | #asFound No grounding of generator | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #No_generator1.png,No_generator2.png System grounding has not been performed. Should an electrical fault develop there will be no way that the available fault current will be redirected into the ground. A touch and step potential could exist and potentially electrocute anyone who touches the generator. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_generator2.png | file://x:/photopub/docs/0000000593/28cbb5a1-628f-4205-a086-cd192f39c534.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3843326b_665b_4a04_aefb_52157ae0c0ac
ELOP-806904-2017 | EL-487473-2017 | 5/1/2017 1:49:49 PM | ASSESS: EL OP: Acceptance | png | #asFound Generator not grounded | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #No_generator1.png,No_generator2.png System grounding has not been performed. Should an electrical fault develop there will be no way that the available fault current will be redirected into the ground. A touch and step potential could exist and potentially electrocute anyone who touches the generator. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_generator1.png | file://x:/photopub/docs/0000000593/3cf7ea05-b511-4619-a6a5-47c3c49f1467.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3843326b_665b_4a04_aefb_52157ae0c0ac
ELIN-811159-2017 | EL-404194-2016 | 5/9/2017 2:36:08 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_Protection.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, a new 15 amp circuits for a receptacle in a laundry area of the lower floor was installed without arc-fault protection. If a series or parallel arc was to occur in the branch circuit, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_Protection.png | file://x:/photopub/docs/0000000598/95a97a0c-64ad-478a-a0b3-9546677131a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbf5e9bc_c3de_4d43_9645_e1058e68b99a
GAIN-812961-2017 | GA-502102-2017 | 5/10/2017 9:40:33 AM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Gaspipe.png The as found condition is gas piping entering a building below grade. The as found hazard is should there be a compromise of the underground piping gas can migrate directly into the building envelope before venting into atmosphere creating an explosion hazard in the structure. | 3 | Underground piping entering a building below grade (unapproved) | Gaspipe.png | file://x:/photopub/docs/0000000598/1f72108d-88f6-425c-be99-2c88b6b86e9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d051a133_531a_471d_8212_458b63fc1808
ELHE-809278-2017 | HE-530137-2017 | 4/26/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Batteries_open_storage.png Lead acid batteries are stored in an area that is not sealed and vented from the rest of the building. Accidental contact could occur resulting in shock injury. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Batteries_open_storage.png | file://x:/photopub/docs/0000000597/23e0a326-d93a-4b0b-9188-574721915f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26462934_edfe_4836_91c5_eacd57d55700
ELOP-759279-2017 | EL-496689-2017 | 3/2/2017 11:06:29 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Main service with no ground indicating lights. | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 3 | #No_lites.png Initial operating permit assessment on old warehouse building being renovated to become a commercial storage facility. The existing electrical service installed many years ago did not have a system in place to advise when there was a fault on a phase. Overcurrent devices would not function in a fault. Shock hazard and danger of equipment malfunction. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | No_lites.png | file://x:/photopub/docs/0000000565/53e1bef9-000b-4ef5-ad60-8daf3bb44120.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1CF56C8C_080F_4924_B5F6_95D2BC646A6C
ELOP-787766-2017 | 6630 | 4/13/2017 7:08:15 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Knockouts1.png,Knockouts2.png In a 200 amp 120/208 volt electrical panel mounted outdoors, openings have been left in the panel which leaves the interior energized electrical components exposed to possible contact or mechanical damage. This could poses a shock hazard to persons, and potential mechanical damage to the panel. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Knockouts2.png | file://x:/photopub/docs/0000000586/0f40c93c-71ea-46a1-b69b-69df851399da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57f5af49_a8ee_4cd7_8dac_3893f5b804b1
ELOP-787766-2017 | 6630 | 4/13/2017 7:08:15 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Knockouts1.png,Knockouts2.png In a 200 amp 120/208 volt electrical panel mounted outdoors, openings have been left in the panel which leaves the interior energized electrical components exposed to possible contact or mechanical damage. This could poses a shock hazard to persons, and potential mechanical damage to the panel. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Knockouts1.png | file://x:/photopub/docs/0000000586/3c1eee7d-ecf9-408e-b6ad-36a9b1279232.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57f5af49_a8ee_4cd7_8dac_3893f5b804b1
GAIN-810072-2017 | GA-349817-2016 | 5/11/2017 11:16:24 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #River_4.png Vent termination from furnace installed with less than the required minimum clearance of 12" to building opening. Products of combustion could enter the interior of the building due to the close proximity of the vent/building opening. Possible exposure to carbon monoxide if products of combustion were to be drawn into the building through the open door. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | River_4.png | file://x:/photopub/docs/0000000599/3b961a2b-706d-4bbd-8da0-e226641ed2e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83a3a95c_8542_4550_b618_8db03f169d01
ELIN-788469-2017 | EL-515536-2017 | 4/6/2017 11:40:41 AM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Ceilings_fan.png The existing 15 amp 120 volt combination ceiling fan/ light combination units in an existing mobile home are attached to non-approved ceiling fan boxes with the Safety cable not fastened. The fans can be subject to coming loose and fall, this is an equipment damage issue. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Ceilings_fan.png | file://x:/photopub/docs/0000000587/b1c04efa-52d3-4b80-98f3-c7b030b457af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8dd974de_68ac_4b73_9c1a_ef21e7cf954f
ELIN-734497-2017 | EL-185943-2014 | 4/10/2017 10:20:34 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Heating_system_water_tank1.png,Heating_system_water_tank2.png The 50 amp 240 volt energized wiring for the heating system non CSA approved electric hot water tank had terminations exposed to contact by persons in the storage room. The wiring is #12 cu and is undersized which creates a thermal hazard. The exposed wiring is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Heating_system_water_tank2.png | file://x:/photopub/docs/0000000587/f1c1e815-ed91-464c-9031-88ab4c7f682b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3aeb3db_4c7b_4331_bd7d_8991d8dcd46e
ELIN-734497-2017 | EL-185943-2014 | 4/10/2017 10:20:34 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Heating_system_water_tank1.png,Heating_system_water_tank2.png The 50 amp 240 volt energized wiring for the heating system non CSA approved electric hot water tank had terminations exposed to contact by persons in the storage room. The wiring is #12 cu and is undersized which creates a thermal hazard. The exposed wiring is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Heating_system_water_tank1.png | file://x:/photopub/docs/0000000587/88c6e42d-7a16-4f7c-89a0-8be44bdc7a7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3aeb3db_4c7b_4331_bd7d_8991d8dcd46e
ELIN-767126-2017 | EL-492136-2017 | 3/2/2017 9:39:01 AM | ASSESS: EL: Service Connection | png | #asFound GFCI receptacle has been removed by builder | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #GFCI_receptacl__GFCI_receptacles_have_been_removed_by_builder1.png,GFCI_receptacl__GFCI_receptacles_have_been_removed_by_builder2.png Temporary construction receptacles require ground fault protection which are installed to prevent shock and injury to workers. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | GFCI_receptacl__GFCI_receptacles_have_been_removed_by_builder2.png | file://x:/photopub/docs/0000000565/74d11647-127a-4faa-a506-d0062d5a73fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f6c9e95_c8a2_40b4_b083_02204c8e2eb2
ELIN-767126-2017 | EL-492136-2017 | 3/2/2017 9:39:01 AM | ASSESS: EL: Service Connection | png | #asFound GFCI receptacle removed by builder | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #GFCI_receptacl__GFCI_receptacles_have_been_removed_by_builder1.png,GFCI_receptacl__GFCI_receptacles_have_been_removed_by_builder2.png Temporary construction receptacles require ground fault protection which are installed to prevent shock and injury to workers. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | GFCI_receptacl__GFCI_receptacles_have_been_removed_by_builder1.png | file://x:/photopub/docs/0000000565/059b339b-3d72-4d46-9d44-6e86172f25a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f6c9e95_c8a2_40b4_b083_02204c8e2eb2
ELHE-783130-2017 | HE-516020-2017 | 3/27/2017 9:07:07 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Electrical service building and wooden service mast | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Electrical_service_building_.png Electrical service room in need of repair Cover on meter base not approved No light in electrical room Mast for support of over head wiring has rotted Non approved meter base cover could result in a shock live parts inside not protected Electrical Equipment in room could fail due to exposure to the weather | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Electrical_service_building_.png | file://x:/photopub/docs/0000000576/37de4ca8-b8f7-4cac-9899-42cb319e2547.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25b1e0f6_a8c6_41f5_b455_832edfbf37ba
EDIN-769095-2017 | ED-382917-2016 | 3/6/2017 1:27:48 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #drop_ceiling_of_the_escape_hatch.png Interior drop ceiling of the escape hatch needs a means to prevent the panel from falling into the cab | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | drop_ceiling_of_the_escape_hatch.png | file://x:/photopub/docs/0000000566/0a88ee3e-cce4-4dd9-bad3-209b4bde48c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29587034_0e44_4688_a754_5518e4e1ef65
GAIN-775854-2017 | GA-504488-2017 | 3/15/2017 3:51:48 PM | ASSESS: GA: Rough-In | png | #asFound At time of inspection no cathodic protection was found | GA058 | Cathodic protection missing causing a hazard | 3 | 3 | #Riser_No_Cathodic_protection.png We found the main riser coming up into an electrical room. If there was a gas leak underground it is possible that it may enter building and cause an explosion, possibly leading to damage and injury. | 3 | Cathodic protection missing causing a hazard | Riser_No_Cathodic_protection.png | file://x:/photopub/docs/0000000572/bf1f68eb-eb5c-466c-884b-f6235641c511.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34659929_d713_4b22_84f4_87e6109ef1b8
GAIN-752770-2017 | GA-487426-2017 | 3/15/2017 4:24:43 PM | ASSESS: GA: Final | png | #asFound No breakaway found on propane dispenser | GA052 | Unprotected temporary hose installations | 3 | 3 | #OJ_pipeline_no_breakway.png There was no breakaway dis-connect on the fill hose at Propane Dispenser. If a a cylinder on the truck is being filled and the hose is left connected, and the driver drives away, there will be a leak. And this could lead to an explosion causing injury or damage. | 3 | Unprotected temporary hose installations | OJ_pipeline_no_breakway.png | file://x:/photopub/docs/0000000572/5007deb2-2cd1-4f80-bf8e-5e8baf8690fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__619ef603_4a3f_4655_98a6_3760ca127bd0
GAIN-771568-2017 | GA-502245-2017 | 3/16/2017 10:36:34 AM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Decal.png The as-found-condition is that two vertical broilers installed in a commercial kitchen have not been certified for use in Canada. The potential hazard is that because the broilers have not been tested to Canadian safety requirements they may operate in an unsafe resulting In harmful emissions or a fire hazard. | 3 | Uncertified appliance connected to gas supply but not in service | Decal.png | file://x:/photopub/docs/0000000572/2db3c522-02ff-442a-a083-4b076b41d0f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5169d870_6ce2_4f68_b862_63b5fdef9d54
GAIN-771054-2017 | GA-508463-2017 | 3/13/2017 12:12:51 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #Unit_heater.png The as-found-condition is that a unit heater has been installed in an occupied space without a provision for combustion air. The potential hazard is that the unit heater will emit harmful emissions such as CO if it is not provided with an adequate air supply to complete combustion. | 4 | Combustion air supply missing | Unit_heater.png | file://x:/photopub/docs/0000000572/56119731-ef5c-433c-82c4-de54164372f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8d7d3ed_5f02_44d9_9e7f_6ccc651b6596
BPVIN-527448-2016 | BPV-276195-2015 | 4/26/2017 10:09:41 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP018 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | 2 | 2 | #Wall_penetrations_1.png,Wall_penetrations_2.png | 2 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | Wall_penetrations_2.png | file://x:/photopub/docs/0000000595/fef861d5-5059-4628-8f2d-5906d930616c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1aecde9d_39b4_4976_b408_9fbfc6627847
BPVIN-803556-2017 | BPV-526986-2017 | 4/26/2017 12:32:37 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 | #Clearances_.png,Clearances_.png | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Clearances_.png | file://x:/photopub/docs/0000000595/0c3ef77e-c254-4baf-ba45-a69b62112a02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f61385d8_070e_4c9e_b1c0_11ac581f9d5a
BPVIN-527448-2016 | BPV-276195-2015 | 4/26/2017 10:09:41 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP018 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | 2 | 2 | #Wall_penetrations_1.png,Wall_penetrations_2.png | 2 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | Wall_penetrations_1.png | file://x:/photopub/docs/0000000595/4ea7ca99-4452-40ab-9b17-f8f455a9a710.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1aecde9d_39b4_4976_b408_9fbfc6627847
BPVOP-765513-2017 | 4493047 | 2/28/2017 8:43:54 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD_s.png Upon the assessment of an Evaporator with MAWP of 200 psig, was found that the Pressure Relief Devices was installed in 2010 and was overdue as per CSA B52. This can contribute to the failure of the evaporator. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_s.png | file://x:/photopub/docs/0000000566/4230f791-7153-48ea-9115-ba9583dfc83d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8f749c6_1b90_4edb_b838_a435b05ffd1a
GAIN-786232-2017 | GA-502329-2017 | 4/3/2017 1:33:36 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Clearance_to_combustible_material_not_maintained.png Clearance to combustible material not maintained. Combustible material with in the clearance area outlined by the manufacturer could cause a fire. | 3 | Clearance to combustible not met | Clearance_to_combustible_material_not_maintained.png | file://x:/photopub/docs/0000000580/6f41ec53-ce80-411e-bb36-d7b3de90d26a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9fcccaf_cb2b_4fab_b1fa_d876258d550a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png | file://x:/photopub/docs/0000000587/eecf7c62-e8db-41a2-89ed-3c518495452e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png | file://x:/photopub/docs/0000000587/585140aa-ec8c-4445-a0c9-dac952cd0285.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELOP-769693-2017 | 5308393 | 3/7/2017 6:09:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL237 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | #Mezzanine_transformers1.png,Mezzanine_transformers2.png,Mezzanine_transformers3.png,Mezzanine_transformers4.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping for combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated to when installed in these environments. This overheating can cause fires within the electrical equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. During an operating permit inspection at a furniture manufacturing shop, the electrical safety officer found electrical equipment that was not rated for a hazardo | 5 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Mezzanine_transformers4.png | file://x:/photopub/docs/0000000568/68ecef4c-aff7-4934-8e3f-07e895ead7b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1261277_bd12_4975_bb20_f5c8e6c66ae5
ELOP-769693-2017 | 5308393 | 3/7/2017 6:09:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL237 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | #Mezzanine_transformers1.png,Mezzanine_transformers2.png,Mezzanine_transformers3.png,Mezzanine_transformers4.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping for combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated to when installed in these environments. This overheating can cause fires within the electrical equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. During an operating permit inspection at a furniture manufacturing shop, the electrical safety officer found electrical equipment that was not rated for a hazardo | 5 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Mezzanine_transformers3.png | file://x:/photopub/docs/0000000568/cacbdedd-a3ca-4999-b2e1-5dc69add3205.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1261277_bd12_4975_bb20_f5c8e6c66ae5
ELOP-769693-2017 | 5308393 | 3/7/2017 6:09:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL237 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | #Mezzanine_transformers1.png,Mezzanine_transformers2.png,Mezzanine_transformers3.png,Mezzanine_transformers4.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping for combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated to when installed in these environments. This overheating can cause fires within the electrical equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. During an operating permit inspection at a furniture manufacturing shop, the electrical safety officer found electrical equipment that was not rated for a hazardo | 5 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Mezzanine_transformers1.png | file://x:/photopub/docs/0000000568/24ef35f5-ba33-4651-b393-ea76bdd451b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1261277_bd12_4975_bb20_f5c8e6c66ae5
ELOP-769693-2017 | 5308393 | 3/7/2017 6:09:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL237 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | #Mezzanine_transformers1.png,Mezzanine_transformers2.png,Mezzanine_transformers3.png,Mezzanine_transformers4.png Woodworking shops are classified as hazardous electrical locations when the shops do not have an adequate dust collection system and good house keeping for combustible dust. This is because the accumulation of combustible dust acts as an insulator and can cause overheating of electrical equipment. Electrical equipment must be rated to when installed in these environments. This overheating can cause fires within the electrical equipment. In addition, fire or sparks from the electrical equipment can ignite the combustible dust layer on the equipment or explosive dust that is suspended in the air. The ignition of the combustible dust can produce a fire ball that will expand and create a larger fire or an explosion within the building. During an operating permit inspection at a furniture manufacturing shop, the electrical safety officer found electrical equipment that was not rated for a hazardo | 5 | Class II, all locations The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Mezzanine_transformers2.png | file://x:/photopub/docs/0000000568/ebd26c90-2137-4092-b242-34e8420a7cc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1261277_bd12_4975_bb20_f5c8e6c66ae5
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png | file://x:/photopub/docs/0000000596/c28a3dff-509e-46f4-8412-1a9e5f9b5a37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png | file://x:/photopub/docs/0000000596/d45995ca-194c-4c55-8da8-8458760be717.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png | file://x:/photopub/docs/0000000596/44e49946-0b91-4c5d-a1aa-0aa4fff50c84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
BPVIN-773681-2017 | BPV-455691-2016 | 3/29/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_room_door.png Upon assessment of Hot Water Boiler with Heating Surface (HS) of 6.0 square meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_door.png | file://x:/photopub/docs/0000000580/0a5f7df3-e520-47f8-ae17-5bba6cdc6246.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8702a89_402c_4738_b44f_19e9b2f20b27
AMOP-813340-2017 | AM-254873-2015 | 5/11/2017 9:48:19 AM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Upper_catwalk_bolts_.png Unused bolted connections on top platform of device, hardware has the potential to come loose and fall on public and personnel below the catwalk. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Upper_catwalk_bolts_.png | file://x:/photopub/docs/0000000599/e5b1fb4b-f215-40ae-bdf0-6efc0a2ea528.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af26cf37_cda0_4bc1_9c3f_50f25e5da44c
GAIN-791418-2017 | GA-519017-2017 | 4/25/2017 9:52:53 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Boiler_flor.png The as-found-condition is that a boiler has been installed on a combustible floor. The potential hazard is that the boiler will radiate heat to the combustible surface, resulting in a high risk of fire damage. | 3 | Clearance to combustible not met | Boiler_flor.png | file://x:/photopub/docs/0000000591/61a25771-74d1-47f5-99e9-19f38ea7d67d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffbe0291_0a0d_4220_9227_fe9b5b59480a
BPVOP-763632-2017 | 5408214 | 3/18/2017 2:16:56 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | #Lowwatercutouts_below_boiler1.png,Lowwatercutouts_below_boiler2.png Found three boilers installed by a non-licensed boiler contractor that had all three low water cut out Safety devices installed contrary to manufacture recommendations, low-water cut outs installed below the boiler and will not prevent a low water condition from overheating and boiler failure. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Lowwatercutouts_below_boiler1.png | file://x:/photopub/docs/0000000573/7692618f-cede-4f8b-ae74-f8edb5edde38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85d1d962_4342_457a_864c_a3f6ac866cff
BPVOP-763632-2017 | 5408214 | 3/18/2017 2:16:56 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | #Lowwatercutouts_below_boiler1.png,Lowwatercutouts_below_boiler2.png Found three boilers installed by a non-licensed boiler contractor that had all three low water cut out Safety devices installed contrary to manufacture recommendations, low-water cut outs installed below the boiler and will not prevent a low water condition from overheating and boiler failure. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Lowwatercutouts_below_boiler2.png | file://x:/photopub/docs/0000000573/087b11fa-b906-4cc6-9d22-d256d3113a32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85d1d962_4342_457a_864c_a3f6ac866cff
ELIN-802760-2017 | EL-397922-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Dental_chir_whips1.png,Dental_chir_whips2.png Dental chair branch circuits are inadequately which includes the junction boxes and the armoured flexible cable. This could cause a shock hazard overtime if person(s) were to pull/walk on the dental branch circuit due to it being damaged and live conductors touching a person(s). Also, this could cause a fire if the branch circuits do not trip the breaker protecting them. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dental_chir_whips2.png | file://x:/photopub/docs/0000000594/e17b9f97-4f6d-4ae8-be9f-04510df69292.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0997dc07_8d0a_45d3_bb29_918dc8b2c307
ELIN-802760-2017 | EL-397922-2016 | 4/27/2017 | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Dental_chir_whips1.png,Dental_chir_whips2.png Dental chair branch circuits are inadequately which includes the junction boxes and the armoured flexible cable. This could cause a shock hazard overtime if person(s) were to pull/walk on the dental branch circuit due to it being damaged and live conductors touching a person(s). Also, this could cause a fire if the branch circuits do not trip the breaker protecting them. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dental_chir_whips1.png | file://x:/photopub/docs/0000000594/4add69d7-2c28-4f45-ace6-e19fa3982b6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0997dc07_8d0a_45d3_bb29_918dc8b2c307
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png | file://x:/photopub/docs/0000000587/cf51bd85-6ad1-42ad-8fee-e852c8bb2e32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png | file://x:/photopub/docs/0000000587/45654099-0b3b-4a2e-aadc-6931e2c6876d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png | file://x:/photopub/docs/0000000587/058acfc9-650d-4b90-a95c-421e52545a5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png | file://x:/photopub/docs/0000000596/5d7bdbbb-a730-4908-984d-90614252cd03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
BPVIN-814331-2017 | UW-533085-2017 | 5/9/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_valve.png Upon assessment of Hot Water Boiler with Heating surface area of 9 quare meters, Maximum Allowable Working Pressure (MAWP) 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has not been pop tested biannually and exceeded required 6year interval for servicing/replacement. Failure to have safety valve tested and serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_valve.png | file://x:/photopub/docs/0000000599/729f1bce-4523-4c28-bed4-4ce6ca0b92e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5805273c_bfc2_441e_9113_f69d54730c95
BPVIN-814331-2017 | UW-533085-2017 | 5/9/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_valve.png Upon assessment of Hot Water Boiler with Heating surface area of 9 quare meters, Maximum Allowable Working Pressure (MAWP) 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has not been pop tested biannually and exceeded required 6year interval for servicing/replacement. Failure to have safety valve tested and serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000599/c1fe15d9-75b8-46c8-a66c-62db852db98b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5805273c_bfc2_441e_9113_f69d54730c95
ELOP-774792-2017 | EL-383085-2016 | 3/14/2017 3:29:23 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Damaged_electrica__damaged_electrical_installations_and_noncompliant1.png,Damaged_electrica__damaged_electrical_installations_and_noncompliant2.png,Damaged_electrica__damaged_electrical_installations_and_noncompliant3.png Building structure is failing and water is flooding through the roof exposing all electrical equipment to water damage. I am permitted work has been installed and is noncompliant creating an electrical shock hazard. Equipment has been ordered disconnect. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Damaged_electrica__damaged_electrical_installations_and_noncompliant1.png | file://x:/photopub/docs/0000000571/8b348fa4-5936-4306-9bd7-9165e79b0d2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38282bbb_9130_4ae3_8ea8_db3632708bbc
ELOP-774792-2017 | EL-383085-2016 | 3/14/2017 3:29:23 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Damaged_electrica__damaged_electrical_installations_and_noncompliant1.png,Damaged_electrica__damaged_electrical_installations_and_noncompliant2.png,Damaged_electrica__damaged_electrical_installations_and_noncompliant3.png Building structure is failing and water is flooding through the roof exposing all electrical equipment to water damage. I am permitted work has been installed and is noncompliant creating an electrical shock hazard. Equipment has been ordered disconnect. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Damaged_electrica__damaged_electrical_installations_and_noncompliant2.png | file://x:/photopub/docs/0000000571/d175bd6e-7172-495d-a73a-bb2767bc7929.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38282bbb_9130_4ae3_8ea8_db3632708bbc
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png | file://x:/photopub/docs/0000000587/f6c8aa12-d226-45f6-be06-e8dcd0b61985.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELHE-795840-2017 | HE-523195-2017 | 4/13/2017 4:36:15 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Made up on site unapproved electrical equipment used in a hazardous location where there is gas powered generator and the wiring is not approved for the use or location. Approved installation and use instructions not complied with as required by manufacturer's approved installation and use instructions | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | #Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only1.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only2.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only3.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only4.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only5.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only7.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only8.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only9.png,Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only10.png Found 120/240 volt single phase gas powered generator installed in an enclosed building structure space while there is regular dry type location electrical equipment (such as extension cords and unapproved non-co | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Gas_powere_generator_in_enclosed_space_with_regular_wiring_method_used_only6.png | file://x:/photopub/docs/0000000587/3b9e937d-7cc1-48eb-9380-fbb360430550.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f179be25_3936_4139_80e6_4aa0db23245a
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png | file://x:/photopub/docs/0000000596/a07714d2-4aa3-4879-994f-3b90582fd354.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png | file://x:/photopub/docs/0000000596/f42c2e14-828c-4d6f-ab70-e89765c9e4d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png | file://x:/photopub/docs/0000000596/19a24449-27f8-4cc8-be6b-ec4e59b45daf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png | file://x:/photopub/docs/0000000596/e6f81c7f-008b-412a-9911-82ae87693c52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png | file://x:/photopub/docs/0000000596/2055e05b-7797-4dbf-ae40-4f285b4818c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
GAIN-785686-2017 | GA-279530-2015 | 4/4/2017 2:30:34 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Boiler.png The as-found-condition is that a boiler has been installed without adequate combustion air supply. The potential hazard is that the boiler will operate in an unsafe manner, resulting in incomplete combustion and the release of harmful emissions such as carbon monoxide. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Boiler.png | file://x:/photopub/docs/0000000582/47ebe034-92a6-43f9-97cb-6e146260433f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90b84a62_4ed1_4e3a_af15_7fc503ebda20
ELOP-774792-2017 | EL-383085-2016 | 3/14/2017 3:29:23 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Damaged_electrica__damaged_electrical_installations_and_noncompliant1.png,Damaged_electrica__damaged_electrical_installations_and_noncompliant2.png,Damaged_electrica__damaged_electrical_installations_and_noncompliant3.png Building structure is failing and water is flooding through the roof exposing all electrical equipment to water damage. I am permitted work has been installed and is noncompliant creating an electrical shock hazard. Equipment has been ordered disconnect. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Damaged_electrica__damaged_electrical_installations_and_noncompliant3.png | file://x:/photopub/docs/0000000571/e420805e-4a38-457a-a1f9-9c48c30418bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38282bbb_9130_4ae3_8ea8_db3632708bbc
ELIN-799344-2017 | EL-512688-2017 | 4/24/2017 5:35:48 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_GFCI_protection.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and make contact with water in a sink. In this installation at a single family dwelling, GFCI protection was not provided for a receptacle within 1.5 m of a washroom sink. This is a potential shock hazard for persons working with cord connected equipment near the washroom sink in this dwelling. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_protection.png | file://x:/photopub/docs/0000000591/6f796844-444b-4e6b-9596-a732c4078d02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c94461bc_ba58_4c8c_87dd_35708f2a733c
GAHE-779511-2017 | HE-514052-2017 | 3/21/2017 12:41:09 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Paloma water heater | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | #Paloma_water_heater.png At time of inspection venting of appliance wasn't connected, this condition causes products of combustion to enter home. | 5 | Venting system not connected or dislodged from energized appliance | Paloma_water_heater.png | file://x:/photopub/docs/0000000574/f3eb5812-3e2d-4693-ad6b-a3aa8252e927.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dea5727c_cda6_4469_ba5b_dc21b62581e5
ELHE-792647-2017 | HE-521098-2017 | 4/10/2017 12:29:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Service_conductors1.png,Service_conductors2.png Service conductors pass over a deck and are accessible to touch. High potential of shock. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Service_conductors1.png | file://x:/photopub/docs/0000000584/239a3370-f947-47c9-a68c-5f75d87909c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3aa56a7b_c8ef_49f7_b420_7459bd5a2c4f
ELOP-786874-2017 | EL-383085-2016 | 4/10/2017 12:45:24 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Office_building1.png,Office_building2.png,Office_building3.png,Office_building4.png Office building is damaged and wiring has been installed without a permit and by unqualified persons. Fixtures and branch circuits are exposed and damaged. Possibility for shock or fire. | 0 | No Created Hazard Identified | Office_building2.png | file://x:/photopub/docs/0000000584/fa13f155-ea4c-423a-92c4-b877b7474f62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56ef76b3_4198_44e0_9fd0_531ee599c79d
ELOP-786874-2017 | EL-383085-2016 | 4/10/2017 12:45:24 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Office_building1.png,Office_building2.png,Office_building3.png,Office_building4.png Office building is damaged and wiring has been installed without a permit and by unqualified persons. Fixtures and branch circuits are exposed and damaged. Possibility for shock or fire. | 0 | No Created Hazard Identified | Office_building4.png | file://x:/photopub/docs/0000000584/6aab2bd0-665d-4f5c-aa5e-77575740e32f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56ef76b3_4198_44e0_9fd0_531ee599c79d
ELOP-786874-2017 | EL-383085-2016 | 4/10/2017 12:45:24 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Office_building1.png,Office_building2.png,Office_building3.png,Office_building4.png Office building is damaged and wiring has been installed without a permit and by unqualified persons. Fixtures and branch circuits are exposed and damaged. Possibility for shock or fire. | 0 | No Created Hazard Identified | Office_building1.png | file://x:/photopub/docs/0000000584/620ecd28-931d-401e-abc3-30d5222ea000.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56ef76b3_4198_44e0_9fd0_531ee599c79d
ELOP-786874-2017 | EL-383085-2016 | 4/10/2017 12:45:24 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Office_building1.png,Office_building2.png,Office_building3.png,Office_building4.png Office building is damaged and wiring has been installed without a permit and by unqualified persons. Fixtures and branch circuits are exposed and damaged. Possibility for shock or fire. | 0 | No Created Hazard Identified | Office_building3.png | file://x:/photopub/docs/0000000584/ff7df534-707a-4f14-9582-eb6bf65f1e06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56ef76b3_4198_44e0_9fd0_531ee599c79d
ELHE-792647-2017 | HE-521098-2017 | 4/10/2017 12:29:58 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Service_conductors1.png,Service_conductors2.png Service conductors pass over a deck and are accessible to touch. High potential of shock. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Service_conductors2.png | file://x:/photopub/docs/0000000584/88bb747e-17f9-4924-9a30-4f4062888397.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3aa56a7b_c8ef_49f7_b420_7459bd5a2c4f
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png | file://x:/photopub/docs/0000000596/b5d13141-1505-4677-b0a0-85859d803986.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
ELOP-810417-2017 | 5398364 | 5/5/2017 11:50:09 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings2.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings3.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings4.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings5.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings6.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings7.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings8.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings9.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings10.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings11.png,Cords_run_through_cabinet_and_fastened_to_walls_ceilings12.png Extension cords and electrical equipment cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. This installation at a grocery store has extension cords and equipment cords that have been plugged | 4 | Conductors, Misuse of flexible cords. | Cords_run_through_cabinet_and_fastened_to_walls_ceilings1.png | file://x:/photopub/docs/0000000596/d401dc07-f5b4-444c-afb3-667f38216731.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__308f9c53_707c_4359_9020_30eaac42a14c
BPVOP-769491-2017 | 4618447 | 3/6/2017 7:47:24 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve.png Owner has not performed annual inspection and service all safety devices and controls since 2014. Lack of following manufacturer recommendations significantly increases the chance of multiple safety device failures that may lead to overheating and failure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000568/775ecf0a-4f58-41e1-8da5-56912b24f54e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a06bec52_a474_4084_b0d2_12014affc84a
GAIN-741925-2017 | GA-445082-2016 | 4/28/2017 2:05:16 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | #DFMUA.png Missing interlocks on exhaust system to shut down direct fired make up air in case of system failure. If interlocks are not in place and there was a system failure there is the possibility of carbon monoxide exposure leading to injury or death. | 3 | Mechanical Air/ventilation supply present, missing interlock | DFMUA.png | file://x:/photopub/docs/0000000596/a04fc17f-9a45-48c8-8ed6-021a44dbd714.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__763e89b1_a2af_4d04_aebc_d92e99e26117
ELIN-798615-2017 | EL-336675-2016 | 4/24/2017 11:22:35 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_fridge_receptacle_cover_plate.png Missing cover plate on energized 120 volt 15 amp fridge receptacle increases the likelihood of electrical shock in the event of accidental contact with energized terminals on receptacle | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_fridge_receptacle_cover_plate.png | file://x:/photopub/docs/0000000590/82a9d0cf-3256-47d3-bf5a-aeaebc80dba5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049644b6_9125_4cac_996b_daa58c416b36
ELHE-793027-2017 | HE-521306-2017 | 4/12/2017 4:49:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Main_distribution_no_cover_access_impeded.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_distribution_no_cover_access_impeded.png | file://x:/photopub/docs/0000000596/f8412698-5381-4384-ac01-025058ecf6f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f786b35a_00bb_4859_a52a_34ca3318e964
ELIN-809272-2017 | EL-528921-2017 | 5/8/2017 1:36:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Not_weatherproof_construction.png Panel is located in an area exposed to the weather and is not of weatherproof construction. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Not_weatherproof_construction.png | file://x:/photopub/docs/0000000598/b31ae2d6-5b28-4f35-9be5-44c3b2515e15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5e03924_b340_4a59_a65a_41087b3ca3ac
ELOP-805837-2017 | EL-521944-2017 | 5/18/2017 7:07:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord_connected_light1.png,Extension_cord_connected_light2.png,Extension_cord_connected_light3.png,Extension_cord_connected_light4.png,Extension_cord_connected_light5.png,Extension_cord_connected_light6.png An extension cord has been used to feed a 102 volt 15 amp light fixture and the cord has been installed in a permanent fashion, the cord is not intended for permanent installation and is supported by wrapping the cord around plumbing pipes. The cord end has also been removed to connect to the light fixture and no fitting or outlet box has been used. This poses a shock hazard to persons and potential mechanical damage to the light, cord and the receptacle powering this set up. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_connected_light6.png | file://x:/photopub/docs/0000000603/12047713-0067-4019-a977-0d2c9595a4c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C224ED52_5DBC_4886_9450_D8ABD8FB13C5
ELIN-772613-2017 | EL-286023-2015 | 5/29/2017 12:44:32 PM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Conduits_between_kiosk_and_lift_station1.png,Conduits_between_kiosk_and_lift_station2.png The contractor has installed an assembly of conduit types that are not approved for this particular installation. There is no mechanical protection installed in a vehicular area and the conduit system is unsupported and energized and readily accessible to the general public. Explosion proof fittings have not been sealed to prevent the flow of explosive gas. This condition may possibly result in equipment damage or personal injury. If the explosive gas contacts the electrical equipment in the control kiosk. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Conduits_between_kiosk_and_lift_station2.png | file://x:/photopub/docs/0000000607/9a4ff61e-1e89-4759-b784-1f1ea5298942.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25a20aec_bcf1_4099_9afd_681bbe079331
ELIN-820260-2017 | EL-536763-2017 | 6/1/2017 7:48:18 AM | ASSESS: EL: Service Connection | png | #asFound No bonding bushing on service conduit. | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #9707_81_Avenue1.png,9707_81_Avenue2.png,9707_81_Avenue3.png,9707_81_Avenue4.png,9707_81_Avenue5.png No protection on feeder conductor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 9707_81_Avenue4.png | file://x:/photopub/docs/0000000609/392d8a5d-3789-43f5-a19d-936d78e3ff25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238636c3_fa67_4931_b5fb_de576427bb82
ELIN-820260-2017 | EL-536763-2017 | 6/1/2017 7:48:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #9707_81_Avenue1.png,9707_81_Avenue2.png,9707_81_Avenue3.png,9707_81_Avenue4.png,9707_81_Avenue5.png No protection on feeder conductor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 9707_81_Avenue2.png | file://x:/photopub/docs/0000000609/225dd5b9-3c99-4598-8ba8-2ae0ea84c058.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238636c3_fa67_4931_b5fb_de576427bb82
ELIN-820260-2017 | EL-536763-2017 | 6/1/2017 7:48:18 AM | ASSESS: EL: Service Connection | png | #asFound Bonding screw in sub-distribution. | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #9707_81_Avenue1.png,9707_81_Avenue2.png,9707_81_Avenue3.png,9707_81_Avenue4.png,9707_81_Avenue5.png No protection on feeder conductor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 9707_81_Avenue3.png | file://x:/photopub/docs/0000000609/be4d5f8c-8940-4b7b-a01d-394ce5dde1e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238636c3_fa67_4931_b5fb_de576427bb82
ELIN-820260-2017 | EL-536763-2017 | 6/1/2017 7:48:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #9707_81_Avenue1.png,9707_81_Avenue2.png,9707_81_Avenue3.png,9707_81_Avenue4.png,9707_81_Avenue5.png No protection on feeder conductor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 9707_81_Avenue5.png | file://x:/photopub/docs/0000000609/0516d146-571f-42aa-913e-a9dc91f2b8a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238636c3_fa67_4931_b5fb_de576427bb82
ELIN-820260-2017 | EL-536763-2017 | 6/1/2017 7:48:18 AM | ASSESS: EL: Service Connection | png | #asFound No protection on feeder. | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #9707_81_Avenue1.png,9707_81_Avenue2.png,9707_81_Avenue3.png,9707_81_Avenue4.png,9707_81_Avenue5.png No protection on feeder conductor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 9707_81_Avenue1.png | file://x:/photopub/docs/0000000609/5ef2edcb-fb82-4821-9f03-f178fa88d6a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238636c3_fa67_4931_b5fb_de576427bb82
EDIN-837459-2017 | ED-327606-2015 | 6/14/2017 5:04:33 PM | ASSESS: ED IN: Acceptance | png | #asFound Roof of building | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Roof_Access_2.png Access to machine room across unlit and low parapet roof with tripping and fall hazards. No handrails around the roof perimeter | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Roof_Access_2.png | file://x:/photopub/docs/0000000616/b784afce-6397-48a8-ae3d-dd98e698cc2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddef20a0_fab3_43c0_aad5_492f1bad892e
EDIN-837460-2017 | ED-327603-2015 | 6/14/2017 4:25:12 PM | ASSESS: ED IN: Acceptance | png | #asFound Machine room access across the roof | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Roof_access.png There are no means provided to prevent tripping and fall hazards to access machine rooms across the roof. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Roof_access.png | file://x:/photopub/docs/0000000616/9dc0172c-dd58-4fa4-b90d-a5e83952157f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c776666_fe1d_4d82_82b2_2b1baa532023
EDIN-837458-2017 | ED-327611-2015 | 6/14/2017 5:08:59 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Roof_MR7.png Access to machine room across roof without handrails and lighting across roof and tripping hazards | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Roof_MR7.png | file://x:/photopub/docs/0000000616/db0638c3-3cfb-42f0-9d7f-6b52839bef0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11914d98_f20f_4ac5_90a7_a7f8b668ba61
EDIN-837456-2017 | ED-327600-2015 | 6/14/2017 5:19:58 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Roof_MR8a.png Access to machine room across roof without handrails, lighting and tripping hazards. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Roof_MR8a.png | file://x:/photopub/docs/0000000616/fc7f6034-f23a-494c-840e-cba6eb49633c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3935bda_7e97_483f_9fd0_8345fde3400f
EDIN-837452-2017 | ED-327598-2015 | 6/14/2017 5:24:05 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Roof_MR9.png Access to machine room is across a roof without handrails, lighting and numerous trip hazards | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Roof_MR9.png | file://x:/photopub/docs/0000000616/de3cbf14-12ca-46d6-a5d3-e23e7990a0a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa1f5a26_3244_4c2c_bed5_8af8665e7584
ELIN-833430-2017 | EL-544741-2017 | 6/13/2017 4:06:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage1.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage2.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage3.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage4.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage5.png Cables are required to be properly supported where they run from, to, and between electrical equipment. This is required to prevent the cables and cable terminations from getting damaged if they are accidentally snagged and pulled on or left in locations where they are susceptible to mechanical damage. This installation has a non-metallic sheathed cable installed for 15A and 20A 120V temporary construction receptacles for a new house under construction. The cable was not properly supported and was left in a location wh | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage4.png | file://x:/photopub/docs/0000000615/a42c7348-1038-4ca0-83e5-0b0a3c0dcab2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__795a9be2_ae7f_44a8_a507_175b41831b55
ELIN-833114-2017 | EL-344206-2016 | 6/13/2017 3:02:04 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Light_fixtures_in_the_crawlspace1.png,Light_fixtures_in_the_crawlspace2.png Light fixtures installed in locations below 2.1M from the floor in readily accessible locations are required to be protected from mechanical damage by a guard or by location. This is required to prevent the fixture from getting damaged and posing a fire or shock hazard. This installation for a new house has four light fixtures that are installed in the crawlspace that are installed lower than 2.1M from the floor and have open exposed light bulbs that could become damaged or could come in contact with combustible materials stored in the crawlspace. Left uncorrected this is a shock and fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Light_fixtures_in_the_crawlspace2.png | file://x:/photopub/docs/0000000615/500e4896-d39e-413d-95de-c13bc25f1071.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1785aa86_a1af_41c1_a4d4_6c950f7944b9
ELIN-846106-2017 | EL-431111-2016 | 6/28/2017 4:30:00 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png,C.png Armoured cable has jacket stripped off and has been run through walls and ceilings in a dwelling. This is a shock hazard as the conductors are exposed to damage and the armour is not electrically continuous/bonded. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B5.png | file://x:/photopub/docs/0000000622/25e11ad5-bc3a-4780-aaca-1abf970dfd7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce62c6b2_a830_4bfa_8f8d_1bfb28c10386
ELIN-846106-2017 | EL-431111-2016 | 6/28/2017 4:30:00 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png,C.png Armoured cable has jacket stripped off and has been run through walls and ceilings in a dwelling. This is a shock hazard as the conductors are exposed to damage and the armour is not electrically continuous/bonded. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | C.png | file://x:/photopub/docs/0000000622/a9b68c8e-a674-4a88-a884-ae67efc57f98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce62c6b2_a830_4bfa_8f8d_1bfb28c10386
ELIN-846106-2017 | EL-431111-2016 | 6/28/2017 4:30:00 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png,C.png Armoured cable has jacket stripped off and has been run through walls and ceilings in a dwelling. This is a shock hazard as the conductors are exposed to damage and the armour is not electrically continuous/bonded. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B2.png | file://x:/photopub/docs/0000000622/5cc948e5-271e-4961-88cb-186af3dfd83c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce62c6b2_a830_4bfa_8f8d_1bfb28c10386
ELIN-846106-2017 | EL-431111-2016 | 6/28/2017 4:30:00 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png,C.png Armoured cable has jacket stripped off and has been run through walls and ceilings in a dwelling. This is a shock hazard as the conductors are exposed to damage and the armour is not electrically continuous/bonded. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B3.png | file://x:/photopub/docs/0000000622/24a99a95-10b3-401b-8d84-9fafe20ecf76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce62c6b2_a830_4bfa_8f8d_1bfb28c10386
ELIN-846343-2017 | EL-515655-2017 | 6/28/2017 1:37:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A.png Service equipment located next to a drive way. This is a shock and fire hazard as the equipment could be struck by a vehicle. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000622/f764c481-b8ab-481e-a083-1e56b30dd987.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff04f2b_c1df_4418_8a27_caf805fa2b21
BPVOP-865242-2017 | 2269288 | 7/25/2017 11:53:00 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 2 | #Safety_Valve.png Upon assessment of low pressure steam heating boiler with 40square meters heating surface it is determined that capacity of safety valve is less than theoretical minimum capacity required. In the event of over-pressure built up in the boiler (due to failure of control and other safety devices) there is possibility of permanent damage or even rupture of pressure boundary of boiler which can lead to incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Valve.png | file://x:/photopub/docs/0000000635/19cfd37b-2302-4e8c-915a-dafc4d7babb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c4bb6d6_f5c7_4a42_93f9_0e9388177b39
ELOP-805837-2017 | EL-521944-2017 | 5/18/2017 7:07:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord_connected_light1.png,Extension_cord_connected_light2.png,Extension_cord_connected_light3.png,Extension_cord_connected_light4.png,Extension_cord_connected_light5.png,Extension_cord_connected_light6.png An extension cord has been used to feed a 102 volt 15 amp light fixture and the cord has been installed in a permanent fashion, the cord is not intended for permanent installation and is supported by wrapping the cord around plumbing pipes. The cord end has also been removed to connect to the light fixture and no fitting or outlet box has been used. This poses a shock hazard to persons and potential mechanical damage to the light, cord and the receptacle powering this set up. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_connected_light5.png | file://x:/photopub/docs/0000000603/a2e67405-3d0b-453c-a9ec-a3efd46aff2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C224ED52_5DBC_4886_9450_D8ABD8FB13C5
ELOP-805837-2017 | EL-521944-2017 | 5/18/2017 7:07:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord_connected_light1.png,Extension_cord_connected_light2.png,Extension_cord_connected_light3.png,Extension_cord_connected_light4.png,Extension_cord_connected_light5.png,Extension_cord_connected_light6.png An extension cord has been used to feed a 102 volt 15 amp light fixture and the cord has been installed in a permanent fashion, the cord is not intended for permanent installation and is supported by wrapping the cord around plumbing pipes. The cord end has also been removed to connect to the light fixture and no fitting or outlet box has been used. This poses a shock hazard to persons and potential mechanical damage to the light, cord and the receptacle powering this set up. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_connected_light4.png | file://x:/photopub/docs/0000000603/3a6bd4e8-f10f-4205-84c6-c65a4a8c07ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C224ED52_5DBC_4886_9450_D8ABD8FB13C5
ELOP-805837-2017 | EL-521944-2017 | 5/18/2017 7:07:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord_connected_light1.png,Extension_cord_connected_light2.png,Extension_cord_connected_light3.png,Extension_cord_connected_light4.png,Extension_cord_connected_light5.png,Extension_cord_connected_light6.png An extension cord has been used to feed a 102 volt 15 amp light fixture and the cord has been installed in a permanent fashion, the cord is not intended for permanent installation and is supported by wrapping the cord around plumbing pipes. The cord end has also been removed to connect to the light fixture and no fitting or outlet box has been used. This poses a shock hazard to persons and potential mechanical damage to the light, cord and the receptacle powering this set up. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_connected_light1.png | file://x:/photopub/docs/0000000603/50c64d9e-7592-4096-ae45-5e9a7c077294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C224ED52_5DBC_4886_9450_D8ABD8FB13C5
ELOP-805837-2017 | EL-521944-2017 | 5/18/2017 7:07:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord_connected_light1.png,Extension_cord_connected_light2.png,Extension_cord_connected_light3.png,Extension_cord_connected_light4.png,Extension_cord_connected_light5.png,Extension_cord_connected_light6.png An extension cord has been used to feed a 102 volt 15 amp light fixture and the cord has been installed in a permanent fashion, the cord is not intended for permanent installation and is supported by wrapping the cord around plumbing pipes. The cord end has also been removed to connect to the light fixture and no fitting or outlet box has been used. This poses a shock hazard to persons and potential mechanical damage to the light, cord and the receptacle powering this set up. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_connected_light3.png | file://x:/photopub/docs/0000000603/e347ace1-ebc4-4317-9be0-0a926505a12c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C224ED52_5DBC_4886_9450_D8ABD8FB13C5
ELOP-805837-2017 | EL-521944-2017 | 5/18/2017 7:07:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord_connected_light1.png,Extension_cord_connected_light2.png,Extension_cord_connected_light3.png,Extension_cord_connected_light4.png,Extension_cord_connected_light5.png,Extension_cord_connected_light6.png An extension cord has been used to feed a 102 volt 15 amp light fixture and the cord has been installed in a permanent fashion, the cord is not intended for permanent installation and is supported by wrapping the cord around plumbing pipes. The cord end has also been removed to connect to the light fixture and no fitting or outlet box has been used. This poses a shock hazard to persons and potential mechanical damage to the light, cord and the receptacle powering this set up. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_connected_light2.png | file://x:/photopub/docs/0000000603/17055a22-ec9c-49c8-9814-02f0b7b62b78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C224ED52_5DBC_4886_9450_D8ABD8FB13C5
ELIN-809591-2017 | EL-530297-2017 | 5/23/2017 1:24:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #One_of_5_locations_flexible_cord_used_in_lieu_of_permanent_wiring_to_equipment_or_for_convenience.png Flexible cord operating a refrigerator, hot tub and other permanent 120 volt 15 amp devices was found attached to structure, run through building construction on an older residence after a service repair. Flexible cord may be mechanically, uv or rain damaged and lead to potential for damage to structures or persons when used in lieu of permanent wiring | 4 | Conductors, Misuse of flexible cords. | One_of_5_locations_flexible_cord_used_in_lieu_of_permanent_wiring_to_equipment_or_for_convenience.png | file://x:/photopub/docs/0000000605/d0c36bc2-de0f-4a6c-8929-05a5429cfb44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dcd427d_6ebf_4069_877e_9c32fea169a2
GAIN-812399-2017 | GA-528982-2017 | 5/15/2017 10:23:27 AM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Underground_line.png Underground line not connected to a gas supply, sitting in an open trench susceptible to damage. If the line becomes damaged or is covered without proper bedding material it could lead to a gas leak. | 3 | Code prohibited practices or materials | Underground_line.png | file://x:/photopub/docs/0000000602/1346c9a7-0c99-4446-9b67-8a2534c90154.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de17036c_dcdd_4402_a369_f6557f2492e8
GAIN-812399-2017 | GA-528982-2017 | 5/15/2017 10:23:27 AM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Underground_line.png Underground line not connected to a gas supply, sitting in an open trench susceptible to damage. If the line becomes damaged or is covered without proper bedding material it could lead to a gas leak. | 3 | Code prohibited practices or materials | Underground_line.png | file://x:/photopub/docs/0000000602/b97ce83d-5771-4e84-949e-cc041b26a556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de17036c_dcdd_4402_a369_f6557f2492e8
ELIN-846106-2017 | EL-431111-2016 | 6/28/2017 4:30:00 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png,C.png Armoured cable has jacket stripped off and has been run through walls and ceilings in a dwelling. This is a shock hazard as the conductors are exposed to damage and the armour is not electrically continuous/bonded. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B4.png | file://x:/photopub/docs/0000000622/95a32c3c-e88b-40c2-8b53-3ecdfd96dfe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce62c6b2_a830_4bfa_8f8d_1bfb28c10386
ELIN-846106-2017 | EL-431111-2016 | 6/28/2017 4:30:00 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png,C.png Armoured cable has jacket stripped off and has been run through walls and ceilings in a dwelling. This is a shock hazard as the conductors are exposed to damage and the armour is not electrically continuous/bonded. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B1.png | file://x:/photopub/docs/0000000622/3dd42dfc-c020-4766-8e08-4baf9b3e763e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce62c6b2_a830_4bfa_8f8d_1bfb28c10386
ELIN-856020-2017 | EL-556321-2017 | 7/13/2017 9:51:07 AM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Main_480_volt_service.png The EXISTING 100 amp 480 volt 3phase 3-wire ungrounded service does not include any Ground Fault Indication, during a ground fault the warning lights would give a visual of a fault and notify personnel, a fault unnoticed is a shock hazard | 3 | Continuity Bonding; method for equipment is not adequate. | Main_480_volt_service.png | file://x:/photopub/docs/0000000630/2b008f38-5dec-4430-a885-097cbcf6b6cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__963b0891_5743_4d05_a3af_146514d34cc3
GAIN-814859-2017 | GA-533422-2017 | 5/15/2017 2:44:39 PM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open__line.png Open gas line installed outdoors with valve in closed position. Valve could be inadvertently opened ,releasing gas from the open line. Possible explosion and or fire risk if a source of ignition was present. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open__line.png | file://x:/photopub/docs/0000000601/45db560c-2ff7-4c39-ac81-641a84fb03bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0128a089_3bef_40a8_9e6d_ff8ff3a324f7
ELIN-833255-2017 | EL-493402-2017 | 6/12/2017 2:03:02 PM | ASSESS: EL: Final | png | #asFound No slip joint installed | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #4.png 100 Amp service does not have a slip joint installed under the meter base. If the pole were to settle or the conduit were to settle the conduit could crack or pull out of the meter base. This is a shock and fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 4.png | file://x:/photopub/docs/0000000614/c3ca87a4-2e91-4564-b2b7-6efbae9ad9d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fe3c959_caaf_40c2_9e1a_b25111288964
ELIN-848633-2017 | EL-421860-2016 | 7/4/2017 4:05:14 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 2 | #A.png Gas line not bonded. This is a shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | A.png | file://x:/photopub/docs/0000000624/2b8ffb4e-a304-4d06-9584-33f56161fa35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cea1d0c7_d296_43ee_a851_38dd260fd57b
ELIN-815910-2017 | EL-368545-2016 | 5/16/2017 11:29:48 AM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png Indoor panels installed in a wet location, this is a shock hazard. | 3 | General Equipment is not approved for the specific use | A2.png | file://x:/photopub/docs/0000000601/c4683887-7b46-432f-a7d9-225c93fc5c29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__846879b1_9cb3_4d25_bf06_ad20fb913197
ELIN-815910-2017 | EL-368545-2016 | 5/16/2017 11:29:48 AM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png Indoor panels installed in a wet location, this is a shock hazard. | 3 | General Equipment is not approved for the specific use | A1.png | file://x:/photopub/docs/0000000601/bb6d8b20-4059-48d9-98f0-499639e012d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__846879b1_9cb3_4d25_bf06_ad20fb913197
ELIN-815910-2017 | EL-368545-2016 | 5/16/2017 11:29:48 AM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png Indoor panels installed in a wet location, this is a shock hazard. | 3 | General Equipment is not approved for the specific use | A3.png | file://x:/photopub/docs/0000000601/8416ac42-8b9a-4d76-babf-b144e7104556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__846879b1_9cb3_4d25_bf06_ad20fb913197
ELIN-852859-2017 | EL-555661-2017 | 7/10/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound -Secondary suite service fed from duplex meter base has not been grounded in the first overcurrent equipment or within the duplex meterbase. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Pic3.png -The secondary suite load center is not rated for "service entrance equipment" and there is no ground electrode connected to the secondary suite service or main duplex meterbase. During a fault condition there may be stray voltages over the electrical equipment leading to accidental electrical shock or fire hazards. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Pic3.png | file://x:/photopub/docs/0000000629/f3714dc2-e5ac-4ca0-ab46-07d3819ac2bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__471c1ba4_2f77_476b_8e2f_7738f63ead09
ELHE-828262-2017 | HE-541398-2017 | 6/1/2017 4:02:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #11.png,12.png A 100 Amp fused disconnect feeds #4 AWG/ 4 conductor flexible cable. This cable feeds a 125 Amp load centre on the dock. The dock panel board feeds many receptacles on the dock and a 30 Amp float home. The fuses are oversized for the conductor that is installed, this is a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 11.png | file://x:/photopub/docs/0000000610/0f33b127-1dd2-4098-bc7d-659143ea010a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2f6644_8989_4332_82f0_6de430046d91
ELHE-828262-2017 | HE-541398-2017 | 6/1/2017 4:02:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #11.png,12.png A 100 Amp fused disconnect feeds #4 AWG/ 4 conductor flexible cable. This cable feeds a 125 Amp load centre on the dock. The dock panel board feeds many receptacles on the dock and a 30 Amp float home. The fuses are oversized for the conductor that is installed, this is a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 12.png | file://x:/photopub/docs/0000000610/6b027cfc-fd4a-4db4-ae22-25b136b52ce4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2f6644_8989_4332_82f0_6de430046d91
GAIN-827932-2017 | GA-474467-2016 | 6/5/2017 3:07:01 PM | ASSESS: GA: Final | png | #asFound | GA118 | Clearance to a moisture exhaust duct | 2 | 2 | #Clearance_to_moisture_exhaust_duct_not_maintained_.png Clearance to moisture exhaust duct. Air intake can be obstructed by laundry lint causing incomplete combustion within the appliance. | 2 | Clearance to a moisture exhaust duct | Clearance_to_moisture_exhaust_duct_not_maintained_.png | file://x:/photopub/docs/0000000611/41e1361d-7a2f-48c2-a67c-62a765c0f4ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d99ba8f2_4ad3_4b96_8478_af4b5db1a622
GAWP-840115-2017 | GA-451761-2016 | 6/19/2017 3:52:56 PM | ASSESS: GA Work In Progress | png | #asFound Appliance air intakes too close to gas meter regulator | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Gas_meter.png Gas furnace air supply piping Is too close to the relief vent of a gas regulator. If the gas regulator reliefs gas it could be drawn into the appliance air intake resulting in a fire or explosion. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Gas_meter.png | file://x:/photopub/docs/0000000618/e84252aa-1d80-4cac-ad0d-abbc83171b8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b78a78a3_2921_49bf_bd8f_239014dbb2db
ELHE-828262-2017 | HE-541398-2017 | 6/1/2017 4:02:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #11.png,12.png A 100 Amp fused disconnect feeds #4 AWG/ 4 conductor flexible cable. This cable feeds a 125 Amp load centre on the dock. The dock panel board feeds many receptacles on the dock and a 30 Amp float home. The fuses are oversized for the conductor that is installed, this is a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 12.png | file://x:/photopub/docs/0000000610/a8a6874b-a656-4ab7-bf96-1584eb147c8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2f6644_8989_4332_82f0_6de430046d91
ELIN-854972-2017 | EL-553618-2017 | 7/17/2017 9:04:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hot_tub_sub_distribution1.png,Hot_tub_sub_distribution2.png,Hot_tub_sub_distribution3.png The sub-distribution panel with GFCI protection for hot tub located in basement mechanical room is missing breaker cover screws and knock out filler. This can fall into the enclosure when the main weather proof cover is opened and can create both a shock and thermal hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hot_tub_sub_distribution1.png | file://x:/photopub/docs/0000000631/947dfa1c-1429-452b-a699-4a4c59061b30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84245896_23ef_43b5_9cf0_2a98db666617
ELIN-857855-2017 | EL-558539-2017 | 7/17/2017 7:48:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 3 | #Temporary_pole1.png,Temporary_pole2.png The 100 amp 120/240 volt temporary service is mounted on a treated 6x6 post with no bracing and buried with approx 600mm of loose fill installed on top of normal grade to create burial depth of temporary pole, the post above grade is approx 17' above top of mound. Mounding of soil does not give sufficient secure footing in front of electrical equipment or proper burial of temporary pole exposing it to susceptible damage, this is a system operation and an equipment damage issue | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Temporary_pole1.png | file://x:/photopub/docs/0000000631/539afc2d-69b5-4ca6-bb2d-bf4757f5fa76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61f0e173_69c3_498a_b09b_d4077cbf4e16
ELIN-854972-2017 | EL-553618-2017 | 7/17/2017 9:04:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hot_tub_sub_distribution1.png,Hot_tub_sub_distribution2.png,Hot_tub_sub_distribution3.png The sub-distribution panel with GFCI protection for hot tub located in basement mechanical room is missing breaker cover screws and knock out filler. This can fall into the enclosure when the main weather proof cover is opened and can create both a shock and thermal hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hot_tub_sub_distribution3.png | file://x:/photopub/docs/0000000631/b8e5e6df-1faa-47b1-aeac-48831f4b1b12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84245896_23ef_43b5_9cf0_2a98db666617
ELIN-857855-2017 | EL-558539-2017 | 7/17/2017 7:48:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 3 | #Temporary_pole1.png,Temporary_pole2.png The 100 amp 120/240 volt temporary service is mounted on a treated 6x6 post with no bracing and buried with approx 600mm of loose fill installed on top of normal grade to create burial depth of temporary pole, the post above grade is approx 17' above top of mound. Mounding of soil does not give sufficient secure footing in front of electrical equipment or proper burial of temporary pole exposing it to susceptible damage, this is a system operation and an equipment damage issue | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Temporary_pole2.png | file://x:/photopub/docs/0000000631/30e7d7b5-042a-48d3-8855-591537aed877.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61f0e173_69c3_498a_b09b_d4077cbf4e16
ELIN-854972-2017 | EL-553618-2017 | 7/17/2017 9:04:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hot_tub_sub_distribution1.png,Hot_tub_sub_distribution2.png,Hot_tub_sub_distribution3.png The sub-distribution panel with GFCI protection for hot tub located in basement mechanical room is missing breaker cover screws and knock out filler. This can fall into the enclosure when the main weather proof cover is opened and can create both a shock and thermal hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hot_tub_sub_distribution2.png | file://x:/photopub/docs/0000000631/d5fbc38e-d158-42cf-8905-f631bcab4e41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84245896_23ef_43b5_9cf0_2a98db666617
GAUP-859604-2017 | UW-559683-2017 | 7/18/2017 9:15:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Propane_cylinder_removed_.png No hazard at time on inspection due to their being no fuel source. | 0 | No Created Hazard Identified | Propane_cylinder_removed_.png | file://x:/photopub/docs/0000000631/d0f7d501-d5bf-4f55-975c-48a299dc9084.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1201fcb1_eda3_46b2_b9ee_c9e08fdf17ea
AMOP-828965-2017 | AM-254468-2015 | 6/1/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Upper_tether_angles.png Upper tether anchor points set at less than 20' from the base of the unit. Manufacturer specifies that upper tether ground anchor point are to be set at 20-30 feet from the base of the unit. Units not anchored as per manufacturer's specification could effect the stability integrity of the unit | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Upper_tether_angles.png | file://x:/photopub/docs/0000000610/70cc0cf4-84e3-4a53-90f6-df0bdf63974e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4237c71_3f22_40dc_85f8_5416f3962bd8
AMOP-829010-2017 | AM-254375-2015 | 6/1/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Tether_not_anchored.png Tether point at multiple location are not anchored. Units not anchored as per manufacturer's specification could effect the stability integrity of the unit. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Tether_not_anchored.png | file://x:/photopub/docs/0000000610/cbb76258-fd66-4990-a2ac-e6db8bd33dc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__530f756f_d001_4d03_a72a_565f95c0c727
AMOP-829017-2017 | AM-397588-2016 | 6/1/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Tether_points_not_anchored_1.png,Tether_points_not_anchored_2.png Tether point at multiple location are not anchored. Units not anchored as per manufacturer's specification could effect the stability integrity of the unit. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Tether_points_not_anchored_1.png | file://x:/photopub/docs/0000000610/845e930b-362e-4c96-9f2e-040fe44dae5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46a2466f_6a55_4570_8a3f_47ef6f783631
ELIN-835112-2017 | EL-452744-2016 | 6/15/2017 10:38:39 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_protection.png,No_AFCI_protection_2.png In a new single dwelling residential construction 15 amp 120 volt receptacles were found with no arc fault protection. This could lead to a thermal effect condition. Picture attached. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_protection.png | file://x:/photopub/docs/0000000617/20f6f9fd-15d2-48ea-a811-fb480269cbd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18f69b19_218b_4f54_a69a_f25eb5249fe8
ELIN-835112-2017 | EL-452744-2016 | 6/15/2017 10:38:39 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_protection.png,No_AFCI_protection_2.png In a new single dwelling residential construction 15 amp 120 volt receptacles were found with no arc fault protection. This could lead to a thermal effect condition. Picture attached. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_protection_2.png | file://x:/photopub/docs/0000000617/f9dc87d7-18be-4749-a245-05ce03940c1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18f69b19_218b_4f54_a69a_f25eb5249fe8
ELIN-858437-2017 | EL-559108-2017 | 7/17/2017 4:27:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Enclosure_not_weatherproof.png Panel board enclosure: This assessment found a residential 200 amp combination panel installed in a location that was not weatherproof. If the main breaker becomes wet it may not operate properly creating a shock and fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Enclosure_not_weatherproof.png | file://x:/photopub/docs/0000000631/29b65a52-0625-483d-8674-bad2d52ce444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73ce2dc7_f655_48a7_90ae_43addcfe4fb9
BPVOP-862068-2017 | BPV-152248-2014 | 7/20/2017 11:34:01 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that horizontal machine mounted air receiver (1.40m long and 0.40m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000633/8560272c-f41c-4bb0-9101-324558622b1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fff5deed_130b_4186_8a19_3b4f7e736d9c
ELHE-828262-2017 | HE-541398-2017 | 6/1/2017 4:02:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Weatherproof receptacles are tampered with, they are no longer weatherproof. | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #11.png,12.png A 100 Amp fused disconnect feeds #4 AWG/ 4 conductor flexible cable. This cable feeds a 125 Amp load centre on the dock. The dock panel board feeds many receptacles on the dock and a 30 Amp float home. The fuses are oversized for the conductor that is installed, this is a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 11.png | file://x:/photopub/docs/0000000610/6c578b17-37cb-433d-96e9-3237433a2435.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be2f6644_8989_4332_82f0_6de430046d91
ELIN-827782-2017 | EL-496465-2017 | 6/5/2017 2:30:16 PM | ASSESS: EL: Final | png | #asFound No cover | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #4.png The outlet box in the soffit does not have a cover installed. This box contains nonmetallic sheathed cable which is not bonded to ground. This is a shock hazard to individual that might come into contact with this conductor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4.png | file://x:/photopub/docs/0000000611/cf8745dc-bd48-4bc7-ae13-93728c6a64d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b3c41d_51de_4ae2_becf_49d6da58e585
GAIN-854558-2017 | GA-525775-2017 | 7/11/2017 3:45:14 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Unsecured_copper_tubing1.png Copper tubing system not secured at connection of an appliance connector for a movable appliance. Copper tubing can be damaged when strained if not secured. | 2 | Physical protection of piping and tubing absent. | Unsecured_copper_tubing1.png | file://x:/photopub/docs/0000000628/84919f6e-ba94-4b84-a6a0-33ea52cb3e81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23c2f44b_e198_4fc8_891b_4351314392ba
GAIN-826850-2017 | GA-540588-2017 | 7/11/2017 1:24:48 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #tubing_and_fittings_not_approved_for_use_.png Unapproved tubing and fittings. Compression fittings used in a gas tubing system can lead to gas leaks causing fire or explosion. | 3 | Non-compliant material/fittings installed | tubing_and_fittings_not_approved_for_use_.png | file://x:/photopub/docs/0000000628/707fa693-0b0f-4a93-81e6-d4921344523d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1a75ebf_92a9_417e_91b3_909af283c8c8
ELIN-854201-2017 | EL-556114-2017 | 7/11/2017 10:40:22 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #2_ground_rods_present_and_only_one_is_connected.png Currently there is only one ground rod connected to the system ground conductor, a second rod is present and is not interconnected with the other rod. In the case of a fault one ground rod may not be sufficient to clear the fault and overcurrent devices may not act as required to clear the fault. A fault situation may provide risk of shock and fire to persons and property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | 2_ground_rods_present_and_only_one_is_connected.png | file://x:/photopub/docs/0000000628/6180f298-14fe-43c7-a7de-10bd310ab8b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bbe99d1_c42e_4f45_be38_75b9acb2439e
ELOP-845826-2017 | 5249977 | 7/5/2017 3:09:37 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Box_without_cover.png Junction box for lighting circuits mounted in the ceiling is without a cover. Junction boxes require covers to protect the spliced conductors inside from accidentally coming in contact with persons or equipment. This situation would pose a risk of shock and fire to persons and property. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Box_without_cover.png | file://x:/photopub/docs/0000000625/90a8070b-615b-4061-9a5e-9d462f9b111f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f30263bf_fe59_4ab6_a6e9_0b268694d6af
AMOP-829017-2017 | AM-397588-2016 | 6/1/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Tether_points_not_anchored_1.png,Tether_points_not_anchored_2.png Tether point at multiple location are not anchored. Units not anchored as per manufacturer's specification could effect the stability integrity of the unit. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Tether_points_not_anchored_2.png | file://x:/photopub/docs/0000000610/9c5e137a-d8f0-4e63-842c-e974ef255243.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46a2466f_6a55_4570_8a3f_47ef6f783631
ELIN-822614-2017 | EL-497137-2017 | 5/31/2017 11:24:45 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #One_receptacle_only_island_split_by_sink.png A kitchen island with a sink located in the center has not been provided a receptacle on one side of the sink. Owners may resort to running cords past sinks or cooktops and put the property and owners at risk | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | One_receptacle_only_island_split_by_sink.png | file://x:/photopub/docs/0000000610/de8db00c-a514-4530-82ee-dfaccb331f5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__246d175b_b167_40e8_8457_a94712fd770c
ELIN-855042-2017 | UW-556920-2017 | 7/12/2017 2:11:53 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Energized conductors exposed to mechanical damage in area accessible to general public. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #View01_feeder_cabling1.png,View01_feeder_cabling2.png Energized overhead cabling exposed to mechanical damage while removed from approved supporting structure and placed in area accessible to general public. This poses an imminent and immediate risk of personal injury (electrocution) and property damage (thermal event/ interface fire). | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | View01_feeder_cabling2.png | file://x:/photopub/docs/0000000630/90ed9057-d8cc-4724-828f-59290dc61ee8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e78c61e1_3fb7_4cdb_8eb9_3a4d0c6c2c85
ELIN-855042-2017 | UW-556920-2017 | 7/12/2017 2:11:53 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Energized conductors exposed to mechanical damage in area accessible to general public. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #View01_feeder_cabling1.png,View01_feeder_cabling2.png Energized overhead cabling exposed to mechanical damage while removed from approved supporting structure and placed in area accessible to general public. This poses an imminent and immediate risk of personal injury (electrocution) and property damage (thermal event/ interface fire). | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | View01_feeder_cabling1.png | file://x:/photopub/docs/0000000630/e3373d01-193c-4938-a8e8-26ab7223fe24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e78c61e1_3fb7_4cdb_8eb9_3a4d0c6c2c85
ELIN-851944-2017 | EL-536240-2017 | 7/7/2017 1:18:19 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 4 | #Unprotected_cables_.png The unfused cable between the electrical meter and the main breaker of the panel is run inside the building and susceptible to damage because it is not protected from mechanical damage. Should these cables be damaged a serious fire hazard will be present. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Unprotected_cables_.png | file://x:/photopub/docs/0000000627/edb5ee6b-de39-441b-8609-74154d6b8c28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75aca629_0b5f_450d_bb77_d4b92a4daa83
GAIN-835144-2017 | GA-544858-2017 | 6/14/2017 2:31:05 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #E_S_3.png Mechanical appliance intake installed with less than the required minimum separation from regulator vent. Failure of the regulator would allow high pressure gas to be relieved into the surrounding area. The possibility exists that the gas could be drawn into the appliance causing a over fire condition. Possible fire risk | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | E_S_3.png | file://x:/photopub/docs/0000000616/3bd44125-e7d9-467b-8682-f285896960c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbe51997_a614_4371_8d63_678ac801487c
ELIN-819957-2017 | EL-496708-2017 | 5/23/2017 8:08:00 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Microwave_and_counter_plug_on_same_circuit.png This assessment found the microwave and counter plug on the same circuit, potentially overloading the circuit with a risk of fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Microwave_and_counter_plug_on_same_circuit.png | file://x:/photopub/docs/0000000604/63dd80f0-9ffa-474d-980d-de426d69e7e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa85b408_52d8_454e_b79c_ce712e22eddb
BPVIN-739628-2017 | BPV-369373-2016 | 6/21/2017 2:46:49 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound No lockable disconnects | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect.png,No_disconnects.png Upon assessment of a hot water boiler with a maximum working pressure of 80 psig and a maximum working temperature of 200 Fahrenheit, it was determined there was no lockable disconnect. This creates risk to personnel and equipment. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_disconnects.png | file://x:/photopub/docs/0000000624/e9ad6c7e-c136-41e4-9ea3-e9fa5dd40b05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a156557a_bb96_4750_9aa5_2b1a2ba4ffed
ELIN-858547-2017 | EL-500585-2017 | 7/18/2017 1:51:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Sub_panel_under_deck.png A 100 amp 120/240 volt sub panel located under a deck was not weatherproof and was located directly under a floor drain system with poly as a barrier. This can result in the equipment being damaged. Picture attached. | 3 | General Equipment is not approved for the specific use | Sub_panel_under_deck.png | file://x:/photopub/docs/0000000632/2fa325b7-4d05-4291-9af9-6d0392c7be44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba675cc_28bc_4ee9_8590_0d4d8892375d
ELIN-859160-2017 | EL-487314-2017 | 7/18/2017 8:08:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 3 | #Bent_servicemast.png In a 200 amp 120/240 volt overhead service repair the service mast was found to be slightly bowed. With the supply conductor length being greater than 35 meters and the weight of the supply conductors the mast is susceptible to further damage because the integrity of the mast has been is compromised. This is an equipment damage issue. Picture attached. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Bent_servicemast.png | file://x:/photopub/docs/0000000632/89bfb523-94b1-411c-997f-b19772783aee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8839131c_1e03_48f7_83b1_255dd9f657f5
BPVOP-839157-2017 | 4071803 | 6/16/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Pressure_relief_valve_exceeded_replacement_interval.png Upon assessment it is determined that a machine mounted horizontal air receiver (0.91m long and 0.40m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Pressure_relief_valve_exceeded_replacement_interval.png | file://x:/photopub/docs/0000000617/7c5bc147-578e-4c4b-99a4-bc9ed6cc761a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aebe86da_31bd_4741_8d96_941ec89231fd
GAIN-676872-2016 | GA-446447-2016 | 6/15/2017 12:02:06 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Furnace_vent.png 2" ABS pipe and fittings used to vent furnace. Code requires vent material to meet ULC S636 standard for vent materials. | 3 | Unapproved venting material | Furnace_vent.png | file://x:/photopub/docs/0000000617/ed597e15-13c5-42da-9639-95b17307e2d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__742f652c_befe_4760_864d_4fcc2d6b327f
ELIN-820466-2017 | EL-490638-2017 | 5/23/2017 1:26:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #B.png No expansion joints, underground conduits are prone to frost heaving and settlement. This is a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | B.png | file://x:/photopub/docs/0000000604/6960fba5-ba6d-4dc4-afc7-da8a62b918e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfba7717_8e97_4a4c_92a7_7aef79f4ab1c
ELIN-820247-2017 | EL-465407-2016 | 5/23/2017 12:55:31 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Are lamp fixture located in close closet, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A4.png | file://x:/photopub/docs/0000000604/14c52dbd-d6d6-49a1-90f6-6d4add392187.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b0a9c24_4b4b_427e_b462_14821bd3934f
ELIN-820247-2017 | EL-465407-2016 | 5/23/2017 12:55:31 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Are lamp fixture located in close closet, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A1.png | file://x:/photopub/docs/0000000604/86cf6cb8-fa04-4166-88fc-21e9a0c780ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b0a9c24_4b4b_427e_b462_14821bd3934f
ELIN-819697-2017 | EL-517397-2017 | 5/23/2017 4:21:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #C.png Lag bolts supporting over head mast installed into the siding. These need to be secured into structural members of the building. This is a fire hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | C.png | file://x:/photopub/docs/0000000604/ce44b61a-ce87-4ad1-ad71-329bb7b1569a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2905d270_b372_42de_95a4_78ece9612c77
ELIN-820247-2017 | EL-465407-2016 | 5/23/2017 12:55:31 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Are lamp fixture located in close closet, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A5.png | file://x:/photopub/docs/0000000604/83db174e-13e4-4d01-8f65-9e5031f93e83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b0a9c24_4b4b_427e_b462_14821bd3934f
ELIN-820247-2017 | EL-465407-2016 | 5/23/2017 12:55:31 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Are lamp fixture located in close closet, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A6.png | file://x:/photopub/docs/0000000604/05ccf8ae-3265-4681-be5e-ec650dfaa3d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b0a9c24_4b4b_427e_b462_14821bd3934f
ELIN-820247-2017 | EL-465407-2016 | 5/23/2017 12:55:31 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Are lamp fixture located in close closet, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A2.png | file://x:/photopub/docs/0000000604/612f8a34-e518-4d22-a14d-657ec1eba7e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b0a9c24_4b4b_427e_b462_14821bd3934f
ELIN-859343-2017 | EL-550720-2017 | 7/20/2017 11:32:16 AM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #No_bond_wire_with_service_conductors.png In a 2x 200 amp 120/240 volt residential duplex service upgrade, the consumer service panels were found to be inadequately bonded to ground. This could lead to a shock hazard situation. Picture attached. | 3 | Continuity Bonding; method for equipment is not adequate. | No_bond_wire_with_service_conductors.png | file://x:/photopub/docs/0000000633/b073faff-2fd6-488f-8c99-90cd1026b10c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__460fd14b_8244_4c63_8a6b_5f022685d0cf
ELIN-842201-2017 | UW-549576-2017 | 6/22/2017 10:21:52 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A.png Cables not supported properly, exposed splices. These are a shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000620/8c660f3d-29b8-481c-9a6c-46a930a2c140.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c61475b9_60f5_4883_b134_1db488f0f0ba
ELOP-841626-2017 | EL-541415-2017 | 6/22/2017 12:41:11 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL298 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #A1.png,A2.png Open holes in panel, this is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A1.png | file://x:/photopub/docs/0000000620/339ef491-d482-4372-97a8-c66389f96687.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__211694CB_F49E_4433_9B5C_0D11359C4B4B
ELOP-841626-2017 | EL-541415-2017 | 6/22/2017 12:41:11 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL298 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #A1.png,A2.png Open holes in panel, this is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A2.png | file://x:/photopub/docs/0000000620/407d9a7e-748b-4f95-92ff-3c86dfecee8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__211694CB_F49E_4433_9B5C_0D11359C4B4B
ELIN-838887-2017 | EL-531103-2017 | 6/19/2017 3:14:06 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | #A.png CAFCI protection not provided. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | A.png | file://x:/photopub/docs/0000000618/a0a23622-9c28-4adf-8dc2-6233bf7cc78a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd609dc1_3393_4ffd_9011_71e9de9a6502
ELIN-837957-2017 | EL-547426-2017 | 6/19/2017 5:17:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Main_disconnect1.png,Main_disconnect2.png The energized 100 amp 480 volt 3-phase distribution equipment located within an existing enclosure not lockable is missing a knock out filler in the bottom of the disconnect, this can become a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Main_disconnect1.png | file://x:/photopub/docs/0000000618/a55a226d-7d03-4086-b939-95044cc40c55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8980d199_c3e2_4b8b_ab0e_5ef47b9fbe9d
ELIN-837957-2017 | EL-547426-2017 | 6/19/2017 5:17:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Main_disconnect1.png,Main_disconnect2.png The energized 100 amp 480 volt 3-phase distribution equipment located within an existing enclosure not lockable is missing a knock out filler in the bottom of the disconnect, this can become a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Main_disconnect2.png | file://x:/photopub/docs/0000000618/39a7fea7-796d-470b-9852-dd4fcd27317f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8980d199_c3e2_4b8b_ab0e_5ef47b9fbe9d
ELIN-846617-2017 | EL-552252-2017 | 7/6/2017 | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #Enclosure_.png | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Enclosure_.png | file://x:/photopub/docs/0000000626/9f61f343-b433-4de3-9474-27b020bf0dac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbd599df_5596_4032_8d48_8661ac6bee6a
ELIN-819399-2017 | EL-518211-2017 | 5/18/2017 2:38:38 PM | ASSESS: EL: Final | png | #asFound Cable is stressed between stud and cable connector. | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #P4.png Feeder cable for the shop sub panel is in stress between the stud and cable connector to the service panel. This may cause cable insulation failure causing fire. Fire could in turn cause property damage, injuries or death to occupants of this house. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | P4.png | file://x:/photopub/docs/0000000603/def6d4bc-952f-4941-a329-a3b3c4e56103.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7124300_3e4a_4a7c_a8eb_3efa9a7df6e7
ELIN-821388-2017 | EL-397709-2016 | 5/25/2017 1:13:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #A.png Open hole in panel, this is a shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | A.png | file://x:/photopub/docs/0000000605/038e6082-8d0b-49e7-ad85-9e509dbd5f31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d15a5a4e_1a81_4b54_9665_74f622dce561
ELIN-821629-2017 | EL-537425-2017 | 5/25/2017 2:21:56 PM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #B.png Loose termination of conductor, this is a fire hazard. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | B.png | file://x:/photopub/docs/0000000605/59ea8573-87f4-413e-ba6f-ba37314ec89a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__880046fc_a4eb_48ab_802e_b6baf1c89641
ELIN-834331-2017 | EL-545234-2017 | 6/12/2017 2:51:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | #Exposed_panel1.png,Exposed_panel2.png A 200 amp / 240 volt panel is installed in a location where it is exposed to the weather and is not enclosed in a weathertight enclosure. This could cause corrosion and damage to the buss and overcurrent devices in the panel rendering them inoperable. | 3 | Category 1 Equipment is not approved for the specific use or location. | Exposed_panel2.png | file://x:/photopub/docs/0000000614/d0624d85-4122-4952-95bf-f428d1e22245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3af87a7_2037_4dc9_a7c8_b436b6773b8c
ELIN-834331-2017 | EL-545234-2017 | 6/12/2017 2:51:58 PM | ASSESS: EL: Service Connection | png | #asFound Service panel is exposed to the weather. | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | #Exposed_panel1.png,Exposed_panel2.png A 200 amp / 240 volt panel is installed in a location where it is exposed to the weather and is not enclosed in a weathertight enclosure. This could cause corrosion and damage to the buss and overcurrent devices in the panel rendering them inoperable. | 3 | Category 1 Equipment is not approved for the specific use or location. | Exposed_panel1.png | file://x:/photopub/docs/0000000614/8ff04130-5eb6-4c90-80c5-0bef0d7cc9bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3af87a7_2037_4dc9_a7c8_b436b6773b8c
BPVIN-827903-2017 | BPV-541160-2017 | 6/1/2017 9:24:06 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP153 | 5.0.1 Operator non-compliance - Procedures not posted | 1 | 1 | #CO2_MONITOR.png,CO2_MONITOR_.png | 1 | 5.0.1 Operator non-compliance - Procedures not posted | CO2_MONITOR.png | file://x:/photopub/docs/0000000609/9127dd09-7f0e-460a-bc6c-48b7dc9b7e2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71c0cf4c_14bb_488f_9c55_778efbcd1202
BPVIN-827903-2017 | BPV-541160-2017 | 6/1/2017 9:24:06 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP153 | 5.0.1 Operator non-compliance - Procedures not posted | 1 | 1 | #CO2_MONITOR.png,CO2_MONITOR_.png | 1 | 5.0.1 Operator non-compliance - Procedures not posted | CO2_MONITOR_.png | file://x:/photopub/docs/0000000609/873a8c46-ebac-4960-b576-3499fe92b567.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71c0cf4c_14bb_488f_9c55_778efbcd1202
ELIN-816314-2017 | EL-526134-2017 | 5/23/2017 2:34:48 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrect_wires_used_.png In an existing single family dwelling, a kitchen renovation resulted in an undersized kitchen counter circuit feeders to be installed. This can lead to a "Thermal Effect" condition. Pic attached. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrect_wires_used_.png | file://x:/photopub/docs/0000000604/f5cf10f6-3fa0-40b4-8cb8-64121920986f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55f8caa4_3c67_4f3d_a8a2_99c46059d9d5
BPVIN-853096-2017 | BPV-525507-2017 | 7/25/2017 11:22:01 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP120 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | 5 | 5 | #Low-Water_Fuel_Cut-Off_Device.png A low-water fuel cut-off device was found not in place. This prevents the boiler from being fired if the water level is below the lowest permissible water level. Operating the burner on a boiler when the water level is low allows the pressure vessel metal to become weakened due to the overheated condition. Ultimately this may lead to a boiler explosion that leads to property damage and fatalities. | 5 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | Low-Water_Fuel_Cut-Off_Device.png | file://x:/photopub/docs/0000000636/75b4f07f-a13e-4472-bfed-bc367006fdb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41402050_ec71_4a69_b763_514c5965fb47
BPVOP-828092-2017 | 2266678 | 6/1/2017 8:48:55 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_without_emergency_shutdown_switch_at_entrance.png Upon assessment of Hot Water Boiler with Heating Surface (HS) of 9.0 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_without_emergency_shutdown_switch_at_entrance.png | file://x:/photopub/docs/0000000610/30b50975-6b6f-4de3-8baf-5093f740ca3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00a87423_0d41_40fe_8ee7_216ad696f94e
AMIN-832255-2017 | AM-434408-2016 | 6/9/2017 8:11:19 AM | ASSESS: AM IN: Acceptance | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Entrance_gates_and_fencing_to_install.png Entrance gates and fences not installers at time of inspection, guests could walk into the path of travel of the device, while in operation. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Entrance_gates_and_fencing_to_install.png | file://x:/photopub/docs/0000000613/ee3d76bb-60fe-4f63-b4d2-0811bcd0a3d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45399848_cb0a_4102_89df_1a97795f36b9
ELIN-821868-2017 | EL-148026-2014 | 5/25/2017 10:38:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Feeder.png An energized 6/3 Teck90 has been connected to a 6/3 NMD90 without an approved junction box and the connections are accessible, this poses a shock hazard and potential damage to the electrical equipment. This connection has also been made at a new 200 amp 120/240V panel which has been requested to connect to the Utility, this could pose a backfeed issue which is also a shock hazard to persons. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Feeder.png | file://x:/photopub/docs/0000000605/1def2c70-6a84-4025-9659-de10318d1045.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b85b311f_e3f0_4fd8_a5a6_c22d48dcaf5c
ELOP-818800-2017 | 3858 | 5/24/2017 11:00:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Branch_Wire.png An energized 14/3 non metallic cable has been damaged but the repair has been done exposed without an outlet box. This poses a shock hazard to persons and potential damage to the wiring as this energized connection is exposed and is not supported. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Branch_Wire.png | file://x:/photopub/docs/0000000605/bfa33e6d-6bf5-44e3-a683-4032d02a60d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B7CE2EBA_1F89_4175_8599_95AB1B60D56E
ELIN-819969-2017 | EL-534397-2017 | 5/23/2017 2:27:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Solar_Panel_Bonding1.png,Solar_Panel_Bonding2.png Four solar panels rated at 260 watt, 30 volt DC, and 9 amp, are not bonded and the metal support frames used are also not bonded. This poses a shock hazard to persons and possible mechanical damage to the equipment as the overcurrent devices may not operate as designed protecting people and property. | 3 | Continuity Bonding; method for equipment is not adequate. | Solar_Panel_Bonding2.png | file://x:/photopub/docs/0000000605/86513021-6287-456d-8490-35cfda747913.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc426e91_ea7b_4e4b_ae4d_c1e3eef83a8c
ELIN-819969-2017 | EL-534397-2017 | 5/23/2017 2:27:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Solar_Panel_Bonding1.png,Solar_Panel_Bonding2.png Four solar panels rated at 260 watt, 30 volt DC, and 9 amp, are not bonded and the metal support frames used are also not bonded. This poses a shock hazard to persons and possible mechanical damage to the equipment as the overcurrent devices may not operate as designed protecting people and property. | 3 | Continuity Bonding; method for equipment is not adequate. | Solar_Panel_Bonding1.png | file://x:/photopub/docs/0000000605/bfe45bee-42a9-40c4-bc6a-2312afea789e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc426e91_ea7b_4e4b_ae4d_c1e3eef83a8c
GAUP-833846-2017 | UW-544980-2017 | 6/9/2017 11:21:26 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #1.png Uncertified gas fireplace was in use up until April 2017. Glass cracked, went onsite to investigate to find a counterfeit testing agency decal. Confirm with Chris Jorgenson and testing agency. | 3 | Uncertified appliance connected to gas supply but not in service | 1.png | file://x:/photopub/docs/0000000614/21d4e4d3-67dd-4ab4-b485-4fba90d80703.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e3a66be_1cb9_42d1_8f92_bc193940ddc2
GAIN-837525-2017 | GA-522312-2017 | 7/20/2017 3:39:15 PM | ASSESS: GA: Final | png | #asFound 1.5 to 1.25 inch piping | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Alpenhorn1.png,Alpenhorn2.png,Alpenhorn3.png Gas piping installed to feed gas for 3 appliances. Appliance BTU rating is too large for piping connected. Appliances are at risk of underfiring, creating a hazard on appliances as well as possibly causing the burner to create unacceptable levels of carbon monoxide in the flame | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Alpenhorn3.png | file://x:/photopub/docs/0000000633/b4df7f73-263e-40ce-ad76-4cb6a404314a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2afd1a59_c34f_4e24_a5a1_f3abf55bdb18
GAIN-837525-2017 | GA-522312-2017 | 7/20/2017 3:39:15 PM | ASSESS: GA: Final | png | #asFound 600,000BTU Load | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Alpenhorn1.png,Alpenhorn2.png,Alpenhorn3.png Gas piping installed to feed gas for 3 appliances. Appliance BTU rating is too large for piping connected. Appliances are at risk of underfiring, creating a hazard on appliances as well as possibly causing the burner to create unacceptable levels of carbon monoxide in the flame | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Alpenhorn2.png | file://x:/photopub/docs/0000000633/80c956bf-7526-4fdd-84fe-08a9f76b7a87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2afd1a59_c34f_4e24_a5a1_f3abf55bdb18
GAIN-837525-2017 | GA-522312-2017 | 7/20/2017 3:39:15 PM | ASSESS: GA: Final | png | #asFound Low Pressure Meter | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Alpenhorn1.png,Alpenhorn2.png,Alpenhorn3.png Gas piping installed to feed gas for 3 appliances. Appliance BTU rating is too large for piping connected. Appliances are at risk of underfiring, creating a hazard on appliances as well as possibly causing the burner to create unacceptable levels of carbon monoxide in the flame | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Alpenhorn1.png | file://x:/photopub/docs/0000000633/49e272cd-82db-42ac-a862-d25587e97121.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2afd1a59_c34f_4e24_a5a1_f3abf55bdb18
ELIN-848941-2017 | EL-398873-2016 | 7/10/2017 10:39:20 AM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png 50A receptacle for a mobile home located in a wet location without a wet location cover. The U ground slot is oriented to the bottom, the outlet boxes are not supported and DB2 conduit is not permitted above ground. This is a fire hazard. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | A1.png | file://x:/photopub/docs/0000000628/f8e781d2-0717-4c8f-9eaf-39c8e2606962.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ab20e00_f1e6_4246_8e46_d49a5bfb58dd
ELIN-848941-2017 | EL-398873-2016 | 7/10/2017 10:39:20 AM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png 50A receptacle for a mobile home located in a wet location without a wet location cover. The U ground slot is oriented to the bottom, the outlet boxes are not supported and DB2 conduit is not permitted above ground. This is a fire hazard. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | A4.png | file://x:/photopub/docs/0000000628/c6418fe8-2d80-4c0b-9af4-f09a9585d322.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ab20e00_f1e6_4246_8e46_d49a5bfb58dd
ELIN-848941-2017 | EL-398873-2016 | 7/10/2017 10:39:20 AM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png 50A receptacle for a mobile home located in a wet location without a wet location cover. The U ground slot is oriented to the bottom, the outlet boxes are not supported and DB2 conduit is not permitted above ground. This is a fire hazard. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | A3.png | file://x:/photopub/docs/0000000628/32e12688-5a95-4103-8b73-0a928c721c5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ab20e00_f1e6_4246_8e46_d49a5bfb58dd
ELIN-848941-2017 | EL-398873-2016 | 7/10/2017 10:39:20 AM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png 50A receptacle for a mobile home located in a wet location without a wet location cover. The U ground slot is oriented to the bottom, the outlet boxes are not supported and DB2 conduit is not permitted above ground. This is a fire hazard. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | A2.png | file://x:/photopub/docs/0000000628/939973bc-1831-4e20-b129-5b39c065c876.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ab20e00_f1e6_4246_8e46_d49a5bfb58dd
GAIN-856531-2017 | GA-537174-2017 | 7/20/2017 9:54:06 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Non_compliant_vent_termination.png Sidewall vent termination must not terminate below 7ft over a public walkway. A risk to public of exposure to flue product occurs if vent termination does not meet clearance requirements. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Non_compliant_vent_termination.png | file://x:/photopub/docs/0000000633/6150963d-a42e-4980-a1e6-526d226ce38a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcf8ff83_bcf9_4c7f_9c3a_177c860c86f1
ELIN-863290-2017 | EL-561484-2017 | 7/24/2017 10:37:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #No_bonding__no_bonding_bush.png Metal raceways feeding a 600 amp 240 volt service are not bonded to the grounding statement correctly. These raceways can inadvertently become energized and if not positively bonded to ground can lead to property damage or injury to persons. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bonding__no_bonding_bush.png | file://x:/photopub/docs/0000000635/f87867c6-3cbd-4e7a-a7b2-36e36a8dd485.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3f23061_0d97_4807_94ce_1e0018351dbd
ELIN-854028-2017 | EL-553097-2017 | 7/12/2017 7:59:34 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #No_gfci_protection.png The temporary service installation includes a 15 amp 120 volt receptacle with no GFCI protection and is protected by a 20 amp breaker, this is both a shock and thermal hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_gfci_protection.png | file://x:/photopub/docs/0000000629/8a57869e-2194-4c4e-bc13-abdc6dbc3248.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06b24776_a06f_4d01_a205_7eac74c19811
GAIN-822579-2017 | GA-537332-2017 | 5/25/2017 4:04:56 PM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Unprotected_CSST1.png,Unprotected_CSST2.png Corrugated stainless steel tubing attached to metal structure without protection from electrical fault. Corrugated stainless steel tubing can be easily damage by electrical faults which can cause an uncontrolled release of gas. | 2 | Physical protection of piping and tubing absent. | Unprotected_CSST2.png | file://x:/photopub/docs/0000000605/6b98d765-fddf-4cec-92fd-93cfe3367b5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1dd6041_8b73_487e_be70_b2106e745382
GAIN-822579-2017 | GA-537332-2017 | 5/25/2017 4:04:56 PM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Unprotected_CSST1.png,Unprotected_CSST2.png Corrugated stainless steel tubing attached to metal structure without protection from electrical fault. Corrugated stainless steel tubing can be easily damage by electrical faults which can cause an uncontrolled release of gas. | 2 | Physical protection of piping and tubing absent. | Unprotected_CSST1.png | file://x:/photopub/docs/0000000605/087b2e3a-4398-4671-a651-712bf6b0f9dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1dd6041_8b73_487e_be70_b2106e745382
ELIN-833430-2017 | EL-544741-2017 | 6/13/2017 4:06:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage1.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage2.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage3.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage4.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage5.png Cables are required to be properly supported where they run from, to, and between electrical equipment. This is required to prevent the cables and cable terminations from getting damaged if they are accidentally snagged and pulled on or left in locations where they are susceptible to mechanical damage. This installation has a non-metallic sheathed cable installed for 15A and 20A 120V temporary construction receptacles for a new house under construction. The cable was not properly supported and was left in a location wh | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage1.png | file://x:/photopub/docs/0000000615/fc2e7c45-c2af-4985-b584-5062fc4d007f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__795a9be2_ae7f_44a8_a507_175b41831b55
ELIN-833430-2017 | EL-544741-2017 | 6/13/2017 4:06:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage1.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage2.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage3.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage4.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage5.png Cables are required to be properly supported where they run from, to, and between electrical equipment. This is required to prevent the cables and cable terminations from getting damaged if they are accidentally snagged and pulled on or left in locations where they are susceptible to mechanical damage. This installation has a non-metallic sheathed cable installed for 15A and 20A 120V temporary construction receptacles for a new house under construction. The cable was not properly supported and was left in a location wh | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage3.png | file://x:/photopub/docs/0000000615/8e481ff3-b1f5-485e-9011-708f6c075f1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__795a9be2_ae7f_44a8_a507_175b41831b55
ELIN-829656-2017 | EL-532827-2017 | 6/13/2017 11:48:15 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Newly_added_washer_circuit_19_was_not_AFCI_protected1.png,Newly_added_washer_circuit_19_was_not_AFCI_protected2.png,Newly_added_washer_circuit_19_was_not_AFCI_protected3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of a receptacle circuit in a new house was not provided with AFCI protection. The branch circuit was for a 15A 120V receptacle for a washing machine in the laundry room. This is a potential fire hazard if an arcing fault occurs on this receptacle branch circuit from the branch circuit wiring or the equipment that is plugged into the receptacle. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Newly_added_washer_circuit_19_was_not_AFCI_protected3.png | file://x:/photopub/docs/0000000615/a0c01cfc-390b-49d8-9be5-dcc9fd297cb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c91d0bf1_4cd9_4278_94fe_1622b6f17f5f
ELIN-833430-2017 | EL-544741-2017 | 6/13/2017 4:06:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage1.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage2.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage3.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage4.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage5.png Cables are required to be properly supported where they run from, to, and between electrical equipment. This is required to prevent the cables and cable terminations from getting damaged if they are accidentally snagged and pulled on or left in locations where they are susceptible to mechanical damage. This installation has a non-metallic sheathed cable installed for 15A and 20A 120V temporary construction receptacles for a new house under construction. The cable was not properly supported and was left in a location wh | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage2.png | file://x:/photopub/docs/0000000615/e4fefff9-7506-4d20-a0fb-297a12171e64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__795a9be2_ae7f_44a8_a507_175b41831b55
ELIN-776245-2017 | EL-006080-2013 | 6/12/2017 3:54:01 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Exterior_rexeptacles.png All but 2 exterior receptacles exposed to weather conditions utilize weather-proof flip one covers and not the in-use covers. This can create a shock hazard with the cord connections being exposed to wet weather conditions | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_rexeptacles.png | file://x:/photopub/docs/0000000621/e8c9e391-10c7-4d66-ae45-eeaac64509d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__438b6f49_8163_404e_9fd9_9a2cee469b6d
ELIN-824352-2017 | EL-444250-2016 | 5/29/2017 4:16:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Z1.png,Z2.png,Z3.png Switches and thermostat is located within 500mm of the bathtub. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Z2.png | file://x:/photopub/docs/0000000607/6952644a-d4b2-4f63-9fab-953005183a1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8f1571d_22e9_424b_ab7b_fb5c451f8dd5
ELIN-824352-2017 | EL-444250-2016 | 5/29/2017 4:16:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Z1.png,Z2.png,Z3.png Switches and thermostat is located within 500mm of the bathtub. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Z3.png | file://x:/photopub/docs/0000000607/e684e411-9b9b-4fa8-a7a3-ea3b957c2ce6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8f1571d_22e9_424b_ab7b_fb5c451f8dd5
ELIN-824352-2017 | EL-444250-2016 | 5/29/2017 4:16:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound The switches and thermostat are located within 500mm of the bathtub. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Z1.png,Z2.png,Z3.png Switches and thermostat is located within 500mm of the bathtub. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Z1.png | file://x:/photopub/docs/0000000607/f4666a9d-e279-46fc-a01a-c6a4ee820f1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8f1571d_22e9_424b_ab7b_fb5c451f8dd5
ELIN-819961-2017 | EL-536511-2017 | 5/23/2017 11:36:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Cables_in_contact_with_duct_work1.png,Cables_in_contact_with_duct_work2.png Non-metallic sheathed cable is required to be installed in locations with an ambient temperature not exceeding 30 Â°C. When the cable is installed adjacent to heating ducts, a 50mm clearance or thermal barrier is required. This is required so that the increased temperature from the heating duct does not cause the cable to exceed the temperature rating of the cable which could lead to insulation breakdown of the conductor. In this installation in a new suite of a single family dwelling, non-metallic cable was installed where the cable came in contact with the heating ducts. When this cable is energized and under load, the conductor insulation could break down and cause a potential a fire hazard or equipment damage. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_contact_with_duct_work1.png | file://x:/photopub/docs/0000000604/5900df9d-d3df-4601-914f-add1a2b070e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292d8e13_96cd_43be_9a74_e312bf81b195
ELIN-819961-2017 | EL-536511-2017 | 5/23/2017 11:36:39 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Cables_in_contact_with_duct_work1.png,Cables_in_contact_with_duct_work2.png Non-metallic sheathed cable is required to be installed in locations with an ambient temperature not exceeding 30 Â°C. When the cable is installed adjacent to heating ducts, a 50mm clearance or thermal barrier is required. This is required so that the increased temperature from the heating duct does not cause the cable to exceed the temperature rating of the cable which could lead to insulation breakdown of the conductor. In this installation in a new suite of a single family dwelling, non-metallic cable was installed where the cable came in contact with the heating ducts. When this cable is energized and under load, the conductor insulation could break down and cause a potential a fire hazard or equipment damage. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_contact_with_duct_work2.png | file://x:/photopub/docs/0000000604/0cb9a5ed-95ea-4a1d-8f9a-c6156472fc36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__292d8e13_96cd_43be_9a74_e312bf81b195
ELIN-834820-2017 | EL-485415-2016 | 6/19/2017 4:23:52 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #AFCI_missing.png At an existing residential home where a basement suite is added, 3x 15amp 120volt outlet circuits were found without Arc-fault protection on the breaker. This can lead to a "Thermal Effect" condition. Pic attached. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | AFCI_missing.png | file://x:/photopub/docs/0000000618/7959ec71-5390-46ff-93e8-9b2ed7d69817.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccf94e1e_9ec6_487c_bfe8_478c74a49247
ELIN-866793-2017 | EL-476825-2016 | 7/27/2017 1:46:01 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Arc_Faults_Needed.png This assessment found that Arc fault breakers for the washer and Vacuum are not installed, which could create a fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Arc_Faults_Needed.png | file://x:/photopub/docs/0000000637/c0bb3c11-4a0a-48f5-9b59-2cedd3be3212.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef345a31_25f9_46fe_8873_936c4b68917a
ELIN-833114-2017 | EL-344206-2016 | 6/13/2017 3:02:04 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Light_fixtures_in_the_crawlspace1.png,Light_fixtures_in_the_crawlspace2.png Light fixtures installed in locations below 2.1M from the floor in readily accessible locations are required to be protected from mechanical damage by a guard or by location. This is required to prevent the fixture from getting damaged and posing a fire or shock hazard. This installation for a new house has four light fixtures that are installed in the crawlspace that are installed lower than 2.1M from the floor and have open exposed light bulbs that could become damaged or could come in contact with combustible materials stored in the crawlspace. Left uncorrected this is a shock and fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Light_fixtures_in_the_crawlspace1.png | file://x:/photopub/docs/0000000615/6289ccce-29f7-43bb-9f90-edbc202400cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1785aa86_a1af_41c1_a4d4_6c950f7944b9
ELIN-823935-2017 | EL-418753-2016 | 6/13/2017 1:57:35 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Recessed_fixture_installed_above_a_shower1.png,Recessed_fixture_installed_above_a_shower2.png Light fixtures are required to be approved for the location when installed in damp or wet locations. This is required to prevent damage to the electrical equipment which create a hazard for persons and property. This installation for a new house has a recessed light fixture that is installed above a shower enclosure in the master bedroom ensuite. The recessed fixture does not have a trim installed on it that will prevent steam vapor or water from contacting the bulb and entering the fixture. This is a potential fire hazard if the electrical socket or interior wiring components of the fixture become corroded over time and electrical components or connections fail. This is a hazard due to breaking glass from the bulb if the hot bulb breaks when exposed to water or steam vapor. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Recessed_fixture_installed_above_a_shower1.png | file://x:/photopub/docs/0000000615/f231b10e-6d11-45c9-a02e-e139464a7b06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2387a15_1f37_413a_910d_825c4229daf2
ELIN-833430-2017 | EL-544741-2017 | 6/13/2017 4:06:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage1.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage2.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage3.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage4.png,Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage5.png Cables are required to be properly supported where they run from, to, and between electrical equipment. This is required to prevent the cables and cable terminations from getting damaged if they are accidentally snagged and pulled on or left in locations where they are susceptible to mechanical damage. This installation has a non-metallic sheathed cable installed for 15A and 20A 120V temporary construction receptacles for a new house under construction. The cable was not properly supported and was left in a location wh | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuit_cable_for_temporary_construction_receptacles_installed_where_exposed_to_damage5.png | file://x:/photopub/docs/0000000615/801a83b3-59bf-47b1-8081-88ffc467d5b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__795a9be2_ae7f_44a8_a507_175b41831b55
BPVOP-856018-2017 | 3897218 | 7/12/2017 12:12:46 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that horizontal machine mounted air receiver (1.22m long and 0.60m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Pressure_relief_valve.png | file://x:/photopub/docs/0000000629/012f1435-9b73-4e03-b382-b088bf5dbf32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__221e7a6d_93c4_4409_8d5a_35e281d96bc6
GAUP-816002-2017 | UW-533425-2017 | 5/15/2017 1:29:16 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Rating Plate | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | #Rating_Plate.png Uncertified Lime Kiln Burner was installed and in operation without the proper permitting in place. Permits required to approve, install and verify start-up procedure to ensure safe functionality of burner. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Rating_Plate.png | file://x:/photopub/docs/0000000601/2aecd606-ecf2-4c9f-8a43-9730004a867c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81f78205_2044_4dfa_9b8b_f6d3e76af1d4
GAIN-826107-2017 | GA-426486-2016 | 5/30/2017 2:34:07 PM | ASSESS: GA: Final | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #relief_regulator.png Full release regulator has been installed and put into service and the vent line off of the regulator has not been extended to a safe location outdoors. If the regulator was to malfunction and over pressurize the downstream side of the regulator the overpressure protection device would open and allow raw gas to escape into the occupied space potentially causing an uncontrolled gas leak in a location where there are ignition sources which could cause a explosion and fire and injuries | 5 | Relief style regulator/device allowed to vent within building/confined space | relief_regulator.png | file://x:/photopub/docs/0000000607/7963f512-6160-4f8e-8d40-99d4edb5bf15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a058e338_3b39_44dd_8e21_aace33894c6c
ELIN-847133-2017 | EL-544575-2017 | 7/13/2017 | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 4 | #Pole_mount_transformers1.png,Pole_mount_transformers2.png,Pole_mount_transformers3.png,No_4_cu_ground_conductor.png The BC Electrical Code requires that every outdoor station operating at high voltage be connected to a station ground electrode with a minimum 2/0 copper conductor. This requirement is to reduce the resistance to the station ground electrode during a fault condition. In this installation for for a new high voltage overhead service, the station ground conductor for two new 100kVA, 14.4kV to 120/240V pole mount transformers was a #4 copper conductor. The smaller #4 copper conductor connected to the station ground electrodes could increase the step and touch voltage near the station ground during an electrical fault condition. This has the potential to create a shock hazard to persons near the ground electrode. | 4 | Installation Grounding; conductor is not properly sized. | Pole_mount_transformers1.png | file://x:/photopub/docs/0000000630/45d60fbb-70fe-4510-98ee-cc4e125a0e07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3eeaaf_1050_4f2d_ba47_9b651412fc4c
ELIN-847133-2017 | EL-544575-2017 | 7/13/2017 | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 4 | #Pole_mount_transformers1.png,Pole_mount_transformers2.png,Pole_mount_transformers3.png,No_4_cu_ground_conductor.png The BC Electrical Code requires that every outdoor station operating at high voltage be connected to a station ground electrode with a minimum 2/0 copper conductor. This requirement is to reduce the resistance to the station ground electrode during a fault condition. In this installation for for a new high voltage overhead service, the station ground conductor for two new 100kVA, 14.4kV to 120/240V pole mount transformers was a #4 copper conductor. The smaller #4 copper conductor connected to the station ground electrodes could increase the step and touch voltage near the station ground during an electrical fault condition. This has the potential to create a shock hazard to persons near the ground electrode. | 4 | Installation Grounding; conductor is not properly sized. | No_4_cu_ground_conductor.png | file://x:/photopub/docs/0000000630/72746258-2862-446e-802f-6e00f8508cd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3eeaaf_1050_4f2d_ba47_9b651412fc4c
ELIN-854063-2017 | EL-555873-2017 | 7/10/2017 10:03:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #A.png No cover plates on receptacles. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000628/7b2bf431-b9e5-4b48-b2bc-e62c8259f206.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__019d1014_9d7c_42d0_82bd_1166be9095bf
AMOP-835471-2017 | AM-543494-2017 | 6/13/2017 12:29:01 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Missing_fencing_and_handrail1.png,Missing_fencing_and_handrail2.png Handrails and fence section missing on an overhead walkway. Unit was not in operation at the time of inspection. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Missing_fencing_and_handrail1.png | file://x:/photopub/docs/0000000615/327b4e4a-414d-42e1-9848-59e470c4f91e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bcb9b33_a852_4254_bc3c_ab2ad3bc384d
ELIN-829656-2017 | EL-532827-2017 | 6/13/2017 11:48:15 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Newly_added_washer_circuit_19_was_not_AFCI_protected1.png,Newly_added_washer_circuit_19_was_not_AFCI_protected2.png,Newly_added_washer_circuit_19_was_not_AFCI_protected3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of a receptacle circuit in a new house was not provided with AFCI protection. The branch circuit was for a 15A 120V receptacle for a washing machine in the laundry room. This is a potential fire hazard if an arcing fault occurs on this receptacle branch circuit from the branch circuit wiring or the equipment that is plugged into the receptacle. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Newly_added_washer_circuit_19_was_not_AFCI_protected1.png | file://x:/photopub/docs/0000000615/c2d7e7f3-7f12-4f2f-81c3-8cc737434d90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c91d0bf1_4cd9_4278_94fe_1622b6f17f5f
ELIN-823935-2017 | EL-418753-2016 | 6/13/2017 1:57:35 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Recessed_fixture_installed_above_a_shower1.png,Recessed_fixture_installed_above_a_shower2.png Light fixtures are required to be approved for the location when installed in damp or wet locations. This is required to prevent damage to the electrical equipment which create a hazard for persons and property. This installation for a new house has a recessed light fixture that is installed above a shower enclosure in the master bedroom ensuite. The recessed fixture does not have a trim installed on it that will prevent steam vapor or water from contacting the bulb and entering the fixture. This is a potential fire hazard if the electrical socket or interior wiring components of the fixture become corroded over time and electrical components or connections fail. This is a hazard due to breaking glass from the bulb if the hot bulb breaks when exposed to water or steam vapor. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Recessed_fixture_installed_above_a_shower2.png | file://x:/photopub/docs/0000000615/6fbe6768-e739-4a11-a619-71d3cef05254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2387a15_1f37_413a_910d_825c4229daf2
ELIN-829656-2017 | EL-532827-2017 | 6/13/2017 11:48:15 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Newly_added_washer_circuit_19_was_not_AFCI_protected1.png,Newly_added_washer_circuit_19_was_not_AFCI_protected2.png,Newly_added_washer_circuit_19_was_not_AFCI_protected3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of a receptacle circuit in a new house was not provided with AFCI protection. The branch circuit was for a 15A 120V receptacle for a washing machine in the laundry room. This is a potential fire hazard if an arcing fault occurs on this receptacle branch circuit from the branch circuit wiring or the equipment that is plugged into the receptacle. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Newly_added_washer_circuit_19_was_not_AFCI_protected2.png | file://x:/photopub/docs/0000000615/3de14ad6-c440-4154-aedc-2ef0f70e16b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c91d0bf1_4cd9_4278_94fe_1622b6f17f5f
ELIN-847133-2017 | EL-544575-2017 | 7/13/2017 | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 4 | #Pole_mount_transformers1.png,Pole_mount_transformers2.png,Pole_mount_transformers3.png,No_4_cu_ground_conductor.png The BC Electrical Code requires that every outdoor station operating at high voltage be connected to a station ground electrode with a minimum 2/0 copper conductor. This requirement is to reduce the resistance to the station ground electrode during a fault condition. In this installation for for a new high voltage overhead service, the station ground conductor for two new 100kVA, 14.4kV to 120/240V pole mount transformers was a #4 copper conductor. The smaller #4 copper conductor connected to the station ground electrodes could increase the step and touch voltage near the station ground during an electrical fault condition. This has the potential to create a shock hazard to persons near the ground electrode. | 4 | Installation Grounding; conductor is not properly sized. | Pole_mount_transformers3.png | file://x:/photopub/docs/0000000630/4ff64490-6aea-4d18-b06f-b5394a3272ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3eeaaf_1050_4f2d_ba47_9b651412fc4c
ELIN-847133-2017 | EL-544575-2017 | 7/13/2017 | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 4 | #Pole_mount_transformers1.png,Pole_mount_transformers2.png,Pole_mount_transformers3.png,No_4_cu_ground_conductor.png The BC Electrical Code requires that every outdoor station operating at high voltage be connected to a station ground electrode with a minimum 2/0 copper conductor. This requirement is to reduce the resistance to the station ground electrode during a fault condition. In this installation for for a new high voltage overhead service, the station ground conductor for two new 100kVA, 14.4kV to 120/240V pole mount transformers was a #4 copper conductor. The smaller #4 copper conductor connected to the station ground electrodes could increase the step and touch voltage near the station ground during an electrical fault condition. This has the potential to create a shock hazard to persons near the ground electrode. | 4 | Installation Grounding; conductor is not properly sized. | Pole_mount_transformers2.png | file://x:/photopub/docs/0000000630/e382681d-d4da-4dbd-be6a-fb38dc05246e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3eeaaf_1050_4f2d_ba47_9b651412fc4c
ELIN-772613-2017 | EL-286023-2015 | 5/29/2017 12:44:32 PM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Conduits_between_kiosk_and_lift_station1.png,Conduits_between_kiosk_and_lift_station2.png The contractor has installed an assembly of conduit types that are not approved for this particular installation. There is no mechanical protection installed in a vehicular area and the conduit system is unsupported and energized and readily accessible to the general public. Explosion proof fittings have not been sealed to prevent the flow of explosive gas. This condition may possibly result in equipment damage or personal injury. If the explosive gas contacts the electrical equipment in the control kiosk. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Conduits_between_kiosk_and_lift_station1.png | file://x:/photopub/docs/0000000607/330b42b9-bacf-4691-bad4-b388ce8e1092.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25a20aec_bcf1_4099_9afd_681bbe079331
ELIN-856649-2017 | EL-557379-2017 | 7/13/2017 1:16:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_cover.png Service panel requested to be connected without the covers in place. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_cover.png | file://x:/photopub/docs/0000000630/a6a455a8-5d61-489f-97df-5ed93b19501d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66b2d50b_0b07_4cc7_8bd8_4873c9692319
ELIN-856649-2017 | EL-557379-2017 | 7/13/2017 1:16:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_cover.png Service panel requested to be connected without the covers in place. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_cover.png | file://x:/photopub/docs/0000000630/742282e5-34f3-43a6-84af-20f85af88932.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66b2d50b_0b07_4cc7_8bd8_4873c9692319
ELIN-856648-2017 | EL-557379-2017 | 7/13/2017 1:07:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Consumer_service_underground.png Consumer service conductor is not buried according to requirements for depth, screened sand, debris or caution tape | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Consumer_service_underground.png | file://x:/photopub/docs/0000000630/814d6dc7-7cb3-47eb-b344-b7a3e2cfb5da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4dd6bd5d_a800_41fe_b0ef_d55f595041a4
ELIN-856649-2017 | EL-557379-2017 | 7/13/2017 1:16:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_cover.png Service panel requested to be connected without the covers in place. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_cover.png | file://x:/photopub/docs/0000000630/296108bf-6e06-4785-9e9a-072ebd69a82e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66b2d50b_0b07_4cc7_8bd8_4873c9692319
ELIN-856648-2017 | EL-557379-2017 | 7/13/2017 1:07:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Consumer_service_underground.png Consumer service conductor is not buried according to requirements for depth, screened sand, debris or caution tape | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Consumer_service_underground.png | file://x:/photopub/docs/0000000630/c73c4389-da72-462a-ab1d-c8e12223cf40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4dd6bd5d_a800_41fe_b0ef_d55f595041a4
ELIN-856648-2017 | EL-557379-2017 | 7/13/2017 1:07:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound ACWU consumer service cable in trench with debris | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Consumer_service_underground.png Consumer service conductor is not buried according to requirements for depth, screened sand, debris or caution tape | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Consumer_service_underground.png | file://x:/photopub/docs/0000000630/df3ed1d4-0b65-42d1-96a3-ef92e5d21e0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4dd6bd5d_a800_41fe_b0ef_d55f595041a4
AMOP-836005-2017 | AM-543507-2017 | 6/8/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 1 | #Repairs_being_conducted_to_stair_landing1.png,Repairs_being_conducted_to_stair_landing2.png Public access stairs to launch area landing was in the state of being repaired at the time of inspection. Landing grade at below normal stair height | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Repairs_being_conducted_to_stair_landing1.png | file://x:/photopub/docs/0000000615/4bca9355-079f-48a1-bb0e-0290ee968b66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9b52142_a6c6_43b5_a015_575a15cb0930
AMOP-836005-2017 | AM-543507-2017 | 6/8/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 1 | #Repairs_being_conducted_to_stair_landing1.png,Repairs_being_conducted_to_stair_landing2.png Public access stairs to launch area landing was in the state of being repaired at the time of inspection. Landing grade at below normal stair height | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Repairs_being_conducted_to_stair_landing2.png | file://x:/photopub/docs/0000000615/837deb6c-e083-44b0-870c-990f4325d7a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9b52142_a6c6_43b5_a015_575a15cb0930
AMOP-835471-2017 | AM-543494-2017 | 6/13/2017 12:29:01 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Missing_fencing_and_handrail1.png,Missing_fencing_and_handrail2.png Handrails and fence section missing on an overhead walkway. Unit was not in operation at the time of inspection. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Missing_fencing_and_handrail2.png | file://x:/photopub/docs/0000000615/f20cd90f-5ce6-4c45-9b53-1cd4399781ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bcb9b33_a852_4254_bc3c_ab2ad3bc384d
GAIN-855302-2017 | GA-552396-2017 | 7/25/2017 1:13:44 PM | ASSESS: GA: Final | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | #Summit_3.png Combustion air ducting not connected to outdoor air supply at time of assessment. Lack of combustion air could result in spilling of combustion products from the vent if the space was to experience a negative condition. Risk of carbon monoxide entering occupied space. Boiler not in service at time of assessment. | 3 | Mechanical Air/ventilation supply present, missing interlock | Summit_3.png | file://x:/photopub/docs/0000000636/ffe8963c-89e6-4f60-8bb8-8536c4e79f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1754b389_ea4b_4efa_9a22_0e6fe9209ed0
ELHE-828189-2017 | HE-541355-2017 | 6/1/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_faceplates1.png,Missing_faceplates2.png 15 amp, 120 volt general use receptacles and switches within a dwelling unit have missing cover plates. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_faceplates2.png | file://x:/photopub/docs/0000000612/d4a1ea58-6098-47b5-ac31-d55bf0961f27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce73e214_1b39_40f5_9d7f_e5399e45d925
ELHE-828189-2017 | HE-541355-2017 | 6/1/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_faceplates1.png,Missing_faceplates2.png 15 amp, 120 volt general use receptacles and switches within a dwelling unit have missing cover plates. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_faceplates1.png | file://x:/photopub/docs/0000000612/d4382a64-ab12-40e4-8aae-1401c964cd88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce73e214_1b39_40f5_9d7f_e5399e45d925
ELIN-825708-2017 | EL-353834-2016 | 5/30/2017 11:21:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #3_gang_supported_1_side_only2.png Electrical boxes must be properly secured to reduce risk of damage to equipment and to ensure a safe installation. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3_gang_supported_1_side_only2.png | file://x:/photopub/docs/0000000608/efe7b29a-78b7-4d48-9045-dde5dec85444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c64327f_6636_4f98_baac_4b6666138ea4
ELIN-826515-2017 | UW-540437-2017 | 5/31/2017 9:17:18 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #B1.png,B2.png,B3.png Undersized feeder cable of 2/0 ACWU supplying a 350 amp switch. This is a fire hazard as the cable is overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | B2.png | file://x:/photopub/docs/0000000608/f84c40e3-31c8-400c-bb6e-4371aedbb7b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed581900_6f1a_4c69_a034_0ff84f616dcd
ELIN-826959-2017 | EL-514310-2017 | 5/31/2017 8:02:52 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Feeder cable installed through bottom plate of wall with in 32mm of the face of the stud. This is a fire hazard as this cable could be hit be a dry wall screw. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | A3.png | file://x:/photopub/docs/0000000608/a51a1824-c793-4c83-986e-027ffdfa5951.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef6df7e6_2c54_4608_84c1_72d5b7c806ac
ELIN-826959-2017 | EL-514310-2017 | 5/31/2017 8:02:52 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Feeder cable installed through bottom plate of wall with in 32mm of the face of the stud. This is a fire hazard as this cable could be hit be a dry wall screw. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | A4.png | file://x:/photopub/docs/0000000608/0a0c4d4f-d9b5-419c-896f-046448ee57f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef6df7e6_2c54_4608_84c1_72d5b7c806ac
BPVOP-826298-2017 | BPV-0000489856-2017 | 5/30/2017 8:13:31 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve.png Upon assessment it is determined that machine mounted horizontal air receiver (1.8m long and 0.60m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000608/bdf460b8-6842-47cc-9c4a-57e656d04314.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20113c36_da96_4b8e_8cef_3f405435f2f6
ELIN-850123-2017 | UW-554273-2017 | 7/5/2017 7:48:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | #V1.png,V2.png,V3.png,V4.png 3C/#2 AWG Aluminum nonmetallic sheathed cable; 3C/ 4/0 ACWU; 3C/ 500 Kcmil ACWU leave a 1200 Amp gutter without additional over current protection as required. These conductors are exposed to currents much higher then their actual ratings. Nonmetallic sheathed cable is not an approved method of installation for this purpose, as no mechanical protection is provided to the conductors. This is a fire and shock hazard to individuals and the buildings that these conductors are located in. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | V3.png | file://x:/photopub/docs/0000000625/9e6f2dd0-fbf5-4aa0-9223-7c1976012b62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0289631_d0ba_40d1_b5bb_32a3bf866812
ELIN-840339-2017 | EL-530453-2017 | 6/21/2017 10:51:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #No_bonding.png Service raceway is not bonded. In the event of a high fault current issue, overcurrent protection may not be activated resulting in potential for shock or fire. | 0 | No Created Hazard Identified | No_bonding.png | file://x:/photopub/docs/0000000619/921ae98d-2d5a-434f-a188-755902e68a6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3e75aed_155c_4d7e_b14d_257148cbccb0
ELIN-864596-2017 | EL-528156-2017 | 7/25/2017 2:20:30 PM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #H.png DB2 installed above ground. This type of conduit is brittle and is only permitted in underground installations. This is a shock and fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | H.png | file://x:/photopub/docs/0000000635/818ef452-f17e-4775-b45d-fb5d7ef82147.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b54f41ff_cece_40e9_9897_8e6722697d0a
BPVOP-823837-2017 | BPV-163601-2014 | 5/29/2017 10:32:55 AM | ASSESS: BPV OP: Re-Certification Boiler | pdf | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Mountain Way Cleaners.pdf During the inspection of a HP Steam boiler with the MAWP of 150 psig 2 large pits were found(same as 2015). These pits can cause failure of the pressure boundary of the boiler shell. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Mountain Way Cleaners.pdf | file://x:/photopub/docs/0000000607/9cc2d9ea-fb92-49e7-8f3a-029eabb6b8f9.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b87537bc_fecf_4706_8715_be7dd8c38492
BPVOP-823837-2017 | BPV-163601-2014 | 5/29/2017 10:32:55 AM | ASSESS: BPV OP: Re-Certification Boiler | pdf | #asFound Photos of the pits done by contractor | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Mountain Way Cleaners.pdf During the inspection of a HP Steam boiler with the MAWP of 150 psig 2 large pits were found(same as 2015). These pits can cause failure of the pressure boundary of the boiler shell. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Mountain Way Cleaners.pdf | file://x:/photopub/docs/0000000607/beb5b18f-c41e-4d8a-a295-5bc5f381343d.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b87537bc_fecf_4706_8715_be7dd8c38492
GAHE-857521-2017 | HE-558610-2017 | 7/13/2017 7:27:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Riser in field with gas hose to house, gas hose cracked | GA062 | Piping/tubing hose installed in a corrosive/hazardous location | 4 | 4 | #Riser_installed_in_field_with_gas_hose1.png,Riser_installed_in_field_with_gas_hose2.png,Riser_installed_in_field_with_gas_hose3.png Found gas riser feeding dwelling installed in a field with 50 feet of gas hose winding through bushes/field and broken at both connection points. It was hazardous because of the environment and condition of the hose. It is possible it will leak or be damaged in one of many ways, then cause a situation that could lead to injury or death. | 4 | Piping/tubing hose installed in a corrosive/hazardous location | Riser_installed_in_field_with_gas_hose1.png | file://x:/photopub/docs/0000000630/9ece3869-465d-4665-bc13-8684a736512b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44b734ff_4013_46d5_8d99_5f8cee771921
GAHE-857521-2017 | HE-558610-2017 | 7/13/2017 7:27:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA062 | Piping/tubing hose installed in a corrosive/hazardous location | 4 | 4 | #Riser_installed_in_field_with_gas_hose1.png,Riser_installed_in_field_with_gas_hose2.png,Riser_installed_in_field_with_gas_hose3.png Found gas riser feeding dwelling installed in a field with 50 feet of gas hose winding through bushes/field and broken at both connection points. It was hazardous because of the environment and condition of the hose. It is possible it will leak or be damaged in one of many ways, then cause a situation that could lead to injury or death. | 4 | Piping/tubing hose installed in a corrosive/hazardous location | Riser_installed_in_field_with_gas_hose2.png | file://x:/photopub/docs/0000000630/c9d09604-bb67-44d3-a367-c2209da60c57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44b734ff_4013_46d5_8d99_5f8cee771921
GAWP-815016-2017 | GA-446190-2016 | 5/12/2017 1:12:24 PM | ASSESS: GA Work In Progress | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Copper_tubing_at_meter.png Copper tubing from meter to house is passing though an area that will have masonry. The tubing is not sleeved or wrapped. This will allow the copper tubing to be in contact with the masonry or grout which is corrosive to the tubing and could lead to a gas leak. | 2 | Physical protection of piping and tubing absent. | Copper_tubing_at_meter.png | file://x:/photopub/docs/0000000600/1c1fbcce-098e-4c24-92ff-43533bca2927.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2f7aa69_6faa_4b39_8a69_5f7d3ad10726
ELOP-840939-2017 | EL-397010-2016 | 6/20/2017 10:14:52 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #DDC_control_panels1.png,DDC_control_panels2.png,DDC_control_panels3.png The 15 amp 120 volt power to the control transformer located below the DDC control panel in the secure mechanical room is subject to accidental contact by persons due to the extra low voltage cable connected from power supply junction box to the DDC control junction box through the cover openings not allowing the covers to be closed, this can lead,to a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | DDC_control_panels2.png | file://x:/photopub/docs/0000000619/01b3d3a5-edea-4d70-99bb-ba1df1aef9dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddc74d6c_b5cc_4800_bf85_2bf96221ced3
ELOP-840939-2017 | EL-397010-2016 | 6/20/2017 10:14:52 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #DDC_control_panels1.png,DDC_control_panels2.png,DDC_control_panels3.png The 15 amp 120 volt power to the control transformer located below the DDC control panel in the secure mechanical room is subject to accidental contact by persons due to the extra low voltage cable connected from power supply junction box to the DDC control junction box through the cover openings not allowing the covers to be closed, this can lead,to a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | DDC_control_panels1.png | file://x:/photopub/docs/0000000619/45b323f2-8109-4bbb-858e-66da0732cb03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddc74d6c_b5cc_4800_bf85_2bf96221ced3
ELOP-840939-2017 | EL-397010-2016 | 6/20/2017 10:14:52 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #DDC_control_panels1.png,DDC_control_panels2.png,DDC_control_panels3.png The 15 amp 120 volt power to the control transformer located below the DDC control panel in the secure mechanical room is subject to accidental contact by persons due to the extra low voltage cable connected from power supply junction box to the DDC control junction box through the cover openings not allowing the covers to be closed, this can lead,to a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | DDC_control_panels3.png | file://x:/photopub/docs/0000000619/8127e4c5-a127-494e-a863-6de997f93374.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddc74d6c_b5cc_4800_bf85_2bf96221ced3
ELHE-850044-2017 | HE-553586-2017 | 7/5/2017 8:21:04 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Shock_hazard.png This assessment found that no panel cover is installed, creating a shock hazard to accidental contact. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Shock_hazard.png | file://x:/photopub/docs/0000000625/cc5754c8-bb4d-42e9-84db-19cb137b9415.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b92999d7_fbc6_4a1f_8c65_8f3dfe689b97
ELIN-862010-2017 | UW-561265-2017 | 7/25/2017 12:49:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #1039_MacDonald1.png,1039_MacDonald2.png,1039_MacDonald3.png Roof of house used support the overhead service. The roof was removed leaving the service conductors and conduit unsupported. The general contractor call BC Hydro to disconnect | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 1039_MacDonald1.png | file://x:/photopub/docs/0000000635/607771f4-9065-4690-957d-da9f2adb82ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1097452_8897_4b72_aa58_5c0c4f3164aa
ELIN-862010-2017 | UW-561265-2017 | 7/25/2017 12:49:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound After disconnect | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #1039_MacDonald1.png,1039_MacDonald2.png,1039_MacDonald3.png Roof of house used support the overhead service. The roof was removed leaving the service conductors and conduit unsupported. The general contractor call BC Hydro to disconnect | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 1039_MacDonald2.png | file://x:/photopub/docs/0000000635/b709ff18-04c8-42bb-89ec-fdaae97837dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1097452_8897_4b72_aa58_5c0c4f3164aa
ELIN-862010-2017 | UW-561265-2017 | 7/25/2017 12:49:56 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #1039_MacDonald1.png,1039_MacDonald2.png,1039_MacDonald3.png Roof of house used support the overhead service. The roof was removed leaving the service conductors and conduit unsupported. The general contractor call BC Hydro to disconnect | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 1039_MacDonald3.png | file://x:/photopub/docs/0000000635/c1b0c2f2-3891-4da5-9859-63f8a2291d5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1097452_8897_4b72_aa58_5c0c4f3164aa
EDRI-831023-2017 | ED-411045-2016 | 6/6/2017 | ASSESS: ED RI: Final | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | #Access_to_hoistway.png Balconies adjacent to the hoistway were not properly guarded, providing access for people to get within 30" of the moving counterweight. | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Access_to_hoistway.png | file://x:/photopub/docs/0000000613/ad76cc9d-8e40-4494-a95c-9e674081f5ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b350359e_ab5e_4b6e_b1cf_49221510932d
GAIN-738714-2017 | GA-418584-2016 | 6/8/2017 7:54:38 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Swing_joint.png | 2 | Physical protection of piping and tubing absent. | Swing_joint.png | file://x:/photopub/docs/0000000613/548944d6-7c92-4d5b-ac2a-4e9be3f6878a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c834766_8106_4cc4_9ba2_7168d2cb7634
BPVOP-833401-2017 | 2260128 | 6/8/2017 9:51:40 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | #Leaky_tube_.png I was notified by the maintenance contractor and during the inspection of a 1965 firetube boiler with MAWP 30 psig a leak in a tube caused by corrosion was found. This can cause an explosion as the water leaks in the combustion chamber. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | Leaky_tube_.png | file://x:/photopub/docs/0000000613/fc036193-cee6-4b4e-be64-234dde253d05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45dcc1c9_b52d_412d_a6a6_ab63e01b045b
ELIN-829228-2017 | EL-541971-2017 | 6/22/2017 9:33:42 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 3 | #Cabtire_permanently_use1.png,Cabtire_permanently_use2.png The 30 amp 120/240 volt flexible #6/#4 cabtire cable was used to sub-feed a loadcentre on the main floor as a permanent wiring method in walls containing thermal insulation. The cable is not approved to be used in permanent wiring methods and is rated as a thermal hazard | 4 | Conductors, Mis-use of flexible cords. | Cabtire_permanently_use2.png | file://x:/photopub/docs/0000000620/f213c894-58aa-4bb3-b459-c25399eb03cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fed9f5c_20b6_445b_a4fc_1ff133533cb4
ELIN-829228-2017 | EL-541971-2017 | 6/22/2017 9:33:42 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 3 | #Cabtire_permanently_use1.png,Cabtire_permanently_use2.png The 30 amp 120/240 volt flexible #6/#4 cabtire cable was used to sub-feed a loadcentre on the main floor as a permanent wiring method in walls containing thermal insulation. The cable is not approved to be used in permanent wiring methods and is rated as a thermal hazard | 4 | Conductors, Mis-use of flexible cords. | Cabtire_permanently_use1.png | file://x:/photopub/docs/0000000620/a4ae128a-0ba7-4f3a-9d21-25fe3d25ebf3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fed9f5c_20b6_445b_a4fc_1ff133533cb4
ELIN-812294-2017 | EL-462403-2016 | 5/16/2017 9:26:40 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Unused_opening_in_main_distribution.png 100 amp, 120/208 volt 3 phase main distribution panel installed in an area accessible to person with unused opening in panels outer box. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Unused_opening_in_main_distribution.png | file://x:/photopub/docs/0000000601/ca856f05-b4e1-4e10-952a-611322191c04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b915f34e_02b4_496d_8031_9817679e3017
ELIN-843365-2017 | EL-548375-2017 | 6/28/2017 | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 2 | #Generator_panel.png During a Silver Label inspection of a used mobile home, a generator panel installation was found. A breaker interlock kit had been installed on two breakers installed in a load centre to create a generator panel. The two breakers were of different ratings, a 125 amp breaker on the utility side, supplied from the main panel, and a 60 amp breaker on the generator side. The generator cord was rated for a 30 amp load. Along with a few 15 amp circuits from this generator panel was a two-pole 100 amp breaker feeding a shop with a full residential suite above. In the event of a power outage, the generator supply would be considerably less than the demand load without load-shedding taking place. Depending on the generator connected at the time of power outage, and its over current protection, this installation could result in equipment damage as well as thermal damage to parts of the installation. | 3 | Protection and control Loading of distribution equipment exceeded | Generator_panel.png | file://x:/photopub/docs/0000000625/7349f782-8051-48d1-bfbd-59679571a263.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b72f9399_2369_4d10_be41_f55c04ab41c0
ELIN-863340-2017 | EL-561575-2017 | 7/24/2017 2:17:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Isolation_screw_left_in_place_.png Sub distribution panel-neutral isolation screw has been left in place in panel. Isolation screw is required to be removed in order to have over-current equipment operate properly in the case of a fault. With the screw in place the over-current device may not sense that a fault has occurred and clear the fault. | 3 | Continuity Bonding; method for equipment is not adequate. | Isolation_screw_left_in_place_.png | file://x:/photopub/docs/0000000634/ecd66dab-b287-4a33-9237-87c1b0850929.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd8da98d_9f27_4485_aa1d_8bc6d97529c2
EDIN-812812-2017 | ED-495371-2017 | 5/12/2017 3:03:29 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED029 | Defect that is: • undetectable by maintenance program • Likely to progress | 3 | 3 | #Hydraulic_pipe_in_contact_with_the_tank.png A hydraulic elevator uses a piping system, hydraulic oil and pump to suspend the elevator cab. Hydraulic pipes are used as part of the piping system. Any leak or rupture of the piping system may cause the elevator to uncontrollably crash to the bottom. During an acceptance assessment it was found that a hydraulic pipe was in direct contact with a sharp edge of the tank. Every time the elevator is used the pressure in the piping causes this pipe to move. The movement of this pipe which is in direct contact with the tank poses a serious risk of perforation if left uncorrected. It was found the elevator contractor failed to recognize the improper installation. This 2 stop hydraulic elevator is located in a newly constructed residential building. | 3 | Defect that is: • undetectable by maintenance program • Likely to progress | Hydraulic_pipe_in_contact_with_the_tank.png | file://x:/photopub/docs/0000000601/b2473bc7-eea0-47cc-87d6-68c9198842f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99d8add2_0467_4dce_8f48_3773f638f370
ELIN-852697-2017 | EL-477796-2016 | 7/10/2017 12:19:13 PM | ASSESS: EL: Final | png | #asFound Energized conductors on gate controller. No covers in place. | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_conductors.png Final assessment of access control gate controllers. For gated residential complex. Two of four motorized gate controller's have been left with energized conductors exposed to accidental contact. Gate system is in use. Shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_conductors.png | file://x:/photopub/docs/0000000628/14fbe15d-3ba2-472a-bd5f-3bba32cd08b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__838a021c_9935_4ecf_bf4b_5c645695b6e9
ELIN-804694-2017 | EL-526586-2017 | 6/8/2017 1:06:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Sub_panel.png In a new multi-family dwelling construction site a 100 amp 120/240 volt temporary sub panel was found to be missing panel fillers. This could lead to a shock hazard situation. Picture attached. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Sub_panel.png | file://x:/photopub/docs/0000000614/32f23424-f8e6-42ac-9931-b71c278bd90d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7a970e3_d958_4cbb_ada7_902a4df1651d
ELOP-778130-2017 | 459 | 6/9/2017 2:13:39 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | #Transformers_typical1.png,Transformers_typical2.png,Transformers_typical3.png Existing installation utilizes grounding attached to various different locations but not interconnected or separate grounding conductors run back to the main systems grounding, this has the ability to create a potential difference during a fault and this is a shock hazard | 3 | Continuity Multiple grounded systems are not interconnected. | Transformers_typical2.png | file://x:/photopub/docs/0000000614/4346c509-cd78-4a62-a702-bc54618c2d58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32b3a009_d87d_4ab7_8f79_31e4c1f52979
ELOP-778130-2017 | 459 | 6/9/2017 2:13:39 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | #Transformers_typical1.png,Transformers_typical2.png,Transformers_typical3.png Existing installation utilizes grounding attached to various different locations but not interconnected or separate grounding conductors run back to the main systems grounding, this has the ability to create a potential difference during a fault and this is a shock hazard | 3 | Continuity Multiple grounded systems are not interconnected. | Transformers_typical3.png | file://x:/photopub/docs/0000000614/c74555c6-3055-4015-a10d-534fde4630ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32b3a009_d87d_4ab7_8f79_31e4c1f52979
ELIN-855036-2017 | EL-551165-2017 | 7/13/2017 11:32:42 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_conductor_at_main_service_terminated_to_enclosure_.png Grounding conductor has been terminated to enclosure. Grounding conductors are required to terminate to the identified conductor /neutral. In the case of a fault overcurrent protection in this case fusing, may not sense the fault and clear it. Risk of fire and shock to property and persons would be present. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_conductor_at_main_service_terminated_to_enclosure_.png | file://x:/photopub/docs/0000000630/ffa8b006-5746-42be-8d24-1474c9c81df8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73166dd7_829c_4337_bc9c_05528ea38e43
AMOP-858283-2017 | 3808312 | 7/17/2017 3:11:59 PM | ASSESS: AM OP: Periodic | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 | #Soil_against_wood_upright.png The wood structure components of a deck is in direct contact with organic soil. Risk of deterioration over long period. | 0 | No Created Hazard Identified | Soil_against_wood_upright.png | file://x:/photopub/docs/0000000632/b6d6f175-68cb-4bee-91ff-93b71c49da3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__409d07a5_7d92_4355_8526_6b9e0dd31843
AMOP-858282-2017 | 3977546 | 7/17/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Handrail_upright_pulling_off_of_deck.png Handrail upright has become partially detached from a deck. Lag screws partially pulled out. This likely reduces the structural integrity off the handrail | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Handrail_upright_pulling_off_of_deck.png | file://x:/photopub/docs/0000000632/5b5eaa7d-eb6a-4805-b931-fa545fe88a47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcb02bf3_d627_496c_b361_e520d286f9a4
AMOP-858289-2017 | 3977544 | 7/17/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Broken_and_missing_bracing_.png Certain sections of wood bracing of a raised landing deck were found to be broken or missing. (Likely due to snow creep over previous winter). Missing bracing would likely reduce the strength of the deck support structure. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Broken_and_missing_bracing_.png | file://x:/photopub/docs/0000000632/345896bd-949e-4ad0-8f81-89674eae8874.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edb415e7_cd00_4df6_b4c8_b5752b4bf25c
ELOP-811597-2017 | 4952 | 6/8/2017 4:10:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Unapproved_control_cabinet_for_truck_hopper_conveyor1.png,Unapproved_control_cabinet_for_truck_hopper_conveyor2.png,Unapproved_control_cabinet_for_truck_hopper_conveyor3.png,Unapproved_control_cabinet_for_truck_hopper_conveyor4.png,Unapproved_control_cabinet_for_truck_hopper_conveyor5.png Electrical control cabinets for industrial equipment are required to be approved and labeled and are required to have enclosures that are suitable for use in the environments they are used in. This installation at an aggregate barge loading facility has a 200A 600V 3 phase control cabinet for a conveyor system that is not approved and does not have an enclosure that is suitable for the wet, dusty, and corrosive environment that it is installed in. This is a shock, arc flash, and fire hazard if the equipment fails because it was not constructed properly or evaluated by a certification agency and is installed in an environment that damages the equipment causing an electrical fault. | 3 | General Equipment is not approved for the specific use | Unapproved_control_cabinet_for_truck_hopper_conveyor1.png | file://x:/photopub/docs/0000000614/71201ea7-0cca-44a4-870d-57955c131cf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0907213d_cf8e_4fc2_b001_0501e6c2af60
ELOP-811597-2017 | 4952 | 6/8/2017 4:10:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Unapproved_control_cabinet_for_truck_hopper_conveyor1.png,Unapproved_control_cabinet_for_truck_hopper_conveyor2.png,Unapproved_control_cabinet_for_truck_hopper_conveyor3.png,Unapproved_control_cabinet_for_truck_hopper_conveyor4.png,Unapproved_control_cabinet_for_truck_hopper_conveyor5.png Electrical control cabinets for industrial equipment are required to be approved and labeled and are required to have enclosures that are suitable for use in the environments they are used in. This installation at an aggregate barge loading facility has a 200A 600V 3 phase control cabinet for a conveyor system that is not approved and does not have an enclosure that is suitable for the wet, dusty, and corrosive environment that it is installed in. This is a shock, arc flash, and fire hazard if the equipment fails because it was not constructed properly or evaluated by a certification agency and is installed in an environment that damages the equipment causing an electrical fault. | 3 | General Equipment is not approved for the specific use | Unapproved_control_cabinet_for_truck_hopper_conveyor3.png | file://x:/photopub/docs/0000000614/c0058160-be12-400b-b202-111072e6d2f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0907213d_cf8e_4fc2_b001_0501e6c2af60
ELIN-826180-2017 | EL-517009-2017 | 6/7/2017 12:16:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png See checklist | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Hazard2.png | file://x:/photopub/docs/0000000612/7eb8ef81-72b2-41dd-8dfe-9b826d4449ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a1c4a6_ac3d_468f_aaaa_70f46da66bdc
ELIN-826180-2017 | EL-517009-2017 | 6/7/2017 12:16:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png See checklist | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Hazard3.png | file://x:/photopub/docs/0000000612/408a80ff-20dc-4a7a-ba99-aca3e5c25130.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a1c4a6_ac3d_468f_aaaa_70f46da66bdc
ELIN-826180-2017 | EL-517009-2017 | 6/7/2017 12:16:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png See checklist | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Hazard4.png | file://x:/photopub/docs/0000000612/ef659fe5-0148-4afc-a825-fa7bf2fcda91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a1c4a6_ac3d_468f_aaaa_70f46da66bdc
ELIN-826180-2017 | EL-517009-2017 | 6/7/2017 12:16:44 PM | ASSESS: EL: Service Connection | png | #asFound No roof over electrical equipment, location of meter in not accessible | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png See checklist | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Hazard1.png | file://x:/photopub/docs/0000000612/b2fe8d5a-b721-49f8-bc04-abe49b5bd6bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a1c4a6_ac3d_468f_aaaa_70f46da66bdc
ELIN-826180-2017 | EL-517009-2017 | 6/7/2017 12:16:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png See checklist | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Hazard5.png | file://x:/photopub/docs/0000000612/e911cd8d-ccdd-4521-b580-7fe7326f8520.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9a1c4a6_ac3d_468f_aaaa_70f46da66bdc
BPVIN-840613-2017 | UW-548632-2017 | 6/19/2017 5:03:34 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_shut_down_switch.png,On_back_wall.png Existing boiler shut off switch is located behind boiler on wall. In an emergency safe access to the shut down switch is needed to avoid injury if fire or flame is coming from the boiler. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_shut_down_switch.png | file://x:/photopub/docs/0000000618/65dc003e-810c-428e-a6a3-e18a07381fd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c1a55f5_07c4_4aee_ac93_629554deeb0f
BPVIN-840613-2017 | UW-548632-2017 | 6/19/2017 5:03:34 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_shut_down_switch.png,On_back_wall.png Existing boiler shut off switch is located behind boiler on wall. In an emergency safe access to the shut down switch is needed to avoid injury if fire or flame is coming from the boiler. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | On_back_wall.png | file://x:/photopub/docs/0000000618/cd039b76-ba19-4553-93a6-3b28f48e2c82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c1a55f5_07c4_4aee_ac93_629554deeb0f
BPVOP-850315-2017 | 2289519 | 6/8/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound Psv1 | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Psvs.png,Safety_valves-.png All pressure relief devices require periodic inspection, testing and service. Upon assessment of a evaporator with a maximum allowable working pressure of 225 psig, it was determined there was no records of service or replacement for the pressure relief devices. Potential exists for a pressure relief device not functioning during a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Psvs.png | file://x:/photopub/docs/0000000625/6fd400a6-38bb-4e22-a7fe-631374d3cf2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__737fb9a3_5991_4050_a236_f198b2d97e71
BPVOP-850322-2017 | 2289518 | 6/8/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Psv_s.png,Safety_valves.png All pressure relief devices require periodic inspection, testing and service. Upon assessment of a condenser with a maximum allowable working pressure of 225 psig, it was determined there was no records of service or replacement for the pressure relief devices. Potential exists for a pressure relief device not functioning during a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Psv_s.png | file://x:/photopub/docs/0000000625/7a97ab03-6a87-404e-9ccf-f0deb8f8e515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fd36b9a_f7f4_4de4_8bab_eb4095e9b4b5
ELIN-808921-2017 | EL-529514-2017 | 5/16/2017 7:31:47 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Protection_required_for_plugs.png This assessment found temporary plugs are to be protected by ground fault protection to avoid a shock hazard during construction. | 3 | Conductors Equipment is not approved for the specific use. | Protection_required_for_plugs.png | file://x:/photopub/docs/0000000601/2d8b28ed-a0ff-4ce0-8761-450fe6181294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84cb5c45_fcaf_4e45_82f4_53038eee6292
ELIN-813192-2017 | EL-497350-2017 | 5/16/2017 7:44:13 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Overheating_potential.png This assessment found electrical cable proximity to heating ducts without protection could cause cable to overheat and the potential for shock and fire hazard exists. | 3 | Conductors Equipment is not approved for the specific use. | Overheating_potential.png | file://x:/photopub/docs/0000000601/1ab82ba2-fc7f-4069-b1fc-4c608534ecb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7365491f_0ac7_4856_b3a2_01d20a7e599f
GAIN-821397-2017 | GA-509003-2017 | 5/26/2017 11:21:00 AM | ASSESS: GA: Final | JPG | #asFound Non-compliant regulator vent termination. | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #IMG_0378.JPG While assessing the installation of a water heater I found the regulator relief vent serving the unit was located too close to the mechanical combustion air intake of the water heater. Should the unit be firing and the regulator relieve, raw gas could be drawn into the combustion chamber over firing the unit. This could lead to an explosion or fire. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | IMG_0378.JPG | file://x:/photopub/docs/0000000606/8c750d8c-2cbd-4ac9-afcc-c265bf6826d0.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1b54c7c_bbf8_4ad3_bb76_1ca21c672899
BPVIN-838950-2017 | UW-547958-2017 | 6/13/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Relief_valve_data_tag2.png This boiler safety relief valve is the original valve, no service records, valve shall be changed or serviced at the next boiler servicing. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve_data_tag2.png | file://x:/photopub/docs/0000000617/13c049b2-1068-49d5-84ac-38ae6365a3bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4967319e_eece_4081_9b7b_fb5f64914dc9
ELIN-826652-2017 | EL-540511-2017 | 6/1/2017 4:23:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Wood_enclosure_not_adequate1.png,Wood_enclosure_not_adequate2.png,Wood_enclosure_not_adequate3.png,Wood_enclosure_not_adequate4.png,Wood_enclosure_not_adequate5.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation for a new house has a 200A 120/240V service installed inside of a wooden enclosure for use during construction of the house. The enclosure is not sealed at the top and the door can not be readily opened and closed because of the way it was constructed. The enclosure is not preventing water from entering the wooden enclosure and getting the electrical panel wet. Left uncorrected this is a shock and a fire hazard if the equipment gets wet, damaged, and fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Wood_enclosure_not_adequate3.png | file://x:/photopub/docs/0000000609/8d8758b6-1112-48d0-974d-953b2074096c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d9915f_2fba_450c_a27a_8b87955943a9
GAIN-830412-2017 | GA-526687-2017 | 6/16/2017 9:43:12 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Denali_3.png Uncapped auxiliary condensate drain connected to blower housing. Risk that products of combustion could be vented from this connection if the condensate trap were to dry out. Risk of carbon monoxide entering occupied space. No evidence of products of combustion noted from drain connection at time of assessment. | 3 | Appliance not installed according to installation instructions | Denali_3.png | file://x:/photopub/docs/0000000617/8b2b7791-6190-46af-b4ff-5cd8cdf332e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d4fc518_67eb_4cde_95bd_368427d8f1dc
BPVIN-739628-2017 | BPV-369373-2016 | 6/21/2017 2:46:49 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound Not lockable | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect.png,No_disconnects.png Upon assessment of a hot water boiler with a maximum working pressure of 80 psig and a maximum working temperature of 200 Fahrenheit, it was determined there was no lockable disconnect. This creates risk to personnel and equipment. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnect.png | file://x:/photopub/docs/0000000620/9b90e8fe-352c-46ed-b8ee-959c7548204d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a156557a_bb96_4750_9aa5_2b1a2ba4ffed
EDIN-846315-2017 | ED-480972-2016 | 6/27/2017 4:38:45 PM | ASSESS: ED IN: Construction Use | png | #asFound No permanent path or handrails provided. Parapet at the room level does not meet code requirements of 42 inches | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Machine_room_access.png Fall hazard present as soon as person exits the stairwell to the roof top to gain access to the machine room. Low parapet and lack of handrails and without a substantial walkway not less than 24 inches wide can cause a person sustain injury or to fall off the roof. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Machine_room_access.png | file://x:/photopub/docs/0000000622/5db1004a-ef90-477c-9938-4ae71b80609a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2f49e1e_78ed_45b5_a41c_8754aa2ae8cf
ELOP-778130-2017 | 459 | 6/9/2017 2:13:39 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | #Transformers_typical1.png,Transformers_typical2.png,Transformers_typical3.png Existing installation utilizes grounding attached to various different locations but not interconnected or separate grounding conductors run back to the main systems grounding, this has the ability to create a potential difference during a fault and this is a shock hazard | 3 | Continuity Multiple grounded systems are not interconnected. | Transformers_typical1.png | file://x:/photopub/docs/0000000614/bd6a328b-0069-49b8-8a46-67022fe8ca90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32b3a009_d87d_4ab7_8f79_31e4c1f52979
BPVIN-739620-2017 | BPV-359906-2016 | 5/15/2017 11:09:55 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound Exp. tank PSV horiz. | BP005 | 1.0.1 Temp/Pressure ratings not met - Manufacturer's Data Report deficiencies | 1 | 1 | #Exp__Tk_psv.png | 1 | 1.0.1 Temp/Pressure ratings not met - Manufacturer's Data Report deficiencies | Exp__Tk_psv.png | file://x:/photopub/docs/0000000603/20b3cc43-7363-465b-9879-9416bc5093b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a99598e1_f6ee_4340_9f18_7181c815b0ff
ELOP-811597-2017 | 4952 | 6/8/2017 4:10:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Unapproved_control_cabinet_for_truck_hopper_conveyor1.png,Unapproved_control_cabinet_for_truck_hopper_conveyor2.png,Unapproved_control_cabinet_for_truck_hopper_conveyor3.png,Unapproved_control_cabinet_for_truck_hopper_conveyor4.png,Unapproved_control_cabinet_for_truck_hopper_conveyor5.png Electrical control cabinets for industrial equipment are required to be approved and labeled and are required to have enclosures that are suitable for use in the environments they are used in. This installation at an aggregate barge loading facility has a 200A 600V 3 phase control cabinet for a conveyor system that is not approved and does not have an enclosure that is suitable for the wet, dusty, and corrosive environment that it is installed in. This is a shock, arc flash, and fire hazard if the equipment fails because it was not constructed properly or evaluated by a certification agency and is installed in an environment that damages the equipment causing an electrical fault. | 3 | General Equipment is not approved for the specific use | Unapproved_control_cabinet_for_truck_hopper_conveyor2.png | file://x:/photopub/docs/0000000614/8df4b2e3-5bcc-4d89-927a-ea80d4dde676.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0907213d_cf8e_4fc2_b001_0501e6c2af60
ELOP-811597-2017 | 4952 | 6/8/2017 4:10:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Unapproved_control_cabinet_for_truck_hopper_conveyor1.png,Unapproved_control_cabinet_for_truck_hopper_conveyor2.png,Unapproved_control_cabinet_for_truck_hopper_conveyor3.png,Unapproved_control_cabinet_for_truck_hopper_conveyor4.png,Unapproved_control_cabinet_for_truck_hopper_conveyor5.png Electrical control cabinets for industrial equipment are required to be approved and labeled and are required to have enclosures that are suitable for use in the environments they are used in. This installation at an aggregate barge loading facility has a 200A 600V 3 phase control cabinet for a conveyor system that is not approved and does not have an enclosure that is suitable for the wet, dusty, and corrosive environment that it is installed in. This is a shock, arc flash, and fire hazard if the equipment fails because it was not constructed properly or evaluated by a certification agency and is installed in an environment that damages the equipment causing an electrical fault. | 3 | General Equipment is not approved for the specific use | Unapproved_control_cabinet_for_truck_hopper_conveyor4.png | file://x:/photopub/docs/0000000614/4a0af55f-a8c9-47c5-a20b-5afcad451d6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0907213d_cf8e_4fc2_b001_0501e6c2af60
ELIN-860034-2017 | UW-559705-2017 | 7/18/2017 10:44:37 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #_No_support_or_anti_abrasion.png Cables feeding 120 volt at 15 amps are fed to receptacles mounted on a dock at a marina. The cables are subject to movement as no accommodation for support of the cables or for protecting against anti abrasion have been provided. The equipment can become energized leading to injury to persons or damage to property | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | _No_support_or_anti_abrasion.png | file://x:/photopub/docs/0000000632/ec465200-2018-43e4-8e5e-3fbf902d98e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc52bbad_e9a7_44e0_a9f6_9786f8ca90a2
ELIN-826652-2017 | EL-540511-2017 | 6/1/2017 4:23:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Wood_enclosure_not_adequate1.png,Wood_enclosure_not_adequate2.png,Wood_enclosure_not_adequate3.png,Wood_enclosure_not_adequate4.png,Wood_enclosure_not_adequate5.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation for a new house has a 200A 120/240V service installed inside of a wooden enclosure for use during construction of the house. The enclosure is not sealed at the top and the door can not be readily opened and closed because of the way it was constructed. The enclosure is not preventing water from entering the wooden enclosure and getting the electrical panel wet. Left uncorrected this is a shock and a fire hazard if the equipment gets wet, damaged, and fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Wood_enclosure_not_adequate1.png | file://x:/photopub/docs/0000000609/b4975d93-210b-4513-b2ce-007e800bb4a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d9915f_2fba_450c_a27a_8b87955943a9
ELIN-826652-2017 | EL-540511-2017 | 6/1/2017 4:23:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Wood_enclosure_not_adequate1.png,Wood_enclosure_not_adequate2.png,Wood_enclosure_not_adequate3.png,Wood_enclosure_not_adequate4.png,Wood_enclosure_not_adequate5.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation for a new house has a 200A 120/240V service installed inside of a wooden enclosure for use during construction of the house. The enclosure is not sealed at the top and the door can not be readily opened and closed because of the way it was constructed. The enclosure is not preventing water from entering the wooden enclosure and getting the electrical panel wet. Left uncorrected this is a shock and a fire hazard if the equipment gets wet, damaged, and fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Wood_enclosure_not_adequate4.png | file://x:/photopub/docs/0000000609/7ce2722f-382f-433b-898d-89fa102c6bfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d9915f_2fba_450c_a27a_8b87955943a9
ELIN-826652-2017 | EL-540511-2017 | 6/1/2017 4:23:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Wood_enclosure_not_adequate1.png,Wood_enclosure_not_adequate2.png,Wood_enclosure_not_adequate3.png,Wood_enclosure_not_adequate4.png,Wood_enclosure_not_adequate5.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation for a new house has a 200A 120/240V service installed inside of a wooden enclosure for use during construction of the house. The enclosure is not sealed at the top and the door can not be readily opened and closed because of the way it was constructed. The enclosure is not preventing water from entering the wooden enclosure and getting the electrical panel wet. Left uncorrected this is a shock and a fire hazard if the equipment gets wet, damaged, and fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Wood_enclosure_not_adequate2.png | file://x:/photopub/docs/0000000609/6224ad94-2751-4c1b-adfa-6adebb8b2e2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d9915f_2fba_450c_a27a_8b87955943a9
ELIN-826652-2017 | EL-540511-2017 | 6/1/2017 4:23:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Wood_enclosure_not_adequate1.png,Wood_enclosure_not_adequate2.png,Wood_enclosure_not_adequate3.png,Wood_enclosure_not_adequate4.png,Wood_enclosure_not_adequate5.png Electrical equipment installed outdoors in a location where it is subject to the weather is required to be adequately protected from the weather either by being installed in an approved weather proof cabinet or being approved for installation in an outdoor location. This is required to protect the equipment from getting wet which can damage and deteriorate the equipment. This installation for a new house has a 200A 120/240V service installed inside of a wooden enclosure for use during construction of the house. The enclosure is not sealed at the top and the door can not be readily opened and closed because of the way it was constructed. The enclosure is not preventing water from entering the wooden enclosure and getting the electrical panel wet. Left uncorrected this is a shock and a fire hazard if the equipment gets wet, damaged, and fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Wood_enclosure_not_adequate5.png | file://x:/photopub/docs/0000000609/4785b01c-da53-4bfd-bbae-28121b5dfade.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d9915f_2fba_450c_a27a_8b87955943a9
ELIN-831336-2017 | EL-539474-2017 | 6/13/2017 3:30:10 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Hood_fan_.png - Hood fan installed above range without cover to wiring junction box. Live conductors could easily being contacted with use of equipment causing possible shock to general home owner. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Hood_fan_.png | file://x:/photopub/docs/0000000615/dde0d409-c51a-45ae-879c-607d00096cad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4400481_d47d_48bf_ba01_2111e9c2e5d9
ELIN-845347-2017 | EL-540503-2017 | 6/27/2017 12:42:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Main_Panel_Protection1.png,Main_Panel_Protection2.png A new 200 amp 120/240 volt electrical panel has been mounted on a new home under construction, the home has no roof yet built and the panel does not have any finished protection provided from the weather or mechanical damage. This poses potential mechanical and electrical damage to the panel and components. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_Panel_Protection2.png | file://x:/photopub/docs/0000000622/b4886219-7b46-4dca-b903-2af796a21673.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ddd585b_c085_4293_b80b_272e295afe28
ELIN-845347-2017 | EL-540503-2017 | 6/27/2017 12:42:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Main_Panel_Protection1.png,Main_Panel_Protection2.png A new 200 amp 120/240 volt electrical panel has been mounted on a new home under construction, the home has no roof yet built and the panel does not have any finished protection provided from the weather or mechanical damage. This poses potential mechanical and electrical damage to the panel and components. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_Panel_Protection1.png | file://x:/photopub/docs/0000000622/59db425b-711a-46dd-8bb9-55819080335a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ddd585b_c085_4293_b80b_272e295afe28
BPVOP-859111-2017 | 3493717 | 7/17/2017 9:37:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Water_tubes_1.png,Water_tubes_2.png,Water_tubes_3.png Water tube boilers are typically constructed of drums,headers and tubes, water tube boilers are used to produce steam or hot water in large quantities.I found a water tube sagging on a 150psi steam boiler due to overheating. This may lead to failure of the water tube pipe due to excessive temperatures and stresses. | 0 | No Created Hazard Identified | Water_tubes_2.png | file://x:/photopub/docs/0000000632/ecd5d601-6c5e-48ca-8b74-ed68f0f5d1fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6635777b_4ac7_4b9b_aa5b_16ddf10bdde3
BPVOP-859111-2017 | 3493717 | 7/17/2017 9:37:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Water_tubes_1.png,Water_tubes_2.png,Water_tubes_3.png Water tube boilers are typically constructed of drums,headers and tubes, water tube boilers are used to produce steam or hot water in large quantities.I found a water tube sagging on a 150psi steam boiler due to overheating. This may lead to failure of the water tube pipe due to excessive temperatures and stresses. | 0 | No Created Hazard Identified | Water_tubes_1.png | file://x:/photopub/docs/0000000632/abbbaa8a-9bdd-442e-a176-c917d64e473a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6635777b_4ac7_4b9b_aa5b_16ddf10bdde3
BPVOP-859111-2017 | 3493717 | 7/17/2017 9:37:53 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Water_tubes_1.png,Water_tubes_2.png,Water_tubes_3.png Water tube boilers are typically constructed of drums,headers and tubes, water tube boilers are used to produce steam or hot water in large quantities.I found a water tube sagging on a 150psi steam boiler due to overheating. This may lead to failure of the water tube pipe due to excessive temperatures and stresses. | 0 | No Created Hazard Identified | Water_tubes_3.png | file://x:/photopub/docs/0000000632/b608b379-529c-45e1-abf8-147a06ebb06a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6635777b_4ac7_4b9b_aa5b_16ddf10bdde3
ELOP-811597-2017 | 4952 | 6/8/2017 4:10:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Unapproved_control_cabinet_for_truck_hopper_conveyor1.png,Unapproved_control_cabinet_for_truck_hopper_conveyor2.png,Unapproved_control_cabinet_for_truck_hopper_conveyor3.png,Unapproved_control_cabinet_for_truck_hopper_conveyor4.png,Unapproved_control_cabinet_for_truck_hopper_conveyor5.png Electrical control cabinets for industrial equipment are required to be approved and labeled and are required to have enclosures that are suitable for use in the environments they are used in. This installation at an aggregate barge loading facility has a 200A 600V 3 phase control cabinet for a conveyor system that is not approved and does not have an enclosure that is suitable for the wet, dusty, and corrosive environment that it is installed in. This is a shock, arc flash, and fire hazard if the equipment fails because it was not constructed properly or evaluated by a certification agency and is installed in an environment that damages the equipment causing an electrical fault. | 3 | General Equipment is not approved for the specific use | Unapproved_control_cabinet_for_truck_hopper_conveyor5.png | file://x:/photopub/docs/0000000614/2553f3c7-4b3e-41c2-8d30-10bc5fa91abb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0907213d_cf8e_4fc2_b001_0501e6c2af60
GAUP-820168-2017 | UW-536681-2017 | 5/24/2017 9:34:14 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA062 | Piping/tubing hose installed in a corrosive/hazardous location | 4 | 4 | #Range.png Flexible rubber appliance connector installed within 9 inches from the side of the burner. Heat given off from burner flame could potentially exceed max temperature of flex connector (150 Degree F) which could cause a failure of the product and create a high fire hazard. | 4 | Piping/tubing hose installed in a corrosive/hazardous location | Range.png | file://x:/photopub/docs/0000000604/b1d33d5b-8be9-434c-a077-8530c261dbd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc744368_ef26_4e22_aec9_01bcda4b524c
ELIN-839176-2017 | EL-548097-2017 | 6/19/2017 10:36:10 AM | ASSESS: EL: Service Connection | png | #asFound Cover plate is not marked as extra duty. | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Cover_plate.png Service connection for a new pole mounted temporary construction service. Two duplex receptacles have been installed to provide construction power for this temporary service. The cover plate used is not marked as a heavy duty type cover plate and therefore, is subject to mechanical damage. If this damage occurs then the receptacles being used to supply construction power will be open to the weather. Therefore, they will be a shock hazard in wet weather. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Cover_plate.png | file://x:/photopub/docs/0000000618/6197a6b1-b2a6-46c2-87d3-0afa662e037b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9ad286a_8293_44ec_a647_ee3c66958905
ELHE-837327-2017 | HE-547096-2017 | 6/14/2017 2:18:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Signage1.png,Signage2.png,Signage3.png Armoured cable run in a location exposed to weather and mechanical damage and with the armour removed creating a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Signage3.png | file://x:/photopub/docs/0000000616/5221ca42-bb16-4c7a-a11b-6710f9e45dbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3892a01e_5bb2_4c6b_ab2b_593857877834
ELHE-837327-2017 | HE-547096-2017 | 6/14/2017 2:18:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Signage1.png,Signage2.png,Signage3.png Armoured cable run in a location exposed to weather and mechanical damage and with the armour removed creating a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Signage2.png | file://x:/photopub/docs/0000000616/199f6e84-403a-413b-859b-18e3896d01d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3892a01e_5bb2_4c6b_ab2b_593857877834
ELHE-837327-2017 | HE-547096-2017 | 6/14/2017 2:18:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Signage1.png,Signage2.png,Signage3.png Armoured cable run in a location exposed to weather and mechanical damage and with the armour removed creating a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Signage1.png | file://x:/photopub/docs/0000000616/e3389d20-e4d0-4747-a505-fc9f9a4aa8da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3892a01e_5bb2_4c6b_ab2b_593857877834
ELIN-835907-2017 | EL-530080-2017 | 6/14/2017 11:17:14 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Exterior_receptacle.png In a new single family dwelling construction a 15 amp 120 volt energized exterior receptacle was found to not include ground fault protection or a weatherproof cover, This receptacle is being used for construction purposes. Energized terminals are exposed to accidental contact and this could lead to a shock hazard situation. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exterior_receptacle.png | file://x:/photopub/docs/0000000616/1fd151b4-25fb-4aac-932d-ab37a2052eea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__714b4e46_230d_4135_9c48_9d1e4a215f4c
ELIN-835168-2017 | EL-513197-2017 | 6/14/2017 1:04:51 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png In a new residential dwelling construction 15/20 amp 120 volt energized receptacles and switches were found to have no covers installed. This could lead to a shock hazard situation. Pictures attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates1.png | file://x:/photopub/docs/0000000616/efdfc072-ccba-49f0-9f2b-8df334b8ecdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddd3892c_ebb8_4733_b559_8c20729b77cb
ELIN-835168-2017 | EL-513197-2017 | 6/14/2017 1:04:51 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png In a new residential dwelling construction 15/20 amp 120 volt energized receptacles and switches were found to have no covers installed. This could lead to a shock hazard situation. Pictures attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates3.png | file://x:/photopub/docs/0000000616/c5a39a4c-dd61-4c3d-9662-39bd05e69a22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddd3892c_ebb8_4733_b559_8c20729b77cb
ELIN-835168-2017 | EL-513197-2017 | 6/14/2017 1:04:51 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png In a new residential dwelling construction 15/20 amp 120 volt energized receptacles and switches were found to have no covers installed. This could lead to a shock hazard situation. Pictures attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates4.png | file://x:/photopub/docs/0000000616/f2e34cc3-25a8-4cef-88b9-74a3baf0a769.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddd3892c_ebb8_4733_b559_8c20729b77cb
ELIN-833606-2017 | EL-531709-2017 | 6/14/2017 9:17:19 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Pan_box_on_exterior_lights.png In a new residential single dwelling installation 15 amp 120 volt exterior lights were found to have the improper box installed for the required box fill. This could lead to the equipment being damaged. Picture attached. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Pan_box_on_exterior_lights.png | file://x:/photopub/docs/0000000616/5ff183c5-6ac0-4b87-b519-fee4aa2a4591.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb872de5_8af5_476a_82bb_cf2aea45aa56
ELIN-835168-2017 | EL-513197-2017 | 6/14/2017 1:04:51 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png In a new residential dwelling construction 15/20 amp 120 volt energized receptacles and switches were found to have no covers installed. This could lead to a shock hazard situation. Pictures attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates2.png | file://x:/photopub/docs/0000000616/59c8f4ef-079d-45f8-8d05-5cc737b5b245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddd3892c_ebb8_4733_b559_8c20729b77cb
ELIN-818135-2017 | 5235095 | 5/19/2017 11:05:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Receptacles_along_wall_line1.png,Receptacles_along_wall_line2.png In a dwelling, the BC Electrical Code requires there be no point measured along the floor line of any usable wall space more than 1.8 m horizontally from a receptacle. This is to ensure that there are adequate number of receptacles to reduce the hazardous use of extension cords and ensure the safe use of electrical appliances. During an electrical assessment for an addition to an existing single family dwelling, several receptacles where found to be greater than 1.8m from any point of useable wall space. Once the building is complete, the lack of receptacles could cause the permanent use of extension cords which could create a potential fire hazard to persons and property inside this dwelling. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacles_along_wall_line1.png | file://x:/photopub/docs/0000000603/82b71332-d6c1-41c9-a8bb-ce3f7d4748dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93fb28f5_54dd_4964_818d_47822f7807cf
ELIN-818135-2017 | 5235095 | 5/19/2017 11:05:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Receptacles_along_wall_line1.png,Receptacles_along_wall_line2.png In a dwelling, the BC Electrical Code requires there be no point measured along the floor line of any usable wall space more than 1.8 m horizontally from a receptacle. This is to ensure that there are adequate number of receptacles to reduce the hazardous use of extension cords and ensure the safe use of electrical appliances. During an electrical assessment for an addition to an existing single family dwelling, several receptacles where found to be greater than 1.8m from any point of useable wall space. Once the building is complete, the lack of receptacles could cause the permanent use of extension cords which could create a potential fire hazard to persons and property inside this dwelling. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacles_along_wall_line2.png | file://x:/photopub/docs/0000000603/aff728aa-c3e1-402c-bbbc-6680fd89bec9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93fb28f5_54dd_4964_818d_47822f7807cf
ELIN-826452-2017 | EL-540378-2017 | 6/2/2017 1:01:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Loadcenter.png There are unused openings in the load centre that are not filled. These could create a shock hazard. The area has a number of small rodents that could enter the panel and become a fire hazard when the bus is shorted. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Loadcenter.png | file://x:/photopub/docs/0000000610/9a22a107-d62a-44e9-ae4c-703b5a4e52a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__584919c6_a692_474b_bedb_a39b3b80ddfb
ELIN-829954-2017 | EL-536988-2017 | 6/5/2017 10:34:05 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 3 | #Hot_and_ground_reversed.png 15 amp 120 volt kitchen counter and heat trace receptacles have the hot conductor reversed with ground . This can cause injury to persons or damage to property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Hot_and_ground_reversed.png | file://x:/photopub/docs/0000000611/73e83fa8-c916-4f44-9e04-9252939fa387.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e4df61d_0079_48e8_a127_9b7b1131aeef
ELHE-831100-2017 | HE-543219-2017 | 6/6/2017 11:11:01 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Energized_receptacle_with_no_cover.png Energized 120v 15 amp existing exterior receptacles were not provided with approved covers, increasing the likelihood of accidental contact with energized electrical terminals and subsequent exposure to electrical shock | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacle_with_no_cover.png | file://x:/photopub/docs/0000000611/ca4229ba-bae8-4427-bfba-e5f8126d5a1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b6244f8_055a_466b_9234_eb7e28351927
ELIN-819812-2017 | UW-536428-2017 | 5/18/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound Broken receptacle without weatherproof cover. | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Outside_receptacle.png Outside receptacle does not have a weatherproof cover and is broken. This could lead to a potential shock hazard if accidentally contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outside_receptacle.png | file://x:/photopub/docs/0000000604/6dc6dcc8-1dff-4a77-9756-46dfe9ded825.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ba2b015_6cc7_4cfc_82bf_d9e1a70cebed
ELIN-860805-2017 | EL-554949-2017 | 7/20/2017 12:34:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Lots_of__lots_of_service_cable_inside_building.png A new residence is being constructed with a 200 amp 240 V service. The service cable conductors are inside of the building in excess of 1.5 m. Damage to this cable can occur during or after construction and can lead to property damage or injury to persons as it lacks effective overcurrent protection | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Lots_of__lots_of_service_cable_inside_building.png | file://x:/photopub/docs/0000000633/ad0f0227-4049-445c-a453-26900f6fe3eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0396782a_a88f_4a14_b416_90c781ccb8b5
ELIN-861177-2017 | EL-520229-2017 | 7/20/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #PVC_under_meter1.png,PVC_under_meter2.png Provisions must made for underground raceways to allow for movement from ground settlement or frost. Expansion and contraction of the raceway must also be considered when exposed to heat or cold. This requirement prevents damage to the electrical installation due to movement of the building, raceway, or ground. In this installation for new underground electrical service to a new building, the 3â€PVC conduit to the pole mount, electrical meter was installed without an expansion joint. Ground movement by settlement or frost and expansion or contraction of the PVC conduit from heat or cold, has the potential to damage the conduit, meter base and conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_under_meter1.png | file://x:/photopub/docs/0000000634/c826d484-ffd8-4c73-be08-78d7165c52f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac6f87c_7d15_4500_a822_2a55ba0b674c
ELIN-861177-2017 | EL-520229-2017 | 7/20/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #PVC_under_meter1.png,PVC_under_meter2.png Provisions must made for underground raceways to allow for movement from ground settlement or frost. Expansion and contraction of the raceway must also be considered when exposed to heat or cold. This requirement prevents damage to the electrical installation due to movement of the building, raceway, or ground. In this installation for new underground electrical service to a new building, the 3â€PVC conduit to the pole mount, electrical meter was installed without an expansion joint. Ground movement by settlement or frost and expansion or contraction of the PVC conduit from heat or cold, has the potential to damage the conduit, meter base and conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_under_meter2.png | file://x:/photopub/docs/0000000634/4e408198-d22a-4152-9ea6-2de6f086837d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac6f87c_7d15_4500_a822_2a55ba0b674c
ELIN-835396-2017 | EL-545815-2017 | 6/13/2017 2:40:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Mast_assembly_kit.png At a new single family residence, a 120/240volt 200amp service was found with a mast kit installed using unapproved product and not supported . This can lead to an "Equipment damage" scenario. Pic attached | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Mast_assembly_kit.png | file://x:/photopub/docs/0000000615/3981b8bb-770b-4a4d-8748-a924c6019bf9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__645e5ee8_e53a_468c_af7d_3f9a128dd2d0
ELIN-836197-2017 | UW-546389-2017 | 6/13/2017 11:51:59 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound After-equipment was SPE 1000 approved | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #before_and_after_photos1.png,before_and_after_photos2.png Electrical equipment did not initially bear evidence of approval as indicated in British Columbia safety authorities electrical information bulletin for approve certification marks. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | before_and_after_photos1.png | file://x:/photopub/docs/0000000615/dc76ddf0-2faa-48d1-b700-f3c1da13a5b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce0b39d5_9eca_4aa2_a0f3_e742056af093
ELIN-836197-2017 | UW-546389-2017 | 6/13/2017 11:51:59 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Before-equipment did not bear evidence of approval | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #before_and_after_photos1.png,before_and_after_photos2.png Electrical equipment did not initially bear evidence of approval as indicated in British Columbia safety authorities electrical information bulletin for approve certification marks. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | before_and_after_photos2.png | file://x:/photopub/docs/0000000615/d5d22cd1-e5b2-4c78-9538-66c570f43e4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce0b39d5_9eca_4aa2_a0f3_e742056af093
ELHE-852128-2017 | HE-555527-2017 | 7/7/2017 12:33:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_terminals.png In an unpermitted grow op installation a 60 amp 120/240 volt feeder cable was found to be terminated to a contactor without the use of a box or approved fitting leaving energized exposed terminals. This could result in a shock and thermal hazard situation. Picture attached. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_terminals.png | file://x:/photopub/docs/0000000633/7ce68b13-ddd9-4a79-ad35-917ea471bf7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__318a575c_60e8_4102_b3b5_0c79e931d2b3
ELIN-827763-2017 | EL-519316-2017 | 6/2/2017 2:58:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Unprotected consumer service cable in excess of 1.5 meter inside the house. | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #P5.png Mechanical damage to unprotected consumer service cable may cause a fire, shock and damage to property or injury/fatality to persons or all of the above. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | P5.png | file://x:/photopub/docs/0000000610/898b110e-5a24-4e1e-833d-7eeab02765b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9187d132_387f_412d_96fa_94d864e9bb75
GAIN-849204-2017 | GA-553922-2017 | 7/11/2017 2:33:12 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Combustion_air.png The as-found condition is that a water heater has been installed without adequate combustion air supply. The potential hazard is that the water heater will not have enough air for proper combustion, resulting in the production of harmful emissions such as carbon monoxide | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air.png | file://x:/photopub/docs/0000000628/9bd57c4e-b9eb-414f-822e-c69f7725cdaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed8428d3_b09a_47a6_8760_03d2a7543cb5
GAHE-829973-2017 | HE-542269-2017 | 6/7/2017 7:42:40 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Add on vent to Direct vent termination in side enclosure living space. | GA152 | Appliance installed and operating. Venting incomplete (example: venting into living space) | 5 | 5 | #NK_MIP_Mobile_Home_Park__unit_21.png,NK_MIP_Mobile_Home_Park__unit_22.png Enclosure added on to 5th wheel trailer in mobile trailer park. Direct vent termination from Recreational Vehicle heater terminated inside the enclosure. The owner adapted single wall vent material to the direct vent termination and ran vent extension through wall to other side of trailer terminating through plastic trailer skirting about 1' above ground level. Direct vent termination is part of the heater design approval and can not be altered. The additional vent adapted could cause the direct vent to fail and prevent combustion air from entering the burner box causing incomplete combustion and production of carbon monoxide in the enclosure living space. | 5 | Appliance installed and operating. Venting incomplete (example: venting into living space) | NK_MIP_Mobile_Home_Park__unit_21.png | file://x:/photopub/docs/0000000612/ed08bd3b-4a18-46e9-a69e-1488f5e1eb77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97ebf79f_3ee0_4969_885f_579ff0cc2399
GAHE-829973-2017 | HE-542269-2017 | 6/7/2017 7:42:40 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound C vent termination from add on from direct vent RV heater termination located in enclosure on opposite side of trailer. | GA152 | Appliance installed and operating. Venting incomplete (example: venting into living space) | 5 | 5 | #NK_MIP_Mobile_Home_Park__unit_21.png,NK_MIP_Mobile_Home_Park__unit_22.png Enclosure added on to 5th wheel trailer in mobile trailer park. Direct vent termination from Recreational Vehicle heater terminated inside the enclosure. The owner adapted single wall vent material to the direct vent termination and ran vent extension through wall to other side of trailer terminating through plastic trailer skirting about 1' above ground level. Direct vent termination is part of the heater design approval and can not be altered. The additional vent adapted could cause the direct vent to fail and prevent combustion air from entering the burner box causing incomplete combustion and production of carbon monoxide in the enclosure living space. | 5 | Appliance installed and operating. Venting incomplete (example: venting into living space) | NK_MIP_Mobile_Home_Park__unit_22.png | file://x:/photopub/docs/0000000612/f8778660-4623-425e-9b7e-48eaafbe083f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97ebf79f_3ee0_4969_885f_579ff0cc2399
EDIN-833393-2017 | ED-412734-2016 | 6/8/2017 9:27:12 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED038 | Non-Safety critical monitoring bypassed or failed: Contractor is not aware of bypass or failure Risk Reg ED-02 | 2 | 2 | #Hatch.png The top of car escape hatch has a plug that is attached to the escape hatch. This plug disables the elevator from running when the escape hatch is opened. The elevator contractor failed to properly attach the plug to the escape hatch. Because the elevator is not disabled from possibly running when the escape hatch is opened, this poses a danger to any person that may use the escape. | 2 | Non-Safety critical monitoring bypassed or failed: Contractor is not aware of bypass or failure Risk Reg ED-02 | Hatch.png | file://x:/photopub/docs/0000000613/cc8b3f91-e727-4770-9db7-6876606a3379.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07a14421_de8f_4bea_a0b0_770b18880081
EDIN-833393-2017 | ED-412734-2016 | 6/8/2017 9:27:12 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED038 | Non-Safety critical monitoring bypassed or failed: Contractor is not aware of bypass or failure Risk Reg ED-02 | 2 | 2 | #Hatch.png The top of car escape hatch has a plug that is attached to the escape hatch. This plug disables the elevator from running when the escape hatch is opened. The elevator contractor failed to properly attach the plug to the escape hatch. Because the elevator is not disabled from possibly running when the escape hatch is opened, this poses a danger to any person that may use the escape. | 2 | Non-Safety critical monitoring bypassed or failed: Contractor is not aware of bypass or failure Risk Reg ED-02 | Hatch.png | file://x:/photopub/docs/0000000613/049b3065-c6a7-44a0-ad9c-df50cf796fee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07a14421_de8f_4bea_a0b0_770b18880081
GAIN-815245-2017 | GA-523451-2017 | 5/25/2017 11:36:01 AM | ASSESS: GA: Final | png | #asFound | GA143 | Open junction box with line voltage not accessible to public | 3 | 3 | #Thrift_2.png Open junction box(no cover) Cover required to prevent incidental contact with wiring. Risk of shock if contact was made with exposed conductors. | 3 | Open junction box with line voltage not accessible to public | Thrift_2.png | file://x:/photopub/docs/0000000605/3b7ccc70-ab1e-4403-8543-50aaa1553098.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a13166e_f0fc_4bd4_8500_a31aa7132764
ELIN-832848-2017 | EL-516996-2017 | 6/13/2017 10:57:09 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_electrode1.png,Ground_electrode2.png In a 120/208 volt, three phase electrical service, the neutral conductor must be connected to ground. A solidly grounded system facilitates a low-impedance fault current path through the grounded service conductor. This enables the overcurrent devices to operate quickly enough to prevent damage to the conductors or equipment. To ensure a solid ground path for the neutral, a ground conductor is connected between the neutral conductor in the service section of the electrical panel and a ground electrode outside. The ground electrode is usually a ground plate below grade or two 3m copper clad ground rods driven full length into the ground, 3m apart. During an assessment at an existing commercial building receiving an electrical service upgrade, the safety officer found only one existing ground rod installed on the exterior of the building with two ground conductors connected to it. The high impedance of this ground connection could cause the overcurrent devices | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_electrode2.png | file://x:/photopub/docs/0000000615/f177f7a1-bc16-4c94-8f94-9f89c8b16324.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e164e56_a258_4562_a743_753b1e9f3f64
ELIN-832848-2017 | EL-516996-2017 | 6/13/2017 10:57:09 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_electrode1.png,Ground_electrode2.png In a 120/208 volt, three phase electrical service, the neutral conductor must be connected to ground. A solidly grounded system facilitates a low-impedance fault current path through the grounded service conductor. This enables the overcurrent devices to operate quickly enough to prevent damage to the conductors or equipment. To ensure a solid ground path for the neutral, a ground conductor is connected between the neutral conductor in the service section of the electrical panel and a ground electrode outside. The ground electrode is usually a ground plate below grade or two 3m copper clad ground rods driven full length into the ground, 3m apart. During an assessment at an existing commercial building receiving an electrical service upgrade, the safety officer found only one existing ground rod installed on the exterior of the building with two ground conductors connected to it. The high impedance of this ground connection could cause the overcurrent devices | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_electrode1.png | file://x:/photopub/docs/0000000615/d16a57a1-2f51-4e5c-a95e-0c0659c973c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e164e56_a258_4562_a743_753b1e9f3f64
ELHE-845974-2017 | HE-551729-2017 | 6/27/2017 11:33:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Outside meterbase | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unfused_conductors1.png,Unfused_conductors2.png,Unfused_conductors3.png The energized and unfused main conductors are exposed for contact by general publlic. The direct contact is through a hole in the 60 amp switch cover where thje operating handle has been removed. This is a shock hazard and a fire hazard as the conductors are unfused. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unfused_conductors1.png | file://x:/photopub/docs/0000000622/bef3b29b-786a-4fd1-8ab1-8fd7c3b1faf0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bd1a5c6_d53d_48b1_a745_b2c54fb335b3
ELHE-845974-2017 | HE-551729-2017 | 6/27/2017 11:33:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Meterbase in garage | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unfused_conductors1.png,Unfused_conductors2.png,Unfused_conductors3.png The energized and unfused main conductors are exposed for contact by general publlic. The direct contact is through a hole in the 60 amp switch cover where thje operating handle has been removed. This is a shock hazard and a fire hazard as the conductors are unfused. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unfused_conductors3.png | file://x:/photopub/docs/0000000622/8ee15693-fa9e-4db3-8b72-4bf9b4504576.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bd1a5c6_d53d_48b1_a745_b2c54fb335b3
ELHE-845974-2017 | HE-551729-2017 | 6/27/2017 11:33:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound 60 amps switch inside | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Unfused_conductors1.png,Unfused_conductors2.png,Unfused_conductors3.png The energized and unfused main conductors are exposed for contact by general publlic. The direct contact is through a hole in the 60 amp switch cover where thje operating handle has been removed. This is a shock hazard and a fire hazard as the conductors are unfused. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Unfused_conductors2.png | file://x:/photopub/docs/0000000622/2289c69f-705c-4bb2-a1fd-3196ef7f1e47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bd1a5c6_d53d_48b1_a745_b2c54fb335b3
GAIN-823551-2017 | GA-519407-2017 | 5/26/2017 9:37:54 AM | ASSESS: GA: Final | png | #asFound Also noted on COI gas hose is not approved for permanent installation (10 feet max) | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Relief_too_close__.png Relief from regulator installed too close to appliance air intake. Gas regulator will relieve gas into appliance causing over firing of burner, or an explosion in combustion chamber | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Relief_too_close__.png | file://x:/photopub/docs/0000000606/f85201e9-5e2f-4079-85ea-5febd54addb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66a37549_fb38_4908_a73a_72fdd161cbff
GAIN-816433-2017 | GA-471796-2016 | 5/26/2017 2:18:46 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Navien.png The as-found condition is that a water heater has been installed without an adequate combustion air supply. The potential hazard is that the boiler will not have enough air for complete combustion, resulting in the production of harmful emissions such as carbon monoxide. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Navien.png | file://x:/photopub/docs/0000000606/c85a6e53-4bde-4548-ab76-55fb0fde66ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b86cd820_a015_45e9_b599_4cddc7eab12e
ELHE-822800-2017 | HE-538026-2017 | 5/25/2017 9:03:36 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Low_hanging_powerline.png Energized Powerlines which have deteriorated due to lack of maintenance are a fire hazard or shock hazard | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Low_hanging_powerline.png | file://x:/photopub/docs/0000000606/be32de8b-e3b5-47b5-a487-8ffa4ec40588.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b698cbb2_2ac2_4e9c_9242_bf0b2a23fb81
ELIN-836416-2017 | EL-545741-2017 | 6/15/2017 10:48:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_conductor_run_through_branch_breaker_section_and_not_terminated_in_required_section1.png,Grounding_conductor_run_through_branch_breaker_section_and_not_terminated_in_required_section2.png Grounding conductor has been run through branch breaker section of sub distribution panel and has been terminated at the sub distribution. Grounding connection is required to be done in the main service enclosure. If a fault were to occur in the branch breaker section this grounding conductor may see stray currents and not allow overcurrent devices to act accordingly and clear the fault. The main service is currently not grounded where it receives its supply this would also affect the operation of overcurrent devices, and would potentially lead to a shock or fire hazard to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_conductor_run_through_branch_breaker_section_and_not_terminated_in_required_section2.png | file://x:/photopub/docs/0000000616/48def788-56f5-49b1-a860-ae9db972d017.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44dab1c5_bde1_43d7_9dc6_8c565113c4d1
ELIN-836416-2017 | EL-545741-2017 | 6/15/2017 10:48:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_conductor_run_through_branch_breaker_section_and_not_terminated_in_required_section1.png,Grounding_conductor_run_through_branch_breaker_section_and_not_terminated_in_required_section2.png Grounding conductor has been run through branch breaker section of sub distribution panel and has been terminated at the sub distribution. Grounding connection is required to be done in the main service enclosure. If a fault were to occur in the branch breaker section this grounding conductor may see stray currents and not allow overcurrent devices to act accordingly and clear the fault. The main service is currently not grounded where it receives its supply this would also affect the operation of overcurrent devices, and would potentially lead to a shock or fire hazard to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_conductor_run_through_branch_breaker_section_and_not_terminated_in_required_section1.png | file://x:/photopub/docs/0000000616/d5ce96d1-5b18-41d5-9baa-c23069efe02e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44dab1c5_bde1_43d7_9dc6_8c565113c4d1
ELOP-836544-2017 | EL-523004-2017 | 6/13/2017 | ASSESS: EL OP: Acceptance | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Energized_t_exposed_to_accidental_contact_1.png,Energized_t_exposed_to_accidental_contact_2.png The energized tees used for temporary power had exposed parts that could be accidentally contacted. This condition could lead to shock or electrocution. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_t_exposed_to_accidental_contact_1.png | file://x:/photopub/docs/0000000616/8355cbb4-ea69-429b-a8ab-45e613bd7541.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__269f4ed4_b37f_4941_b803_5112f1e20653
ELOP-836544-2017 | EL-523004-2017 | 6/13/2017 | ASSESS: EL OP: Acceptance | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Energized_t_exposed_to_accidental_contact_1.png,Energized_t_exposed_to_accidental_contact_2.png The energized tees used for temporary power had exposed parts that could be accidentally contacted. This condition could lead to shock or electrocution. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_t_exposed_to_accidental_contact_2.png | file://x:/photopub/docs/0000000616/dd88ed9b-1b16-4a75-b34a-06deca9748e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__269f4ed4_b37f_4941_b803_5112f1e20653
ELIN-840680-2017 | EL-485576-2016 | 6/19/2017 5:29:52 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL175 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | 2 | 2 | #No_motor_disconnecting_means.png A motor disconnecting means must be provided within sight of the motor and 3m so service personnel have control over the electrical supply | 2 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | No_motor_disconnecting_means.png | file://x:/photopub/docs/0000000618/a9cae0a3-4eff-43bb-bead-6ecf65ab9b1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef5ad40f_8a7d_4852_9024_a99518182b8d
ELHE-858271-2017 | HE-559035-2017 | 7/14/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Compressor_motor_missing_cover_.png - Motor pressure/limit switch mouted at 6" from the floor missing its cover. Conductors in box are live and easily accessible to persons working in this area exposing them to a high risk of shock. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Compressor_motor_missing_cover_.png | file://x:/photopub/docs/0000000632/3a74fdcf-75b1-454c-84b7-4df8387fb28e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b6b5f38_48b1_4286_a7cd_0a254c668903
AMOP-831339-2017 | 3808315 | 6/7/2017 2:01:18 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Anchor_bolt_nut_loose.png Loose anchore bolt nut identified for mast support structure. Although the nut was found to be loose, because of the width of the support structure and the fact that the structure is under the compression of the zipline rope there is no deemed loss to the structural stability of the mast structure. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Anchor_bolt_nut_loose.png | file://x:/photopub/docs/0000000615/11c5ecb3-de02-4aa4-9757-a3803e83734f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be8c653b_f988_43bb_8031_a79c48568e00
ELIN-825708-2017 | EL-353834-2016 | 5/30/2017 11:21:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #3_gang_supported_1_side_only2.png Electrical boxes must be properly secured to reduce risk of damage to equipment and to ensure a safe installation. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3_gang_supported_1_side_only2.png | file://x:/photopub/docs/0000000608/a7fd06fd-6301-4591-8283-4a3afa85b892.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c64327f_6636_4f98_baac_4b6666138ea4
ELIN-826959-2017 | EL-514310-2017 | 5/31/2017 8:02:52 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Feeder cable installed through bottom plate of wall with in 32mm of the face of the stud. This is a fire hazard as this cable could be hit be a dry wall screw. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | A2.png | file://x:/photopub/docs/0000000608/574b80a9-b8e0-4c6e-a386-d28c846b9818.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef6df7e6_2c54_4608_84c1_72d5b7c806ac
ELIN-826515-2017 | UW-540437-2017 | 5/31/2017 9:17:18 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #B1.png,B2.png,B3.png Undersized feeder cable of 2/0 ACWU supplying a 350 amp switch. This is a fire hazard as the cable is overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | B1.png | file://x:/photopub/docs/0000000608/a41ebfb9-8c27-435a-90d6-276461e2f7bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed581900_6f1a_4c69_a034_0ff84f616dcd
ELIN-826515-2017 | UW-540437-2017 | 5/31/2017 9:17:18 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | #B1.png,B2.png,B3.png Undersized feeder cable of 2/0 ACWU supplying a 350 amp switch. This is a fire hazard as the cable is overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | B3.png | file://x:/photopub/docs/0000000608/71a21f6d-dd3a-4fb6-82a7-319c3df59f2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed581900_6f1a_4c69_a034_0ff84f616dcd
ELIN-826959-2017 | EL-514310-2017 | 5/31/2017 8:02:52 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Feeder cable installed through bottom plate of wall with in 32mm of the face of the stud. This is a fire hazard as this cable could be hit be a dry wall screw. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | A1.png | file://x:/photopub/docs/0000000608/49b046af-de0c-40dc-b056-4c953869d7ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef6df7e6_2c54_4608_84c1_72d5b7c806ac
ELIN-850123-2017 | UW-554273-2017 | 7/5/2017 7:48:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | #V1.png,V2.png,V3.png,V4.png 3C/#2 AWG Aluminum nonmetallic sheathed cable; 3C/ 4/0 ACWU; 3C/ 500 Kcmil ACWU leave a 1200 Amp gutter without additional over current protection as required. These conductors are exposed to currents much higher then their actual ratings. Nonmetallic sheathed cable is not an approved method of installation for this purpose, as no mechanical protection is provided to the conductors. This is a fire and shock hazard to individuals and the buildings that these conductors are located in. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | V4.png | file://x:/photopub/docs/0000000625/d863b021-0c83-4784-891c-191d764c5534.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0289631_d0ba_40d1_b5bb_32a3bf866812
ELIN-850123-2017 | UW-554273-2017 | 7/5/2017 7:48:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | #V1.png,V2.png,V3.png,V4.png 3C/#2 AWG Aluminum nonmetallic sheathed cable; 3C/ 4/0 ACWU; 3C/ 500 Kcmil ACWU leave a 1200 Amp gutter without additional over current protection as required. These conductors are exposed to currents much higher then their actual ratings. Nonmetallic sheathed cable is not an approved method of installation for this purpose, as no mechanical protection is provided to the conductors. This is a fire and shock hazard to individuals and the buildings that these conductors are located in. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | V2.png | file://x:/photopub/docs/0000000625/975e4bc0-ec98-426a-b31e-539f29e96980.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0289631_d0ba_40d1_b5bb_32a3bf866812
ELIN-850123-2017 | UW-554273-2017 | 7/5/2017 7:48:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound No over current protection | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | #V1.png,V2.png,V3.png,V4.png 3C/#2 AWG Aluminum nonmetallic sheathed cable; 3C/ 4/0 ACWU; 3C/ 500 Kcmil ACWU leave a 1200 Amp gutter without additional over current protection as required. These conductors are exposed to currents much higher then their actual ratings. Nonmetallic sheathed cable is not an approved method of installation for this purpose, as no mechanical protection is provided to the conductors. This is a fire and shock hazard to individuals and the buildings that these conductors are located in. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | V1.png | file://x:/photopub/docs/0000000625/77a02602-1155-49a1-91ee-e16c2492a650.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0289631_d0ba_40d1_b5bb_32a3bf866812
ELIN-865254-2017 | EL-515655-2017 | 7/26/2017 4:35:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png Non metallic sheathed cable in contact with heating sources and exposed to mechanical damage in attic. This is s shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A1.png | file://x:/photopub/docs/0000000636/34d789b4-b82c-4832-9231-1f7623af3c0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20108e04_11bb_43b7_92c8_91214d150306
ELIN-865254-2017 | EL-515655-2017 | 7/26/2017 4:35:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png Non metallic sheathed cable in contact with heating sources and exposed to mechanical damage in attic. This is s shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A3.png | file://x:/photopub/docs/0000000636/4ed5ef94-1fe1-4ec1-acb2-109622502b89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20108e04_11bb_43b7_92c8_91214d150306
ELIN-865254-2017 | EL-515655-2017 | 7/26/2017 4:35:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png Non metallic sheathed cable in contact with heating sources and exposed to mechanical damage in attic. This is s shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A2.png | file://x:/photopub/docs/0000000636/8396c847-739d-40c6-8c76-d8a053df43a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20108e04_11bb_43b7_92c8_91214d150306
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P53.png | file://x:/photopub/docs/0000000607/74c357c8-cfb8-434c-914f-01eea629cbb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P52.png | file://x:/photopub/docs/0000000607/63585f66-aee6-417b-8cac-351c05eed10d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P55.png | file://x:/photopub/docs/0000000607/4d305baa-c529-4609-849a-1bbac8f15a36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Cables are subject to heat and mechanical damages. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P51.png | file://x:/photopub/docs/0000000607/bdb5af68-6363-43e3-9840-d2cc8317a954.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P54.png | file://x:/photopub/docs/0000000607/a3f903f4-6517-43ee-816a-28299e9b1f6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P57.png | file://x:/photopub/docs/0000000607/15ad30b9-4f85-4662-9422-379ef57a66fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
ELIN-846703-2017 | EL-401144-2016 | 6/29/2017 12:31:07 PM | ASSESS: EL: Final | png | #asFound | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Damaged_meterbase_hub_.png Meter base hub damaged and no longer waterproof | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Damaged_meterbase_hub_.png | file://x:/photopub/docs/0000000624/af2a63a5-129e-4704-9cd7-c2b1879d8eb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8f9427a_2ecb_42cb_a45c_0273eab10265
ELIN-836972-2017 | EL-515647-2017 | 6/16/2017 5:57:15 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacles_within_1_5_m_of_sink1.png,Receptacles_within_1_5_m_of_sink2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and made contact with water in a sink. In this installation at a new dental clinic, GFCI protection was not provided for a receptacle within 1.5 m of the staff kitchen sink and two receptacles near an equipment sink. This is a potential shock hazard for persons working with cord connected equipment near these sinks in this dental clinic. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacles_within_1_5_m_of_sink1.png | file://x:/photopub/docs/0000000617/6cc22bbb-da20-49eb-81f6-3404ab6e65ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76ca13e9_5481_4041_93aa_da1bca37b099
ELIN-779796-2017 | EL-437324-2016 | 5/29/2017 3:04:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_and_temp_supply1.png,Service_and_temp_supply2.png,Service_and_temp_supply3.png,Service_and_temp_supply4.png,Service_and_temp_supply5.png Distribution has been supplied with single conductors, crossing exposed property and driveway, from a neighbouring pump house (resident at neighbouring property was not available at time of assessment). Covers for panels are missing. Homeowner has been advised to disconnect installation. Installation was energized at time of assessment and left to homeowner to de-energize, as per BCSA policy. Hazard exists for damage to conductors resulting in shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_and_temp_supply4.png | file://x:/photopub/docs/0000000607/37ccb005-ef59-474a-a3f6-547b24c4a779.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ced1bdc0_63f1_4f8b_8e46_7051a0a6264c
ELIN-779796-2017 | EL-437324-2016 | 5/29/2017 3:04:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_and_temp_supply1.png,Service_and_temp_supply2.png,Service_and_temp_supply3.png,Service_and_temp_supply4.png,Service_and_temp_supply5.png Distribution has been supplied with single conductors, crossing exposed property and driveway, from a neighbouring pump house (resident at neighbouring property was not available at time of assessment). Covers for panels are missing. Homeowner has been advised to disconnect installation. Installation was energized at time of assessment and left to homeowner to de-energize, as per BCSA policy. Hazard exists for damage to conductors resulting in shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_and_temp_supply3.png | file://x:/photopub/docs/0000000607/46172aaa-d3d4-4f86-b939-6b6aa71b6834.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ced1bdc0_63f1_4f8b_8e46_7051a0a6264c
ELIN-779796-2017 | EL-437324-2016 | 5/29/2017 3:04:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_and_temp_supply1.png,Service_and_temp_supply2.png,Service_and_temp_supply3.png,Service_and_temp_supply4.png,Service_and_temp_supply5.png Distribution has been supplied with single conductors, crossing exposed property and driveway, from a neighbouring pump house (resident at neighbouring property was not available at time of assessment). Covers for panels are missing. Homeowner has been advised to disconnect installation. Installation was energized at time of assessment and left to homeowner to de-energize, as per BCSA policy. Hazard exists for damage to conductors resulting in shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_and_temp_supply2.png | file://x:/photopub/docs/0000000607/4e4147c4-0f81-4323-87df-93cd43388502.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ced1bdc0_63f1_4f8b_8e46_7051a0a6264c
ELIN-779796-2017 | EL-437324-2016 | 5/29/2017 3:04:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_and_temp_supply1.png,Service_and_temp_supply2.png,Service_and_temp_supply3.png,Service_and_temp_supply4.png,Service_and_temp_supply5.png Distribution has been supplied with single conductors, crossing exposed property and driveway, from a neighbouring pump house (resident at neighbouring property was not available at time of assessment). Covers for panels are missing. Homeowner has been advised to disconnect installation. Installation was energized at time of assessment and left to homeowner to de-energize, as per BCSA policy. Hazard exists for damage to conductors resulting in shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_and_temp_supply5.png | file://x:/photopub/docs/0000000607/ec7a231d-65cf-44fc-bd4a-b110bea5ccb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ced1bdc0_63f1_4f8b_8e46_7051a0a6264c
ELIN-779796-2017 | EL-437324-2016 | 5/29/2017 3:04:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_and_temp_supply1.png,Service_and_temp_supply2.png,Service_and_temp_supply3.png,Service_and_temp_supply4.png,Service_and_temp_supply5.png Distribution has been supplied with single conductors, crossing exposed property and driveway, from a neighbouring pump house (resident at neighbouring property was not available at time of assessment). Covers for panels are missing. Homeowner has been advised to disconnect installation. Installation was energized at time of assessment and left to homeowner to de-energize, as per BCSA policy. Hazard exists for damage to conductors resulting in shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_and_temp_supply1.png | file://x:/photopub/docs/0000000607/afe1b205-0929-477c-a6f5-1b2de715dc02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ced1bdc0_63f1_4f8b_8e46_7051a0a6264c
GAWP-840414-2017 | GA-536038-2017 | 6/20/2017 2:39:35 PM | ASSESS: GA Work In Progress | png | #asFound Victaullic fittings on boiler | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Boiler_fitting.png Found un certified Victaullic fittings on boiler piping. If temperature went beyond the rating of the fittings, they may fail and cause boiler piping to leak creating a hazard to anyone in the vicinity. | 3 | Non-compliant material/fittings installed | Boiler_fitting.png | file://x:/photopub/docs/0000000618/dc294bf0-f578-49c0-b747-f221335b39f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__017aa3f8_5fd2_4547_a13c_d3fda4e15100
ELHE-844910-2017 | HE-551013-2017 | 6/23/2017 10:17:33 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Panel with no cover and wires disconnected from over current device. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Live_panel.png The code requires all energized electrical equipment to be secure and inaccessible to contact. This code requirement is to protect against electrical shock. Upon inspection of this property it was observed that there were many open and exposed electrical panels. These exposed components of electrical equipment were accesable to the public and could result in personal injury including shock , burns or electrocution. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Live_panel.png | file://x:/photopub/docs/0000000621/d19d1138-c420-4a41-9b65-70e647d8e7a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc5176a1_1c39_47e4_8ac4_f66bec93a2ff
GAHE-822046-2017 | HE-537592-2017 | 5/24/2017 12:47:57 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Base_furnace1.png,Base_furnace2.png Furnace and ducting not installed on floor, approximately 12" space between bottom of up flow furnace and floor suspended by plumbing strapping. Strain on furnace cabinet could break duct work, gas piping or venting system | 3 | Appliance not installed according to installation instructions | Base_furnace1.png | file://x:/photopub/docs/0000000605/7190a9b7-256c-421e-87ea-ca820a956d94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72cd1e57_757c_4c5a_8750_79875c189156
GAHE-822046-2017 | HE-537592-2017 | 5/24/2017 12:47:57 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Base_furnace1.png,Base_furnace2.png Furnace and ducting not installed on floor, approximately 12" space between bottom of up flow furnace and floor suspended by plumbing strapping. Strain on furnace cabinet could break duct work, gas piping or venting system | 3 | Appliance not installed according to installation instructions | Base_furnace2.png | file://x:/photopub/docs/0000000605/4ed99e46-51fc-4848-8e50-fadcb4fecefe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72cd1e57_757c_4c5a_8750_79875c189156
GAIN-811653-2017 | GA-481007-2016 | 5/25/2017 9:44:36 AM | ASSESS: GA: Final | png | #asFound | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | #Gas_leak.png When entering mechanical room, I could smell evidence of gas odor, a leak was found on Corrugated Stainless Steal line that was energized but capped off, line was isolated and de-energized by turning off the gas supply at the meter. The leak of gas in a building could cause a fire or explosion | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Gas_leak.png | file://x:/photopub/docs/0000000605/a52f1df6-6fd5-4113-b230-35a164df95fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b9050a_1318_4df1_82a3_07265ec5e0c6
ELIN-825684-2017 | EL-533282-2017 | 5/30/2017 11:31:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Gas bonding conductor not installed. | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Gas.png Rough wire of new single family dwelling. The metallic gas piping has not been bonded to ground. Therefore, a cable faulting to the gas line may not trip an overcurrent device. This could lead to a shock hazard by inadvertent contact or a fire hazard if the overcurrent device affected does not trip. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas.png | file://x:/photopub/docs/0000000607/ebb746b5-5617-47aa-a853-a51b6029be24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc32c9e0_10ab_4eee_9210_102648307a66
ELOP-837859-2017 | 6560 | 6/15/2017 9:21:36 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Panel.png Panel breaker spaces removed on energized panels leaving exposed electrical bus and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel.png | file://x:/photopub/docs/0000000616/01624869-ff8c-46e4-983c-4ad718b7cf82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f114dfa_1825_42d4_a37a_05228f1d619c
ELIN-846734-2017 | EL-550560-2017 | 7/4/2017 11:51:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Typical_westinghouse_breaker_in_SQD_panel.png The 15 amp 120 volt Westinghouse breakers located in both the main residence and the Suite are installed in SQ D. panelboards and they do not seat correctly within the panels nor are they approved to be used in another manufacturers equipment. ESO removed both panel covers for inspection and both breakers fell out of the panels when covers were removed. The breakers have not been tested or approved for this use and the poor mounting of the breakers will create both a thermal hazard and cause equipment damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Typical_westinghouse_breaker_in_SQD_panel.png | file://x:/photopub/docs/0000000625/1965af08-a6ea-48f4-ac0b-4e4b615dc99b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0773bda0_0fd8_4dc6_a27c_43c07f5fae8a
ELOP-811609-2017 | EL-057475-2013 | 5/12/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #25KV_1000KVA_outdoor_unit_substation1.png,25KV_1000KVA_outdoor_unit_substation2.png,25KV_1000KVA_outdoor_unit_substation3.png,25KV_1000KVA_outdoor_unit_substation4.png,25KV_1000KVA_outdoor_unit_substation5.png,25KV_1000KVA_outdoor_unit_substation6.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equ | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 25KV_1000KVA_outdoor_unit_substation4.png | file://x:/photopub/docs/0000000600/3af35f00-c998-41d3-8ab6-83bddde00bdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c43c1ea3_795a_4f20_ac41_9c5661f9e699
ELOP-811609-2017 | EL-057475-2013 | 5/12/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #25KV_1000KVA_outdoor_unit_substation1.png,25KV_1000KVA_outdoor_unit_substation2.png,25KV_1000KVA_outdoor_unit_substation3.png,25KV_1000KVA_outdoor_unit_substation4.png,25KV_1000KVA_outdoor_unit_substation5.png,25KV_1000KVA_outdoor_unit_substation6.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equ | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 25KV_1000KVA_outdoor_unit_substation2.png | file://x:/photopub/docs/0000000600/d20b03b0-fc4a-4dbc-92b8-7ee031e43224.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c43c1ea3_795a_4f20_ac41_9c5661f9e699
ELOP-811609-2017 | EL-057475-2013 | 5/12/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #25KV_1000KVA_outdoor_unit_substation1.png,25KV_1000KVA_outdoor_unit_substation2.png,25KV_1000KVA_outdoor_unit_substation3.png,25KV_1000KVA_outdoor_unit_substation4.png,25KV_1000KVA_outdoor_unit_substation5.png,25KV_1000KVA_outdoor_unit_substation6.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equ | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 25KV_1000KVA_outdoor_unit_substation1.png | file://x:/photopub/docs/0000000600/315d68f7-8e4c-4b01-acde-a8dae71cb198.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c43c1ea3_795a_4f20_ac41_9c5661f9e699
ELOP-811609-2017 | EL-057475-2013 | 5/12/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #25KV_1000KVA_outdoor_unit_substation1.png,25KV_1000KVA_outdoor_unit_substation2.png,25KV_1000KVA_outdoor_unit_substation3.png,25KV_1000KVA_outdoor_unit_substation4.png,25KV_1000KVA_outdoor_unit_substation5.png,25KV_1000KVA_outdoor_unit_substation6.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equ | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 25KV_1000KVA_outdoor_unit_substation5.png | file://x:/photopub/docs/0000000600/f7038fa7-9bd8-4104-aca1-508fe6e6122a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c43c1ea3_795a_4f20_ac41_9c5661f9e699
ELIN-836972-2017 | EL-515647-2017 | 6/16/2017 5:57:15 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacles_within_1_5_m_of_sink1.png,Receptacles_within_1_5_m_of_sink2.png Ground-fault circuit interrupters (GFCI's) are required to be installed for outlets within 1.5m of a sink. GFCI's monitor the current flowing in a circuit and will open the circuit if the GFCI senses a difference of 5 mA. This prevents dangerous levels of current from flowing through a person if they where holding a faulty appliance and made contact with water in a sink. In this installation at a new dental clinic, GFCI protection was not provided for a receptacle within 1.5 m of the staff kitchen sink and two receptacles near an equipment sink. This is a potential shock hazard for persons working with cord connected equipment near these sinks in this dental clinic. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacles_within_1_5_m_of_sink2.png | file://x:/photopub/docs/0000000617/1bed5fa5-2aae-4d48-8fdd-92175596c722.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76ca13e9_5481_4041_93aa_da1bca37b099
BPVOP-517698-2016 | 2263501 | 5/17/2017 11:02:50 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #SRV.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve on a 15 psi low pressure steam boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 0 | No Created Hazard Identified | SRV.png | file://x:/photopub/docs/0000000621/efa25355-4669-40b5-a722-1f90c3a71f89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a5d40a0_0fee_42f5_a71c_52292a8b3e4e
ELIN-830342-2017 | EL-476843-2016 | 6/29/2017 9:53:44 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #6833_HWY_61.png,6833_HWY_62.png PV SOURCE CIRCUITS BETWEEN STRING ARRAY AND RACEWAY TO COMBINER BOX ARE SUCCEPTIBLE TO MECHANICAL DAMAGE RESULTING FROM SLIDING SNOW. RACEWAY CONTAINING PV SOURCE CIRCUITS IS SUCCEPTIBLE TO SLIDING SNOW. BATTERY BANK IS INSTALLED IN AN UNACCEPTABLE FASHION WITH ENERGIZED, EXPOSED TERMINALS, NOT CONTAINED IN AN APPROVED ENCLOSURE OR IN A ROOM ACCESSIBLE TO AUTHORIZED PERSONS ONLY. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 6833_HWY_62.png | file://x:/photopub/docs/0000000623/0c372046-4ee2-4cb0-9a4c-b47feebd2685.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14269b92_deb1_4390_8b9e_143edf39b57b
ELIN-830342-2017 | EL-476843-2016 | 6/29/2017 9:53:44 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL041 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #6833_HWY_61.png,6833_HWY_62.png PV SOURCE CIRCUITS BETWEEN STRING ARRAY AND RACEWAY TO COMBINER BOX ARE SUCCEPTIBLE TO MECHANICAL DAMAGE RESULTING FROM SLIDING SNOW. RACEWAY CONTAINING PV SOURCE CIRCUITS IS SUCCEPTIBLE TO SLIDING SNOW. BATTERY BANK IS INSTALLED IN AN UNACCEPTABLE FASHION WITH ENERGIZED, EXPOSED TERMINALS, NOT CONTAINED IN AN APPROVED ENCLOSURE OR IN A ROOM ACCESSIBLE TO AUTHORIZED PERSONS ONLY. | 3 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 6833_HWY_61.png | file://x:/photopub/docs/0000000623/27fcb998-3402-4c64-94fc-657b17e410d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14269b92_deb1_4390_8b9e_143edf39b57b
ELOP-811609-2017 | EL-057475-2013 | 5/12/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #25KV_1000KVA_outdoor_unit_substation1.png,25KV_1000KVA_outdoor_unit_substation2.png,25KV_1000KVA_outdoor_unit_substation3.png,25KV_1000KVA_outdoor_unit_substation4.png,25KV_1000KVA_outdoor_unit_substation5.png,25KV_1000KVA_outdoor_unit_substation6.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equ | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 25KV_1000KVA_outdoor_unit_substation6.png | file://x:/photopub/docs/0000000600/4b2c47b9-f55b-415e-a4cd-24285cccd460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c43c1ea3_795a_4f20_ac41_9c5661f9e699
ELOP-811609-2017 | EL-057475-2013 | 5/12/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #25KV_1000KVA_outdoor_unit_substation1.png,25KV_1000KVA_outdoor_unit_substation2.png,25KV_1000KVA_outdoor_unit_substation3.png,25KV_1000KVA_outdoor_unit_substation4.png,25KV_1000KVA_outdoor_unit_substation5.png,25KV_1000KVA_outdoor_unit_substation6.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equ | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 25KV_1000KVA_outdoor_unit_substation3.png | file://x:/photopub/docs/0000000600/92f66fb4-0127-4305-8994-88f76ec7d241.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c43c1ea3_795a_4f20_ac41_9c5661f9e699
ELIN-837953-2017 | EL-546430-2017 | 6/19/2017 5:37:12 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_cable_connections1.png,Service_cable_connections2.png,Service_cable_connections3.png,Service_cable_connections4.png,Service_cable_connections5.png,Service_cable_connections6.png Connections installed for conductors located outdoors are required to be rated for use in wet location. Connections between neutral supported cable conductors and grounded service conductors are required to be of the compression type. Service cables are not permitted to be spliced in boxes that contain other conductors. These requirements are intended to prevent connections from becoming damaged by exposure to weather, to ensure a solid connection for the grounded service conductor, and to prevent service conductors from contacting other conductors. This installation of a 30A 120/240V overhead service installed to provide power to an office at a mill site had service conductor connections between neutral supported cable and teck90 cable on the exterior of the building that were made using twist on wire connectors that wer | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_cable_connections4.png | file://x:/photopub/docs/0000000618/cc632c5b-5802-4ca5-9c83-c5f7d9473a93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb48671_9c20_438b_b6e3_dbc7c2127fe3
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened2.png | file://x:/photopub/docs/0000000618/6a1340d4-7dee-40a6-8ab5-91ef1503bee0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened3.png | file://x:/photopub/docs/0000000618/7d7aea61-1997-48f7-86a5-531b32241397.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
ELIN-837953-2017 | EL-546430-2017 | 6/19/2017 5:37:12 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_cable_connections1.png,Service_cable_connections2.png,Service_cable_connections3.png,Service_cable_connections4.png,Service_cable_connections5.png,Service_cable_connections6.png Connections installed for conductors located outdoors are required to be rated for use in wet location. Connections between neutral supported cable conductors and grounded service conductors are required to be of the compression type. Service cables are not permitted to be spliced in boxes that contain other conductors. These requirements are intended to prevent connections from becoming damaged by exposure to weather, to ensure a solid connection for the grounded service conductor, and to prevent service conductors from contacting other conductors. This installation of a 30A 120/240V overhead service installed to provide power to an office at a mill site had service conductor connections between neutral supported cable and teck90 cable on the exterior of the building that were made using twist on wire connectors that wer | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_cable_connections6.png | file://x:/photopub/docs/0000000618/e3222c86-40d2-4f50-9054-1768a4f76721.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb48671_9c20_438b_b6e3_dbc7c2127fe3
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened4.png | file://x:/photopub/docs/0000000618/a30dfc77-864d-4a4d-a0ea-86b9528511f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
ELIN-837953-2017 | EL-546430-2017 | 6/19/2017 5:37:12 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_cable_connections1.png,Service_cable_connections2.png,Service_cable_connections3.png,Service_cable_connections4.png,Service_cable_connections5.png,Service_cable_connections6.png Connections installed for conductors located outdoors are required to be rated for use in wet location. Connections between neutral supported cable conductors and grounded service conductors are required to be of the compression type. Service cables are not permitted to be spliced in boxes that contain other conductors. These requirements are intended to prevent connections from becoming damaged by exposure to weather, to ensure a solid connection for the grounded service conductor, and to prevent service conductors from contacting other conductors. This installation of a 30A 120/240V overhead service installed to provide power to an office at a mill site had service conductor connections between neutral supported cable and teck90 cable on the exterior of the building that were made using twist on wire connectors that wer | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_cable_connections5.png | file://x:/photopub/docs/0000000618/408c8769-c5be-42ee-af91-6a6f0531fa6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb48671_9c20_438b_b6e3_dbc7c2127fe3
GAIN-826121-2017 | GA-540112-2017 | 6/14/2017 9:05:08 AM | ASSESS: GA: Final | png | #asFound Installation Instructions | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Venting21.png,Venting22.png,Venting23.png,Venting24.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting21.png | file://x:/photopub/docs/0000000616/8bb00f3b-6de4-47f7-bb4c-5d16c674bd3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__503e1bb2_9735_4838_9dd6_5262b231bf33
GAIN-826121-2017 | GA-540112-2017 | 6/14/2017 9:05:08 AM | ASSESS: GA: Final | png | #asFound No Insulation | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Venting21.png,Venting22.png,Venting23.png,Venting24.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting22.png | file://x:/photopub/docs/0000000616/93ca1904-bb90-495e-aa11-c38a52c0b196.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__503e1bb2_9735_4838_9dd6_5262b231bf33
GAIN-826121-2017 | GA-540112-2017 | 6/14/2017 9:05:08 AM | ASSESS: GA: Final | png | #asFound No hangers | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Venting21.png,Venting22.png,Venting23.png,Venting24.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting24.png | file://x:/photopub/docs/0000000616/89b62738-304d-46e2-b264-fe7752edac22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__503e1bb2_9735_4838_9dd6_5262b231bf33
GAIN-826121-2017 | GA-540112-2017 | 6/14/2017 9:05:08 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Venting21.png,Venting22.png,Venting23.png,Venting24.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting23.png | file://x:/photopub/docs/0000000616/9b46e97a-7909-46a9-abbb-273265d6c0fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__503e1bb2_9735_4838_9dd6_5262b231bf33
ELIN-860028-2017 | EL-546486-2017 | 7/20/2017 10:50:12 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 3 | #Range_cord.png Energized range cord. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Range_cord.png | file://x:/photopub/docs/0000000633/86e0df20-005f-487c-8fb7-7c5567f77f92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a0004e4_c181_43c3_a196_9d3e677eb774
ELIN-865329-2017 | EL-540787-2017 | 7/26/2017 12:20:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Cables are not protected in the stud hole closer than 32 mm from its surface on wall board side. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P4.png Mechanical damage to electrical cable may cause shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P4.png | file://x:/photopub/docs/0000000636/c6a58063-500d-43a6-98cc-845fb82a47c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56adca90_676d_4a3c_b516_e55f8cec7fd3
ELIN-837953-2017 | EL-546430-2017 | 6/19/2017 5:37:12 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_cable_connections1.png,Service_cable_connections2.png,Service_cable_connections3.png,Service_cable_connections4.png,Service_cable_connections5.png,Service_cable_connections6.png Connections installed for conductors located outdoors are required to be rated for use in wet location. Connections between neutral supported cable conductors and grounded service conductors are required to be of the compression type. Service cables are not permitted to be spliced in boxes that contain other conductors. These requirements are intended to prevent connections from becoming damaged by exposure to weather, to ensure a solid connection for the grounded service conductor, and to prevent service conductors from contacting other conductors. This installation of a 30A 120/240V overhead service installed to provide power to an office at a mill site had service conductor connections between neutral supported cable and teck90 cable on the exterior of the building that were made using twist on wire connectors that wer | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_cable_connections1.png | file://x:/photopub/docs/0000000619/24bc4036-31de-4e0b-b5e5-738912f59cb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb48671_9c20_438b_b6e3_dbc7c2127fe3
ELIN-837953-2017 | EL-546430-2017 | 6/19/2017 5:37:12 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_cable_connections1.png,Service_cable_connections2.png,Service_cable_connections3.png,Service_cable_connections4.png,Service_cable_connections5.png,Service_cable_connections6.png Connections installed for conductors located outdoors are required to be rated for use in wet location. Connections between neutral supported cable conductors and grounded service conductors are required to be of the compression type. Service cables are not permitted to be spliced in boxes that contain other conductors. These requirements are intended to prevent connections from becoming damaged by exposure to weather, to ensure a solid connection for the grounded service conductor, and to prevent service conductors from contacting other conductors. This installation of a 30A 120/240V overhead service installed to provide power to an office at a mill site had service conductor connections between neutral supported cable and teck90 cable on the exterior of the building that were made using twist on wire connectors that wer | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_cable_connections3.png | file://x:/photopub/docs/0000000619/f2ad6c23-13a2-42ec-b85b-9e1ecac080ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb48671_9c20_438b_b6e3_dbc7c2127fe3
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened1.png | file://x:/photopub/docs/0000000619/14580e39-3a4c-4069-8b18-bf583c88a15a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened5.png | file://x:/photopub/docs/0000000619/2525cba7-60db-45ff-8249-3f3bb55feb10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
ELIN-837953-2017 | EL-546430-2017 | 6/19/2017 5:37:12 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Service_cable_connections1.png,Service_cable_connections2.png,Service_cable_connections3.png,Service_cable_connections4.png,Service_cable_connections5.png,Service_cable_connections6.png Connections installed for conductors located outdoors are required to be rated for use in wet location. Connections between neutral supported cable conductors and grounded service conductors are required to be of the compression type. Service cables are not permitted to be spliced in boxes that contain other conductors. These requirements are intended to prevent connections from becoming damaged by exposure to weather, to ensure a solid connection for the grounded service conductor, and to prevent service conductors from contacting other conductors. This installation of a 30A 120/240V overhead service installed to provide power to an office at a mill site had service conductor connections between neutral supported cable and teck90 cable on the exterior of the building that were made using twist on wire connectors that wer | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Service_cable_connections2.png | file://x:/photopub/docs/0000000619/fb916b0b-f27f-4220-b774-6d383f600871.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb48671_9c20_438b_b6e3_dbc7c2127fe3
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened7.png | file://x:/photopub/docs/0000000619/35e2faa4-4018-4ddf-8d5c-e8a9fce5cde6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
EDIN-838213-2017 | ED-423359-2016 | 6/15/2017 2:16:39 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED025 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | 3 | 3 | #Hoistway_opening_from_the_roof_level1.png,Hoistway_opening_from_the_roof_level2.png The Protective ventilation Covers installed on the building protect the open areas of the elevator openings of the elevator hoistway. During a Construction Use Assessment it was found the opening in the hoistway was not protected. This opening is directly over the very top of the hoistway and poses a serious fall hazard into the hoistway to anyone working in the area. It was found that the General Contractor failed to install any protection over the opening. This newly constructed 14 stop MRL traction elevator is located in a residential building. | 3 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | Hoistway_opening_from_the_roof_level1.png | file://x:/photopub/docs/0000000616/f06a557f-fdf5-42b8-abfc-60149334ac96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41dbba56_d7db_4e18_88ad_d6e932d0fc82
EDIN-838213-2017 | ED-423359-2016 | 6/15/2017 2:16:39 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED025 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | 3 | 3 | #Hoistway_opening_from_the_roof_level1.png,Hoistway_opening_from_the_roof_level2.png The Protective ventilation Covers installed on the building protect the open areas of the elevator openings of the elevator hoistway. During a Construction Use Assessment it was found the opening in the hoistway was not protected. This opening is directly over the very top of the hoistway and poses a serious fall hazard into the hoistway to anyone working in the area. It was found that the General Contractor failed to install any protection over the opening. This newly constructed 14 stop MRL traction elevator is located in a residential building. | 3 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | Hoistway_opening_from_the_roof_level2.png | file://x:/photopub/docs/0000000616/53e6ef8c-a04c-423c-a890-035fa1f0f689.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41dbba56_d7db_4e18_88ad_d6e932d0fc82
ELIN-860166-2017 | EL-552600-2017 | 7/25/2017 8:39:09 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #No_mechanical_protection.png At an existing single family dwelling, a new 200amp 120/240volt 1phase service is being installed at the new garage location with the mechanical protection on the consumers service cable not in place. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | No_mechanical_protection.png | file://x:/photopub/docs/0000000635/4508000c-9070-4133-97bd-9ec319ef965b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72aafa1a_942c_449c_bb5e_f47776b68a97
ELIN-834893-2017 | EL-531719-2017 | 6/13/2017 11:59:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Mechanical protection not provided for service conduit or cables. These cables are at risk of damage from nails and screws. This is a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | A4.png | file://x:/photopub/docs/0000000615/d98c48ef-44f3-4886-b631-a753f9fd4828.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43aefb53_e16c_411a_bf41_8507dd3c9ce8
ELIN-834893-2017 | EL-531719-2017 | 6/13/2017 11:59:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Mechanical protection not provided for service conduit or cables. These cables are at risk of damage from nails and screws. This is a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | A2.png | file://x:/photopub/docs/0000000615/a2f57250-03ac-4ec4-a95a-e22762e9c714.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43aefb53_e16c_411a_bf41_8507dd3c9ce8
ELIN-834893-2017 | EL-531719-2017 | 6/13/2017 11:59:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Mechanical protection not provided for service conduit or cables. These cables are at risk of damage from nails and screws. This is a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | A3.png | file://x:/photopub/docs/0000000615/17592d67-3706-4e4f-aae8-cec2d2219a28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43aefb53_e16c_411a_bf41_8507dd3c9ce8
ELIN-834893-2017 | EL-531719-2017 | 6/13/2017 11:59:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Mechanical protection not provided for service conduit or cables. These cables are at risk of damage from nails and screws. This is a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | A1.png | file://x:/photopub/docs/0000000615/27699de4-8ae2-417e-a8f7-e22864bbdc50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43aefb53_e16c_411a_bf41_8507dd3c9ce8
BPVOP-849638-2017 | UW-554038-2017 | 3/30/2017 | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 4 | #5.png During assessment, I found that the set relief pressure of a safety relief valve was 200 psig where as the attached compressed air tank maximum allowable working pressure was 170 psig. There is a possibility that during an overpressure condition, the safety relief valve will not protect the pressure vessel and it may lead to a catastrophic failure/rupture. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 5.png | file://x:/photopub/docs/0000000624/47340490-bbbb-4db8-9629-07231e6474f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa115e3e_7574_4e81_9cf4_e6f5f6dc5b8a
ELIN-824453-2017 | EL-508092-2017 | 6/20/2017 4:13:49 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Locknuts_and_cable_connectors_not_tightened1.png,Locknuts_and_cable_connectors_not_tightened2.png,Locknuts_and_cable_connectors_not_tightened3.png,Locknuts_and_cable_connectors_not_tightened4.png,Locknuts_and_cable_connectors_not_tightened5.png,Locknuts_and_cable_connectors_not_tightened6.png,Locknuts_and_cable_connectors_not_tightened7.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and preventing metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a newly upgraded 800A 120/208V 3 phase service and sub-service equipment for a comm | 3 | Continuity Bonding; method for equipment is not adequate. | Locknuts_and_cable_connectors_not_tightened6.png | file://x:/photopub/docs/0000000619/bdddb696-d97b-450f-970a-b8f414f8063a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e8c935a_a298_4b9e_8165_2f223b9f67f6
ELIN-846420-2017 | EL-551480-2017 | 7/19/2017 12:51:44 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #Receptacles__not_to_spacing_requirement.png Receptacles for a renovated kitchen have not been spaced to allow for connection of standard household appliances that operate at 120 volts and 15 amps. This can lead to the use of extension cords and lead to injury to persons or damage to property | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Receptacles__not_to_spacing_requirement.png | file://x:/photopub/docs/0000000633/96115c6b-86e6-4ff2-8cc3-2e6c5686beb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a75f245_f122_43fb_9622_a392ffc55578
BPVOP-838313-2017 | 4140486 | 6/14/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_low_water_cut_out.png No low water cut out provided on outlet boiler piping to shut off burner when boiler runs out of water level. Low-water will have burner flame impinge upon metal and cause metal to overheat and melt down causing possible uncontrolled release of energy, which will cause equipment damage and possible injury to personnel in close proximity. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_low_water_cut_out.png | file://x:/photopub/docs/0000000616/3ba11fd9-0ce0-4966-a0ed-a569910ce969.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__834c00e1_c8db_4334_8058_99a2b816bb85
GAUP-837835-2017 | UW-547344-2017 | 6/15/2017 4:49:12 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 | #Unstable.png Propane cylinder moved and installed on pallet and unstable ground beside open construction hole. Cylinder could fall into new cleared footings damaging tank or injuring people | 2 | Container not set upon compliant base | Unstable.png | file://x:/photopub/docs/0000000617/33353143-4c9f-47dd-8cd1-fc8dc0fbfb8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0ba12f0_b00f_429c_88d2_c0819b72871b
ELIN-826854-2017 | UW-536428-2017 | 5/31/2017 1:55:50 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Bare_live_parts1.png,Bare_live_parts2.png,Bare_live_parts3.png Bare live parts were exposed to accidental contact. This could lead to a shock hazard or potential fire. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Bare_live_parts2.png | file://x:/photopub/docs/0000000608/bb66c79b-66fb-4c92-bc65-c2c3c220d2e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95d0a921_a663_4283_bcb1_9d9ba85e66bd
ELIN-826854-2017 | UW-536428-2017 | 5/31/2017 1:55:50 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Bare_live_parts1.png,Bare_live_parts2.png,Bare_live_parts3.png Bare live parts were exposed to accidental contact. This could lead to a shock hazard or potential fire. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Bare_live_parts3.png | file://x:/photopub/docs/0000000608/d413dde6-a302-49e0-8ab3-64681f6ebab4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95d0a921_a663_4283_bcb1_9d9ba85e66bd
ELIN-826854-2017 | UW-536428-2017 | 5/31/2017 1:55:50 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Bare_live_parts1.png,Bare_live_parts2.png,Bare_live_parts3.png Bare live parts were exposed to accidental contact. This could lead to a shock hazard or potential fire. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Bare_live_parts1.png | file://x:/photopub/docs/0000000608/f8f39e1c-60bd-4ef0-a397-a7ea85532fc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95d0a921_a663_4283_bcb1_9d9ba85e66bd
GAUP-831796-2017 | UW-543585-2017 | 6/9/2017 7:39:57 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Boiler.png IBC boiler in operation with combustion air disconnected from appliance and resting on top of the boiler. Insufficient air for boiler operation. Boiler had malfunctioned before arriving onsite, display shows high limit safety tripped. Got contractor to shut down appliance and lock out breaker as no electrical disconnect switch exists. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Boiler.png | file://x:/photopub/docs/0000000613/a2b04b7b-f3e9-40a9-bec7-b0ce603cd46a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__090849d7_e3c4_4d94_8308_1fb3ae55b02f
ELHE-850117-2017 | HE-554268-2017 | 7/4/2017 3:57:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #71.png,72.png,73.png,74.png,75.png A 3C/ 4/0 ACWU is fed off a 1200 Amp fused disconnect and gutter without over current protection. 4/0 ACWU maximum ampacity is 180 Amps. This conductor is unsupported in the electrical room and unprotected where it enters and exits the underground portion of the trench. This conductor is exposed to mechanical damage on the exterior of an outbuilding. This is a shock hazard if the conductor is damaged by an individual. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 73.png | file://x:/photopub/docs/0000000625/5391cca9-d750-4d1b-810f-0e0c741b131e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18bf324f_3f82_4925_b428_0437478ae661
ELHE-850117-2017 | HE-554268-2017 | 7/4/2017 3:57:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #71.png,72.png,73.png,74.png,75.png A 3C/ 4/0 ACWU is fed off a 1200 Amp fused disconnect and gutter without over current protection. 4/0 ACWU maximum ampacity is 180 Amps. This conductor is unsupported in the electrical room and unprotected where it enters and exits the underground portion of the trench. This conductor is exposed to mechanical damage on the exterior of an outbuilding. This is a shock hazard if the conductor is damaged by an individual. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 72.png | file://x:/photopub/docs/0000000625/fcaa6d4c-a417-483b-9fa2-d94f3804c78d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18bf324f_3f82_4925_b428_0437478ae661
ELOP-841605-2017 | 5880 | 7/24/2017 2:48:39 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound Panel missing | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 2 | #G.png Unused openings in electrical equipment have not been filled. Duct tape was used in place of a proper metal panel. This is a fire hazard as duct tape would not hold an explosive electrical fire should it occur. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | G.png | file://x:/photopub/docs/0000000635/c9058464-00b2-405d-93dc-44129a7db8f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30A2426A_4972_4E77_8A92_560E1AC51294
ELIN-815056-2017 | UW-533575-2017 | 5/15/2017 9:02:05 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound As found work when the exterior cover was removed. Load side metre base jaws are electrically energized. | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #as_found_work1.png,as_found_work2.png Owner has made electrical modifications to the electrical system creating a shock hazard whereby someone could accidentally touch the metre base and be electrocuted. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | as_found_work2.png | file://x:/photopub/docs/0000000602/c916f41f-bcaf-4758-9cc5-b55c731a9e2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26487593_3505_450c_bed2_2977f9df18b6
ELIN-815056-2017 | UW-533575-2017 | 5/15/2017 9:02:05 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Three conductor number two, aluminum nonmetallic sheath cable fed from temporary construction service to the load side of the house or base | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #as_found_work1.png,as_found_work2.png Owner has made electrical modifications to the electrical system creating a shock hazard whereby someone could accidentally touch the metre base and be electrocuted. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | as_found_work1.png | file://x:/photopub/docs/0000000602/a3dabf5b-6801-42a5-aaf5-0e3d199e2dc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26487593_3505_450c_bed2_2977f9df18b6
ELHE-850117-2017 | HE-554268-2017 | 7/4/2017 3:57:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #71.png,72.png,73.png,74.png,75.png A 3C/ 4/0 ACWU is fed off a 1200 Amp fused disconnect and gutter without over current protection. 4/0 ACWU maximum ampacity is 180 Amps. This conductor is unsupported in the electrical room and unprotected where it enters and exits the underground portion of the trench. This conductor is exposed to mechanical damage on the exterior of an outbuilding. This is a shock hazard if the conductor is damaged by an individual. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 75.png | file://x:/photopub/docs/0000000625/b20878c4-06e1-462f-a04a-42750a22df09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18bf324f_3f82_4925_b428_0437478ae661
ELHE-850117-2017 | HE-554268-2017 | 7/4/2017 3:57:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #71.png,72.png,73.png,74.png,75.png A 3C/ 4/0 ACWU is fed off a 1200 Amp fused disconnect and gutter without over current protection. 4/0 ACWU maximum ampacity is 180 Amps. This conductor is unsupported in the electrical room and unprotected where it enters and exits the underground portion of the trench. This conductor is exposed to mechanical damage on the exterior of an outbuilding. This is a shock hazard if the conductor is damaged by an individual. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 74.png | file://x:/photopub/docs/0000000625/d50c7b12-5538-4da2-951d-ffffe0b911b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18bf324f_3f82_4925_b428_0437478ae661
ELHE-850117-2017 | HE-554268-2017 | 7/4/2017 3:57:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Unfused conductor fed from 1200 Amp system | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #71.png,72.png,73.png,74.png,75.png A 3C/ 4/0 ACWU is fed off a 1200 Amp fused disconnect and gutter without over current protection. 4/0 ACWU maximum ampacity is 180 Amps. This conductor is unsupported in the electrical room and unprotected where it enters and exits the underground portion of the trench. This conductor is exposed to mechanical damage on the exterior of an outbuilding. This is a shock hazard if the conductor is damaged by an individual. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 71.png | file://x:/photopub/docs/0000000625/a76138c5-f266-42a6-afe6-8e47c755b071.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18bf324f_3f82_4925_b428_0437478ae661
ELHE-861310-2017 | HE-560912-2017 | 7/17/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_.png Open breaker spaces on an energized panel leaving exposed electrical parts and a potential shock hazard in a locked electrical room. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_.png | file://x:/photopub/docs/0000000632/10f300d3-6bf8-469c-a6f9-49f8e4167f65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80082fb2_04d3_46e4_a530_eca8c2ad26d6
ELIN-822136-2017 | EL-537629-2017 | 5/30/2017 10:21:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | #Transformer_clearance1.png,Transformer_clearance2.png,Transformer_clearance3.png A dry type transformer is located inside a building within 300 mm of combustible surfaces on 2 sides. This condition could lead to a potential fire hazard. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Transformer_clearance3.png | file://x:/photopub/docs/0000000607/3495d151-117a-4516-a2ec-d980a2e12474.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__770c86f9_abe8_4a08_b136_5842285ab5ec
ELIN-822136-2017 | EL-537629-2017 | 5/30/2017 10:21:29 AM | ASSESS: EL: Service Connection | png | #asFound 240 and 180mm clearance from osb and ply wood walls. | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | #Transformer_clearance1.png,Transformer_clearance2.png,Transformer_clearance3.png A dry type transformer is located inside a building within 300 mm of combustible surfaces on 2 sides. This condition could lead to a potential fire hazard. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Transformer_clearance1.png | file://x:/photopub/docs/0000000607/f7342ba2-53bc-403e-87b5-b3c0a9074867.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__770c86f9_abe8_4a08_b136_5842285ab5ec
ELIN-822136-2017 | EL-537629-2017 | 5/30/2017 10:21:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | #Transformer_clearance1.png,Transformer_clearance2.png,Transformer_clearance3.png A dry type transformer is located inside a building within 300 mm of combustible surfaces on 2 sides. This condition could lead to a potential fire hazard. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | Transformer_clearance2.png | file://x:/photopub/docs/0000000607/8cf5619a-8a92-4feb-84dc-4e7b998f9931.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__770c86f9_abe8_4a08_b136_5842285ab5ec
GAIN-862518-2017 | GA-560640-2017 | 7/25/2017 4:23:43 PM | ASSESS: GA: Final | png | #asFound Temporary hoses no protection | GA052 | Unprotected temporary hose installations | 3 | 3 | #Temp_hoses_no_protection1.png,Temp_hoses_no_protection2.png Found multiple areas with camp Gas Installation where temporary Gas hoses were installed with no protection. A person can trip over high gas pressure hose, break hose and have a high gas pressure leak possibly leading to damage or injury. | 3 | Unprotected temporary hose installations | Temp_hoses_no_protection2.png | file://x:/photopub/docs/0000000635/077162eb-8a82-4090-8014-2e5eb7793638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f96bf82d_bf04_4ed3_a7dd_6f6d4c3423c6
GAIN-862518-2017 | GA-560640-2017 | 7/25/2017 4:23:43 PM | ASSESS: GA: Final | png | #asFound | GA052 | Unprotected temporary hose installations | 3 | 3 | #Temp_hoses_no_protection1.png,Temp_hoses_no_protection2.png Found multiple areas with camp Gas Installation where temporary Gas hoses were installed with no protection. A person can trip over high gas pressure hose, break hose and have a high gas pressure leak possibly leading to damage or injury. | 3 | Unprotected temporary hose installations | Temp_hoses_no_protection1.png | file://x:/photopub/docs/0000000635/9e828f04-3795-431d-a6dc-fca2a6a94138.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f96bf82d_bf04_4ed3_a7dd_6f6d4c3423c6
ELIN-829675-2017 | EL-537467-2017 | 6/6/2017 10:03:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_in_excess_of_1_5m.png Service conductors enter building in excess of 1.5 m. Possibility for fire or shock in event of high fault current. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_in_excess_of_1_5m.png | file://x:/photopub/docs/0000000611/78847937-8cf8-4204-82ef-260f3472749d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f78e7a7_5e2b_4a86_acb6_39afc78f1e4a
ELIN-835668-2017 | EL-522192-2017 | 6/14/2017 11:56:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_run_up_through_floor_in_exposed_location.png Service cables installed in a location where they are subject to mechanical damage may fail and create severe fire or shock hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_run_up_through_floor_in_exposed_location.png | file://x:/photopub/docs/0000000616/d4312dbf-6ba9-4209-8538-e79ba800e0a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfb8e5f4_13f4_461e_a4ef_05358d0a8c8e
GAHE-837716-2017 | HE-547290-2017 | 6/15/2017 7:55:48 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | #Tank.png Propane tank paced by propane supplier installed against a combustible building. Clearances to be maintained to ensure proper access | 3 | Clearance to combustibles not maintained | Tank.png | file://x:/photopub/docs/0000000616/6dd2adcb-132c-4d00-9b89-5885faaf5bb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42c8f7e9_9453_4a00_9c43_92a54d6f8420
ELIN-816142-2017 | EL-534390-2017 | 5/17/2017 10:56:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Main_distbution_energize_with_panel_cover_removed.png 120/240 volt 200 amp panelboard was found with no panel cover and exposed energized parts accessible to persons. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Main_distbution_energize_with_panel_cover_removed.png | file://x:/photopub/docs/0000000602/39da0a6f-08a9-4428-bf5c-7574a79655ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d65c1bee_dc12_4e73_97df_9603d9648998
ELIN-836883-2017 | EL-546776-2017 | 6/15/2017 10:23:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cable/service conduit and propane tanks located in the driveway of a commercial bakery. This is a hazard as the service conductors and tanks are subject to mechanical damage which could result in a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A2.png | file://x:/photopub/docs/0000000617/418a451e-6bc3-4a9d-b191-1cfac228022f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b623b8c0_7ff7_4293_ba90_01ba930dd42b
ELIN-836883-2017 | EL-546776-2017 | 6/15/2017 10:23:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cable/service conduit and propane tanks located in the driveway of a commercial bakery. This is a hazard as the service conductors and tanks are subject to mechanical damage which could result in a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A3.png | file://x:/photopub/docs/0000000617/ab1723ea-8cdf-4af0-8862-52c99e300b0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b623b8c0_7ff7_4293_ba90_01ba930dd42b
ELIN-836883-2017 | EL-546776-2017 | 6/15/2017 10:23:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cable/service conduit and propane tanks located in the driveway of a commercial bakery. This is a hazard as the service conductors and tanks are subject to mechanical damage which could result in a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A4.png | file://x:/photopub/docs/0000000617/ed65f73a-c87b-4cb4-9c3e-8c9503a6b7ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b623b8c0_7ff7_4293_ba90_01ba930dd42b
ELIN-836883-2017 | EL-546776-2017 | 6/15/2017 10:23:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cable/service conduit and propane tanks located in the driveway of a commercial bakery. This is a hazard as the service conductors and tanks are subject to mechanical damage which could result in a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A1.png | file://x:/photopub/docs/0000000617/23ed13f4-fd6d-44c8-934f-0b1b3c82d8ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b623b8c0_7ff7_4293_ba90_01ba930dd42b
ELIN-825954-2017 | EL-517113-2017 | 5/31/2017 12:16:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #51.png,52.png Expansion joints on main 400 Amp feeder conduits have not been installed correctly. By not setting the expansion joint to the proper position (1/2 way) the expansion joint will not function properly. In this situation if the pole settles the PVC pipe will be damaged leaving exposed conductors. This is a shock hazard to any individuals in the area. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 52.png | file://x:/photopub/docs/0000000608/6f0c6763-582b-4859-8e36-f47192d6fae0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e75dd78_4bfb_4ad1_b440_c926abb5ac02
ELIN-825954-2017 | EL-517113-2017 | 5/31/2017 12:16:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #51.png,52.png Expansion joints on main 400 Amp feeder conduits have not been installed correctly. By not setting the expansion joint to the proper position (1/2 way) the expansion joint will not function properly. In this situation if the pole settles the PVC pipe will be damaged leaving exposed conductors. This is a shock hazard to any individuals in the area. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 51.png | file://x:/photopub/docs/0000000608/75d7e26d-50e9-4fd0-ba3f-098118672f8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e75dd78_4bfb_4ad1_b440_c926abb5ac02
ELIN-823845-2017 | EL-515805-2017 | 6/1/2017 2:04:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #100A_rated_main_service_box.png The existing 100A main service supplies two fully equipped dwelling units which exceeds its capacity | 3 | Protection and control Loading of distribution equipment exceeded. | 100A_rated_main_service_box.png | file://x:/photopub/docs/0000000609/32c404d9-4f60-4cae-b7b8-c874d3208416.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cdd5112_b5b4_4e9d_a300_f54828b4cb62
GAIN-790654-2017 | GA-497269-2017 | 6/14/2017 6:59:34 PM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Common_venting_oversized.png 6" common vent is used to vent two appliances. On appliance has been removed from common vent, common vent is now oversized due to the other appliance requiring a 4" vent. Under certain circumstances flue gases may cool too quick and fall back down vent, entering home through draft hood of appliance, possible carbon monoxide poisoning may occur to occupants of home | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Common_venting_oversized.png | file://x:/photopub/docs/0000000616/01487935-8160-4206-863c-afa9a3aff826.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0471ddd2_f5c9_44d3_a779_43481a3ffbcc
BPVOP-864232-2017 | 2271384 | 7/24/2017 1:19:29 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SAFETY_VALVE.png Upon assessment of Low Pressure steam Boiler with Heating surface area of 37 square meters, it was determined that safety valve has exceeded the required 5year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and/or steam and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE.png | file://x:/photopub/docs/0000000634/b5733dc9-ae8a-432a-ba0d-84e5c00e46b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14248115_5b56_4dbd_958a_7a75cf15e35c
BPVOP-864227-2017 | 2271382 | 7/24/2017 11:20:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Valve_1.png,Safety_Valve_2.png Upon assessment of Low Pressure steam Boiler with Heating surface area of 237 square meters, it was determined that safety valves have exceeded the required 5year interval for servicing/replacement. Failure to have safety valves serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and/or steam and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Valve_2.png | file://x:/photopub/docs/0000000634/2ac4bb05-d115-4c86-b7ea-c10e9c4bffac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5dd7f1a_aaaa_476c_aff5_ea5f4966be33
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png | file://x:/photopub/docs/0000000622/96bddd04-129d-4a75-9736-6c9525ff4b43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png | file://x:/photopub/docs/0000000622/11164f03-e72d-4c4b-801e-d86ec9d042de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-854746-2017 | EL-556244-2017 | 7/11/2017 5:02:59 PM | ASSESS: EL: Service Connection | png | #asFound Temporary construction enclosure is not weather proof. | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | #G.png Temporary construction enclosure is not weatherproof enclosure as required by NO: IB-EL-2016-03. This is a shock hazard as moisture can enter the Type 1 rated equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | G.png | file://x:/photopub/docs/0000000629/ff1a265f-989f-407f-8f68-94c4accd4490.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37697248_f54e_4d23_8e5a_968d3ddf52a2
ELIN-828694-2017 | EL-458835-2016 | 6/5/2017 1:01:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #O.png AC90 cable not terminated properly. Conductors are subject to damage. This is a Fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | O.png | file://x:/photopub/docs/0000000611/ad840eb6-2421-4428-82dd-3b779d6f9472.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b60ffbb_94de_43ce_825b_76e3a8834406
ELIN-829649-2017 | EL-524588-2017 | 6/5/2017 3:35:41 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #A1.png,A2.png | 0 | No Created Hazard Identified | A2.png | file://x:/photopub/docs/0000000611/bb49c5c1-b254-4981-80cf-73509bf243e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c08e7ce_57c6_48de_9ead_f5f92a9fcd94
ELIN-829649-2017 | EL-524588-2017 | 6/5/2017 3:35:41 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #A1.png,A2.png | 0 | No Created Hazard Identified | A1.png | file://x:/photopub/docs/0000000611/414f94c5-57fe-44cb-b94c-2f3cf6d327e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c08e7ce_57c6_48de_9ead_f5f92a9fcd94
EDIN-836651-2017 | ED-435006-2016 | 6/14/2017 8:02:33 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | #Door_open_and_close_button.png The Door Open and Door Close Buttons for both the front and rear doors are used during a Fire Emergency Operation (FEO) to operate the doors. During an acceptance assessment it was found the Door Open and Door Close Button failed to operate on both the front and rear doors. Without the proper operation of these buttons it would not be possible for firefighters to properly use the elevator if needed for a FEO. Without the use of this elevator if needed for an emergency, people's lives will be put at risk. It was found the elevator contractor failed to have enough time to properly test the elevator and correct the operation of the Door Open and Close Buttons. This 8 stop MRL traction elevator is located in a newly constructed residential building. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Door_open_and_close_button.png | file://x:/photopub/docs/0000000616/eef70a12-4a28-40e6-bb82-4a2ab0aec13f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc8d64ea_42a8_4a98_aca5_67ae27bac721
ELHE-827260-2017 | HE-540798-2017 | 5/31/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Service conductors after the dwelling had been relocated. | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #Pic7.png -Existing single family dwelling was relocated approximately 12 feet to the East, raised one level and placed on a new concrete foundation. -The existing energized overhead service was relocated along with the dwelling causing the overhead service triplex to have excessive slack and is now in contact with the neighbors roof. -Height of sagging service conductors are not mechanically protected as there is approximately a 10 foot loop directly above meterbase. -New wood trusses and framing have been installed causing the service conductor to run inside the dwelling exterior wall and back out. - the relocation of the dwelling and service conductors have altered the installation and that the conductors are unfused from hydro they may be mechanically damaged causing electrical shock or fire hazards. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Pic7.png | file://x:/photopub/docs/0000000609/4326bdb8-4c37-4c63-9b4b-8a63c0e9962d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f1b1f85_bada_4a0e_9e89_19ab915cafbf
GAIN-832166-2017 | GA-282621-2015 | 6/13/2017 12:31:11 PM | ASSESS: GA: Final | png | #asFound Propane cylinder without vehicle protection in place. | GA024 | No protection Low traffic | 3 | 3 | #Propane_cylinder.png Propane cylinder does not have vehicle protection in place to prevent a vehicle from sliding into cylinder. | 3 | No protection Low traffic | Propane_cylinder.png | file://x:/photopub/docs/0000000616/d5583afd-c32a-4ebc-8ea0-eed883f80c70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad30871a_dbcf_445d_a3f4_88141fc25add
ELIN-837246-2017 | EL-546320-2017 | 6/15/2017 2:52:01 PM | ASSESS: EL: Final | png | #asFound DB2 conduit and fittings are used above grade level. This is a thin wall conduit. | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #DB2_.png Service connection for new temporary construction service. The thin wall conduit that provides mechanical protection for the service conductors below ground has been used above grade level. This does not provide adequate mechanical protection for the service conductors. The unfused service conductors can be exposed by damage to this thin wall conduit. Shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | DB2_.png | file://x:/photopub/docs/0000000616/242d0ae9-e5d1-46de-b876-92265ee47dc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c81197b1_0a5f_4342_a920_d9beac9287fc
GAIN-798434-2017 | GA-523657-2017 | 5/7/2017 5:02:17 PM | ASSESS: GA: Final | png | #asFound . | GA024 | No protection Low traffic | 3 | 3 | #unprotected_propane_containers.png Propane container with no vehicle protection in a low traffic area. Propane containers must be protected to prevent a vehicle from contacting the container and damaging the tank or piping. A damaged container of piping could cause an uncontrolled release of gas. | 3 | No protection Low traffic | unprotected_propane_containers.png | file://x:/photopub/docs/0000000605/19499dc6-b71b-4b1d-bfb0-10632b15c0bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e522891_7310_4c36_a5a0_048c8ad35a5c
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png | file://x:/photopub/docs/0000000622/f15ad775-95e5-4072-9aba-53fa7798f752.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png | file://x:/photopub/docs/0000000622/6cca6597-9728-48c6-935c-99c4dc0b0051.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png | file://x:/photopub/docs/0000000622/61a19009-6387-465c-ad00-63b694c60971.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
GAIN-828956-2017 | GA-525424-2017 | 6/6/2017 9:36:19 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Deep_fryer.png Commercial deep fat fryer installed next to an open flame burner without a dividing shield. This could lead to a grease fire. | 3 | Clearance to combustible not met | Deep_fryer.png | file://x:/photopub/docs/0000000611/c16b72c7-54da-4f2a-b080-9f5fc14d56f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__906772a0_530c_4057_8983_4358477f7805
GAIN-825446-2017 | GA-536585-2017 | 6/5/2017 3:54:33 PM | ASSESS: GA: Final | png | #asFound | GA143 | Open junction box with line voltage not accessible to public | 3 | 3 | #G_D_PLUM.png Cover plate not installed on receptacle for gas range.(120 volts) Risk of accidental contact with exposed conductors. Shock hazard. | 3 | Open junction box with line voltage not accessible to public | G_D_PLUM.png | file://x:/photopub/docs/0000000611/e8d8cfb9-a4a0-4204-ac00-50ea354a738b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f9420f_1db4_4631_be05_1b06ba97af8b
ELIN-827858-2017 | EL-499789-2017 | 6/6/2017 9:28:33 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Outlet_not_supported_on_both_sides.png Outlets box is not supported on both sides. This could be a hazard if the outlet box was to fall off or come apart from the wooden stud that it is secured to on one side. This could cause the conductors and outlet box devices to short. This would cause nuisance tripping. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Outlet_not_supported_on_both_sides.png | file://x:/photopub/docs/0000000611/e2908c74-c435-482b-bd47-b46bef899d10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54e2718a_8206_41de_8d86_29a7ab653fed
ELIN-842944-2017 | EL-317625-2015 | 6/27/2017 12:39:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms1.png,No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms2.png,No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of new receptacles and circuits in a new house was not provided with AFCI protection. The branch circuit was for 15A 120V receptacles in two bedrooms. This is a potential fire hazard if an arcing fault occurs on these receptacles or branch circuit from the branch circuit wiring or the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms3.png | file://x:/photopub/docs/0000000622/1dfa1661-3caa-4993-924e-34ef903d2552.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5002495f_e6c1_418e_a49b_e744ef7a3052
ELIN-842944-2017 | EL-317625-2015 | 6/27/2017 12:39:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms1.png,No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms2.png,No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of new receptacles and circuits in a new house was not provided with AFCI protection. The branch circuit was for 15A 120V receptacles in two bedrooms. This is a potential fire hazard if an arcing fault occurs on these receptacles or branch circuit from the branch circuit wiring or the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms2.png | file://x:/photopub/docs/0000000622/bbaf947c-87c0-4f42-8d1e-c2d583c21780.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5002495f_e6c1_418e_a49b_e744ef7a3052
GAIN-846992-2017 | GA-549513-2017 | 7/4/2017 11:18:23 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Volrath.png Fuel rich flame on grill. Possible incomplete combustion caused excessive pressure/air shutter setting. Risk of exposure to carbon monoxide | 3 | Appliance not installed according to installation instructions | Volrath.png | file://x:/photopub/docs/0000000624/4dd76e2c-d011-4414-bc62-aa43b4bc4193.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bf79913_1a30_45ba_a8dd_6e130366b65e
ELHE-821968-2017 | HE-536639-2017 | 5/25/2017 8:33:25 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #Meter2.png It was declared by renter that current meter base was left exposed the entire time she lived there 4.5 years. The hazard is shock and it was very probable an incident would have occurred if not corrected. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Meter2.png | file://x:/photopub/docs/0000000606/18d94818-e55a-4df9-a533-51814833937c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4d09c7_36e0_4c0d_b3d9_5131331604b4
ELIN-824452-2017 | EL-536945-2017 | 5/29/2017 2:11:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #Undersized_service_conductors1.png,Undersized_service_conductors2.png,Undersized_service_conductors3.png Service conductors are undersized for the commercial/industrial application which they are serving. This could be a possible fire hazard if the service conductors exceeded their ratings because the overcurrent device protecting them is sized to protect larger conductors. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Undersized_service_conductors3.png | file://x:/photopub/docs/0000000607/124fa99c-edc7-43e2-a7c5-3e8503bb7279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5565889_d168_4aee_b1d8_73a9919bb654
ELIN-824452-2017 | EL-536945-2017 | 5/29/2017 2:11:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #Undersized_service_conductors1.png,Undersized_service_conductors2.png,Undersized_service_conductors3.png Service conductors are undersized for the commercial/industrial application which they are serving. This could be a possible fire hazard if the service conductors exceeded their ratings because the overcurrent device protecting them is sized to protect larger conductors. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Undersized_service_conductors1.png | file://x:/photopub/docs/0000000607/1f473372-f32e-4115-ba08-c31d93307c16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5565889_d168_4aee_b1d8_73a9919bb654
ELIN-824452-2017 | EL-536945-2017 | 5/29/2017 2:11:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #Undersized_service_conductors1.png,Undersized_service_conductors2.png,Undersized_service_conductors3.png Service conductors are undersized for the commercial/industrial application which they are serving. This could be a possible fire hazard if the service conductors exceeded their ratings because the overcurrent device protecting them is sized to protect larger conductors. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Undersized_service_conductors2.png | file://x:/photopub/docs/0000000607/72f7ffef-a72f-4d28-b0b9-c29c260cb1e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5565889_d168_4aee_b1d8_73a9919bb654
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png | file://x:/photopub/docs/0000000622/cdb26b9f-90af-490d-8dee-fbed260c3994.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-823925-2017 | EL-532705-2017 | 5/29/2017 12:29:16 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Copper gas line coming into the house has not been bonded. | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Gas_bond.png Rough wire of new single-family dwelling. The metallic gas line has not had a bonding conductor installed to allow overcurrent devices to trip if voltage is impressed on the metallic gas line. Shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_bond.png | file://x:/photopub/docs/0000000607/fb286b9f-0a0f-4211-93a0-0c26e964de1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56d1b1c8_1e69_440f_a684_856e7014b352
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png | file://x:/photopub/docs/0000000622/53cb4d0d-fd81-4123-b8fc-2c37c5da77c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png | file://x:/photopub/docs/0000000622/23e4d119-f20d-4e94-a313-7cc80b521843.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
ELIN-842944-2017 | EL-317625-2015 | 6/27/2017 12:39:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms1.png,No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms2.png,No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms3.png The code requires most receptacle branch circuits to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation of new receptacles and circuits in a new house was not provided with AFCI protection. The branch circuit was for 15A 120V receptacles in two bedrooms. This is a potential fire hazard if an arcing fault occurs on these receptacles or branch circuit from the branch circuit wiring or the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_protection_for_receptacles_and_circuit_in_two_bedrooms1.png | file://x:/photopub/docs/0000000622/9b4d11be-f9e7-430d-86f9-df0803fa433e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5002495f_e6c1_418e_a49b_e744ef7a3052
ELIN-841112-2017 | EL-530851-2017 | 6/27/2017 5:53:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil2.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil3.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil4.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil5.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil6.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil7.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil8.png,350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil9.png Conductor termination lugs in electrical equipment are required to be sized and approved for the conductor size and type that are terminated to them. This is required to ensure a solid conductor connection to the equipment is made without damage to the conductor or the termination lug. When conductors that are larger than the rated size of termin | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 350_Kcmil_conductors_terminated_into_lugs_rated_for_maximum_250_Kcmil1.png | file://x:/photopub/docs/0000000622/53593a14-f9bd-4c91-8faf-98482aa456cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d162968_3dcd_42d4_8126_b3009c5e77e1
BPVOP-845402-2017 | 2255317 | 6/27/2017 9:46:59 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Copied certificates | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Certificates.png The heating plant is not being supervised after normal working hours (day shift) by a 4th Class Engineer as required by the Power Engineers Regulations. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Certificates.png | file://x:/photopub/docs/0000000623/90f4a022-25d5-4593-acb4-9ff2b1d0c53f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e05df79_bf9c_4089_a8af_bcab7d4103ef
ELIN-845189-2017 | EL-551236-2017 | 6/27/2017 1:33:29 PM | ASSESS: EL: Service Connection | png | #asFound Photo of the neutral connection in the meter base. The neutral buss in the meter base has not been isolated from ground as required. It is connected to the meter base container by a metal mounting strap. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Neutral_.png Service connection for new pole mounted irrigation service. The meter base used for revenue metering has been installed after the service switch and the neutral conductor has not been isolated from ground as required. Therefore, in the event of a fault, the neutral conductor may not be able to function to clear the fault. Shock and fire hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Neutral_.png | file://x:/photopub/docs/0000000622/7bf1d61d-453a-456e-babf-4daeadd2ae08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__914f2a27_c566_4ac6_a14e_73e5cdee6222
ELHE-844774-2017 | HE-550928-2017 | 6/27/2017 12:13:34 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Open splices or nonmetallic sheeted cable in the basement of a single family dwelling. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Open_splices.png Respond to request from the City of Chilliwack for assistance with a single family dwelling. Open splices on wiring in a basement ceiling of a single family dwelling with numerous occupants. Shock and fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Open_splices.png | file://x:/photopub/docs/0000000622/bcd5f728-4315-41b8-8ad9-f94d6b7db9b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06d5f890_7ee4_49d0_8ef0_4c5d7246d614
ELHE-860114-2017 | HE-555298-2017 | 7/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_Plates1.png,No_Plates2.png,No_Plates3.png,No_Plates4.png Receptacles and switches in a dwelling are required to be covered by a plate. This to keep persons from coming in accidental contact with the energized electrical terminals on the side of the device. During a hazard elimination for a dwelling used for as a rental unit, devices throughout the dwelling were found with no cover plates. This is a potential shock hazard for persons that may come in contact with the energized terminals on the devices. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_Plates4.png | file://x:/photopub/docs/0000000632/387c5d50-bf4a-4b59-9a6d-97794ca6a2c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2351708_454c_4b88_8fb3_125da64c688d
ELHE-860114-2017 | HE-555298-2017 | 7/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_Plates1.png,No_Plates2.png,No_Plates3.png,No_Plates4.png Receptacles and switches in a dwelling are required to be covered by a plate. This to keep persons from coming in accidental contact with the energized electrical terminals on the side of the device. During a hazard elimination for a dwelling used for as a rental unit, devices throughout the dwelling were found with no cover plates. This is a potential shock hazard for persons that may come in contact with the energized terminals on the devices. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_Plates2.png | file://x:/photopub/docs/0000000632/f9011123-bbe7-4ec5-b1de-f4873927feb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2351708_454c_4b88_8fb3_125da64c688d
ELHE-860114-2017 | HE-555298-2017 | 7/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_Plates1.png,No_Plates2.png,No_Plates3.png,No_Plates4.png Receptacles and switches in a dwelling are required to be covered by a plate. This to keep persons from coming in accidental contact with the energized electrical terminals on the side of the device. During a hazard elimination for a dwelling used for as a rental unit, devices throughout the dwelling were found with no cover plates. This is a potential shock hazard for persons that may come in contact with the energized terminals on the devices. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_Plates1.png | file://x:/photopub/docs/0000000632/a6eaf705-1074-4a47-a61c-f0adecd4e186.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2351708_454c_4b88_8fb3_125da64c688d
ELHE-860114-2017 | HE-555298-2017 | 7/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #No_Plates1.png,No_Plates2.png,No_Plates3.png,No_Plates4.png Receptacles and switches in a dwelling are required to be covered by a plate. This to keep persons from coming in accidental contact with the energized electrical terminals on the side of the device. During a hazard elimination for a dwelling used for as a rental unit, devices throughout the dwelling were found with no cover plates. This is a potential shock hazard for persons that may come in contact with the energized terminals on the devices. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_Plates3.png | file://x:/photopub/docs/0000000632/de11e399-828e-4d0d-b886-20aa91a75a90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2351708_454c_4b88_8fb3_125da64c688d
ELIN-824442-2017 | EL-519316-2017 | 5/29/2017 1:14:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P51.png,P52.png,P53.png,P54.png,P55.png,P56.png,P57.png Mechanical damage to cables may cause fire,shock, injury or fatality. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P56.png | file://x:/photopub/docs/0000000607/d9f5a269-de80-4eea-a552-68a61f357cbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab2b7009_f692_4bc8_9b6b_9aea9e633032
GAHE-839167-2017 | HE-548094-2017 | 6/16/2017 1:05:48 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA112 | Leaking or Failing special venting system (Carbon Monoxide present in space) | 5 | 5 | #Vents_in_building.png The as found condition was 3 operational unit heater vent terminations were located inside a building. The as found hazard is products of combustion venting into a structure can lead to deadly CO exposure by occupants of the building | 5 | Leaking or Failing special venting system (Carbon Monoxide present in space) | Vents_in_building.png | file://x:/photopub/docs/0000000617/2901db78-0e74-447f-8868-174894c4e57c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b095d33_9dff_435f_adec_1797f6eda5c7
EDIN-846138-2017 | ED-418743-2016 | 6/27/2017 2:04:36 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #Cwt__.png Proper running clearance for counterweight sling to rail | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Cwt__.png | file://x:/photopub/docs/0000000622/9b652e93-f739-4fec-ad47-2b9cf3d816c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3bc87b7_b9dc_473a_985f_3458d5cdcc06
ELIN-822164-2017 | EL-537355-2017 | 5/25/2017 9:58:59 AM | ASSESS: EL: Service Connection | png | #asFound Plywood supporting Type 3R enclosure | EL000 | No Created Hazard Identified | 0 | 0 | #4.png Type 3R weather proof enclosure is supported with plywood. Plywood is not an approved means of support. This is a shock hazard as the equipment could easily become dislodged from the pole on which it is installed. | 0 | No Created Hazard Identified | 4.png | file://x:/photopub/docs/0000000605/439beb49-b8a6-4a1f-b5c6-0767549920f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a823c1f9_a2ec_4fe7_b761_e281336a756a
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust2.png | file://x:/photopub/docs/0000000634/0e1ffc4e-ac84-43c4-b911-5083cbacc733.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
ELOP-862261-2017 | 464 | 7/20/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Armoured_cables1.png,Armoured_cables2.png Armoured cable not engaged to connector with exposed insulated conductors in wood processing facility. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Armoured_cables1.png | file://x:/photopub/docs/0000000634/53282019-6d8e-4c61-8298-743bc0854ecb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b2fe5be_720f_42c5_8778_65a088578a76
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust3.png | file://x:/photopub/docs/0000000634/8d48daab-1be9-4a07-a971-561d242b99f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust6.png | file://x:/photopub/docs/0000000634/79d1af16-27d5-4b50-8ccc-a47f8652667d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
BPVIN-826573-2017 | UW-540468-2017 | 6/7/2017 2:10:47 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | #Sideways_safety_valve.png Found Safety relief valve installed at the back of the boiler outlet header in the sideways position. Debris from the outlet of the boiler will collect in the sideways mounted inlet forming a blockage that may harden and inhibit or restrict the movement of the safety relief valve. Without the ability of the Safety relief valve to open an unsafe build up of pressure will occur with possible equipment failure and injury to personnel in close proximity. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Sideways_safety_valve.png | file://x:/photopub/docs/0000000612/06dfa9f0-38ab-4e1f-807c-76d9194d8762.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8eb72267_4de9_4bd3_978a_7140cc0537c8
EDIN-822543-2017 | ED-426398-2016 | 5/24/2017 7:18:17 PM | ASSESS: ED IN: Construction Use | png | #asFound There are non-elevator related material stored at the top of the stairs leading to the machine room. The stairs is not mounted to a solid foundation it is floating at the bottom of the stairs. When walking up or down the stairs the stairs will bounce up and down about 2 inches. This situation can cause a person to loose their balance and fall. | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Stairs.png The stairs leading to the machine room is not fastened to a solid foundation. The stair is currently floating in the air. The stair is unstable. A person walking up or down the stairs will bounce up and down about 2" which will cause a person to loose their balance and fall. The path leading to the machine is also unlit and non-elevator related material being stored at the top of the stairs will cause a person to trip over them and not allow a person to completely open the door to the machine room | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Stairs.png | file://x:/photopub/docs/0000000605/f7250a0f-6057-49c0-8a80-ccbe3d4f852e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4695fba4_0022_4f9e_a6ef_e8e11e3f24d1
ELIN-836929-2017 | EL-546798-2017 | 6/15/2017 11:53:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Main_distribution.png 200 amp, 120/240 volt type 1 main distribution panel installed where panel is subject to outdoor weather elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution.png | file://x:/photopub/docs/0000000617/9abed4a1-dbff-4b39-abb7-6ed66f0445f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__572016bb_4e02_45ca_8a24_e9cf484bb1bd
ELIN-845762-2017 | EL-551578-2017 | 6/28/2017 3:08:07 PM | ASSESS: EL: Final | png | #asFound 20 amp breaker protecting receptacle rated at 15 amps. | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | #Receptacle_breaker.png Service connection for Recreational Vehicle service mounted on pole. Receptacle mounted on pole for vehicle use has had a circuit breaker installed that is too large to protect the device. Overfused. Fire hazard. | 4 | Protection and control Interrupt ratings are not adequate for the installation | Receptacle_breaker.png | file://x:/photopub/docs/0000000622/545e0523-f487-482a-b059-caff12711188.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60d5aac8_beb2_40fe_aa17_2c0d88846b2f
GAIN-849614-2017 | GA-546131-2017 | 7/20/2017 3:08:41 PM | ASSESS: GA: Final | png | #asFound Vent | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Uninsulated_vent.png At time of inspection venting was not protected from freezing this condition could cause furnace to shut down. | 3 | Appliance not installed according to installation instructions | Uninsulated_vent.png | file://x:/photopub/docs/0000000633/647c65bb-ff44-4302-a6e0-f6755e12c039.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b9413cb_8f02_4ace_a939_7283f7567096
GAIN-849372-2017 | GA-510689-2017 | 7/11/2017 2:28:21 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #ABS_fernco_coulping.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | ABS_fernco_coulping.png | file://x:/photopub/docs/0000000629/2c45a813-25d4-439b-b9b4-eb86d6348ecf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__234d7c45_a5a9_4c62_b62f_35f798e7bf7f
BPVOP-849644-2017 | BPV-152718-2014 | 7/3/2017 7:24:36 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Relief_valve.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve.png | file://x:/photopub/docs/0000000624/48e16ed4-1c94-4fc7-b78a-ae572115fab7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__808bbedb_654f_42eb_bd6e_5ec4e37e89cc
BPVOP-849645-2017 | BPV-152717-2014 | 7/3/2017 7:40:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Relief_valve-1.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve-1.png | file://x:/photopub/docs/0000000624/ae3cc624-6a09-460d-aa72-ee6b90d8fd1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d136b03_6b1c_46bb_a0b2_9b8f6ff4a244
BPVOP-849646-2017 | BPV-152473-2014 | 7/3/2017 8:16:18 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #No_service_records.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | No_service_records.png | file://x:/photopub/docs/0000000624/3be1d0b2-9821-4e30-a3b8-44ee73711b54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c12c4e0_22c2_4418_b2e0_42f7ac188f7e
BPVOP-849647-2017 | BPV-152474-2014 | 7/3/2017 8:25:51 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #1.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 1.png | file://x:/photopub/docs/0000000624/71e39c82-412e-47f6-b255-ea9a24feb1ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19512c2a_13af_4c7f_9eb4_6f748e408e7d
ELIN-848052-2017 | EL-543120-2017 | 6/30/2017 10:43:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 4 | #Unfused_200_A.png The main power cable a 200 amp unfused cable between meter and panel is not adequately protected from nail damage. Should this cable be struck with a nail or cut with a tool it can lead to afire. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unfused_200_A.png | file://x:/photopub/docs/0000000624/f0158804-b97a-40c5-8eac-0b91e7a0d451.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dd36cc4_3f7b_4b75_b117_3382a6588eb1
ELIN-866019-2017 | EL-528862-2017 | 7/28/2017 3:35:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Ground_at_meter_base_.png,Neutral_bond_in_panel.png In an electrical service, the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation of a 200A electrical panel for a new dwelling, the bonding strap between the neutral buss and the bonding buss was not removed inside the panel when the neutral conductor had been bonded at the electrical meter. If an electrical fault was to occur inside the dwelling, there is the potential for unbalanced fault currents to flow through the metal of the electrical panel and bonding system. These fault currents are a potential shock hazard for any persons in contact with the electrical system. . | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Ground_at_meter_base_.png | file://x:/photopub/docs/0000000637/194c6ee3-7981-4087-b52f-ee8a7376ae58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9c93358_f8a6_459b_b17e_e81722baebc9
ELIN-866019-2017 | EL-528862-2017 | 7/28/2017 3:35:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Ground_at_meter_base_.png,Neutral_bond_in_panel.png In an electrical service, the grounded service conductor is required to be connected to a ground electrode at the supply side of the service disconnect only. This is to prevent neutral currents from circulating through the bonding system and to carry any unbalanced fault currents back to the source. In this installation of a 200A electrical panel for a new dwelling, the bonding strap between the neutral buss and the bonding buss was not removed inside the panel when the neutral conductor had been bonded at the electrical meter. If an electrical fault was to occur inside the dwelling, there is the potential for unbalanced fault currents to flow through the metal of the electrical panel and bonding system. These fault currents are a potential shock hazard for any persons in contact with the electrical system. . | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bond_in_panel.png | file://x:/photopub/docs/0000000637/9f56b595-ae05-4557-9752-11d55796f862.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9c93358_f8a6_459b_b17e_e81722baebc9
ELIN-829979-2017 | EL-454510-2016 | 6/9/2017 10:38:59 AM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | #In-bonded_metallic_pull_box.png All metallic pull boxes interposed in non-metallic raceway systems must be bonded to prevent electric shock if an energized conductor should make contact | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | In-bonded_metallic_pull_box.png | file://x:/photopub/docs/0000000613/d4065a74-0bca-41e8-b5f4-b17515de699b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c733a0b9_6621_497e_ab31_3e576a21f7b1
ELIN-817766-2017 | EL-525642-2017 | 5/18/2017 1:35:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Open_panel.png This assessment found open panel in a residential home that can creat a shock hazard | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Open_panel.png | file://x:/photopub/docs/0000000603/9d15378f-c921-4ac7-a7e8-ae994ea26c62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32e008aa_5be9_4f58_9188_c30e5d9023d8
ELIN-812066-2017 | EL-523635-2017 | 5/18/2017 1:06:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Unapproved_connector.png At a new single family dwelling location, a 200amp 240volt service was found in an energized state with the consumer service cable installed using an oversized and unapproved cable connector. This can lead to a "Shock Hazard" scenario. Pic attached. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unapproved_connector.png | file://x:/photopub/docs/0000000603/02741348-d03f-4c29-9672-7abb3e53a551.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96cb290c_582e_4e3c_9a23_ce8490e0823d
GAIN-854443-2017 | GA-549640-2017 | 7/10/2017 2:22:48 PM | ASSESS: GA: Rough-In | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Unprotected_copper_tubing_through_masonry.png Copper tubing passing through a masonry wall unprotected. Tubing can be damaged from contact with masonry causing leaks. | 2 | Physical protection of piping and tubing absent. | Unprotected_copper_tubing_through_masonry.png | file://x:/photopub/docs/0000000628/e32acc7c-81fe-4b6e-9d59-737e246c13e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63745fef_15cd_4809_9d18_b71c7dd64716
ELHE-852706-2017 | HE-555756-2017 | 7/10/2017 3:07:30 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cover missing from fixture, this is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A2.png | file://x:/photopub/docs/0000000628/bc3c655e-877f-45b7-af37-5530b954d7aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d82c53_e4bf_4a73_8f1f_fdcd37128802
ELHE-852706-2017 | HE-555756-2017 | 7/10/2017 3:07:30 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cover missing from fixture, this is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A3.png | file://x:/photopub/docs/0000000628/ea3bc46b-c0ee-4035-9885-2beb75049363.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d82c53_e4bf_4a73_8f1f_fdcd37128802
ELHE-852706-2017 | HE-555756-2017 | 7/10/2017 3:07:30 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cover missing from fixture, this is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A4.png | file://x:/photopub/docs/0000000628/90169fd2-e7c3-46ed-8680-0b50eb87e189.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d82c53_e4bf_4a73_8f1f_fdcd37128802
ELHE-852706-2017 | HE-555756-2017 | 7/10/2017 3:07:30 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png Cover missing from fixture, this is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A1.png | file://x:/photopub/docs/0000000628/4a430958-82be-4406-b73c-52d391d573b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d82c53_e4bf_4a73_8f1f_fdcd37128802
EDRI-864062-2017 | ED-542215-2017 | 7/24/2017 9:45:41 AM | ASSESS: ED RI: Initial | png | #asFound Roof hatch on hoist has a safety switch so hoist will not run if hatch is open. Safety switch was not adjusted so hatch could be completely open while hoist running. | ED038 | Non-Safety critical monitoring bypassed or failed: Contractor is not aware of bypass or failure Risk Reg ED-02 | 2 | 2 | #Hatch_open.png Roof hatch on hoist has a safety switch so hoist will not run if hatch is open. Safety switch was not adjusted so hatch could be completely open while hoist running. | 2 | Non-Safety critical monitoring bypassed or failed: Contractor is not aware of bypass or failure Risk Reg ED-02 | Hatch_open.png | file://x:/photopub/docs/0000000634/266b2e9f-25e3-4168-a5d7-d4499d4d7e6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__931c706a_d976_49f5_ab9e_cb7e6b05f24c
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png | file://x:/photopub/docs/0000000632/b062e9d2-da62-43a3-a675-0c553ba36f94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
BPVIN-839318-2017 | BPV-547186-2017 | 6/20/2017 11:37:37 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #REMOTE_SHUTDOWN_SWITCH_-_BOILER.png No remote shutdown switch found for installed high pressure steam boiler. The remote shutdown switch allows the boiler operator to shutdown the boiler from a safe distance should the unit be experiencing pressure boundary failure where high pressure and high temperature steam may be escaping from the unit. Or in the case of boiler furnace failure allowing flames and hot gas to escape in to the boiler room. In both cases you would want to shut the unit down from a safe distance to prevent serious injury to the operator and minimize property damage.. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | REMOTE_SHUTDOWN_SWITCH_-_BOILER.png | file://x:/photopub/docs/0000000619/efc401b8-1abd-4c52-8c2a-d90c2a216f72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5eb25c70_9995_4470_8ab5_8686f15a0b1c
ELIN-852476-2017 | EL-367906-2016 | 7/17/2017 10:16:29 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #_All_AFC_I__AFC_I_breakers_in_off_position_when_this_photo_taken.png In the new dwelling branch circuits feeding receptacles in the main living area are not provided AFC I protection in the event of an arc fault. These 120 V 15 amp receptacles where not properly protected can lead to property damage or injury to persons | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | _All_AFC_I__AFC_I_breakers_in_off_position_when_this_photo_taken.png | file://x:/photopub/docs/0000000631/fec24d36-4313-449a-ade8-f3d727e81835.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47ef6d8e_be8f_4711_b63b_4a69bcf67ea4
ELIN-821494-2017 | EL-431740-2016 | 5/29/2017 1:49:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Secondary suite consumer service encasement in concrete. | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Pic2.png -Secondary suite consumer service cable is installed in concrete form with less than 50mm of concrete all around cable. The consumer service cable is unfused from hydro and the concrete installation is not sufficient to mechanically protect the cable from accidental electrical shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Pic2.png | file://x:/photopub/docs/0000000607/7c1f90a9-458c-4103-8934-1aba88d3b1c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03fc21c0_a536_47ee_91a3_c476016899f3
ELIN-818127-2017 | EL-532545-2017 | 6/22/2017 1:45:14 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Heat_trace.png At an existing single family modular home, a 15amp 120volt extension cord plugged into an exterior outlet was found in an energized state with the heat trace plugged into it under the modular unit. This can lead to an "Thermal Effect" scenario. Pic attached. | 4 | Conductors, Misuse of flexible cords. | Heat_trace.png | file://x:/photopub/docs/0000000620/34fc5c84-b4ab-4c93-9967-720aba0080e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__797db6d8_fe1c_460c_8a5b_a5077e2d11d6
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection7.png | file://x:/photopub/docs/0000000632/aa0ddc51-9462-491c-a7a1-f19e83561691.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png | file://x:/photopub/docs/0000000632/23de3e06-598c-46fa-b3af-01e56c2939ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png | file://x:/photopub/docs/0000000632/28fe770d-6f9c-417c-8828-25f8ed7656c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png | file://x:/photopub/docs/0000000632/ae6fae92-d266-4e87-bc63-89068fd4af54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
GAIN-861186-2017 | GA-560801-2017 | 7/21/2017 2:10:45 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #Pool_boiler1.png,Pool_boiler2.png -Gas fired boilers require a fresh air supply feeding the room where these boilers are installed. This is necessary for boilers to achieve complete combustion when they are running. I observed a pool boiler installed and running with no combustion air supply feeding the room. This could result in the boiler starving for air, incomplete combustion, the production of carbon monoxide and negative physical effects for anyone in the direct vicinity of the boiler. | 4 | Combustion air supply missing | Pool_boiler1.png | file://x:/photopub/docs/0000000634/b8909b8e-e7ba-4f4a-8edd-07886222d329.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5b4d4f3_ecb4_48e3_8d93_e9bc7fc8bd7a
GAIN-861186-2017 | GA-560801-2017 | 7/21/2017 2:10:45 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #Pool_boiler1.png,Pool_boiler2.png -Gas fired boilers require a fresh air supply feeding the room where these boilers are installed. This is necessary for boilers to achieve complete combustion when they are running. I observed a pool boiler installed and running with no combustion air supply feeding the room. This could result in the boiler starving for air, incomplete combustion, the production of carbon monoxide and negative physical effects for anyone in the direct vicinity of the boiler. | 4 | Combustion air supply missing | Pool_boiler2.png | file://x:/photopub/docs/0000000634/1534dd12-65d2-44db-975a-8fc44c845c84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5b4d4f3_ecb4_48e3_8d93_e9bc7fc8bd7a
EDOP-854001-2017 | ED -0000276284-2015 | 7/5/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED014 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 3 | 3 | #ED_23208_water.png Water was infiltrating the door lock circuitry and may cause the elevator to run with the door open. | 3 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | ED_23208_water.png | file://x:/photopub/docs/0000000628/8dcb674c-256b-4275-bbda-28b1060cf930.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00c61550_258e_491f_84f8_985ce4651fd1
ELIN-819399-2017 | EL-518211-2017 | 5/18/2017 2:38:38 PM | ASSESS: EL: Final | png | #asFound Cable is stressed between stud and cable connector. | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #P4.png Feeder cable for the shop sub panel is in stress between the stud and cable connector to the service panel. This may cause cable insulation failure causing fire. Fire could in turn cause property damage, injuries or death to occupants of this house. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | P4.png | file://x:/photopub/docs/0000000603/bc543dd6-0699-4e96-89af-ae544c87a9ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7124300_3e4a_4a7c_a8eb_3efa9a7df6e7
ELIN-841012-2017 | EL-384259-2016 | 7/6/2017 7:36:25 AM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | #Panel_1.png,Panel_2.png Multiple receptacle circuits installed without Arc fault protection. Arc faults are a leading cause of fires, with out proper breaker installed increases risk of fire. | 3 | Protection and control Low voltage protection damaged or not provided. | Panel_2.png | file://x:/photopub/docs/0000000626/8dc37171-7caa-406f-9084-6981bfdd4c26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__573d2bcd_6ce3_4a68_b216_411492a0cd35
ELIN-841012-2017 | EL-384259-2016 | 7/6/2017 7:36:25 AM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | #Panel_1.png,Panel_2.png Multiple receptacle circuits installed without Arc fault protection. Arc faults are a leading cause of fires, with out proper breaker installed increases risk of fire. | 3 | Protection and control Low voltage protection damaged or not provided. | Panel_1.png | file://x:/photopub/docs/0000000626/04ca468f-0199-4daa-816b-579c47a7e6d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__573d2bcd_6ce3_4a68_b216_411492a0cd35
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png | file://x:/photopub/docs/0000000632/f25a9b96-538f-463c-9ceb-e925ea888425.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
ELIN-857419-2017 | EL-546746-2017 | 7/18/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection1.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection3.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection4.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection5.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection6.png,Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_th | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_and_branch_circiut_cables_pass_through_structural_members_closer_than_32mm_from_the_face_of_members_and_do_not_have_mechanical_protection2.png | file://x:/photopub/docs/0000000632/3fc2e9f0-b8df-4a5a-8c67-91da20a2dfe8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4adc41cc_0cf8_48e1_b721_e95315058646
GAIN-836217-2017 | GA-454392-2016 | 6/13/2017 11:56:55 AM | ASSESS: GA: Final | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | #Supports.png The piping connection at a propane cylinder installation is supported on an untreated wood post design entrenched at a shallow depth. Should environmental conditions such as snow or heavy rain affect the post negatively the piping system could collapse, subjecting the regulator to moisture in the relief or physical strain on the materials. | 3 | No protection Low traffic | Supports.png | file://x:/photopub/docs/0000000615/d6118bca-566b-49a8-b699-eca2498d7ffb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd7280f0_1b75_4500_a46e_00115fda207d
ELIN-843665-2017 | EL-543186-2017 | 6/26/2017 12:59:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Main_Ground1.png,Main_Ground2.png In the new 100 amp 240 volt service, a 100 amp Meterbase complete with a 100 amp Main Breaker has been supplied but the Service Equipment has not been effectively grounded. The grounding electrode and attached #6 copper conductor have been terminated at the Panel instead. This poses a shock hazard to persons and potential damage to the electrical equipment as the Main Service Breaker may not operate as designed, and the path for unwanted fault current may not travel back to the supply transformer. Unwanted circulating currents may also be present. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_Ground2.png | file://x:/photopub/docs/0000000621/599bfbcb-9df8-43f3-b521-d961c3b6a2bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82d9dfe6_63f8_4671_94b7_8375d0555fe5
ELIN-843665-2017 | EL-543186-2017 | 6/26/2017 12:59:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Main_Ground1.png,Main_Ground2.png In the new 100 amp 240 volt service, a 100 amp Meterbase complete with a 100 amp Main Breaker has been supplied but the Service Equipment has not been effectively grounded. The grounding electrode and attached #6 copper conductor have been terminated at the Panel instead. This poses a shock hazard to persons and potential damage to the electrical equipment as the Main Service Breaker may not operate as designed, and the path for unwanted fault current may not travel back to the supply transformer. Unwanted circulating currents may also be present. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_Ground1.png | file://x:/photopub/docs/0000000621/51064c74-eb91-4a2d-975a-56a0aabeb888.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82d9dfe6_63f8_4671_94b7_8375d0555fe5
ELHE-831927-2017 | HE-543663-2017 | 6/7/2017 9:13:14 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Outlet_box_with_missing_light_fixture.png Exterior 120 volt outlet box for light fixture has no fixture or cover installed, with exposed conductors that can be energized; thus, increasing the likelihood of electrical shock. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlet_box_with_missing_light_fixture.png | file://x:/photopub/docs/0000000612/89c0f740-8611-4d6f-86ac-f1f562fa48b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63a725c3_2b0c_452a_ba28_191105ee4017
ELIN-841248-2017 | EL-540987-2017 | 6/21/2017 1:37:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Shock_hazard.png This assessment found the switch in the bathroom too close to the bathtub, which creates a potential shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Shock_hazard.png | file://x:/photopub/docs/0000000619/0b3b5d4a-f4ee-4e90-8794-24653c2315b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d70694d_bd4c_494e_a206_c5fd74a6b99f
ELIN-841253-2017 | EL-540989-2017 | 6/21/2017 1:47:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Potential_shock_hazard.png This assessment found a switch was installed too close to the bathtub, creating a potential shock hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Potential_shock_hazard.png | file://x:/photopub/docs/0000000619/17605b80-d818-4211-9ece-97c7a8fad690.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f95ebcc0_ca9a_458d_b967_3ea31336f7fc
GAIN-846998-2017 | GA-398952-2016 | 6/28/2017 2:58:26 PM | ASSESS: GA: Rough-In | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting.png The as found condition is the vent on a radiant tube heater was composed unsealed b-type vent material contrary to the manufacturers requirements. The as found hazard is that unsealed and unapproved vent materials can leak products of combustion into the structure subjecting occupants to carbon monoxide hazards. | 3 | Unapproved venting material | Venting.png | file://x:/photopub/docs/0000000622/7a2b48e4-0977-49d8-8e0f-35cabbaba9db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__472aba04_ff6b_457b_ba48_95f62fa07cef
GAIN-559631-2016 | GA-376388-2016 | 7/17/2017 8:06:16 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Reg_and_exhaust.png A pressure regulator is installed within clearances of an exhaust vent. exhaust vent could condensate on to Regulator causing regulator to not function properly. Possibility of regulator failing and shutting gas off to building | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Reg_and_exhaust.png | file://x:/photopub/docs/0000000631/dc0e550b-5b2d-41f1-b7b7-64f1154be851.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a7ba576_1d64_42b9_bf4b_03310582b00a
GAHE-826245-2017 | HE-540210-2017 | 5/30/2017 12:26:12 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA162 | Defective appliance accessory or component with imminent risk of injury or property damage | 5 | 5 | #Fire_damaged_equipment1.png,Fire_damaged_equipment2.png,Fire_damaged_equipment3.png Propane dispenser at a gas station was exposed/damaged by fire. The propane tank and pump interlocks were left open and on. This could have resulted in someone turning the dispenser pump on and allowing liquid propane to flow from the tank to the badly damaged dispenser causing an uncontrolled amount of propane to spray from the damaged hoses and resulting in a serious fire. | 5 | Defective appliance accessory or component with imminent risk of injury or property damage | Fire_damaged_equipment1.png | file://x:/photopub/docs/0000000608/9fcd503e-8132-4ebe-bbba-ec2b0cfb6925.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d4d56d_30d6_4e00_8c71_a020efe12e39
GAHE-826245-2017 | HE-540210-2017 | 5/30/2017 12:26:12 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA162 | Defective appliance accessory or component with imminent risk of injury or property damage | 5 | 5 | #Fire_damaged_equipment1.png,Fire_damaged_equipment2.png,Fire_damaged_equipment3.png Propane dispenser at a gas station was exposed/damaged by fire. The propane tank and pump interlocks were left open and on. This could have resulted in someone turning the dispenser pump on and allowing liquid propane to flow from the tank to the badly damaged dispenser causing an uncontrolled amount of propane to spray from the damaged hoses and resulting in a serious fire. | 5 | Defective appliance accessory or component with imminent risk of injury or property damage | Fire_damaged_equipment2.png | file://x:/photopub/docs/0000000608/156625d2-f40d-484b-88eb-f81da6be6157.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d4d56d_30d6_4e00_8c71_a020efe12e39
GAHE-826245-2017 | HE-540210-2017 | 5/30/2017 12:26:12 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA162 | Defective appliance accessory or component with imminent risk of injury or property damage | 5 | 5 | #Fire_damaged_equipment1.png,Fire_damaged_equipment2.png,Fire_damaged_equipment3.png Propane dispenser at a gas station was exposed/damaged by fire. The propane tank and pump interlocks were left open and on. This could have resulted in someone turning the dispenser pump on and allowing liquid propane to flow from the tank to the badly damaged dispenser causing an uncontrolled amount of propane to spray from the damaged hoses and resulting in a serious fire. | 5 | Defective appliance accessory or component with imminent risk of injury or property damage | Fire_damaged_equipment3.png | file://x:/photopub/docs/0000000608/02c9e784-d959-44de-8a1e-db76a7e24d44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d4d56d_30d6_4e00_8c71_a020efe12e39
BPVIN-477714-2015 | UW-312620-2015 | 7/17/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound PSV discharge pipe support | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 3 | #support.png,Unsupported_vessel.png Air receiver support legs are not anchored to the floor, only sitting in position. If the vessel were to be struck by equipment or move from earthquake forces or possibly process flow forces, it could move. This could cause other damage to piping and potentially cause a rupture and release. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | support.png | file://x:/photopub/docs/0000000633/b52ffdf6-02af-49db-8fc4-a1a48835a880.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bde0893_6816_4926_a88e_57a4fe215d18
ELIN-817996-2017 | EL-508875-2017 | 5/17/2017 11:38:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Cable_on_the_Shore.png This assessment found that the cable on the shore line could move with the tides causing cable to become damaged, creating a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable_on_the_Shore.png | file://x:/photopub/docs/0000000602/a41d2e55-fd72-46fd-b126-8aac4932a145.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0ca068e_602e_4872_b113_2cd2b1f16e8e
BPVOP-699546-2016 | 2287907 | 6/7/2017 1:53:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP136 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | 4 | 4 | #PRD_.png Upon the assessment of a DHW Storage Tank with MAWP of 125 psig, was found that the Pressure Relief Valve had no tag and failed the pressure test. This can contribute to the failure of the pressure vessel. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | PRD_.png | file://x:/photopub/docs/0000000612/f912d697-2db5-424f-aecc-c05d488ff20d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7f8a747_7857_4a82_a238_3c22c0aa0ed9
ELIN-822231-2017 | EL-529421-2017 | 6/7/2017 12:21:56 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Branch_circuit_not_approved_for_main_distribution.png 20 amp, 120/240 volt branch circuit breaker installed in a main distribution panel. Branch circuit breaker not approved for main distribution. This could cause equipment damage. | 3 | General Equipment is not approved for the specific use | Branch_circuit_not_approved_for_main_distribution.png | file://x:/photopub/docs/0000000613/65f011d0-9359-4993-9ad6-914d67143861.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6d3be99_aa05_49e3_b5dc_6ce634df1561
GAIN-851851-2017 | GA-550995-2017 | 7/26/2017 1:36:20 PM | ASSESS: GA: Final | png | #asFound | GA143 | Open junction box with line voltage not accessible to public | 3 | 3 | #E_s_3.png Open junction box installed in closet. Risk of accidental contact with energized conductors. Risk of shock. | 3 | Open junction box with line voltage not accessible to public | E_s_3.png | file://x:/photopub/docs/0000000636/696a6fe5-ee3a-4930-b236-8fac1b9b5e43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88a94c24_2f9c_4c85_b2f9_2454f59f32ac
ELIN-815556-2017 | EL-533788-2017 | 5/17/2017 3:59:20 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood1.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood2.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood3.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood4.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood5.png Materials used for electrical installations are required to be approved. This is required to ensure that installed electrical equipment is tested and certified to a standard and will operate properly and safely. This installation at a mobile home has a 100A 120/240V meter base that has been used as a junction box for the feeder cable installed from the electrical room to the mobile home electrical panel. The meter base has been jumpered with plumbing strapping, and the meter base cover is made of plywood. Plumbing strapping and the plywood cover are not approved electrical components. Left uncorrected this is a potential shock and fire hazard if | 3 | General Equipment is not approved for the specific use | Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood3.png | file://x:/photopub/docs/0000000602/98282cdf-e8b8-4834-b180-bdc206cc32fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5662bf6e_5405_478e_bb40_69246d52d28d
ELIN-815556-2017 | EL-533788-2017 | 5/17/2017 3:59:20 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood1.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood2.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood3.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood4.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood5.png Materials used for electrical installations are required to be approved. This is required to ensure that installed electrical equipment is tested and certified to a standard and will operate properly and safely. This installation at a mobile home has a 100A 120/240V meter base that has been used as a junction box for the feeder cable installed from the electrical room to the mobile home electrical panel. The meter base has been jumpered with plumbing strapping, and the meter base cover is made of plywood. Plumbing strapping and the plywood cover are not approved electrical components. Left uncorrected this is a potential shock and fire hazard if | 3 | General Equipment is not approved for the specific use | Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood5.png | file://x:/photopub/docs/0000000602/8088fe2b-7d2f-4cf4-a7c6-c87ebf8d1769.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5662bf6e_5405_478e_bb40_69246d52d28d
ELIN-815556-2017 | EL-533788-2017 | 5/17/2017 3:59:20 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood1.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood2.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood3.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood4.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood5.png Materials used for electrical installations are required to be approved. This is required to ensure that installed electrical equipment is tested and certified to a standard and will operate properly and safely. This installation at a mobile home has a 100A 120/240V meter base that has been used as a junction box for the feeder cable installed from the electrical room to the mobile home electrical panel. The meter base has been jumpered with plumbing strapping, and the meter base cover is made of plywood. Plumbing strapping and the plywood cover are not approved electrical components. Left uncorrected this is a potential shock and fire hazard if | 3 | General Equipment is not approved for the specific use | Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood1.png | file://x:/photopub/docs/0000000602/b48aaeb4-e642-42dc-bfd6-47525fd57205.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5662bf6e_5405_478e_bb40_69246d52d28d
ELIN-815556-2017 | EL-533788-2017 | 5/17/2017 3:59:20 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood1.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood2.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood3.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood4.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood5.png Materials used for electrical installations are required to be approved. This is required to ensure that installed electrical equipment is tested and certified to a standard and will operate properly and safely. This installation at a mobile home has a 100A 120/240V meter base that has been used as a junction box for the feeder cable installed from the electrical room to the mobile home electrical panel. The meter base has been jumpered with plumbing strapping, and the meter base cover is made of plywood. Plumbing strapping and the plywood cover are not approved electrical components. Left uncorrected this is a potential shock and fire hazard if | 3 | General Equipment is not approved for the specific use | Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood4.png | file://x:/photopub/docs/0000000602/e1ceabc2-d90c-4f51-8b46-87bb46f0fff5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5662bf6e_5405_478e_bb40_69246d52d28d
ELIN-815556-2017 | EL-533788-2017 | 5/17/2017 3:59:20 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood1.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood2.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood3.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood4.png,Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood5.png Materials used for electrical installations are required to be approved. This is required to ensure that installed electrical equipment is tested and certified to a standard and will operate properly and safely. This installation at a mobile home has a 100A 120/240V meter base that has been used as a junction box for the feeder cable installed from the electrical room to the mobile home electrical panel. The meter base has been jumpered with plumbing strapping, and the meter base cover is made of plywood. Plumbing strapping and the plywood cover are not approved electrical components. Left uncorrected this is a potential shock and fire hazard if | 3 | General Equipment is not approved for the specific use | Meter_base_jumpered_with_plumbing_strapping_and_covered_with_plywood2.png | file://x:/photopub/docs/0000000602/d006fb77-b971-47a7-9b61-6eda2d10e13c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5662bf6e_5405_478e_bb40_69246d52d28d
ELHE-828650-2017 | HE-541665-2017 | 6/2/2017 11:46:45 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Energized Garage panel with no cover, wiring entering the front of the panel and no anti short protection on the armoured cable. | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel.png Hazard elimination on residential agricultural operation requested by the city of Chilliwack. Detached garage wired without a permit and has open splices and other shock and fire hazards. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel.png | file://x:/photopub/docs/0000000610/d9d1640d-ddc7-44a3-8c40-5b6e4bccdfb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f8386fa_50e9_4183_96d0_c354ac96bf4f
BPVOP-812533-2017 | 2295987 | 5/9/2017 10:39:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | #Scale.png,Scale.png | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale.png | file://x:/photopub/docs/0000000603/84ef9b8c-536c-4607-9033-229f6dcc6875.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f83efa9_ac91_443b_adb2_44c18431ae6c
ELIN-811181-2017 | EL-530517-2017 | 5/11/2017 | ASSESS: EL: Final | png | #asFound -water pump termination with open air spliced. | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #water_pump_connection_.png -water pump for a food trailer has been terminated and spliced together open air with a piece of flexible cord and male plug end attached. Conductors have not been mechanically protected or guarded from people or equipment may lead to damage and or shock /fire hazards. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | water_pump_connection_.png | file://x:/photopub/docs/0000000603/5e1f649f-1408-432d-b4b5-89837e59c1ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a5d99f8_8ef5_489b_880e_9103f8581379
GAIN-824955-2017 | GA-493501-2017 | 7/26/2017 4:04:52 PM | ASSESS: GA: Final | png | #asFound No relief attached on pool boiler Raypac | GA144 | Missing mandatory safety controls | 4 | 4 | #No_relief_installed_boiler1.png,No_relief_installed_boiler2.png -Over pressure protection device not found on the equipment at the time of inspection. -If no pressure relief valve on the equipment, The equipment may explode/fail in the event of a pressure build up | 4 | Missing mandatory safety controls | No_relief_installed_boiler2.png | file://x:/photopub/docs/0000000637/1c3e1c6e-40cd-454f-820c-693be418ea4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4dd213b_c04b_4e02_9f65_19b1ec7e401a
GAIN-824955-2017 | GA-493501-2017 | 7/26/2017 4:04:52 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #No_relief_installed_boiler1.png,No_relief_installed_boiler2.png -Over pressure protection device not found on the equipment at the time of inspection. -If no pressure relief valve on the equipment, The equipment may explode/fail in the event of a pressure build up | 4 | Missing mandatory safety controls | No_relief_installed_boiler1.png | file://x:/photopub/docs/0000000637/49d3c6cd-c8fd-4ae4-af14-a2784ff4601b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4dd213b_c04b_4e02_9f65_19b1ec7e401a
BPVOP-835211-2017 | BPV-0000120948-2014 | 6/6/2017 | ASSESS: BPV OP: Re-Certification REF/PV | pdf | #asFound Inspection Photos | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #9-BPV-120948-2014 PV11P5025 FC Photos.pdf The Pressure Relief Device set pressure was 200 psi, the Maximum Allowable Working Pressure (MAWP) of the pressure vessel is 125 psi. This is 75 psi over the MAWP.. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 9-BPV-120948-2014 PV11P5025 FC Photos.pdf | file://x:/photopub/docs/0000000616/e4dc808c-4881-45e5-81e8-b83382d6b147.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3706cca9_0169_4ead_906a_1913467c00e3
BPVOP-835211-2017 | BPV-0000120948-2014 | 6/6/2017 | ASSESS: BPV OP: Re-Certification REF/PV | pdf | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #9-BPV-120948-2014 PV11P5025 FC Photos.pdf The Pressure Relief Device set pressure was 200 psi, the Maximum Allowable Working Pressure (MAWP) of the pressure vessel is 125 psi. This is 75 psi over the MAWP.. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 9-BPV-120948-2014 PV11P5025 FC Photos.pdf | file://x:/photopub/docs/0000000616/7486e089-1d1d-414d-8d90-0892d459ee66.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3706cca9_0169_4ead_906a_1913467c00e3
ELIN-852773-2017 | EL-538332-2017 | 7/7/2017 1:45:21 PM | ASSESS: EL: Final | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shop.png The remote subpanel cover is not in place exposing the panel bus. This is a potential shock hazard. The panel is located in a detached shop. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shop.png | file://x:/photopub/docs/0000000627/7653a31a-f195-4ab0-a6f7-9e39bc7d2313.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1913dbbf_1c07_4f81_a39c_747cd33e371c
BPVOP-805603-2017 | 2984926 | 7/13/2017 10:23:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_1.png,Safety_Relief_Valve_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was under the relief capacity required by the boiler. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_2.png | file://x:/photopub/docs/0000000630/fd1c42a9-d3a1-4316-bad8-739099733db0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00896849_d6b7_4efc_af24_65ec019fc7e2
ELIN-809671-2017 | EL-487021-2017 | 5/19/2017 12:49:45 PM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | #Service1.png,Service2.png,Service3.png The de-energized 200 amp 120/240 volt consumer identified conductors are not labelled allowing the possibility of the utility to energize the wrong conductor and enclosure and ground system. This can create an equipment damage, thermal and sock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Service2.png | file://x:/photopub/docs/0000000604/8c748e80-ef1f-49d7-ad71-893440bb95da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9a77c62_0118_4c9b_8f68_ef94a34d3bd6
ELIN-809671-2017 | EL-487021-2017 | 5/19/2017 12:49:45 PM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | #Service1.png,Service2.png,Service3.png The de-energized 200 amp 120/240 volt consumer identified conductors are not labelled allowing the possibility of the utility to energize the wrong conductor and enclosure and ground system. This can create an equipment damage, thermal and sock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Service3.png | file://x:/photopub/docs/0000000604/8f1cb1ac-e3fb-4388-b3eb-a0e6949083ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9a77c62_0118_4c9b_8f68_ef94a34d3bd6
ELIN-809671-2017 | EL-487021-2017 | 5/19/2017 12:49:45 PM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | #Service1.png,Service2.png,Service3.png The de-energized 200 amp 120/240 volt consumer identified conductors are not labelled allowing the possibility of the utility to energize the wrong conductor and enclosure and ground system. This can create an equipment damage, thermal and sock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Service1.png | file://x:/photopub/docs/0000000604/6b23fddf-862d-48f6-896f-5a4ffc883592.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9a77c62_0118_4c9b_8f68_ef94a34d3bd6
ELIN-826062-2017 | UW-540066-2017 | 5/31/2017 7:31:17 AM | ASSESS: EL: Final | png | #asFound Flexible cord | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #21.png,22.png Flexible cords (extension cords) have been installed thru holes in the building, buried underground and, permanently attached to chain link fence.These cords are being used as a permanent installation and are not rated for this type of use. Correct installation practices have not been observed as the work was done by an individual without any qualifications. This is a motor vehicle sales lot with large amounts of pedestrian traffic in the area where the cords were buried. The use of flexible cords in this matter is a shock hazard to individuals walking in the area or coming into contact with the fence. | 4 | Conductors, Misuse of flexible cords. | 21.png | file://x:/photopub/docs/0000000608/bc9b5bac-9fd6-4ef9-a349-f7f9eeb7d0c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9f27faa_b1a0_4aeb_980a_dbdeede8c933
ELIN-826062-2017 | UW-540066-2017 | 5/31/2017 7:31:17 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #21.png,22.png Flexible cords (extension cords) have been installed thru holes in the building, buried underground and, permanently attached to chain link fence.These cords are being used as a permanent installation and are not rated for this type of use. Correct installation practices have not been observed as the work was done by an individual without any qualifications. This is a motor vehicle sales lot with large amounts of pedestrian traffic in the area where the cords were buried. The use of flexible cords in this matter is a shock hazard to individuals walking in the area or coming into contact with the fence. | 4 | Conductors, Misuse of flexible cords. | 22.png | file://x:/photopub/docs/0000000608/d12dc9f5-f453-40de-889f-5e74ab4a9330.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9f27faa_b1a0_4aeb_980a_dbdeede8c933
GAIN-856214-2017 | GA-487280-2017 | 7/13/2017 10:44:01 AM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Riser.png Underground plastic gas lines ran indoors under the building foundation to several ranges in the kitchen. If ever there was a leak, it would go undetected under the building foundation. Potential for a large volume of gas to build up underground until it finds an ignition source. | 3 | Underground piping entering a building below grade (unapproved) | Riser.png | file://x:/photopub/docs/0000000630/d42afdcc-bbf2-4bb2-be76-b2929639757f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a09f1ba9_61d7_47b4_b2b8_fe659b873956
ELIN-849979-2017 | EL-549492-2017 | 7/27/2017 8:59:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Service.png The code requires that the neutral bus of main service be grounded. The object of grounding the electrical system and non-current carrying metal parts is to connect the earth. The neutral bus was not grounded. This system in a fault would not provide a secondary path to ground. | 4 | Installation Grounding; conductor is not continuous. | Service.png | file://x:/photopub/docs/0000000637/8573a30f-43ae-4d40-95f8-58d5d0156af4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b141f2d1_ab66_4ce1_b085_ab718535da99
BPVOP-805603-2017 | 2984926 | 7/13/2017 10:23:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_1.png,Safety_Relief_Valve_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was under the relief capacity required by the boiler. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_1.png | file://x:/photopub/docs/0000000630/e7f07e8a-f6b3-4f33-b598-15f2819b0c33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00896849_d6b7_4efc_af24_65ec019fc7e2
AMOP-832277-2017 | 4457843 | 6/7/2017 9:15:01 AM | ASSESS: AM OP: Periodic | png | #asFound | AM046 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | #Bypass_Residential_Grade_Lighting_Switch.png Two bumper buggy passenger seatbelt safety inter-locks were bypassed via hardwiring of a residential grade lighting switch. This was done by personnel so the buggies could remain in service without making proper repairs or part replacement to the the PCU interlock module. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Bypass_Residential_Grade_Lighting_Switch.png | file://x:/photopub/docs/0000000613/2b448000-4dda-4881-9b68-0f633f4036a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98675d1f_5778_4eac_b9d2_7e3494ea231a
EDRI-841056-2017 | ED-494585-2017 | 6/21/2017 8:24:24 AM | ASSESS: ED RI: Extension | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | #Missing_Hoarding.png | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Missing_Hoarding.png | file://x:/photopub/docs/0000000619/b9172a93-ff27-4759-97c2-b4c49f7e410d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc376125_ce13_4e64_bb03_ed4c506d368c
GAIN-853638-2017 | GA-490645-2017 | 7/11/2017 10:51:05 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Inlet_air__inlet_air_supply.png Combustion air supply to 8 appliances has been terminated in a roof flashing with not enough clearance above the roofline. When it snows the accumulation of snow could block the inlet air supply causing the appliances fail, being that this is a chicken barn and if there is a loss of heat could cause death to the chickens | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Inlet_air__inlet_air_supply.png | file://x:/photopub/docs/0000000628/61ff93d3-0fa1-4961-bafe-0e1e889cca53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fc7103e_ecf1_4f45_968f_8a7624e95208
BPVIN-749718-2017 | BPV-291430-2015 | 7/19/2017 12:15:07 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound Air inlet duct 7" x 19" | BP021 | 1.0.2 Clearances/Maintenance - Boiler/ machinery rooms do not have adequate lighting, ventilation for habitability, or combustion air and personal safety, and general safety requirements are poor. | 2 | 2 | #Inletair.png The ventilation provided to the boiler room is inadequate, inlet ducting is too small. This room requires a 500 square inch opening. Only 131 square inches is provided. This could lead to poor boiler performance with inadequate combustion air and also lead to reduced breathable oxygen in the room. | 2 | 1.0.2 Clearances/Maintenance - Boiler/ machinery rooms do not have adequate lighting, ventilation for habitability, or combustion air and personal safety, and general safety requirements are poor. | Inletair.png | file://x:/photopub/docs/0000000633/a74eface-fb64-46c6-9f66-202cebc7eed4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6963d20_053a_4835_84e9_9927d4764deb
BPVOP-841298-2017 | 2296399 | 6/14/2017 | ASSESS: BPV OP: Repair Boiler | png | #asFound 8 cracks ground and prepped for welding. | BP000 | No Created Hazard Identified | 0 | 0 | #LP56561-cracks.png None observed. | 0 | No Created Hazard Identified | LP56561-cracks.png | file://x:/photopub/docs/0000000619/6ff58ba2-b43d-4049-abfc-926ea5dde4de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ebadef1_cd0c_4be6_a33c_a60798c6d2eb
ELIN-835431-2017 | UW-543600-2017 | 6/5/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Heat_trace1.png,Heat_trace2.png,Heat_trace3.png Armoured cable not terminated in box creating a shock or fire hazard if energized. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Heat_trace2.png | file://x:/photopub/docs/0000000614/932bfffa-43e4-4dfe-ba12-792d0838ec47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fe769ba_f7d6_4555_b098_d35cde908e7c
ELIN-835431-2017 | UW-543600-2017 | 6/5/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Heat_trace1.png,Heat_trace2.png,Heat_trace3.png Armoured cable not terminated in box creating a shock or fire hazard if energized. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Heat_trace1.png | file://x:/photopub/docs/0000000614/fe13cec8-73d9-464b-897e-9c36aaa07752.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fe769ba_f7d6_4555_b098_d35cde908e7c
ELIN-835431-2017 | UW-543600-2017 | 6/5/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Heat_trace1.png,Heat_trace2.png,Heat_trace3.png Armoured cable not terminated in box creating a shock or fire hazard if energized. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Heat_trace3.png | file://x:/photopub/docs/0000000614/9bec2b26-a73d-4b6f-a57b-dce53d717b6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fe769ba_f7d6_4555_b098_d35cde908e7c
ELIN-859994-2017 | EL-559224-2017 | 7/19/2017 8:16:21 AM | ASSESS: EL: Final | png | #asFound Ground in meter base | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | #Q1.png,Q2.png System ground conductor #6 AWG bare copper has been installed in the meter base to a bonding lug. The AC system neutral conductor is not bonded to ground. This is a fire and shock hazard as the system over current devices will not operate properly. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Q1.png | file://x:/photopub/docs/0000000632/351c43f7-399d-4016-abab-b65267d0e9b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4fdbe86_ba29_4a93_a12d_f0b50f7dce7a
ELIN-859994-2017 | EL-559224-2017 | 7/19/2017 8:16:21 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | #Q1.png,Q2.png System ground conductor #6 AWG bare copper has been installed in the meter base to a bonding lug. The AC system neutral conductor is not bonded to ground. This is a fire and shock hazard as the system over current devices will not operate properly. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Q2.png | file://x:/photopub/docs/0000000632/89cd52d8-ba21-47ae-ad56-78f247d30288.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4fdbe86_ba29_4a93_a12d_f0b50f7dce7a
ELIN-822369-2017 | EL-537783-2017 | 5/29/2017 12:16:36 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Overloaded_neutral.png A 3 wire circuit operating at 120 volts and a cumulative 30 amps is connected in such a way as the 15 amp rated neutral conductor can be exposed to as much as 30 amps, which can lead to injury to persons or damage to property. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Overloaded_neutral.png | file://x:/photopub/docs/0000000607/a34ffb42-098e-4d41-8948-f820de23d62b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1731813_cca6_4bb9_82b3_eb163b95cc1c
ELIN-827307-2017 | EL-540833-2017 | 6/1/2017 5:22:29 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Electrical_panel_mounted_in_outdoor_location1.png,Electrical_panel_mounted_in_outdoor_location2.png Electrical equipment for outdoor use must be rated for the type of environment. This is required to protect the equipment against environmental conditions which could cause water or moisture to enter the equipment. In this installation at a single family dwelling, an electrical panel that was rated for dry, indoor use was found mounted in an outdoor location inside a wooden enclosure. Over time, water or moisture could enter this electrical panel which could create a potential shock hazard to persons that touch this panel or equipment failure from corrosion. | 3 | General Equipment is not approved for the specific use | Electrical_panel_mounted_in_outdoor_location2.png | file://x:/photopub/docs/0000000610/0af533fb-7ce1-42da-ae54-4767fbb67f93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39bc46b1_06dd_49e0_be51_a21fdfe8e11c
ELIN-827307-2017 | EL-540833-2017 | 6/1/2017 5:22:29 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Electrical_panel_mounted_in_outdoor_location1.png,Electrical_panel_mounted_in_outdoor_location2.png Electrical equipment for outdoor use must be rated for the type of environment. This is required to protect the equipment against environmental conditions which could cause water or moisture to enter the equipment. In this installation at a single family dwelling, an electrical panel that was rated for dry, indoor use was found mounted in an outdoor location inside a wooden enclosure. Over time, water or moisture could enter this electrical panel which could create a potential shock hazard to persons that touch this panel or equipment failure from corrosion. | 3 | General Equipment is not approved for the specific use | Electrical_panel_mounted_in_outdoor_location1.png | file://x:/photopub/docs/0000000610/1b94ec68-323f-4904-9ced-a113a20489c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39bc46b1_06dd_49e0_be51_a21fdfe8e11c
GAIN-834343-2017 | GA-472972-2016 | 6/12/2017 11:23:51 AM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #Furnace_air_intake.png Furnace air intake is too close to the meter regulator relief port. If the gas regulator reliefs gas it could be drawn into the furnace air intake resulting in a fire or explosion. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Furnace_air_intake.png | file://x:/photopub/docs/0000000615/ea981b64-8438-46c8-a86f-898e6b1cc670.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1143ed52_cbff_4e73_aa7b_6d41f0e243c2
GAIN-819954-2017 | GA-515658-2017 | 5/25/2017 7:49:41 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #1.png Soldered joints have a melting point of 212 degree F, below the minimum of 1000 degrees required for gas piping. Any small fire in furnace room would melt gas soldered connections creating extreme hazard of open ignited gas lines. | 3 | Non-compliant material/fittings installed | 1.png | file://x:/photopub/docs/0000000605/4c94056f-a4b1-4851-b604-ef8ca60e3ab6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e5b3639_65fd_4017_b139_c34193761cca
GAIN-779259-2017 | GA-503636-2017 | 4/5/2017 9:02:37 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Boiler_relief1.png,Boiler_relief2.png Each boiler requires a safety relief valve and they must be ahead of all isolation valves. Without relief valves in the proper location, the pressure vessel could become an explosion hazard should the vessel over-pressurize and isolation valves are closed | 3 | Appliance not installed according to installation instructions | Boiler_relief2.png | file://x:/photopub/docs/0000000616/2ea8e685-ae7b-4774-bd1d-5effae7fe76b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3bc732_c0a2_4dde_8d09_5bc25d84df62
GAIN-779259-2017 | GA-503636-2017 | 4/5/2017 9:02:37 AM | ASSESS: GA: Final | png | #asFound Relief valves are in wrong place | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Boiler_relief1.png,Boiler_relief2.png Each boiler requires a safety relief valve and they must be ahead of all isolation valves. Without relief valves in the proper location, the pressure vessel could become an explosion hazard should the vessel over-pressurize and isolation valves are closed | 3 | Appliance not installed according to installation instructions | Boiler_relief1.png | file://x:/photopub/docs/0000000616/c61d1f66-1ac8-4e7f-8f92-7db8e5a542d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3bc732_c0a2_4dde_8d09_5bc25d84df62
ELIN-861735-2017 | EL-559833-2017 | 7/27/2017 12:01:22 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_Cord.png A 15 amp 120 volt extension cord has been permanently installed and run through a hole in the mobile homes structure to feed power from an exterior 15 amp GFCI receptacle to a 15 amp 120 volt heat trace tape under the mobile home. | 4 | Conductors, Misuse of flexible cords. | Extension_Cord.png | file://x:/photopub/docs/0000000637/f4336749-a3ba-4ab8-a97d-01fc86567588.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6baa95f7_198f_4ff0_8c83_29d34b693df1
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust4.png | file://x:/photopub/docs/0000000634/1df57e40-810c-4552-a719-685ac446236c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust7.png | file://x:/photopub/docs/0000000634/7a7451f6-e3d8-4f4b-9fde-08250a135cf1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust5.png | file://x:/photopub/docs/0000000634/d8cdb8e1-4e3f-43db-b9d7-c9840601808c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
ELOP-855438-2017 | 464 | 7/20/2017 1:37:24 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL240 | Class III Area is classified, accumulations of fibres or flyings are observed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Wood Dust Accumulations in multiple locations created explosion hazard. | 3 | Class III Area is classified, accumulations of fibres or flyings are observed. | Wood_dust1.png | file://x:/photopub/docs/0000000634/9c611921-2380-4c76-bcaf-ad3cf5383d16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fae032c9_fc71_44eb_b1dd_ab0722263c29
ELOP-862261-2017 | 464 | 7/20/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Armoured_cables1.png,Armoured_cables2.png Armoured cable not engaged to connector with exposed insulated conductors in wood processing facility. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Armoured_cables2.png | file://x:/photopub/docs/0000000634/b40b6eb2-d4ce-42e4-a034-3fca196b920f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b2fe5be_720f_42c5_8778_65a088578a76
BPVOP-845402-2017 | 2255317 | 6/27/2017 9:46:59 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Certificate of qualifications. | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Certificates.png The heating plant is not being supervised after normal working hours (day shift) by a 4th Class Engineer as required by the Power Engineers Regulations. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Certificates.png | file://x:/photopub/docs/0000000623/5debd5aa-545b-4b60-9223-ac44a4dda7c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e05df79_bf9c_4089_a8af_bcab7d4103ef
ELIN-862224-2017 | EL-477092-2016 | 7/27/2017 5:19:21 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_afci.png The new 15 amps 120 volt branch circuits for receptacles in newly added addition did not include AFCI protection, this can become a thermal hazard | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_afci.png | file://x:/photopub/docs/0000000637/9a8583d2-fe08-4f4a-8477-5626d1030351.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb4c24ca_b1ad_4eb1_8231_6d2aa301235e
ELIN-865897-2017 | EL-517195-2017 | 7/27/2017 7:44:39 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_AFCI_protection_on_cct_19.png In a new residential addition construction a 15amp 120 volt circuit was not to have arc fault circuit interruption protection. This can result in a thermal effect situation. Picture attached. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_AFCI_protection_on_cct_19.png | file://x:/photopub/docs/0000000637/b85e87a3-7130-436f-8e5b-3013d43fab05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59c49f33_6645_4e54_851d_60f5d8ff82c9
GAIN-838293-2017 | GA-527163-2017 | 7/6/2017 2:44:47 PM | ASSESS: GA: Final | JPG | #asFound Unvented relief style regulator installed indoors. | GA018 | Venting of pressure relief device indoors where source of ignition is present | 5 | 5 | #image1.JPG While assessing an installation I found a relief style regulator installed indoors without the relief vent piped outdoors. Should the regulator relieve raw gas would be dumped into the occupied space until it found a source of ignition which would result in a fire or explosion. This installation was valved off at both the regulator and meter. | 5 | Venting of pressure relief device indoors where source of ignition is present | image1.JPG | file://x:/photopub/docs/0000000626/29eb59b5-d37f-4183-9b26-b9dfef59a90c.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__853a625d_6c58_4349_9c90_2a915c2c7afe
AMOP-827837-2017 | UW-541131-2017 | 6/2/2017 9:47:10 AM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Missing_railings_and_landings_1.png,Missing_railings_and_landings_2.png,Missing_railings_and_landings_3.png Missing handrails and stairway landings, could b a fall hazard for guests if work not completed. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Missing_railings_and_landings_1.png | file://x:/photopub/docs/0000000609/781c42d6-9c26-4a56-b482-6323d06ca8de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61247831_fa18_45d1_9f85_90ba11816be7
AMOP-827837-2017 | UW-541131-2017 | 6/2/2017 9:47:10 AM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Missing_railings_and_landings_1.png,Missing_railings_and_landings_2.png,Missing_railings_and_landings_3.png Missing handrails and stairway landings, could b a fall hazard for guests if work not completed. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Missing_railings_and_landings_2.png | file://x:/photopub/docs/0000000609/40801923-af66-4f50-8b4c-b7b1ae72ae54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61247831_fa18_45d1_9f85_90ba11816be7
AMOP-827837-2017 | UW-541131-2017 | 6/2/2017 9:47:10 AM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Missing_railings_and_landings_1.png,Missing_railings_and_landings_2.png,Missing_railings_and_landings_3.png Missing handrails and stairway landings, could b a fall hazard for guests if work not completed. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Missing_railings_and_landings_3.png | file://x:/photopub/docs/0000000609/1f9fa459-00ee-4799-ae5f-e04c98633b7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61247831_fa18_45d1_9f85_90ba11816be7
AMOP-827832-2017 | UW-541120-2017 | 6/2/2017 10:30:26 AM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Railings_decking_to_complete1.png,Railings_decking_to_complete2.png railings and decking work was not completed at time of inspection, could be a fall hazard if not completed. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Railings_decking_to_complete1.png | file://x:/photopub/docs/0000000609/6e3d732d-3baf-4f75-b797-5ec6dee7a20c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__beda777d_f08c_48ec_8c77_b7f83d375127
BPVOP-850315-2017 | 2289519 | 6/8/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Psvs.png,Safety_valves-.png All pressure relief devices require periodic inspection, testing and service. Upon assessment of a evaporator with a maximum allowable working pressure of 225 psig, it was determined there was no records of service or replacement for the pressure relief devices. Potential exists for a pressure relief device not functioning during a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valves-.png | file://x:/photopub/docs/0000000625/c9faa94f-86ab-41b6-b8d9-e43ef4276dde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__737fb9a3_5991_4050_a236_f198b2d97e71
BPVOP-850322-2017 | 2289518 | 6/8/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Psv_s.png,Safety_valves.png All pressure relief devices require periodic inspection, testing and service. Upon assessment of a condenser with a maximum allowable working pressure of 225 psig, it was determined there was no records of service or replacement for the pressure relief devices. Potential exists for a pressure relief device not functioning during a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valves.png | file://x:/photopub/docs/0000000625/be92cbdd-3026-4759-a390-2d9d962c497b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fd36b9a_f7f4_4de4_8bab_eb4095e9b4b5
BPVOP-863138-2017 | 3805684 | 7/21/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Fireside_tubes.png Upon the fireside inspection of a Hot Water Boiler with MAWP of 150 psig and manufactured in 1977, significant corrosion and pitting was found. This can contribute to the failure of the boiler tubes. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Fireside_tubes.png | file://x:/photopub/docs/0000000634/fd3ed763-9d22-4099-9cfe-a99c7f4a1bc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d78632ba_a369_4de4_a24a_2cbaac89af3e
ELIN-831578-2017 | EL-541332-2017 | 6/7/2017 10:46:32 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Fan outlet box is not approved for the use. | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Fan_.png Rough wire of new single-family dwelling. A plastic outlet box has been used in the living room to attempt to support a pendant type of fan. The box is not suitable to support that type of weight especially if the fan blades are not balanced correctly. Damage to the equipment and danger to persons in the area upon a failure of the box. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fan_.png | file://x:/photopub/docs/0000000612/36d92f1e-844c-4c2f-8d72-98500dc53fb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a2b22df_c13d_41be_a6f1_9c48460d4349
ELIN-847657-2017 | EL-511234-2017 | 6/30/2017 2:29:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Unapproved_pole1.png,Unapproved_pole2.png,Unapproved_pole3.png,Unapproved_pole4.png Unapproved metre pole. Possibility for failure and iresulting in fire or shock. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Unapproved_pole4.png | file://x:/photopub/docs/0000000624/b7d96678-7fe9-435a-b7f1-fae0a900abad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1161b1b_462e_4b23_9970_2d70c745b1d2
ELIN-847657-2017 | EL-511234-2017 | 6/30/2017 2:29:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Unapproved_pole1.png,Unapproved_pole2.png,Unapproved_pole3.png,Unapproved_pole4.png Unapproved metre pole. Possibility for failure and iresulting in fire or shock. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Unapproved_pole1.png | file://x:/photopub/docs/0000000624/f1ca9245-ad06-4429-aee9-1bd93da51a99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1161b1b_462e_4b23_9970_2d70c745b1d2
ELIN-847657-2017 | EL-511234-2017 | 6/30/2017 2:29:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Unapproved_pole1.png,Unapproved_pole2.png,Unapproved_pole3.png,Unapproved_pole4.png Unapproved metre pole. Possibility for failure and iresulting in fire or shock. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Unapproved_pole2.png | file://x:/photopub/docs/0000000624/c0f0e4af-0039-4c1b-9b2a-fbd79a02a1f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1161b1b_462e_4b23_9970_2d70c745b1d2
ELIN-847657-2017 | EL-511234-2017 | 6/30/2017 2:29:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Unapproved_pole1.png,Unapproved_pole2.png,Unapproved_pole3.png,Unapproved_pole4.png Unapproved metre pole. Possibility for failure and iresulting in fire or shock. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Unapproved_pole3.png | file://x:/photopub/docs/0000000624/7877916d-0d37-4026-8bad-aaa10042486c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1161b1b_462e_4b23_9970_2d70c745b1d2
ELIN-543666-2016 | EL-301436-2015 | 5/16/2017 8:18:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #15790_Rose_Prairie_Road1.png,15790_Rose_Prairie_Road2.png,15790_Rose_Prairie_Road3.png Service conductors do not enter the service box. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 15790_Rose_Prairie_Road3.png | file://x:/photopub/docs/0000000601/7f02b55b-4d71-4956-b265-268427fd7037.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acab0af5_2b9d_4821_8760_e3c3c427d210
ELIN-543666-2016 | EL-301436-2015 | 5/16/2017 8:18:57 PM | ASSESS: EL: Service Connection | png | #asFound Conductors entering consumer ear side of service. | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #15790_Rose_Prairie_Road1.png,15790_Rose_Prairie_Road2.png,15790_Rose_Prairie_Road3.png Service conductors do not enter the service box. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 15790_Rose_Prairie_Road1.png | file://x:/photopub/docs/0000000601/e15edd72-e8ca-4f62-a0bf-19740bf49c62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acab0af5_2b9d_4821_8760_e3c3c427d210
BPVOP-863165-2017 | 2271461 | 7/21/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Temperature_and_pressure_relief_valve.png Upon assessment it is determined that domestic hot water storage tank(3.0m long and 1.50m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 125psig and Maximum Allowable Working Temperature (MAWT) of 650* fahrenheit has a temperature and pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Temperature_and_pressure_relief_valve.png | file://x:/photopub/docs/0000000634/558ee64a-c5e8-4a84-a0f8-b6f13a06397c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebfacbdc_bbf9_4791_8e97_d5e574a8b297
ELIN-846433-2017 | EL-548890-2017 | 6/30/2017 9:20:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #A.png Outlet box hanging from conductors. Outlet box not supported. Soow flexible cable entered into box with a non metallic sheathed cable connector. No gfci protection for outlets used for construction power. | 4 | Conductors, Misuse of flexible cords. | A.png | file://x:/photopub/docs/0000000623/52f9c360-4d2e-485b-ac94-ffb716b14ac0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02a0277d_9059_49f9_8e8c_9f9e1f169495
AMOP-827832-2017 | UW-541120-2017 | 6/2/2017 10:30:26 AM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Railings_decking_to_complete1.png,Railings_decking_to_complete2.png railings and decking work was not completed at time of inspection, could be a fall hazard if not completed. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Railings_decking_to_complete2.png | file://x:/photopub/docs/0000000609/a2d768ed-be78-47fc-86f8-e0e9c7cf172c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__beda777d_f08c_48ec_8c77_b7f83d375127
ELIN-828673-2017 | EL-535887-2017 | 6/6/2017 10:05:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | #A1.png,A2.png,A3.png,A4.png Cables in contact with heating ducts. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A4.png | file://x:/photopub/docs/0000000611/002cf69e-bd9c-4091-a12f-b677fbe2f179.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28c5bae1_868c_4299_9d20_664a1736a6fd
ELIN-828673-2017 | EL-535887-2017 | 6/6/2017 10:05:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | #A1.png,A2.png,A3.png,A4.png Cables in contact with heating ducts. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A2.png | file://x:/photopub/docs/0000000611/eb979fcc-311d-4b0d-80b7-890f5d049f38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28c5bae1_868c_4299_9d20_664a1736a6fd
ELIN-828673-2017 | EL-535887-2017 | 6/6/2017 10:05:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | #A1.png,A2.png,A3.png,A4.png Cables in contact with heating ducts. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A1.png | file://x:/photopub/docs/0000000611/cfcf14b1-4dd3-4dbe-a988-80375f92b8c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28c5bae1_868c_4299_9d20_664a1736a6fd
ELIN-828673-2017 | EL-535887-2017 | 6/6/2017 10:05:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | #A1.png,A2.png,A3.png,A4.png Cables in contact with heating ducts. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A3.png | file://x:/photopub/docs/0000000611/4ad7e170-1ede-4eb2-a8ca-38eac7b200d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28c5bae1_868c_4299_9d20_664a1736a6fd
ELOP-855065-2017 | 4967931 | 7/11/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Flexible_cord_used_as_permanent_wiring.png 15 amp, 120 volt flexible cord has been attached to structure and used as permanent wiring. This is a thermal issue. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_permanent_wiring.png | file://x:/photopub/docs/0000000631/230698a2-dcbc-4073-964a-50fc89bbc575.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1334835d_642d_4cfd_a4a2_ae913fddf3d9
ELIN-842049-2017 | EL-544969-2017 | 6/27/2017 12:28:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Plywood_mount.png At an existing single family dwelling, a new overhead 200amp 120/240volt 1phase service pole is being installed without the approved mounting hardware on the power pole being installed. This can lead to an "Equipment Damage" Scenario. Pic attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Plywood_mount.png | file://x:/photopub/docs/0000000622/efa0b99b-587b-4895-b462-77afe790a800.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51773e19_4d88_48f2_a385_73731a840816
GAIN-851675-2017 | GA-527030-2017 | 7/7/2017 2:56:29 PM | ASSESS: GA: Final | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | #Gas_connector1.png | 3 | Non-certified appliance connector | Gas_connector1.png | file://x:/photopub/docs/0000000627/930550df-fdd3-4b34-975f-3e8b61a6139e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86bcc24e_2963_4350_90fb_6acd18aaa794
GAIN-825985-2017 | GA-539922-2017 | 5/31/2017 12:29:44 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #ABS_venting_material_not_approved_for_application1.png,ABS_venting_material_not_approved_for_application2.png,ABS_venting_material_not_approved_for_application3.png,ABS_venting_material_not_approved_for_application4.png ABS venting material is not approved for application. Venting products exceeding the temperature rating of ABS venting material can cause deterioration and possible leakage of the venting system. | 3 | Unapproved venting material | ABS_venting_material_not_approved_for_application1.png | file://x:/photopub/docs/0000000608/b0436ec1-4f91-48d1-b901-7ac6616dd83c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c7aeae4_7164_4bdb_bb64_6070964d146c
GAIN-825985-2017 | GA-539922-2017 | 5/31/2017 12:29:44 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #ABS_venting_material_not_approved_for_application1.png,ABS_venting_material_not_approved_for_application2.png,ABS_venting_material_not_approved_for_application3.png,ABS_venting_material_not_approved_for_application4.png ABS venting material is not approved for application. Venting products exceeding the temperature rating of ABS venting material can cause deterioration and possible leakage of the venting system. | 3 | Unapproved venting material | ABS_venting_material_not_approved_for_application4.png | file://x:/photopub/docs/0000000608/62cc9573-6c94-4d3f-960c-a0bbcaea26a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c7aeae4_7164_4bdb_bb64_6070964d146c
ELIN-839560-2017 | EL-546693-2017 | 6/27/2017 2:59:36 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_Cord.png At an existing modular home recertification, a 15amp 120volt Exterior outlet box was found to supply power to the heat tracing underside of unit. This can lead to a "Thermal Effect" condition. Pic attached. | 4 | Conductors, Misuse of flexible cords. | Extension_Cord.png | file://x:/photopub/docs/0000000622/ae1fef22-cc79-4db9-9e27-8eabfeebd46f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e82937fb_9d8a_42eb_af92_3837eeae2e64
BPVIN-847118-2017 | UW-552660-2017 | 9/21/2017 1:09:56 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound Water heater nameplate. | BP000 | No Created Hazard Identified | 0 | 0 | #Nameplate.png An emergency disconnect switch used to shut down the heaters from a remote location, i.e outside of the boiler room is not provided. No lockable isolation switch is provided to assure zero energy to the heaters if maintenance is required on them. | 0 | No Created Hazard Identified | Nameplate.png | file://x:/photopub/docs/0000000624/946e12a6-e5d2-4652-883e-3c8b271a818e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da83d662_d220_4b7d_8ac3_c4561a8f7246
ELIN-848814-2017 | EL-551127-2017 | 7/4/2017 9:42:14 AM | ASSESS: EL: Service Connection | png | #asFound The label on this meter base clearly shows that it is approved for use with copper conductors only. | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Meter_base.png Service connection for a temporary construction service. The meter base for revenue metering is approved for use with copper conductors only. A meter base has been installed with aluminum conductors as well as copper conductors. There is a danger of a fire hazard because the meter base is not approved for use with aluminum conductors. The aluminum conductors can react with the lugs approved for use only with copper conductors. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_base.png | file://x:/photopub/docs/0000000624/7f6bc7b2-7666-4a46-918b-4539895490ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bedb26a3_7ac6_45bd_b702_c4ca8a8ca1b1
ELHE-811129-2017 | HE-531087-2017 | 4/11/2017 11:14:51 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Modified_light_fixture_in_school.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Modified_light_fixture_in_school.png | file://x:/photopub/docs/0000000601/d1e72f4a-d90f-447f-96e3-0ca96a5c1eb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15838b9a_f3dc_4b79_8b37_d2d905a26cf5
ELHE-811129-2017 | HE-531087-2017 | 4/11/2017 11:14:51 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Modified_light_fixture_in_school.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Modified_light_fixture_in_school.png | file://x:/photopub/docs/0000000601/f549f09c-5927-4818-aa06-e1360b12f4e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15838b9a_f3dc_4b79_8b37_d2d905a26cf5
ELHE-811129-2017 | HE-531087-2017 | 4/11/2017 11:14:51 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | #Modified_light_fixture_in_school.png Covers must be provided for electrical equipment to prevent shock injury. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Modified_light_fixture_in_school.png | file://x:/photopub/docs/0000000601/7f7ecfea-80f9-438d-b164-cea56d508f9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15838b9a_f3dc_4b79_8b37_d2d905a26cf5
GAIN-825985-2017 | GA-539922-2017 | 5/31/2017 12:29:44 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #ABS_venting_material_not_approved_for_application1.png,ABS_venting_material_not_approved_for_application2.png,ABS_venting_material_not_approved_for_application3.png,ABS_venting_material_not_approved_for_application4.png ABS venting material is not approved for application. Venting products exceeding the temperature rating of ABS venting material can cause deterioration and possible leakage of the venting system. | 3 | Unapproved venting material | ABS_venting_material_not_approved_for_application2.png | file://x:/photopub/docs/0000000608/cfc0827e-c73d-4afd-bab3-431862cbef86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c7aeae4_7164_4bdb_bb64_6070964d146c
GAIN-825985-2017 | GA-539922-2017 | 5/31/2017 12:29:44 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #ABS_venting_material_not_approved_for_application1.png,ABS_venting_material_not_approved_for_application2.png,ABS_venting_material_not_approved_for_application3.png,ABS_venting_material_not_approved_for_application4.png ABS venting material is not approved for application. Venting products exceeding the temperature rating of ABS venting material can cause deterioration and possible leakage of the venting system. | 3 | Unapproved venting material | ABS_venting_material_not_approved_for_application3.png | file://x:/photopub/docs/0000000608/4afbd868-2408-407c-8b88-5e7eaff4350a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c7aeae4_7164_4bdb_bb64_6070964d146c
BPVOP-827070-2017 | 2291749 | 7/17/2017 | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound Uncalibrated gauge | BP096 | 2.0.1 Control system may overrun - No servicing or testing program in place and no record or validation of any servicing and testing | 3 | 3 | #Pressgage.png Owner has not established or conducted scheduled servicing/testing of all safety devices associated with the boiler or gas systems. | 3 | 2.0.1 Control system may overrun - No servicing or testing program in place and no record or validation of any servicing and testing | Pressgage.png | file://x:/photopub/docs/0000000632/110dfa4d-c508-4019-8589-0e4a8845f370.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3D1C098C_98F3_45A6_BEB2_4E79A781C58F
BPVOP-860463-2017 | BPV-0000389321-2016 | 7/18/2017 3:44:07 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | #No_low_water_cut_out.png Boiler model requires a low water cut off device with a manual reset. Boiler found in operation with flow switch safety device that does not meet code. The risk is that an actual low water condition would not shut the boiler flame off and this would cause the boiler to overheat and melt causing damage to equipment and risk of injury to personnel in close proximity. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | No_low_water_cut_out.png | file://x:/photopub/docs/0000000633/531931ca-2f13-40d1-b61d-90b811ecdc20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a799dfb7_2147_4f6a_9e0b_a0d9a5d8a4d0
ELIN-853643-2017 | EL-551240-2017 | 7/11/2017 9:40:24 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Shower_stall_receptacles.png The 15 amp 120 volt GFCI receptacles in the main floor washroom are located within 500mm of the shower stall. Shower stall construction does not provide enough evidence the receptacles will be located a minimum of 500mm from opening, this can create a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Shower_stall_receptacles.png | file://x:/photopub/docs/0000000629/3145eb26-5b39-4a80-b207-fce6b1a20da5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82752218_10f3_4884_a160_22e6a19a2590
ELIN-826934-2017 | EL-437927-2016 | 6/1/2017 1:35:47 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Energized_panel.png Main service panel is energized. Branch circuit breaker locations are missing breakers or fillers, thus leaving exposed energized bussing. Accidental contact with bussing may result in shock or arc flash for persons and equipment. Room is not normaly accessible to the public this is a locked site | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Energized_panel.png | file://x:/photopub/docs/0000000609/ce5a684a-ebd0-4201-a229-9c1368b31c9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc4bdb8b_08a7_4116_adb5_c3dc8795f993
ELIN-820464-2017 | EL-514356-2017 | 6/13/2017 10:35:38 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #No_GFCI.png In a new residential garage construction two 15 amp 120 volt outdoor receptacles were found to have no ground fault protection. This could lead to a shock hazard situation. Picture attached. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_GFCI.png | file://x:/photopub/docs/0000000615/6c8ebd4c-925a-4ff3-a3f1-985bb8a817b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1388d4c4_f885_4cf3_8659_6dc6a31e82ee
ELIN-850524-2017 | EL-542915-2017 | 7/5/2017 12:18:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_Connection1.png,Grounding_Connection2.png A new 200 amp 240 volt service has been installed but the ground wire from the grounding electrode has been terminated at a bonding lug in the Panel instead of the neutral bar. This poses a shock hazard and potential damage to the equipment has fault currents and neutral currents may not travel back to the supply transformer or allow the main breaker to trip, these currents could be present on the Electrical Equipment. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_Connection2.png | file://x:/photopub/docs/0000000626/f88cbf22-0994-4fb1-b063-56e1e00d5394.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cdbd274_6b6d_4db5_8b00_ad0a894b12ef
ELIN-850524-2017 | EL-542915-2017 | 7/5/2017 12:18:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_Connection1.png,Grounding_Connection2.png A new 200 amp 240 volt service has been installed but the ground wire from the grounding electrode has been terminated at a bonding lug in the Panel instead of the neutral bar. This poses a shock hazard and potential damage to the equipment has fault currents and neutral currents may not travel back to the supply transformer or allow the main breaker to trip, these currents could be present on the Electrical Equipment. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_Connection1.png | file://x:/photopub/docs/0000000626/f6579477-3a9d-4cc0-b690-25bf2535bb89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cdbd274_6b6d_4db5_8b00_ad0a894b12ef
BPVOP-859238-2017 | BPV-035121-2013 | 7/17/2017 11:14:52 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound An emergency shutdown switch must be installed on the boiler and placed just outside the boiler room door or just inside where it can be reached without entering the boiler room door. | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Shutdown_switch.png Boiler does not have remote emergency shut down switch located outside the door or just inside the door allowing the boiler to be shut down without entering the boiler room in the event of an emergency. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Shutdown_switch.png | file://x:/photopub/docs/0000000634/365a73e3-6db9-4e54-81f3-1358bdc10eb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1be5f04_5f8e_42fb_bb57_69228265a811
AMOP-821585-2017 | 2053183 | 5/24/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #indications_of_cracking1.png,indications_of_cracking2.png,indications_of_cracking3.png,indications_of_cracking4.png,indications_of_cracking5.png Multiple indications of cracking and corrosion on ride; trolley's, sweeps, track and decking all have discontinuities | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | indications_of_cracking5.png | file://x:/photopub/docs/0000000606/b361476d-fbff-491c-9e03-9f46c53b0b46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b339e9cb_d512_486c_9b9b_5bf456379025
AMOP-821585-2017 | 2053183 | 5/24/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #indications_of_cracking1.png,indications_of_cracking2.png,indications_of_cracking3.png,indications_of_cracking4.png,indications_of_cracking5.png Multiple indications of cracking and corrosion on ride; trolley's, sweeps, track and decking all have discontinuities | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | indications_of_cracking1.png | file://x:/photopub/docs/0000000606/c8b7d74f-8c0b-42bc-af84-ec80ed846c24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b339e9cb_d512_486c_9b9b_5bf456379025
AMOP-821585-2017 | 2053183 | 5/24/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #indications_of_cracking1.png,indications_of_cracking2.png,indications_of_cracking3.png,indications_of_cracking4.png,indications_of_cracking5.png Multiple indications of cracking and corrosion on ride; trolley's, sweeps, track and decking all have discontinuities | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | indications_of_cracking3.png | file://x:/photopub/docs/0000000606/9fc03906-5659-4bf1-8001-a6938d3005b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b339e9cb_d512_486c_9b9b_5bf456379025
ELHE-828238-2017 | HE-541385-2017 | 5/24/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #Supply_service_connection_.png At a new resort sub-division, a new single family dwelling, 100amp 120/240volt supply service was found energized with unapproved mounting support. This can lead to an "Equipment Damage" situation. Pic attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Supply_service_connection_.png | file://x:/photopub/docs/0000000609/92226d87-8847-412b-9e1c-42f503a01a17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ce072dc_9dde_4f71_940b_74ef1938e0c9
ELIN-843107-2017 | EL-537437-2017 | 6/28/2017 3:10:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Improperly_bonded_grounded_service_conductors1.png,Improperly_bonded_grounded_service_conductors2.png In a single family dwelling renovation service upgrade the 200 amp 120/240 volt service and feeder conductors were found to be improperly bonded to ground. Improperly bonded and grounded service and feeder conductors can create alternate paths to ground creating a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Improperly_bonded_grounded_service_conductors2.png | file://x:/photopub/docs/0000000623/8cde06d4-7dd7-4567-8f11-4fb57d09fc5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d40ec9_3680_4892_8f78_f193d8480930
ELIN-843107-2017 | EL-537437-2017 | 6/28/2017 3:10:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Improperly_bonded_grounded_service_conductors1.png,Improperly_bonded_grounded_service_conductors2.png In a single family dwelling renovation service upgrade the 200 amp 120/240 volt service and feeder conductors were found to be improperly bonded to ground. Improperly bonded and grounded service and feeder conductors can create alternate paths to ground creating a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Improperly_bonded_grounded_service_conductors1.png | file://x:/photopub/docs/0000000623/b1da7a23-7df6-4cd9-90c8-ca867c9d702b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93d40ec9_3680_4892_8f78_f193d8480930
ELIN-844392-2017 | EL-545303-2017 | 6/28/2017 8:59:12 AM | ASSESS: EL: Final | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 2 | #2.png Service mast conduit was extended during renovation. Mast and service conductors were left inside of the dwelling for greater distance of 1.5m. This is a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 2.png | file://x:/photopub/docs/0000000623/3f60e44f-7d5d-429c-9c88-9a0e866da65e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1615dc8a_bfef_4caf_9c7a_c9fd7f19e360
AMOP-821585-2017 | 2053183 | 5/24/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #indications_of_cracking1.png,indications_of_cracking2.png,indications_of_cracking3.png,indications_of_cracking4.png,indications_of_cracking5.png Multiple indications of cracking and corrosion on ride; trolley's, sweeps, track and decking all have discontinuities | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | indications_of_cracking2.png | file://x:/photopub/docs/0000000606/2d4585a5-5777-47f9-b992-390a09214aa2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b339e9cb_d512_486c_9b9b_5bf456379025
ELIN-861533-2017 | EL-560470-2017 | 7/24/2017 2:25:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Cable11.png,Cable12.png,Cable13.png,Cable14.png,Cable15.png ACWU cable installed underground without inspection request, no sand present around cable at time of assessment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable14.png | file://x:/photopub/docs/0000000634/80deba6a-b94b-4a05-8799-7eb41da4e288.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4c4885_6d70_42c4_9b7a_1db5218980b2
ELIN-861533-2017 | EL-560470-2017 | 7/24/2017 2:25:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Cable11.png,Cable12.png,Cable13.png,Cable14.png,Cable15.png ACWU cable installed underground without inspection request, no sand present around cable at time of assessment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable11.png | file://x:/photopub/docs/0000000634/8681deef-e6b6-49cb-80fc-47b6b341099a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4c4885_6d70_42c4_9b7a_1db5218980b2
ELIN-861533-2017 | EL-560470-2017 | 7/24/2017 2:25:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Cable11.png,Cable12.png,Cable13.png,Cable14.png,Cable15.png ACWU cable installed underground without inspection request, no sand present around cable at time of assessment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable13.png | file://x:/photopub/docs/0000000634/27800c78-a0cc-4d87-8230-6807b95a77e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4c4885_6d70_42c4_9b7a_1db5218980b2
ELIN-861533-2017 | EL-560470-2017 | 7/24/2017 2:25:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Cable11.png,Cable12.png,Cable13.png,Cable14.png,Cable15.png ACWU cable installed underground without inspection request, no sand present around cable at time of assessment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable12.png | file://x:/photopub/docs/0000000634/503a235e-c917-465f-a020-61f7faf46628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4c4885_6d70_42c4_9b7a_1db5218980b2
ELIN-861533-2017 | EL-560470-2017 | 7/24/2017 2:25:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound ACWU cable installed underground without inspection request, no sand present around cable at time of assessment. | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Cable11.png,Cable12.png,Cable13.png,Cable14.png,Cable15.png ACWU cable installed underground without inspection request, no sand present around cable at time of assessment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cable15.png | file://x:/photopub/docs/0000000634/80c1ee65-138e-4d6a-bb9e-07f4d4e9c235.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4c4885_6d70_42c4_9b7a_1db5218980b2
ELIN-825053-2017 | EL-422767-2016 | 5/31/2017 10:15:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Cable_located_at_pinch_point_in_truss.png Non metallic sheathed cable has been installed at a pinch point in a truss next to a metal truss plate. If there is any settling of the structure there is risk of a short circuit which could arc and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_located_at_pinch_point_in_truss.png | file://x:/photopub/docs/0000000610/85ed188e-ad52-451f-bec6-8992898398ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2892f721_0df4_4fea_9f9e_30c5cb7e92ed
ELIN-825053-2017 | EL-422767-2016 | 5/31/2017 10:15:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Cable_located_at_pinch_point_in_truss.png Non metallic sheathed cable has been installed at a pinch point in a truss next to a metal truss plate. If there is any settling of the structure there is risk of a short circuit which could arc and cause a fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_located_at_pinch_point_in_truss.png | file://x:/photopub/docs/0000000610/02d271fc-4c20-4404-821e-3cda191a279a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2892f721_0df4_4fea_9f9e_30c5cb7e92ed
GAIN-826192-2017 | GA-506725-2017 | 6/5/2017 9:42:55 PM | ASSESS: GA: Final | png | #asFound Return air grills installed in the same enclosure as the air intake for the furnace | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Return_air_.png Downflow Furnace circulating return air installed in the same enclosure as the air intake for the furnace and Water Heater. This could potentially cause combustion air problems for the furnace and water heater, which in turn the improper burning of propane could be created causing carbon monoxide. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Return_air_.png | file://x:/photopub/docs/0000000611/aef682c1-f290-4f76-aada-7b6fe3306da6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05d604a6_fe99_4ffc_add7_d458907fc46b
ELOP-823315-2017 | 5400239 | 6/5/2017 11:47:58 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Ac901.png,Ac902.png,Ac903.png Armoured cable not terminated in a box creating a potential shock or fire hazard if energized. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Ac903.png | file://x:/photopub/docs/0000000611/b318c0f3-f1e3-4c0d-a182-6210f9c68f5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb829ea4_18c1_4501_bb30_8a5b12afa9cd
ELOP-823315-2017 | 5400239 | 6/5/2017 11:47:58 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Ac901.png,Ac902.png,Ac903.png Armoured cable not terminated in a box creating a potential shock or fire hazard if energized. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Ac901.png | file://x:/photopub/docs/0000000611/5cb47fc0-2e82-4c3e-bf84-0f77ccf546de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb829ea4_18c1_4501_bb30_8a5b12afa9cd
GAIN-850665-2017 | GA-552201-2017 | 7/12/2017 1:18:11 PM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Deepfat_fryer.png The as-found condition is that an uncertified deep fat fryer has been installed in a commercial kitchen. The potential hazard is that because the uncertified piece of equipment has not been tested to see if it conforms to accepted gas safety standards, the equipment could operate in an unsafe manner resulting in a fire hazard and injury. | 3 | Uncertified appliance connected to gas supply but not in service | Deepfat_fryer.png | file://x:/photopub/docs/0000000629/34800598-c839-4b36-93c9-adf4df1202dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__837e49c2_3ab8_4ce3_945c_8be539769f08
GAIN-854882-2017 | GA-526859-2017 | 7/12/2017 10:25:01 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent.png Unapproved fittings used for exhaust of Navien water heater. High temp S636 fittings are required. Fittings installed are not designed for exhaust outlet temperatures and could fail over time causing spillage of flue gases into the mechanical room. | 3 | Unapproved venting material | Vent.png | file://x:/photopub/docs/0000000629/e065f491-2ebd-46e8-82a3-c02dd2788b2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04ad7763_03c5_4515_b440_872d174146d4
GAWP-837038-2017 | GA-483297-2016 | 6/14/2017 1:05:58 PM | ASSESS: GA Work In Progress | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Furnace_air_intake2.png Furnace air intake pipe is to close to the relief vent of the gas regulators on the gas meters. If the regulators were to vent gas the air intakes may suck the gas into the appliance possibly leading to fire or explosion. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Furnace_air_intake2.png | file://x:/photopub/docs/0000000616/9661c201-fe9d-44cb-a095-690f792ed523.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__384aa8cd_1982_4d3e_8fe0_c7ea2ede0ee6
GAWP-837039-2017 | GA-367052-2016 | 6/14/2017 12:55:10 PM | ASSESS: GA Work In Progress | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Furnace_air_intake.png Furnace air intake pipe is to close to the relief vent of the gas regulators on the gas meters. If the regulators were to vent gas the air intakes may suck the gas into the appliance possibly leading to fire or explosion. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Furnace_air_intake.png | file://x:/photopub/docs/0000000616/db704e65-7fd0-4af2-9e53-429fb377beef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5b3d0ca_9de6_4eac_90b4_9a982ec98099
BPOP-823156-2017 | BPV-455132-2015 | 5/25/2017 1:20:01 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | #Relief_roof.png Propane tank relief valve installed under a building roof, if relief discharges it will be obstructed. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Relief_roof.png | file://x:/photopub/docs/0000000605/17d82eda-e2c4-4d5a-a49e-1355e0d90648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__610cbd49_83eb_458a_97f0_ddc08df6097a
ELOP-823315-2017 | 5400239 | 6/5/2017 11:47:58 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Ac901.png,Ac902.png,Ac903.png Armoured cable not terminated in a box creating a potential shock or fire hazard if energized. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Ac902.png | file://x:/photopub/docs/0000000611/20bf6dbb-2ae6-4bb1-831b-fe3b2f2783c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb829ea4_18c1_4501_bb30_8a5b12afa9cd
ELOP-841625-2017 | EL-536304-2017 | 7/5/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound Panel fillers missing | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #V.png A 225 Amp 600 volt distribution panel was missing panel fillers. The panel door was closed and the panel is in a locked electrical room only accessible by maintenance staff. This is a potential shock hazard to an individual working in the area. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | V.png | file://x:/photopub/docs/0000000626/7ab54ab6-3b1f-4210-aaba-abc4feeb7c68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__AA945073_5E6F_4619_AF76_AD2DDFD8A2C4
BPVIN-867234-2017 | UW-564561-2017 | 7/27/2017 3:14:33 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD1.png,PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of an Air Receiver part of system with MAWP of 165 psig, I found a Pressure Relief Device not replaced within the last 5 years as per CSA B51-2014. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD2.png | file://x:/photopub/docs/0000000637/16354987-0ed9-4af6-b1a8-d70ef8713fc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__707ccb3e_fdfb_4425_9a2c_ad59c8c44ee3
BPVIN-867234-2017 | UW-564561-2017 | 7/27/2017 3:14:33 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD1.png,PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of an Air Receiver part of system with MAWP of 165 psig, I found a Pressure Relief Device not replaced within the last 5 years as per CSA B51-2014. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD1.png | file://x:/photopub/docs/0000000637/d4b4025d-ba56-4342-9810-394c8a3096d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__707ccb3e_fdfb_4425_9a2c_ad59c8c44ee3
GAIN-838600-2017 | GA-355438-2016 | 6/26/2017 12:55:40 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Asfound.png The as found condition was an installed brass fitting unapproved for the system. The as found hazard is unapproved fittings could be subject to undo wear and strain leading to a potentially hazardous gas leak. | 3 | Non-compliant material/fittings installed | Asfound.png | file://x:/photopub/docs/0000000621/cb5706b4-5e6c-4219-b47e-d73921c6932f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__887a7568_6bf7_4133_91b1_ac3e1acc87ad
BPVOP-830304-2017 | BPV-481182-2016 | 6/5/2017 1:39:41 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP112 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping under size | 3 | 3 | #Relief_valve_discharge.png The safety relief valve is not discharging to a safe location allowing the possibility of overflow or spray back into an area meant for human occupation. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping under size | Relief_valve_discharge.png | file://x:/photopub/docs/0000000610/a983ea7f-9fd3-4f21-8d2e-aeb5b00667f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e9da78f_6f6e_4011_92a8_c0dfe748dac4
ELIN-827809-2017 | EL-508595-2017 | 6/5/2017 2:35:41 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Gas_range_plug.png This assessment found that the gas range receptacle is not dedicated and is on with living room plugs and the hood fan, that could cause overloading on the circuit. This has the potential for fire in the event of a breaker failure. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Gas_range_plug.png | file://x:/photopub/docs/0000000611/6e87f28f-d5b9-4b73-ba8a-6e395fd4005f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e722bd1_665a_43f8_9dc5_c7027c52d1a8
ELHE-833277-2017 | HE-544664-2017 | 6/8/2017 6:08:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | #Service_ground1.png,Service_ground2.png,Service_ground3.png In a 120/240 volt, single phase electrical service, the neutral conductor must be connected to ground. A solidly grounded system facilitates a low-impedance fault current path through the grounded service conductor. This enables the overcurrent devices to operate quickly enough to prevent damage to the conductors or equipment. To ensure a solid ground path for the neutral, a ground conductor is connected between the neutral conductor in the service section of the electrical panel and a ground electrode outside. The ground electrode is usually a ground plate below grade or two 3m copper clad ground rods driven full length into the ground. During an assessment at an existing dwelling, the safety officer found only one ground rod installed on the exterior of the building. The ground rod was installed approximately 2.4m into the ground. The ground clamp used to connect the ground conductor to the rod was broken. The high impedance of this ground c | 3 | Continuity Bonding conductor is not observed or broken | Service_ground1.png | file://x:/photopub/docs/0000000613/ec8a29e3-e0bf-4411-8af4-95669f2deb82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53809ac1_030a_4d66_b4b5_97ed8bab9b37
ELHE-833277-2017 | HE-544664-2017 | 6/8/2017 6:08:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | #Service_ground1.png,Service_ground2.png,Service_ground3.png In a 120/240 volt, single phase electrical service, the neutral conductor must be connected to ground. A solidly grounded system facilitates a low-impedance fault current path through the grounded service conductor. This enables the overcurrent devices to operate quickly enough to prevent damage to the conductors or equipment. To ensure a solid ground path for the neutral, a ground conductor is connected between the neutral conductor in the service section of the electrical panel and a ground electrode outside. The ground electrode is usually a ground plate below grade or two 3m copper clad ground rods driven full length into the ground. During an assessment at an existing dwelling, the safety officer found only one ground rod installed on the exterior of the building. The ground rod was installed approximately 2.4m into the ground. The ground clamp used to connect the ground conductor to the rod was broken. The high impedance of this ground c | 3 | Continuity Bonding conductor is not observed or broken | Service_ground3.png | file://x:/photopub/docs/0000000613/d6a80e4a-cac5-4e14-a58b-9bbff1735223.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53809ac1_030a_4d66_b4b5_97ed8bab9b37
ELHE-833277-2017 | HE-544664-2017 | 6/8/2017 6:08:56 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | #Service_ground1.png,Service_ground2.png,Service_ground3.png In a 120/240 volt, single phase electrical service, the neutral conductor must be connected to ground. A solidly grounded system facilitates a low-impedance fault current path through the grounded service conductor. This enables the overcurrent devices to operate quickly enough to prevent damage to the conductors or equipment. To ensure a solid ground path for the neutral, a ground conductor is connected between the neutral conductor in the service section of the electrical panel and a ground electrode outside. The ground electrode is usually a ground plate below grade or two 3m copper clad ground rods driven full length into the ground. During an assessment at an existing dwelling, the safety officer found only one ground rod installed on the exterior of the building. The ground rod was installed approximately 2.4m into the ground. The ground clamp used to connect the ground conductor to the rod was broken. The high impedance of this ground c | 3 | Continuity Bonding conductor is not observed or broken | Service_ground2.png | file://x:/photopub/docs/0000000613/16e977f0-961a-44cf-bef7-9f1e049f6220.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53809ac1_030a_4d66_b4b5_97ed8bab9b37
GAIN-854554-2017 | GA-510059-2017 | 7/12/2017 11:41:04 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Unprotected_copper_tubing.png Physical protection of copper tubing absent. Copper tubing can be damaged when not appropriately secured at the connection to an appliance connector. | 2 | Physical protection of piping and tubing absent. | Unprotected_copper_tubing.png | file://x:/photopub/docs/0000000630/1666fba0-d9bf-4e5a-b7e4-6ac3cbcc6ec0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__416549f3_fb55_428a_bcca_e01cd2b90305
ELIN-840289-2017 | EL-437324-2016 | 6/19/2017 11:42:36 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Sub_distribution_supply1.png,Sub_distribution_supply2.png,Sub_distribution_supply3.png Sup distribution is being supplied by circuits run on the ground from the neighbouring property. Potential for shock or fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Sub_distribution_supply2.png | file://x:/photopub/docs/0000000618/e5b8d9fc-0f03-4f5d-8957-b3f862fdd9ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d696cf5_1af1_4e37_9367_b3c89a03ed33
ELIN-840289-2017 | EL-437324-2016 | 6/19/2017 11:42:36 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Sub_distribution_supply1.png,Sub_distribution_supply2.png,Sub_distribution_supply3.png Sup distribution is being supplied by circuits run on the ground from the neighbouring property. Potential for shock or fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Sub_distribution_supply1.png | file://x:/photopub/docs/0000000618/29a5e7ad-7108-46f9-809a-f447e50d5f54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d696cf5_1af1_4e37_9367_b3c89a03ed33
ELIN-840289-2017 | EL-437324-2016 | 6/19/2017 11:42:36 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Sub_distribution_supply1.png,Sub_distribution_supply2.png,Sub_distribution_supply3.png Sup distribution is being supplied by circuits run on the ground from the neighbouring property. Potential for shock or fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Sub_distribution_supply3.png | file://x:/photopub/docs/0000000618/00af2d90-93f7-4cc7-bce3-dc27e70facc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d696cf5_1af1_4e37_9367_b3c89a03ed33
ELIN-836451-2017 | UW-546583-2017 | 6/13/2017 3:10:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound as found | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Receptacle.png 120 Volt convenience receptacles are not supported adequately creating a potential shock and fire hazard. The receptacle pushes in a 1/2" when used. | 4 | Installation of electrical equipment Fixtures without suitable support. | Receptacle.png | file://x:/photopub/docs/0000000615/656403bb-6cae-44fc-abf2-008674b3ec71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d12f0a5d_d579_482b_9448_2e52ba3ac331
GAIN-817013-2017 | GA-529239-2017 | 5/29/2017 3:02:19 PM | ASSESS: GA: Rough-In | png | #asFound | GA100 | Hazards created by exhaust fans | 3 | 3 | #Dryer_operation_creates_a_negative_atmosphere_in_the_room_.png Conditions created by an exhaust fan do not allow for the natural vent operation of another appliance. This condition can lead to the appliance spilling flue products into the occupied space and exposure of the occupants to flue products. | 3 | Hazards created by exhaust fans | Dryer_operation_creates_a_negative_atmosphere_in_the_room_.png | file://x:/photopub/docs/0000000607/c94372e4-3f05-4695-8698-f6e4579171ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1b0d408_c276_4b47_8f39_e9b014ce756a
GAIN-822710-2017 | GA-408122-2016 | 5/29/2017 1:02:19 PM | ASSESS: GA: Final | png | #asFound | GA092 | Single appliance under fired = < 10 % due to improper sizing | 2 | 2 | #Undersized_regulator_for_tankless_water_heater_.png Regulator undersized for single appliance. Undersized regulator can cause insufficient gas supply for combustion creating incomplete combustion. | 2 | Single appliance under fired = < 10 % due to improper sizing | Undersized_regulator_for_tankless_water_heater_.png | file://x:/photopub/docs/0000000607/340b25f4-4275-4a9f-92de-2dc07687e4fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9da0144e_2b8c_4562_a5fb_72a6b0494e59
GAIN-846637-2017 | GA-552270-2017 | 6/30/2017 11:06:29 AM | ASSESS: GA: Final | png | #asFound | GA079 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | 3 | 3 | #Garys4.png Used regulator no longer approved for 2 lb inlet pressure. Regulator may not lock up and allow down stream pressure to exceed the pressure rating of appliance components. Possible over fire condition creating carbon monoxide. | 3 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | Garys4.png | file://x:/photopub/docs/0000000625/975e6cd6-f1b8-4442-8183-641e420da42a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64996ea8_0687_438b_b089_62b99f72f2c1
GAIN-826269-2017 | GA-399989-2016 | 6/1/2017 12:54:55 PM | ASSESS: GA: Final | png | #asFound Inadequately sized combustion air duct. | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Combustion_air_duct.png The size of the existing duct that supplies air to the water heater is to small according the the requirements of the manufacturer. This could potentially cause the water heater to not operate correctly and begin to produce harmful byproducts during the process of burning the natural gas. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air_duct.png | file://x:/photopub/docs/0000000609/534db9f2-c47e-4874-b8a4-a42026820351.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a30d973_76c0_497a_8cbe_4682ef9875cd
ELIN-828699-2017 | EL-475071-2016 | 6/8/2017 10:17:45 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Temp_power_2.png Temporary power provided for floor finishing is not entered into distribution panel by use of approved connectors. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_power_2.png | file://x:/photopub/docs/0000000613/259210ae-c35d-47b2-8743-d775748d1ba5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd2cf480_3251_4aeb_a86d_e8115b161eac
ELIN-864032-2017 | EL-561174-2017 | 7/25/2017 1:20:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Bare_primary_protector.png | 0 | No Created Hazard Identified | Bare_primary_protector.png | file://x:/photopub/docs/0000000635/5cab904d-03c0-4551-a754-228cef901d36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd4f352f_3977_42d9_9328_4844fbebc59b
ELIN-830256-2017 | UW-542735-2017 | 6/5/2017 3:26:16 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Cover_plates_missing_.png Energized electrical outlets do not have cover plates on them. This condition could lead to accidental contact of energized terminals and cause a shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Cover_plates_missing_.png | file://x:/photopub/docs/0000000611/8c8609e5-5d6d-4f89-8319-6bb5fce99a72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4420630_2bd5_47e9_9d97_3edc0fbaeb6f
AMOP-835992-2017 | AM-543510-2017 | 6/8/2017 4:59:37 PM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Water_leaking_from_flume_joint.png Chlorinated water is leaking onto a steel support structure from a flume joint. Chlorinated water dripping onto steel would result in corrosion and weakening of the support structure. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Water_leaking_from_flume_joint.png | file://x:/photopub/docs/0000000620/2b58aba1-fc3f-4e74-b240-78e438d77983.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db9ac719_2c26_4c89_9182_12b70dd0ed3f
ELIN-862257-2017 | EL-395636-2016 | 7/21/2017 9:54:50 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png Cables entered into panel without connectors through the front opening. This is a shock and fire hazard. The armour of the cables are not bonded and the cables and terminations are subject to strain. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A2.png | file://x:/photopub/docs/0000000634/69c784b4-c36d-41f9-adb9-9b00099e031d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c71c0b3_aaf3_4abb_a163_e03932b1520a
ELIN-860567-2017 | EL-560462-2017 | 7/21/2017 1:45:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png Type 1 panel installed in a wet location. A proper weather proof enclosure has not been provided. This is a shock hazard. | 3 | General Equipment is not approved for the specific use | B1.png | file://x:/photopub/docs/0000000634/83f71caa-66ea-4f56-9dce-89db2f9984f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f7d6c18_1ed1_44d6_978a_d076aab9f3ac
ELIN-860567-2017 | EL-560462-2017 | 7/21/2017 1:45:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png Type 1 panel installed in a wet location. A proper weather proof enclosure has not been provided. This is a shock hazard. | 3 | General Equipment is not approved for the specific use | B2.png | file://x:/photopub/docs/0000000634/8a50ca11-724e-48af-8c4b-005a91794068.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f7d6c18_1ed1_44d6_978a_d076aab9f3ac
ELIN-862257-2017 | EL-395636-2016 | 7/21/2017 9:54:50 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png Cables entered into panel without connectors through the front opening. This is a shock and fire hazard. The armour of the cables are not bonded and the cables and terminations are subject to strain. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A1.png | file://x:/photopub/docs/0000000634/2c96be09-470b-472e-b6ca-1bb96685daa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c71c0b3_aaf3_4abb_a163_e03932b1520a
ELIN-860567-2017 | EL-560462-2017 | 7/21/2017 1:45:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png Type 1 panel installed in a wet location. A proper weather proof enclosure has not been provided. This is a shock hazard. | 3 | General Equipment is not approved for the specific use | B3.png | file://x:/photopub/docs/0000000634/37ec09fd-dc7a-4e15-9eb0-c06c5156cb13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f7d6c18_1ed1_44d6_978a_d076aab9f3ac
AMOP-846625-2017 | 4789889 | 6/29/2017 2:17:58 PM | ASSESS: AM OP: Incident | png | #asFound | AM012 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | 3 | 3 | #Sweep_connection_to_hub1.png,Sweep_connection_to_hub2.png,Sweep_connection_to_hub3.png Sweep failed at hub connection when ride was between cycles (no load), sweep connection could fail while the device is in a cycle with riders. | 3 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | Sweep_connection_to_hub3.png | file://x:/photopub/docs/0000000623/8948e85b-9722-4e1c-b915-4b17c7441e6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b6fba9c_4e5c_4851_8ad9_23b6a56ed383
AMOP-846625-2017 | 4789889 | 6/29/2017 2:17:58 PM | ASSESS: AM OP: Incident | png | #asFound | AM012 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | 3 | 3 | #Sweep_connection_to_hub1.png,Sweep_connection_to_hub2.png,Sweep_connection_to_hub3.png Sweep failed at hub connection when ride was between cycles (no load), sweep connection could fail while the device is in a cycle with riders. | 3 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | Sweep_connection_to_hub2.png | file://x:/photopub/docs/0000000623/43cbad0c-621e-4712-9d5e-f88303b58ed6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b6fba9c_4e5c_4851_8ad9_23b6a56ed383
AMOP-846625-2017 | 4789889 | 6/29/2017 2:17:58 PM | ASSESS: AM OP: Incident | png | #asFound | AM012 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | 3 | 3 | #Sweep_connection_to_hub1.png,Sweep_connection_to_hub2.png,Sweep_connection_to_hub3.png Sweep failed at hub connection when ride was between cycles (no load), sweep connection could fail while the device is in a cycle with riders. | 3 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | Sweep_connection_to_hub1.png | file://x:/photopub/docs/0000000623/8b3aaa1b-99b8-4e03-bcc9-94546e6166af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b6fba9c_4e5c_4851_8ad9_23b6a56ed383
ELIN-866389-2017 | UW-564169-2017 | 7/26/2017 3:00:40 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMD_wiring_exposed_to_weather_.png Wire that is rated for dry or damp locations was used in a location that is exposed to the weather. This could lead to the insulation degrading to a point where there is a potential shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | NMD_wiring_exposed_to_weather_.png | file://x:/photopub/docs/0000000636/cc674574-0494-4f76-bf5a-2695116c6be2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af25eec5_9745_4036_a1bf_0dc4cb2b2511
GAIN-833836-2017 | GA-544959-2017 | 6/13/2017 11:56:35 AM | ASSESS: GA: Final | png | #asFound | GA139 | Incorrect appliance type installed for application | 3 | 3 | #Roof_top_unit_.png The as-found condition is that the roof top unit, only certified for outdoor use has been installed indoors. The potential hazard is that the unit will not function as per the manufacturer's intentions and may result in poor combustion and the production of carbon monoxide, which could enter the make-up air supply to the building. | 3 | Incorrect appliance type installed for application | Roof_top_unit_.png | file://x:/photopub/docs/0000000615/693cfd48-1ed3-4517-856a-cea470446f73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__657ad78c_f1fc_4301_b351_90402b721dd2
GAIN-809657-2017 | GA-519661-2017 | 5/19/2017 3:47:30 PM | ASSESS: GA: Final | png | #asFound | GA135 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | 2 | 2 | #Relief1.png,Relief2.png Boiler side had 2 pressure relief valves, none on domestic side, 1 relief not piped to floor, other in wrong orientation | 2 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | Relief2.png | file://x:/photopub/docs/0000000604/c2617916-2f7d-46d0-afa6-0ab425643d42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bed62097_fb9e_4be7_a5e6_24eed26098ba
GAIN-809657-2017 | GA-519661-2017 | 5/19/2017 3:47:30 PM | ASSESS: GA: Final | png | #asFound | GA135 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | 2 | 2 | #Relief1.png,Relief2.png Boiler side had 2 pressure relief valves, none on domestic side, 1 relief not piped to floor, other in wrong orientation | 2 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | Relief1.png | file://x:/photopub/docs/0000000604/62401ff2-d85f-4e82-a71d-057ee4fe43b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bed62097_fb9e_4be7_a5e6_24eed26098ba
ELIN-813619-2017 | EL-532483-2017 | 5/19/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_cable_exposed_to_damage_in_food_truck1.png,NMD90_cable_exposed_to_damage_in_food_truck2.png,NMD90_cable_exposed_to_damage_in_food_truck3.png,NMD90_cable_exposed_to_damage_in_food_truck4.png,NMD90_cable_exposed_to_damage_in_food_truck5.png,NMD90_cable_exposed_to_damage_in_food_truck6.png Non-metallic sheathed cables (NMD90) are required to be installed in areas where they will not be subject to mechanical damage after installation. This installation for wiring in a mobile food truck has exposed NMD90 cables a several locations at light fixtures, junction boxes, and the panel board. This is a shock and fire hazard if the sheathing on the cable and conductor insulation gets damaged and person or objects contact energized conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_cable_exposed_to_damage_in_food_truck4.png | file://x:/photopub/docs/0000000604/efe9b798-a070-4d7a-9cf3-9fed6ba8dd49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__527485c7_b061_4d2f_be13_0cad39b6772f
ELIN-813619-2017 | EL-532483-2017 | 5/19/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_cable_exposed_to_damage_in_food_truck1.png,NMD90_cable_exposed_to_damage_in_food_truck2.png,NMD90_cable_exposed_to_damage_in_food_truck3.png,NMD90_cable_exposed_to_damage_in_food_truck4.png,NMD90_cable_exposed_to_damage_in_food_truck5.png,NMD90_cable_exposed_to_damage_in_food_truck6.png Non-metallic sheathed cables (NMD90) are required to be installed in areas where they will not be subject to mechanical damage after installation. This installation for wiring in a mobile food truck has exposed NMD90 cables a several locations at light fixtures, junction boxes, and the panel board. This is a shock and fire hazard if the sheathing on the cable and conductor insulation gets damaged and person or objects contact energized conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_cable_exposed_to_damage_in_food_truck3.png | file://x:/photopub/docs/0000000604/7b1a556b-b76f-4dbb-ba4c-7e08249192ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__527485c7_b061_4d2f_be13_0cad39b6772f
ELIN-813619-2017 | EL-532483-2017 | 5/19/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_cable_exposed_to_damage_in_food_truck1.png,NMD90_cable_exposed_to_damage_in_food_truck2.png,NMD90_cable_exposed_to_damage_in_food_truck3.png,NMD90_cable_exposed_to_damage_in_food_truck4.png,NMD90_cable_exposed_to_damage_in_food_truck5.png,NMD90_cable_exposed_to_damage_in_food_truck6.png Non-metallic sheathed cables (NMD90) are required to be installed in areas where they will not be subject to mechanical damage after installation. This installation for wiring in a mobile food truck has exposed NMD90 cables a several locations at light fixtures, junction boxes, and the panel board. This is a shock and fire hazard if the sheathing on the cable and conductor insulation gets damaged and person or objects contact energized conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_cable_exposed_to_damage_in_food_truck5.png | file://x:/photopub/docs/0000000604/ab0db149-fc46-4c9d-a985-41a7bb200aae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__527485c7_b061_4d2f_be13_0cad39b6772f
ELIN-813619-2017 | EL-532483-2017 | 5/19/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_cable_exposed_to_damage_in_food_truck1.png,NMD90_cable_exposed_to_damage_in_food_truck2.png,NMD90_cable_exposed_to_damage_in_food_truck3.png,NMD90_cable_exposed_to_damage_in_food_truck4.png,NMD90_cable_exposed_to_damage_in_food_truck5.png,NMD90_cable_exposed_to_damage_in_food_truck6.png Non-metallic sheathed cables (NMD90) are required to be installed in areas where they will not be subject to mechanical damage after installation. This installation for wiring in a mobile food truck has exposed NMD90 cables a several locations at light fixtures, junction boxes, and the panel board. This is a shock and fire hazard if the sheathing on the cable and conductor insulation gets damaged and person or objects contact energized conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_cable_exposed_to_damage_in_food_truck2.png | file://x:/photopub/docs/0000000604/10a11883-cca3-42e1-ac2b-a572139cc468.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__527485c7_b061_4d2f_be13_0cad39b6772f
ELIN-813619-2017 | EL-532483-2017 | 5/19/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_cable_exposed_to_damage_in_food_truck1.png,NMD90_cable_exposed_to_damage_in_food_truck2.png,NMD90_cable_exposed_to_damage_in_food_truck3.png,NMD90_cable_exposed_to_damage_in_food_truck4.png,NMD90_cable_exposed_to_damage_in_food_truck5.png,NMD90_cable_exposed_to_damage_in_food_truck6.png Non-metallic sheathed cables (NMD90) are required to be installed in areas where they will not be subject to mechanical damage after installation. This installation for wiring in a mobile food truck has exposed NMD90 cables a several locations at light fixtures, junction boxes, and the panel board. This is a shock and fire hazard if the sheathing on the cable and conductor insulation gets damaged and person or objects contact energized conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_cable_exposed_to_damage_in_food_truck6.png | file://x:/photopub/docs/0000000604/edfee286-80a0-46be-b646-3969c55f5858.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__527485c7_b061_4d2f_be13_0cad39b6772f
ELIN-813619-2017 | EL-532483-2017 | 5/19/2017 | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_cable_exposed_to_damage_in_food_truck1.png,NMD90_cable_exposed_to_damage_in_food_truck2.png,NMD90_cable_exposed_to_damage_in_food_truck3.png,NMD90_cable_exposed_to_damage_in_food_truck4.png,NMD90_cable_exposed_to_damage_in_food_truck5.png,NMD90_cable_exposed_to_damage_in_food_truck6.png Non-metallic sheathed cables (NMD90) are required to be installed in areas where they will not be subject to mechanical damage after installation. This installation for wiring in a mobile food truck has exposed NMD90 cables a several locations at light fixtures, junction boxes, and the panel board. This is a shock and fire hazard if the sheathing on the cable and conductor insulation gets damaged and person or objects contact energized conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_cable_exposed_to_damage_in_food_truck1.png | file://x:/photopub/docs/0000000604/3ffb667b-8272-43e5-a0c9-543f47bc42cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__527485c7_b061_4d2f_be13_0cad39b6772f
GAUP-838410-2017 | UW-547747-2017 | 6/15/2017 4:35:12 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #Bakery.png Corrugated stainless steel tubing missing bond connection. Corrugated stainless steel tubing is highly susceptible to electrical fault damage which could lead to uncontrolled release of gas. Possible explosion and or fire risk. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Bakery.png | file://x:/photopub/docs/0000000616/1d164bd7-3e3a-4cb7-a11e-5d7b6149596d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__551a8003_1b21_48d0_a2f6_390e99fe6e37
AMOP-861206-2017 | 2047090 | 7/19/2017 5:33:17 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Supply_valve.png The waterslide supply valve was not locked in position, water supply could be inadvertently adjusted changing, the designed characteristics of the slide. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Supply_valve.png | file://x:/photopub/docs/0000000633/7e86b1dc-34b6-4ba9-809a-a06ad1e76a86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57d9b0c7_18f9_4b6a_8370_1e75aff7136c
GAIN-863215-2017 | GA-561579-2017 | 7/24/2017 9:06:06 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent.png The as-found condition is that the vent from a roof top unit terminates within 6 feet of a mechanical air inlet to a building. The potential hazard is that the mechanical air inlet will draw harmful products of combustion, such as carbon monoxide, into the air supply of the building, posing a risk to human health, | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent.png | file://x:/photopub/docs/0000000635/f0f844aa-0cb7-4fbb-b138-79bf0fd7d970.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a982e79_78a6_4b58_8b73_3d6543cb4ca0
ELIN-859651-2017 | EL-558984-2017 | 7/26/2017 5:28:54 PM | ASSESS: EL: Final | png | #asFound | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png Electrical service conductors are required to be de-energized prior to working on them. This is required to prevent shock, arc flash, and fire hazards during the installation and to protect persons and property from these hazards after the installation is completed. During installation for a service upgrade from 70A 120/240V to 200A 120/240V a certified electrician completed work under a home owner's | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png | file://x:/photopub/docs/0000000637/ad8203f9-96ae-4a6c-850d-eceadcdb9e35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02e8ee1c_7c0d_4340_9548_3c883efff8b6
BPVIN-854361-2017 | UW-556514-2017 | 7/10/2017 12:50:31 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that vertical air receiver (1.6m long and 0.65m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 5 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000628/7fc4f3a6-7952-4144-81c6-eb2187f1746d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2d578a3_3fa6_4764_a3fd_96901458da1f
AMOP-835999-2017 | AM-543502-2017 | 6/8/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Necking_of_diagonal_brace_.png Necking observed of a diagonal brace of the launch deck support structure. Necking effects the structural integrity of the brace | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Necking_of_diagonal_brace_.png | file://x:/photopub/docs/0000000615/2ec9d094-270b-4cf0-8d71-3dc4bace9fb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13e5aa82_44d4_470c_bf78_3f7ddc708597
AMOP-850150-2017 | 3194488 | 7/5/2017 3:00:48 PM | ASSESS: AM OP: Incident | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 | #Areas_of_derailment1.png,Areas_of_derailment2.png,Areas_of_derailment3.png,Areas_of_derailment4.png Rail Gauge and elevations are not being properly inspected, railway that is out of Gauge and Elevation can cause derails of the train. | 0 | No Created Hazard Identified | Areas_of_derailment2.png | file://x:/photopub/docs/0000000626/0448dcdd-8a17-469a-8346-4b71b6d235d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0206b562_3088_41c6_9b03_e6ede893aa4b
AMOP-850150-2017 | 3194488 | 7/5/2017 3:00:48 PM | ASSESS: AM OP: Incident | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 | #Areas_of_derailment1.png,Areas_of_derailment2.png,Areas_of_derailment3.png,Areas_of_derailment4.png Rail Gauge and elevations are not being properly inspected, railway that is out of Gauge and Elevation can cause derails of the train. | 0 | No Created Hazard Identified | Areas_of_derailment1.png | file://x:/photopub/docs/0000000626/5a0d9e45-0366-4b21-bd74-fa93f7b8d93f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0206b562_3088_41c6_9b03_e6ede893aa4b
AMOP-850150-2017 | 3194488 | 7/5/2017 3:00:48 PM | ASSESS: AM OP: Incident | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 | #Areas_of_derailment1.png,Areas_of_derailment2.png,Areas_of_derailment3.png,Areas_of_derailment4.png Rail Gauge and elevations are not being properly inspected, railway that is out of Gauge and Elevation can cause derails of the train. | 0 | No Created Hazard Identified | Areas_of_derailment3.png | file://x:/photopub/docs/0000000626/c6f9d8a7-04e1-4288-893a-b3a2e3ac9708.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0206b562_3088_41c6_9b03_e6ede893aa4b
AMOP-850150-2017 | 3194488 | 7/5/2017 3:00:48 PM | ASSESS: AM OP: Incident | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 | #Areas_of_derailment1.png,Areas_of_derailment2.png,Areas_of_derailment3.png,Areas_of_derailment4.png Rail Gauge and elevations are not being properly inspected, railway that is out of Gauge and Elevation can cause derails of the train. | 0 | No Created Hazard Identified | Areas_of_derailment4.png | file://x:/photopub/docs/0000000626/38586e11-e2d1-4570-8759-6f39b145cde8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0206b562_3088_41c6_9b03_e6ede893aa4b
GAHE-857521-2017 | HE-558610-2017 | 7/13/2017 7:27:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA062 | Piping/tubing hose installed in a corrosive/hazardous location | 4 | 4 | #Riser_installed_in_field_with_gas_hose1.png,Riser_installed_in_field_with_gas_hose2.png,Riser_installed_in_field_with_gas_hose3.png Found gas riser feeding dwelling installed in a field with 50 feet of gas hose winding through bushes/field and broken at both connection points. It was hazardous because of the environment and condition of the hose. It is possible it will leak or be damaged in one of many ways, then cause a situation that could lead to injury or death. | 4 | Piping/tubing hose installed in a corrosive/hazardous location | Riser_installed_in_field_with_gas_hose3.png | file://x:/photopub/docs/0000000630/3b453b0a-406d-41d5-8d79-36de0921d2ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44b734ff_4013_46d5_8d99_5f8cee771921
GAUP-843289-2017 | UW-550220-2017 | 6/29/2017 3:12:57 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #Mutter6.png Underground piping exposed to pressure in excess of 10 PSI. Risk of the propane reverting back to liquid. Possible damage to regulators and downstream equipment that is approved for vapour pressure only. Possible fire and or carbon monoxide risk. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Mutter6.png | file://x:/photopub/docs/0000000624/be0974b7-13e8-4d96-8364-199f26a782c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a003f56b_8e0c_46c9_a880_eb1632a9ae3d
ELIN-810273-2017 | EL-527048-2017 | 5/12/2017 | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Upgraded_service_.png -Point of attachment is below the minimum clearance allowed over walkways where the overhead conductors may be in contact accidentally with people or equipment without adequate mechanical protection. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Upgraded_service_.png | file://x:/photopub/docs/0000000603/2eddd8f8-4b0a-4b86-8863-8258d5a7de97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0865f091_5ae5_4735_a207_7b21cca1773c
EDRI-828791-2017 | ED-464173-2016 | 6/2/2017 | ASSESS: ED RI: Extension | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Bicycle_bottomed_out.png The personnel hoist is powered by a travel cable that is kept taught during operation by a tensioning 'bicycle' that adds weight to the cable and keeps it running parallel to the personnel hoist structure. At the bottom level the bicycle was hitting the ground before the hoist stopped, creating slack in the cable and the possibility for the slack cable to get snagged and possibly damaged. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Bicycle_bottomed_out.png | file://x:/photopub/docs/0000000611/df19d409-79d4-4223-810e-cba075dd27be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4118e56_b178_427f_a3b7_734eab372d00
ELOP-659937-2016 | 5222317 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Unbonded_water_pipe_and_600V_equipment_in_the_pump_room1.png,Unbonded_water_pipe_and_600V_equipment_in_the_pump_room2.png Metal water piping systems are required to be bonded to ground. This is required to ensure that the piping is kept at an equipotential with other metal objects that could become energized. This installation at a well pump house has metal water piping that is not bonded to ground. The service equipment and motor pump circuits are rated at 600V. This is a potential shock hazard if the metal pipe becomes energized and persons or objects contact it. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Unbonded_water_pipe_and_600V_equipment_in_the_pump_room1.png | file://x:/photopub/docs/0000000607/647b61d9-ddb9-4210-8af6-3c192a20f44b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26C54B4E_81EE_435B_876A_4491FBE34055
ELIN-854517-2017 | EL-556345-2017 | 7/11/2017 10:05:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Type_SOW_emerges_from_weatherhead_into_an_exposed_location.png Flexible cords and cables are subject to deterioration when continually exposed to outdoor locations in the sun. | 3 | Conductors Equipment is not approved for the specific use. | Type_SOW_emerges_from_weatherhead_into_an_exposed_location.png | file://x:/photopub/docs/0000000629/e4e89ea2-15b0-4116-b826-24f64ca0ef93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11a473e9_ea53_4de9_af89_e28df547e19b
ELIN-817154-2017 | EL-527517-2017 | 5/17/2017 2:53:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #J.png Cable run through stud with in 32mm of the face of the stud. This is a shock and fire hazard as the cable could be hit by a drywall screw. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | J.png | file://x:/photopub/docs/0000000602/31df0a88-a0d8-4c1f-8586-ba9d80c442fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fe927c4_ba55_4194_b145_03da15a4614c
ELIN-817480-2017 | EL-431738-2016 | 5/17/2017 2:22:43 PM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #G.png Armour not bonded. Metal armoured cables need to have the armour bonded to the system so the over current device will operate if a problem arises with the cable. The armour needs to be in contact with the metal connector. This is a fire and shock hazard. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | G.png | file://x:/photopub/docs/0000000602/f27c39e2-2509-45ac-bf07-105c98906e10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0bffbc5_c9ee_4f14_bb92_354311390394
ELIN-808472-2017 | EL-426363-2016 | 5/16/2017 9:27:37 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Panel_location1.png,Panel_location2.png Panel location is not approved due to possible weather hazards. Overtime rain and water could damage the breakers located in the panels. This could cause the breakers to be faulty overtime which could cause a fire due to the conductors overheating. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_location2.png | file://x:/photopub/docs/0000000602/f4e1b508-6663-45ee-a451-ee94fe6c2ae1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7598f261_a46b_4c84_aea2_7d6061792f96
ELIN-808472-2017 | EL-426363-2016 | 5/16/2017 9:27:37 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Panel_location1.png,Panel_location2.png Panel location is not approved due to possible weather hazards. Overtime rain and water could damage the breakers located in the panels. This could cause the breakers to be faulty overtime which could cause a fire due to the conductors overheating. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_location1.png | file://x:/photopub/docs/0000000602/b8d6be7c-49bd-4ea7-8834-e27185888ba2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7598f261_a46b_4c84_aea2_7d6061792f96
GAIN-853869-2017 | GA-550170-2017 | 7/21/2017 9:35:23 AM | ASSESS: GA: Rough-In | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent_termination_.png The as-found condition is that the vent serving a water heater has a plastic, unapproved cap fitted at the termination. the potential hazard is that the flue gasses will not exhaust correctly, causing building damage and a hazard to human health via harmful products of combustion such as carbon monoxide. The plastic cap is also a combustible material that could create a fire hazard. | 3 | Unapproved venting material | Vent_termination_.png | file://x:/photopub/docs/0000000633/1682787f-f547-425d-a683-aba91d624040.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94b3a68e_e179_44b3_a285_16682301a51d
GAIN-813764-2017 | GA-226848-2015 | 5/12/2017 2:33:53 PM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Fire.png Uncertified gas fire display installed but not in operation. Potential for failure of unapproved device or parts creating possible fire hazard | 3 | Uncertified appliance connected to gas supply but not in service | Fire.png | file://x:/photopub/docs/0000000600/03fd765d-818c-4266-ae2a-5148c025d3d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2b871b9_5f34_48bd_812f_191db162525d
ELOP-765709-2017 | EL-482569-2016 | 6/6/2017 11:21:14 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Receptacles1.png,Receptacles2.png Receptacles are required to have cover plates installed. This is to protect from conductive material coming in contact with the energized terminals on the side of the receptacle through the opening around the receptacle. In this installation at an existing restaurant kitchen, several of the existing receptacles had damaged or missing cover plates. This is a potential shock hazard for persons working in this kitchen. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Receptacles1.png | file://x:/photopub/docs/0000000611/da9d0e92-fee5-4c6b-b266-1f0cf9864638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__FD7DAA79_09E2_432A_B95B_28C475A3240A
ELOP-765709-2017 | EL-482569-2016 | 6/6/2017 11:21:14 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Receptacles1.png,Receptacles2.png Receptacles are required to have cover plates installed. This is to protect from conductive material coming in contact with the energized terminals on the side of the receptacle through the opening around the receptacle. In this installation at an existing restaurant kitchen, several of the existing receptacles had damaged or missing cover plates. This is a potential shock hazard for persons working in this kitchen. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Receptacles2.png | file://x:/photopub/docs/0000000611/4e1c7b84-a48c-4e3f-89bc-e3423ad186f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__FD7DAA79_09E2_432A_B95B_28C475A3240A
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer5.png | file://x:/photopub/docs/0000000607/afbcab7d-0da7-4d84-b8bb-7baf4fc96c36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELOP-659937-2016 | 5222317 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Unbonded_water_pipe_and_600V_equipment_in_the_pump_room1.png,Unbonded_water_pipe_and_600V_equipment_in_the_pump_room2.png Metal water piping systems are required to be bonded to ground. This is required to ensure that the piping is kept at an equipotential with other metal objects that could become energized. This installation at a well pump house has metal water piping that is not bonded to ground. The service equipment and motor pump circuits are rated at 600V. This is a potential shock hazard if the metal pipe becomes energized and persons or objects contact it. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Unbonded_water_pipe_and_600V_equipment_in_the_pump_room2.png | file://x:/photopub/docs/0000000607/dcf589db-39a6-461e-8d7d-c09e7b836b16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26C54B4E_81EE_435B_876A_4491FBE34055
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer3.png | file://x:/photopub/docs/0000000607/baa50b3d-30df-443a-9535-a32848852396.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png | file://x:/photopub/docs/0000000607/9700bb3e-3ae7-4897-b6b6-cfc06524db35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
GAIN-850831-2017 | GA-430938-2016 | 7/18/2017 2:22:06 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Un-trapped_condensate_lines.png -Found 2 on demand water heaters installed and in operation in the back room of a Tim Hortons restaurant. These water heaters are designed to have condensate in the venting and therefore need to have condensate drains installed at the lowest point of the venting. These condensate drain lines must have a trap installed so that condensate can accumulate in the trap and prevent flue gases from being pushed through the drain and into the space. In the case of the two water heaters found, the drain lines were installed without traps and flue gases were able to leak into the space. This could expose employees to carbon monoxide in the flue gases and lead to negative physical effects. | 3 | Leaking or failing special venting system (Minor) | Un-trapped_condensate_lines.png | file://x:/photopub/docs/0000000632/a78060b9-9622-442a-b4d3-018d383e879e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45f3b8eb_5909_412b_9ed5_dc5cd3b49131
GAIN-858986-2017 | GA-552407-2017 | 7/18/2017 11:24:28 AM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 2 | #Uncertified_appliance.png Appliance must be certified by an approved certification agency to ensure safe operation as outlined in nationally recognized standard. An uncertified appliance can cause a risk of fire or explosion. | 3 | Uncertified appliance connected to gas supply but not in service | Uncertified_appliance.png | file://x:/photopub/docs/0000000632/e1564aff-4709-43b4-9ee8-c31b6742b668.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cab7eac_913e_45b4_a619_17c75d1837ff
GAIN-823660-2017 | GA-511945-2017 | 5/26/2017 6:42:28 AM | ASSESS: GA: Rough-In | png | #asFound Gas off to fireplaces no evidence of 2psi-inches regulators. | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #fireplaces_installed_1.png,fireplaces_installed_2.png,fireplaces_installed_3.png -delivery pressure to fireplaces was not corret. The delivery pressure to an appliance has to match the appliances rating plate if the pressure is in of excess of what is allowed it could cause component and appliance failure leading to property damage and or CO exposure. | 4 | Appliance regulator not installed, incorrect delivery pressure | fireplaces_installed_1.png | file://x:/photopub/docs/0000000606/5f684df5-326d-4dcb-9729-d787d3354272.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0372ba9_f91a_40bc_b88b_4a863e7a5873
GAIN-823660-2017 | GA-511945-2017 | 5/26/2017 6:42:28 AM | ASSESS: GA: Rough-In | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #fireplaces_installed_1.png,fireplaces_installed_2.png,fireplaces_installed_3.png -delivery pressure to fireplaces was not corret. The delivery pressure to an appliance has to match the appliances rating plate if the pressure is in of excess of what is allowed it could cause component and appliance failure leading to property damage and or CO exposure. | 4 | Appliance regulator not installed, incorrect delivery pressure | fireplaces_installed_2.png | file://x:/photopub/docs/0000000606/6d80078b-a1b0-44a7-9930-eb6b873e582d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0372ba9_f91a_40bc_b88b_4a863e7a5873
GAIN-823660-2017 | GA-511945-2017 | 5/26/2017 6:42:28 AM | ASSESS: GA: Rough-In | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #fireplaces_installed_1.png,fireplaces_installed_2.png,fireplaces_installed_3.png -delivery pressure to fireplaces was not corret. The delivery pressure to an appliance has to match the appliances rating plate if the pressure is in of excess of what is allowed it could cause component and appliance failure leading to property damage and or CO exposure. | 4 | Appliance regulator not installed, incorrect delivery pressure | fireplaces_installed_3.png | file://x:/photopub/docs/0000000606/ab7a6a40-48dc-477d-92dd-8a611ed25ee4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0372ba9_f91a_40bc_b88b_4a863e7a5873
ELIN-845976-2017 | EL-517762-2017 | 6/28/2017 1:51:43 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Cables may get damaged from drywall screws etc. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #P6.png Cables could be damaged by drywall screws etc and may cause arching and cause fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | P6.png | file://x:/photopub/docs/0000000622/e5e3aaf3-24aa-411b-b370-1ea5bcc895c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58990742_5a1f_4472_bc98_1d73d9b66b53
ELHE-832011-2017 | HE-543310-2017 | 6/7/2017 11:08:46 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Cable insulation chewed up by rats may cause a short circuit and fire. | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #P6.png Damaged insulation may cause a short resulting in house fire and fatalities. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | P6.png | file://x:/photopub/docs/0000000612/0cd63d21-d6fa-4d40-abe5-c277bd5a78d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59d0a43c_d448_4b8e_8ba6_3105700cf462
ELIN-840650-2017 | EL-527563-2017 | 6/19/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_receptacle.png The BC Electrical Code requires an adequate number of receptacles to be installed throughout a dwelling unit. For walls of finished rooms, this requirement is no point along the floor line of a finished wall shall be more than 1.8m horizontally from a receptacle. This requirement is to facilitate the use of electrical appliances and to minimize the use of extension cords. During a rough wire assessment for a home owner for a basement renovation in an existing single family dwelling, the safety officer found a point along the floor line of a finished wall more than 1.8m horizontally from a receptacle. The lack of receptacles along this wall could facilitate the permanent use of extension cords which could create a fire hazard in this dwelling. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_receptacle.png | file://x:/photopub/docs/0000000619/32812ba9-354a-4c51-970d-b948aa37d355.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fbe4817_f738_44c3_853b_3fc75a96112c
GAIN-823767-2017 | GA-537784-2017 | 5/29/2017 1:53:29 PM | ASSESS: GA: Final | JPG | #asFound Appliance regulator being fed with higher than rated inlet gas pressure | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #image1.JPG A residential gas range top was installed with too high of incoming gas pressure. The appliance gas regulator that comes with the range is rated for a maximum inlet pressure of 1/2 psi. It was found with 2psi incoming pressure. When fed with too high of a gas pressure, these regulators cannot regulate the flow of gas properly and could lead to an excessively large flame and potential fire hazard. | 3 | Appliance not installed according to installation instructions | image1.JPG | file://x:/photopub/docs/0000000607/f06e8f49-e413-4911-870e-3441b8a8edc3.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__760c8e32_edd8_4daa_a78b_471f4091386e
ELIN-840458-2017 | EL-529090-2017 | 6/19/2017 3:03:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Ground_with_no_support_or_protection.png At a new single family dwelling, a new 200amp 1phase 120/240volt service was found with the ground conductor not adequately supported or mechanically protected. This can lead to an "Equipment Damage" situation. Pic attached | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_with_no_support_or_protection.png | file://x:/photopub/docs/0000000618/c56e5258-afa1-420d-971c-7e939b589a22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cb6b625f_d876_4c7e_b36e_f2f8606cf5b2
ELHE-825062-2017 | HE-539345-2017 | 5/25/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Bonding_for_service_equipment_is_rusted_out1.png,Bonding_for_service_equipment_is_rusted_out2.png,Bonding_for_service_equipment_is_rusted_out3.png Bonding for service equipment is incomplete due to rusting of equipment. Rust has eliminated the possibility of equipotential bonding because the continuity of boding all metal parts to ensure the same potential is eliminated. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Bonding_for_service_equipment_is_rusted_out1.png | file://x:/photopub/docs/0000000606/ab52fbd3-0cfe-4b46-8571-9c3ddbb0f697.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6566eae1_e71a_4b0d_bd21_f4b0fc2506b7
ELHE-825062-2017 | HE-539345-2017 | 5/25/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Bonding_for_service_equipment_is_rusted_out1.png,Bonding_for_service_equipment_is_rusted_out2.png,Bonding_for_service_equipment_is_rusted_out3.png Bonding for service equipment is incomplete due to rusting of equipment. Rust has eliminated the possibility of equipotential bonding because the continuity of boding all metal parts to ensure the same potential is eliminated. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Bonding_for_service_equipment_is_rusted_out2.png | file://x:/photopub/docs/0000000606/ed9a949f-6100-4110-a55a-e1d784e48a8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6566eae1_e71a_4b0d_bd21_f4b0fc2506b7
ELHE-825062-2017 | HE-539345-2017 | 5/25/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Bonding_for_service_equipment_is_rusted_out1.png,Bonding_for_service_equipment_is_rusted_out2.png,Bonding_for_service_equipment_is_rusted_out3.png Bonding for service equipment is incomplete due to rusting of equipment. Rust has eliminated the possibility of equipotential bonding because the continuity of boding all metal parts to ensure the same potential is eliminated. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Bonding_for_service_equipment_is_rusted_out3.png | file://x:/photopub/docs/0000000606/4f7f96aa-a3f6-4a91-8a9e-25692071daaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6566eae1_e71a_4b0d_bd21_f4b0fc2506b7
ELIN-831219-2017 | EL-506809-2017 | 6/7/2017 11:24:32 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Kitchen in bottom of duplex | EL038 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3 | 3 | #1.png This duplex is being wired as a single family dwelling. The service is not individually fed for a duplex. This is a fire hazard. | 3 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 1.png | file://x:/photopub/docs/0000000612/35e0de5a-5f10-4f47-8a7e-a7600ced162b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aaf4e6df_243b_4279_a4d0_99ebfa44788e
ELIN-864668-2017 | EL-482908-2016 | 7/25/2017 1:16:28 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #Plug_required_on_peninsula.png This assessment found that no receptacle was installed on the peninsula, this could cause a shock hazard when appliance cords run across counter surfaces. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Plug_required_on_peninsula.png | file://x:/photopub/docs/0000000635/05d2ecef-bcc5-4431-8037-79f8d6fab870.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c91e6ff_c047_4724_ba66_9d9775a606a4
EDOP-815184-2017 | 2050562 | 4/26/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED023 | Conspicuous location Preventative measure removed or damaged to an extend where they are rendered ineffective Contact with Object/human inevitable Contact could result in excessive life &/or property damage | 5 | 5 | #Counterweight_buffer.png A buffer is a device that provides a controlled stop of a descending car or counterweight travelling beyond its normal limit of travel. A buffer absorbs and dissipates the kinetic energy. During a regular inspection it was found that the counterweight buffer was not secured in place. When there is not proper buffer engagement this could cause serious injury to Elevator passengers. | 5 | Conspicuous location Preventative measure removed or damaged to an extend where they are rendered ineffective Contact with Object/human inevitable Contact could result in excessive life &/or property damage | Counterweight_buffer.png | file://x:/photopub/docs/0000000600/876d841f-5f31-4c8b-91b1-7be8ba370d01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff04a126_abd6_43eb_93cd_eb496fcf5445
ELIN-850834-2017 | EL-455169-2016 | 7/6/2017 2:26:54 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Arc_fault_breakers_not_installed_where_required_.png Arc fault protection is not installed for receptacle circuits where required, arc fault protection provides protection to property and persons. Arc fault protection senses minor faults in circuits which would not be sensed or cleared by conventional over current devices. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Arc_fault_breakers_not_installed_where_required_.png | file://x:/photopub/docs/0000000626/64b1be5a-4491-475a-a890-6d9238aef03a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b14f15e_b124_4635_925b_7e5f5f8b93b4
ELIN-852275-2017 | EL-258071-2015 | 7/7/2017 1:35:48 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png Energized branch circuit cables/wiring and terminals at switches, receptacles and lighting boxes are required to have boxes with cover plates installed on them. This is required to prevent accidental contact with energized terminals and conductors at electrical equipment. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation for a new house has energized terminals and wiring exposed to contact at switc | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png | file://x:/photopub/docs/0000000627/7c548fe5-ee8e-4de5-ab6a-0266dbc8b113.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0e84821_6538_4a51_8d02_2dc8cb0794d7
ELHE-831157-2017 | HE-543261-2017 | 6/6/2017 1:04:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Service1.png,Service2.png,Service3.png Service conductors passed through a metal roof and main distribution panel has been left energized and open. Possibility for fault current from exposed equipment and electric shock or equipment damage from fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Service3.png | file://x:/photopub/docs/0000000611/1403487d-6425-4027-9490-0975a545f642.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70341aea_7303_4762_ac5b_faf6e3583aaf
ELIN-841079-2017 | EL-549008-2017 | 6/21/2017 12:36:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound DB2 conduit below panel. The orange is a telephone conduit for underground use. | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #DB2__.png Rough wire of new single family dwelling. A thin wall conduit made for underground use has been installed above grade without mechanical protection. This conduit houses the conductors to the dwelling. If the conduit is damaged the conductors can be damaged resulting in shock or fire. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | DB2__.png | file://x:/photopub/docs/0000000619/c158322f-4c80-4bbd-bff8-73608b878e92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1053630_7aa3_466f_86ea_626e85d78b0b
ELIN-861286-2017 | EL-182984-2014 | 7/19/2017 2:02:34 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Non_approved_cord_connected_light1.png,Non_approved_cord_connected_light2.png In a new livestock facility a 15 amp 120 volt non approved cord connected lamp was found to be hanging from roof trusses with an open, unprotected lamp. This could lead to a shock, thermal and equipment damage situation. Pictures attached. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Non_approved_cord_connected_light1.png | file://x:/photopub/docs/0000000633/789db25c-5d04-4aac-a464-ce3c3111404e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d486cb2_d179_4cdb_9054_9a9c586ab94d
ELIN-860284-2017 | EL-558478-2017 | 7/19/2017 2:59:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #Loose_fill_around_pole.png In a new overhead 200 amp 120/240 volt service for a winery the combination meter base was found not to have proper secure footing within 1 meter. This could result in thermal and equipment damage. Picture attached. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Loose_fill_around_pole.png | file://x:/photopub/docs/0000000633/c70bab1e-9199-449b-acee-53857fb16a4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__030424d5_da15_45c1_94bb_ba0646a5668e
ELIN-861286-2017 | EL-182984-2014 | 7/19/2017 2:02:34 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Non_approved_cord_connected_light1.png,Non_approved_cord_connected_light2.png In a new livestock facility a 15 amp 120 volt non approved cord connected lamp was found to be hanging from roof trusses with an open, unprotected lamp. This could lead to a shock, thermal and equipment damage situation. Pictures attached. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Non_approved_cord_connected_light2.png | file://x:/photopub/docs/0000000633/6c2f68a4-55fb-4f0a-a9fd-a0b102d99ebc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d486cb2_d179_4cdb_9054_9a9c586ab94d
ELIN-853335-2017 | EL-539610-2017 | 7/12/2017 10:42:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Service_Cable.png The Service Cable for a 200 amp 120/240 volt Service has been run underground in a trench from the Service Pole to the new building but is exposed in the trench and has not been completely back filled or protected from mechanical damage. This poses a shock hazard to persons and potential damage to the electrical components. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Service_Cable.png | file://x:/photopub/docs/0000000629/c601b1fa-b51b-4b27-a113-0109e14b3910.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76323b69_c3ec_4a22_b150_85eb22533e1a
ELHE-831157-2017 | HE-543261-2017 | 6/6/2017 1:04:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Service1.png,Service2.png,Service3.png Service conductors passed through a metal roof and main distribution panel has been left energized and open. Possibility for fault current from exposed equipment and electric shock or equipment damage from fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Service1.png | file://x:/photopub/docs/0000000611/ed9ddf2e-3f13-4d56-8fdd-e3dd173caa8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70341aea_7303_4762_ac5b_faf6e3583aaf
ELHE-831157-2017 | HE-543261-2017 | 6/6/2017 1:04:00 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Service1.png,Service2.png,Service3.png Service conductors passed through a metal roof and main distribution panel has been left energized and open. Possibility for fault current from exposed equipment and electric shock or equipment damage from fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Service2.png | file://x:/photopub/docs/0000000611/34afe214-c7d4-4157-b346-50b07874b18b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70341aea_7303_4762_ac5b_faf6e3583aaf
ELIN-825682-2017 | EL-387982-2016 | 5/30/2017 1:45:03 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound Flexible cord is wedged thru plywood wall and pinched by the panel cover where it has been hard wired into the panel. This is a shock and fire hazard as the flexible cord is not rated for this type of use or installation. | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | #2.png Flexible cord has been wedged thru a gap in the buildings sheathing. This cord has then been hard connected to a breaker in the panel. The cord is being pinched by the panel and panel cover. This same cord is also buried underground outside. The improper use of this flexible cord has created a shock and fire hazard in this building. | 4 | Conductors, Mis-use of flexible cords. | 2.png | file://x:/photopub/docs/0000000607/fbca0761-1797-4f04-a1b1-5b5b485fb432.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7685d80d_b47b_4170_a0f1_0a1915c525b6
ELIN-824462-2017 | EL-522224-2017 | 5/29/2017 10:34:33 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Panel_Schedule.png The 15 amp 120 volt receptacle branch circuits for the washer and microwave have not been provided with AFCI protection. This could result in a shock hazard or potential mechanical damage to the appliance and branch wiring. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panel_Schedule.png | file://x:/photopub/docs/0000000607/2103d921-c366-40d8-b420-ac8d15086f61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0726b9d_0097_4722_bce0_d76a34a44d50
ELHE-820146-2017 | HE-536672-2017 | 5/23/2017 6:48:04 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL043 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only | 4 | 4 | #Generator1.png,Generator2.png The belt drive on a 45KW 480 volt 67.5 amp hydro electric generator is exposed and has no guard or mechanical protection provided. This poses a safety risk to authorized persons accessing the shack to service or check the equipment and operation. It also poses a risk of mechanical damage to the belt and generator. | 4 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only | Generator1.png | file://x:/photopub/docs/0000000604/fd852f7a-9b3c-49b8-86d9-d3b18af4e628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7651eb1_b40a_460f_b45f_71665a5c6bdd
ELHE-820146-2017 | HE-536672-2017 | 5/23/2017 6:48:04 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL043 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only | 4 | 4 | #Generator1.png,Generator2.png The belt drive on a 45KW 480 volt 67.5 amp hydro electric generator is exposed and has no guard or mechanical protection provided. This poses a safety risk to authorized persons accessing the shack to service or check the equipment and operation. It also poses a risk of mechanical damage to the belt and generator. | 4 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only | Generator2.png | file://x:/photopub/docs/0000000604/36d68ad2-2a05-4439-ae11-92e2fced93f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7651eb1_b40a_460f_b45f_71665a5c6bdd
GAIN-816869-2017 | GA-531166-2017 | 5/23/2017 2:05:38 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #York.png Exhaust vent termination installed with less than the required separation from building opening. As found 24", required under 8.14.8, 36" Risk of products of combustion being drawn into the occupied portion of the structure. Possible exposure to carbon monoxide. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | York.png | file://x:/photopub/docs/0000000604/712d4421-9ca3-493d-b685-06626acc8a51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fed0f496_f913_4182_8672_33fb5e53f46f
ELIN-852275-2017 | EL-258071-2015 | 7/7/2017 1:35:48 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png Energized branch circuit cables/wiring and terminals at switches, receptacles and lighting boxes are required to have boxes with cover plates installed on them. This is required to prevent accidental contact with energized terminals and conductors at electrical equipment. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation for a new house has energized terminals and wiring exposed to contact at switc | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png | file://x:/photopub/docs/0000000627/90d7cddf-84f4-4f53-ac4f-92e943762674.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0e84821_6538_4a51_8d02_2dc8cb0794d7
ELIN-852275-2017 | EL-258071-2015 | 7/7/2017 1:35:48 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png Energized branch circuit cables/wiring and terminals at switches, receptacles and lighting boxes are required to have boxes with cover plates installed on them. This is required to prevent accidental contact with energized terminals and conductors at electrical equipment. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation for a new house has energized terminals and wiring exposed to contact at switc | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png | file://x:/photopub/docs/0000000627/2f7a9279-b4e4-43be-8baa-dd00a4572b8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0e84821_6538_4a51_8d02_2dc8cb0794d7
ELIN-849205-2017 | EL-552797-2017 | 7/6/2017 2:53:12 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Flexible_cord_through_main_compartment_feeding_permanent_hot_tub.png A hot tub operating at 240 volts and 40 amps was found to be connected using flexible cord. Permanent equipment when fed with flexible cord can result in deterioration of the cord or conductors that can result in damage to buildings or injury to persons. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_through_main_compartment_feeding_permanent_hot_tub.png | file://x:/photopub/docs/0000000627/966194be-33a5-4714-9a67-9a1826cf5bcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5eb74484_6f6e_4f16_984e_61258cf15daa
ELOP-825413-2017 | EL-100594-2014 | 5/30/2017 10:13:30 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | #Forklift1.png,Forklift2.png Forklift battery chargers at height without evidence of secure mounting methods creating a crush hazard for persons working near the equipment. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Forklift1.png | file://x:/photopub/docs/0000000607/1a3c19ed-8821-446c-a1d5-b0d976884a1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ba08f31_24f0_4568_b0cc_591d24097394
ELOP-825413-2017 | EL-100594-2014 | 5/30/2017 10:13:30 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | #Forklift1.png,Forklift2.png Forklift battery chargers at height without evidence of secure mounting methods creating a crush hazard for persons working near the equipment. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Forklift2.png | file://x:/photopub/docs/0000000607/8340ae4d-186b-4c39-96f9-a7bc33d37664.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ba08f31_24f0_4568_b0cc_591d24097394
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png | file://x:/photopub/docs/0000000607/56e3afb6-90a5-439d-9f75-f57c8606bb94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png | file://x:/photopub/docs/0000000607/cecbfdd7-782c-4145-83a9-c391804dc7fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png | file://x:/photopub/docs/0000000607/1f288d81-3cfd-4236-960a-02c78299b735.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer7.png | file://x:/photopub/docs/0000000607/531bcdcf-eb93-4d47-be78-f91b668f0f47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer1.png | file://x:/photopub/docs/0000000607/0f7c7728-c416-447c-ac2d-b887f2180836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer4.png | file://x:/photopub/docs/0000000607/6ed1ab24-273a-4f1c-812e-5595a4d7d053.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELOP-841623-2017 | EL-548093-2017 | 7/13/2017 8:25:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Roof built around overhead conductors | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Y.png 600 Amp 208 Volt overhead service conductors entering the building are exposed to accidental contact by individuals. An addition of a flat roof to the building without changing the location of the overhead conductors has created a shock hazard to individuals in this area. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Y.png | file://x:/photopub/docs/0000000630/50af9513-463f-4190-9c4c-ae795aeba8ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8966A969_6ACC_440C_A33C_35F6DACCC0E8
ELIN-852275-2017 | EL-258071-2015 | 7/7/2017 1:35:48 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png Energized branch circuit cables/wiring and terminals at switches, receptacles and lighting boxes are required to have boxes with cover plates installed on them. This is required to prevent accidental contact with energized terminals and conductors at electrical equipment. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation for a new house has energized terminals and wiring exposed to contact at switc | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png | file://x:/photopub/docs/0000000627/660a691d-8fed-4da2-ab31-0d9b4693a246.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0e84821_6538_4a51_8d02_2dc8cb0794d7
GAIN-837001-2017 | GA-454392-2016 | 6/16/2017 8:25:22 AM | ASSESS: GA: Final | png | #asFound | GA079 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | 3 | 3 | #Connector.png The as found condition was a gas system designed to deliver 2 psi (pounds per square inch) to a range top with a maximum inlet pressure of 1/2 psi. The as found hazard is over-pressurization of an appliance can lead to a failure of the appliance regulator leading to excessive flame at the burners. This could lead to operator injury or environmental damage. | 3 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | Connector.png | file://x:/photopub/docs/0000000617/773953f8-4bd0-4e74-9878-4e5a76bcb9a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e446785_ff39_488d_91b8_b4129cd729c2
GAIN-851708-2017 | GA-549319-2017 | 7/7/2017 1:12:46 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Best_west_3.png Moisture exhaust from commercial dryers installed with less than the required 6" clearance to combustibles. Lint build up in the vent could catch fire causing excessive temperature within the venting. Combustible material in the immediate vicinity of the vent could also catch fire due to the high temperatures.. | 3 | Clearance to combustible not met | Best_west_3.png | file://x:/photopub/docs/0000000627/e05bb0aa-bffe-4776-8682-9b545f1d5a99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a628d259_f54d_4639_b8f2_8c9307a1624f
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png | file://x:/photopub/docs/0000000607/8c9b5289-fcfe-4232-a264-215fa5fc1720.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png | file://x:/photopub/docs/0000000607/3e475d3c-d940-421f-8418-5742167804d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer6.png | file://x:/photopub/docs/0000000607/c6e6c135-1956-4bea-906c-2900a17fe28a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELIN-824866-2017 | EL-519494-2017 | 6/1/2017 1:25:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | #Bond_conductor_not_sized_properly.png 400 amp, 120/208 volt 3 phase electrical system is installed having PVC raceways for the feeder cables. The bonding conductor for these feeders is not sized correctly. This is a shock hazard. | 2 | Continuity Bonding; conductor is not properly sized. | Bond_conductor_not_sized_properly.png | file://x:/photopub/docs/0000000609/12305f86-efc1-4428-ab3f-4fba922c78c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24830672_7a65_4350_95d6_f59e0f53dadf
ELIN-852631-2017 | EL-552965-2017 | 7/10/2017 7:22:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Temporary_Enclosure1.png,Temporary_Enclosure2.png,Temporary_Enclosure3.png A new 200 amp 120/240 volt Main Electrical Panel has been installed in a home under construction and has been provided with a temporary enclosure but it does not adequately protect the electrical equipment from the weather or possible mechanical damage that could be present while the home in being built. This could result is damage and possible failure of the equipment, it also could present a shock hazard to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_Enclosure3.png | file://x:/photopub/docs/0000000628/dc5af409-aab3-4c67-a14a-4321986acc69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27a4da05_e91d_402b_b15c_3f5b62d65c77
ELIN-852631-2017 | EL-552965-2017 | 7/10/2017 7:22:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Temporary_Enclosure1.png,Temporary_Enclosure2.png,Temporary_Enclosure3.png A new 200 amp 120/240 volt Main Electrical Panel has been installed in a home under construction and has been provided with a temporary enclosure but it does not adequately protect the electrical equipment from the weather or possible mechanical damage that could be present while the home in being built. This could result is damage and possible failure of the equipment, it also could present a shock hazard to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_Enclosure2.png | file://x:/photopub/docs/0000000628/fec8b23b-d59e-43f4-b338-76c71a2656b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27a4da05_e91d_402b_b15c_3f5b62d65c77
ELIN-852631-2017 | EL-552965-2017 | 7/10/2017 7:22:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Temporary_Enclosure1.png,Temporary_Enclosure2.png,Temporary_Enclosure3.png A new 200 amp 120/240 volt Main Electrical Panel has been installed in a home under construction and has been provided with a temporary enclosure but it does not adequately protect the electrical equipment from the weather or possible mechanical damage that could be present while the home in being built. This could result is damage and possible failure of the equipment, it also could present a shock hazard to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_Enclosure1.png | file://x:/photopub/docs/0000000628/e3892d2c-eae3-495d-bf9f-afbf8249b469.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27a4da05_e91d_402b_b15c_3f5b62d65c77
ELIN-853471-2017 | EL-451024-2016 | 7/10/2017 3:26:53 PM | ASSESS: EL: Final | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | #Hot_tub_receptacle.png A 15 amp 120 volt receptacle has been placed within 3m of a hot tub but does not have GFCI protection, this poses a shock hazard to persons and possible damage to the electrical equipment. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Hot_tub_receptacle.png | file://x:/photopub/docs/0000000628/f08dccbb-f209-4e8d-9c9e-b3c20a238bc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b1f6c21_fa03_4ab6_986e_2f6632dcfd4b
ELIN-852275-2017 | EL-258071-2015 | 7/7/2017 1:35:48 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png Energized branch circuit cables/wiring and terminals at switches, receptacles and lighting boxes are required to have boxes with cover plates installed on them. This is required to prevent accidental contact with energized terminals and conductors at electrical equipment. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation for a new house has energized terminals and wiring exposed to contact at switc | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png | file://x:/photopub/docs/0000000627/89f7a29f-66e5-40d4-838d-af4265a78211.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0e84821_6538_4a51_8d02_2dc8cb0794d7
ELIN-852275-2017 | EL-258071-2015 | 7/7/2017 1:35:48 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables1.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables2.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables4.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables5.png,Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables6.png Energized branch circuit cables/wiring and terminals at switches, receptacles and lighting boxes are required to have boxes with cover plates installed on them. This is required to prevent accidental contact with energized terminals and conductors at electrical equipment. It is also required to protect devices, wiring, and connections from mechanical damage and to contain thermal energy in the event that wiring or equipment is damaged or fails. This installation for a new house has energized terminals and wiring exposed to contact at switc | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_at_devices_and_conductors_in_outlet_boxes_and_at_cables3.png | file://x:/photopub/docs/0000000627/af055b9c-81e7-4ba9-9836-a85fe309d313.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0e84821_6538_4a51_8d02_2dc8cb0794d7
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png | file://x:/photopub/docs/0000000607/6719e04d-006f-4192-8d99-22a3a1885fe3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELOP-655784-2016 | 5224474 | 5/25/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD2.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD3.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD4.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD5.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD6.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD7.png,Capacitor_with_open_terminals_and_open_wiring_at_VFD8.png Electrical wiring and equipment is required to be installed as it was intended and approved to be installed. Open wiring and terminals for electrical equipment is generally not approved and can pose a shock and fire hazard if persons or objects contact or damage the wiring or components. This installation at a well pump kiosk has open 240V 60A wiring and terminals at a capacitor that was connected to a variable frequency drive for a submersible well pump motor. The open terminals at the top of the capacitor have been covered by a plumbing cap fitting th | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Capacitor_with_open_terminals_and_open_wiring_at_VFD1.png | file://x:/photopub/docs/0000000607/297da52a-a66f-4561-a543-811ea8250bae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DCCB8AB1_B6AE_4EF7_80D2_5712F9C24B7E
ELIN-821986-2017 | EL-536974-2017 | 5/29/2017 12:14:44 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Ungrounded_generator_in_a_mobile_display_trailer1.png,Ungrounded_generator_in_a_mobile_display_trailer2.png,Ungrounded_generator_in_a_mobile_display_trailer3.png,Ungrounded_generator_in_a_mobile_display_trailer4.png,Ungrounded_generator_in_a_mobile_display_trailer5.png,Ungrounded_generator_in_a_mobile_display_trailer6.png,Ungrounded_generator_in_a_mobile_display_trailer7.png Electrical systems are required to be grounded to reduce the danger of electric shock or property damage by providing a low impedance path for fault current back to the source and to establish an equipotential plane such that the possibility of a potential difference between metal parts is minimized. This installation has a 30KW 120/208V 3phase generator installed inside of a tractor trailer that is being used as a mobile display unit. The generator and the trailer are not grounded as required by code. This is a potential shock and fire hazard if there is a fault on the electrical system and persons or objects contact energized electrica | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Ungrounded_generator_in_a_mobile_display_trailer2.png | file://x:/photopub/docs/0000000607/81924a84-8b6d-4c24-817e-d66f6d70c531.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef628c5_9e33_415d_a819_04cdd5a8be78
ELIN-831431-2017 | EL-519372-2017 | 6/8/2017 2:50:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Gas_Range_Plug.png This assessment found that the gas range plug is on with the washer plug, potentially overloading the circuit and causing a fire in a failure. | 3 | Conductors Equipment is not approved for the specific use. | Gas_range_plug.png | file://x:/photopub/docs/0000000613/301f9756-fbde-4db6-9f7e-3dbc6bed2a15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__040c5764_937c_410f_802a_78b6e44e6699
ELIN-831201-2017 | EL-540987-2017 | 6/8/2017 1:45:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Needs_Mechanical_protection.png This assessment found that no mechanical protection on Service conduit that can be damaged by siders causing potential fire if hit by nails or screws | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Needs_Mechanical_protection.png | file://x:/photopub/docs/0000000613/a874fef3-1d03-4530-998d-3b81298c86bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6beda25_d24d_4221_92c0_88bccab8f297
ELIN-831429-2017 | EL-540989-2017 | 6/8/2017 1:56:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Mechanical_protection_required.png This assessment found that no mechanical protection on the service conduit, which can damage the wire inside the conduit by the siders nailing or screwing, causing a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Mechanical_protection_required.png | file://x:/photopub/docs/0000000613/f7e8e9ab-6355-4f32-900f-ed040156a501.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6ca390c_b397_418f_8d3d_dd95c3571f93
ELIN-831431-2017 | EL-519372-2017 | 6/8/2017 2:50:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Gas_Range_Plug.png This assessment found that the gas range plug is on with the washer plug, potentially overloading the circuit and causing a fire in a failure. | 3 | Conductors Equipment is not approved for the specific use. | Gas_Range_Plug.png | file://x:/photopub/docs/0000000613/7572fd6c-87cc-456c-b9bb-cdfa01813f8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__040c5764_937c_410f_802a_78b6e44e6699
GAHE-837713-2017 | HE-547287-2017 | 6/15/2017 6:45:32 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Water_heater1.png,Water_heater2.png Water heater installed in commercial kitchen with no make up air, and kitchen exhaust hood in place. Water heater not vented to the outdoors, when tested water heater spillage out of the draft hood occurred at all times. The as found hazard is products of combustion venting into a structure can lead to deadly CO exposure by occupants of the building | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Water_heater1.png | file://x:/photopub/docs/0000000616/16bfe856-0793-46be-a593-fa2e89273e0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34d8ef22_a616_4641_b65c_154436c17ec6
GAHE-837713-2017 | HE-547287-2017 | 6/15/2017 6:45:32 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Water_heater1.png,Water_heater2.png Water heater installed in commercial kitchen with no make up air, and kitchen exhaust hood in place. Water heater not vented to the outdoors, when tested water heater spillage out of the draft hood occurred at all times. The as found hazard is products of combustion venting into a structure can lead to deadly CO exposure by occupants of the building | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Water_heater2.png | file://x:/photopub/docs/0000000616/4518453d-bb36-46cf-ad26-830e285c6563.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34d8ef22_a616_4641_b65c_154436c17ec6
ELIN-833514-2017 | EL-524110-2017 | 6/15/2017 12:06:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | #Main_ground_on_equipment__sub_feed_neutral_in_main_compartment_on_main_neutral_lug.png A or new 200 amp 240 volt single phase residential service has been installed. The main system ground conductor was installed incorrectly which could lead to unreliable reaction of overcurrent devices in the structure that could lead to property damage or injury to persons | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_ground_on_equipment__sub_feed_neutral_in_main_compartment_on_main_neutral_lug.png | file://x:/photopub/docs/0000000617/b56d0742-d05f-4597-9b4e-e89244022632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc1a5aba_7e14_42cb_951d_76dd7bc54091
GAHE-854523-2017 | HE-556641-2017 | 7/13/2017 3:52:53 PM | ASSESS: GA HE: Hazard Elimination | jpg | #asFound Mounting hardware | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #DSC01393_Uninstalled_cooktop_parts.jpg The as-found condition is that a range top has been installed without the correct mounting hardware, resulting in a range top that is subject to movement. The potential hazard is that the range top will move at an inopportune time while being used resulting in possible burns and fire damage | 3 | Appliance not installed according to installation instructions | DSC01393_Uninstalled_cooktop_parts.jpg | file://x:/photopub/docs/0000000630/f7633bc6-1962-444d-90b6-54c21b9e596b.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9863b447_629e_423b_a128_e6b0153bde7f
ELIN-861806-2017 | EL-561118-2017 | 7/21/2017 12:26:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound This photo shows 2 inch Type DB2 conduit and 2 inch DB2 fitting to adapt type DB2 conduit to 2 inch rigid PVC conduit. It has been installed above grade in the wall of the electrical room on the exterior of the house. Concrete encasement stops below the DB 2 fitting. | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #DB2_.png Rough wire of new single-family dwelling. The conduit feeding the electrical panel in the house is a thin wall conduit for use below grade and it and associated fittings must be encased in 50 MM of concrete when installed above grade to avoid mechanical damage. Shock hazard when conductors are exposed by damage to the thin wall conduit. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | DB2_.png | file://x:/photopub/docs/0000000634/c035f362-43de-4252-88d0-ccda9032f822.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec908a5a_915b_417e_81b6_9bb8ec5feab2
ELIN-826191-2017 | EL-535990-2017 | 5/31/2017 11:22:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_cable_not_connected_at_neutral.png System grounding conductor has been left coiled in main service enclosure. Provisions for grounding connection on identified conductor bussing have been provided inside the enclosure. If system was to be energized and a fault were to occur, the overcurrent device would potentially not sense a fault and there would not be a path to ground as it is not connected currently. This may result in shock and damage to persons and equipment. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_cable_not_connected_at_neutral.png | file://x:/photopub/docs/0000000608/611e6c71-beb3-4338-8f96-f3a38586cd4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b157ec8_d107_4a69_b7e2_c7d7afbe527b
ELIN-826191-2017 | EL-535990-2017 | 5/31/2017 11:22:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_cable_not_connected_at_neutral.png System grounding conductor has been left coiled in main service enclosure. Provisions for grounding connection on identified conductor bussing have been provided inside the enclosure. If system was to be energized and a fault were to occur, the overcurrent device would potentially not sense a fault and there would not be a path to ground as it is not connected currently. This may result in shock and damage to persons and equipment. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_cable_not_connected_at_neutral.png | file://x:/photopub/docs/0000000608/f0863988-6d21-4dc9-ac73-6bb98e37ced8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b157ec8_d107_4a69_b7e2_c7d7afbe527b
ELIN-825887-2017 | EL-532084-2017 | 5/31/2017 2:21:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_conduit_and_meter_enclosure_inside_building1.png,Service_conduit_and_meter_enclosure_inside_building2.png Service upgrade: currently meter enclosure, service conductors and conduit are located within the inside of the building. Utility overcurrent devices do not provide adequate protection to these conductors and they are required to be installed on the exterior of buildings to reduce the risk of shock and fire to persons and property in the case of a fault. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_conduit_and_meter_enclosure_inside_building1.png | file://x:/photopub/docs/0000000608/ebc5b20b-4157-40d9-82a3-39da409b8f81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47fa3e46_dd8f_4aeb_a1d3_c1dad681f9b8
ELIN-825887-2017 | EL-532084-2017 | 5/31/2017 2:21:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Service_conduit_and_meter_enclosure_inside_building1.png,Service_conduit_and_meter_enclosure_inside_building2.png Service upgrade: currently meter enclosure, service conductors and conduit are located within the inside of the building. Utility overcurrent devices do not provide adequate protection to these conductors and they are required to be installed on the exterior of buildings to reduce the risk of shock and fire to persons and property in the case of a fault. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_conduit_and_meter_enclosure_inside_building2.png | file://x:/photopub/docs/0000000608/3bc41c95-eb68-4298-8396-df2150301a09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47fa3e46_dd8f_4aeb_a1d3_c1dad681f9b8
ELIN-833576-2017 | EL-544287-2017 | 6/12/2017 1:29:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Conduit.png - 3" service conduit installed on side of house with no expansion joint. Underground portion of conduit that is buried to nearest BC Hydro transformer could shift due to frost or settling causing damage to this conduit or meterbase. Worst case being exposing the unprotected BC Hydro service conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Conduit.png | file://x:/photopub/docs/0000000615/c3eadde3-412b-4b91-947d-6659b336af1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecb1dc19_0e52_40d2_acc5_df2fd023197c
ELIN-834765-2017 | EL-542775-2017 | 6/15/2017 | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Open_splice.png Branch circuit wiring splices and connections to light fixtures are required to be made in electrical outlet boxes. This is required to protect the wiring and connections, providing a means for mounting devices and fixtures, and to contain thermal energy in the event that the wiring, equipment, or connections fail. This existing installation in a barn/shop structure of a residential property has 15A 120V wiring that is not spliced in outlet boxes and connections to light fixtures that are not contained in outlet boxes. Energized conductors and connections of the wiring and light fixtures are open and subject to damage and are not installed in boxes or enclosures that can contain thermal energy. This is a fire hazard if an electrical failure or damage to equipment and connections occur. It is also a potential shock hazard if a person or object contacts the energized conductors/connections of branch circuit wiring or light fixtures. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Open_splice.png | file://x:/photopub/docs/0000000617/f3b7312f-6772-4888-ba35-3c9b3bf2f5a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9dac8cc5_7c28_4158_88fc_7b492846f72e
ELIN-838033-2017 | EL-543130-2017 | 6/21/2017 2:41:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | #Guy_wire_assembly.png At a new single family residence, a new 200amp 1phase 120/240 service pole was found with the anchor and guy assembly incorrectly installed. The is can lead to a "Shock Hazard" scenario. Pic attached. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Guy_wire_assembly.png | file://x:/photopub/docs/0000000619/203ce00e-ce85-465d-8040-62bebb42d6fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__882fb10e_2dac_48b2_8295_f93f04d0ad4d
BPVIN-825507-2017 | BPV-188774-2014 | 5/30/2017 1:51:18 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound Typical hot water heating boiler drain valve that is used to drain the boiler. Valve is usually installed on the boiler to fully drain the unit. | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 3 | #Boiler_Drain_Valve.png The drain valve provides a means of draining the boiler completely during times of shutdown or layup. If untreated water is allowed to sit in a boiler this may promote boiler metal corrosion and weakening of the unit. In outdoor installations boilers flooded with water during shutdown or layup may be susceptible to freeze up and lead to potential damage to boiler pressure boundary. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | Boiler_Drain_Valve.png | file://x:/photopub/docs/0000000607/4eaad20e-1641-4c1a-8c7d-2b98e7d572da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f69ac3f8_96d7_494d_9c04_3e13201dd16b
ELHE-836753-2017 | HE-546741-2017 | 6/13/2017 10:16:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Armoured_cable1.png,Armoured_cable2.png Energized armoured cables branch circuit without boxes, connectors or cover plates. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Armoured_cable1.png | file://x:/photopub/docs/0000000616/aa0f5bdf-979f-4bca-bcc5-d81b46681880.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd90bd33_5a17_4d44_9d4d_ab903e1f986c
ELHE-836753-2017 | HE-546741-2017 | 6/13/2017 10:16:05 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Armoured_cable1.png,Armoured_cable2.png Energized armoured cables branch circuit without boxes, connectors or cover plates. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Armoured_cable2.png | file://x:/photopub/docs/0000000616/fda0ceea-8581-4f13-add9-ad9be28a31af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd90bd33_5a17_4d44_9d4d_ab903e1f986c
ELIN-859660-2017 | EL-541888-2017 | 7/18/2017 12:21:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Energized_panel11.png,Energized_panel12.png Energized panel found without covers installed | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Energized_panel12.png | file://x:/photopub/docs/0000000632/e0acec18-428f-4762-877d-4af2fd75c0b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed26fc53_489f_4c54_8fe5_820e703e2f69
ELIN-859660-2017 | EL-541888-2017 | 7/18/2017 12:21:21 PM | ASSESS: EL: Service Connection | png | #asFound Panel found in renovated residential space energized and without covers installed | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Energized_panel11.png,Energized_panel12.png Energized panel found without covers installed | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Energized_panel11.png | file://x:/photopub/docs/0000000632/734ef7a9-d557-436c-8ffb-9dd2e9c22cc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed26fc53_489f_4c54_8fe5_820e703e2f69
GAIN-838538-2017 | GA-546847-2017 | 6/19/2017 1:03:50 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Range_clearances1.png Commercial gas range installed to close to a combustible wall. This may lead to fire. | 3 | Clearance to combustible not met | Range_clearances1.png | file://x:/photopub/docs/0000000618/4a234ce6-e114-4a21-ab14-5febf3713370.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__465c96f2_cdb9_4b00_85f1_a669c27bc003
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated5.png | file://x:/photopub/docs/0000000623/8e78cebe-3b21-42fa-a015-e9de198de7c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-826750-2017 | EL-540541-2017 | 6/5/2017 10:29:00 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Non_functional_GFCI_receptacle_in_bathroom.png 120 volt 15 amp bathroom counter receptacle is not functioning properly and is not ground fault protected, which increases the likelihood of prolonged electrical shock should a fault to ground occur. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Non_functional_GFCI_receptacle_in_bathroom.png | file://x:/photopub/docs/0000000610/3ae160e8-c63a-40dc-8cf2-be88cf3aac1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__605a9b26_1261_448f_8c5a_69ba09845ffc
ELIN-845843-2017 | EL-503219-2017 | 6/29/2017 3:52:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Outlet_box_hanging1.png,Outlet_box_hanging2.png Conductors exposed to damaging strain. Outlet box not supported. Connector is not approved for flexible cords. This is a fire and shock hazard. | 4 | Conductors, Misuse of flexible cords. | Outlet_box_hanging2.png | file://x:/photopub/docs/0000000623/3540de27-a85e-414f-89c6-2808a9525763.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d08087cf_d59c_40bc_a511_9e5ab994e205
ELIN-845843-2017 | EL-503219-2017 | 6/29/2017 3:52:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Outlet_box_hanging1.png,Outlet_box_hanging2.png Conductors exposed to damaging strain. Outlet box not supported. Connector is not approved for flexible cords. This is a fire and shock hazard. | 4 | Conductors, Misuse of flexible cords. | Outlet_box_hanging1.png | file://x:/photopub/docs/0000000623/4885422a-4194-4bb1-935a-a70b7953a9d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d08087cf_d59c_40bc_a511_9e5ab994e205
BPVOP-864617-2017 | UW-562994-2017 | 7/24/2017 10:16:01 PM | ASSESS: BPV OP: Compliance REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Relief_valve.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this Air Receiver. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced/replaced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve.png | file://x:/photopub/docs/0000000634/8b76affa-81bc-4e5a-9417-9b479b3502ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__faf96776_5265_421e_b3f8_8199d1b6c676
ELIN-843525-2017 | EL-487271-2017 | 7/5/2017 4:01:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Loose_locknuts_on_rigid_metal_and_cable_connectors1.png,Loose_locknuts_on_rigid_metal_and_cable_connectors2.png,Loose_locknuts_on_rigid_metal_and_cable_connectors3.png,Loose_locknuts_on_rigid_metal_and_cable_connectors4.png,Loose_locknuts_on_rigid_metal_and_cable_connectors5.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and to prevent metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 600A 120/240V 1 phase service and sub-service equipment for a agricultural poultry building. The service equipment and sub-service equipmen | 3 | Continuity Bonding; method for equipment is not adequate. | Loose_locknuts_on_rigid_metal_and_cable_connectors1.png | file://x:/photopub/docs/0000000625/fb3c3821-8f14-4d06-9600-62fc8d31d473.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811a534d_e660_4b93_bd75_8a73b6f3a731
ELIN-843525-2017 | EL-487271-2017 | 7/5/2017 4:01:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Loose_locknuts_on_rigid_metal_and_cable_connectors1.png,Loose_locknuts_on_rigid_metal_and_cable_connectors2.png,Loose_locknuts_on_rigid_metal_and_cable_connectors3.png,Loose_locknuts_on_rigid_metal_and_cable_connectors4.png,Loose_locknuts_on_rigid_metal_and_cable_connectors5.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and to prevent metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 600A 120/240V 1 phase service and sub-service equipment for a agricultural poultry building. The service equipment and sub-service equipmen | 3 | Continuity Bonding; method for equipment is not adequate. | Loose_locknuts_on_rigid_metal_and_cable_connectors3.png | file://x:/photopub/docs/0000000625/337cc914-f0af-42a0-8458-851c9c2272f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811a534d_e660_4b93_bd75_8a73b6f3a731
ELHE-852154-2017 | HE-555546-2017 | 7/6/2017 2:44:41 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Pole is built into the structure. Due to the CONDITONING and rot the pole is pulling away from the building | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | #Derelict_Pole.png Consumer service pole is in very poor condition. There is evidence of dry rot. Sound density very low. Cracking is severe and all the way through the cross section. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Derelict_Pole.png | file://x:/photopub/docs/0000000627/ed613350-41d0-45fc-8a3c-a83e4290de13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb0ebad6_c90a_4b5b_b012_43c43fd8d785
ELIN-824667-2017 | EL-378658-2016 | 5/29/2017 2:56:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Step_up_step_down_transformers1.png,Step_up_step_down_transformers2.png The primary 240 volt volt and secondary 120-240 volt feeder cables on the 100 KVA step up/step down transformers are protected with 400 amp fusing. The parallel cable feeders are undersized and can create a thermal hazard should the load rise to its fusing/transformer allowable potential | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Step_up_step_down_transformers2.png | file://x:/photopub/docs/0000000608/69a26818-bf55-439e-af02-ec8cf2dba9cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e74308de_3113_4837_8cf2_bdf8c32b8a2c
ELIN-824667-2017 | EL-378658-2016 | 5/29/2017 2:56:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Step_up_step_down_transformers1.png,Step_up_step_down_transformers2.png The primary 240 volt volt and secondary 120-240 volt feeder cables on the 100 KVA step up/step down transformers are protected with 400 amp fusing. The parallel cable feeders are undersized and can create a thermal hazard should the load rise to its fusing/transformer allowable potential | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Step_up_step_down_transformers1.png | file://x:/photopub/docs/0000000608/4ea150dc-65fc-4240-94f7-a715d2968013.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e74308de_3113_4837_8cf2_bdf8c32b8a2c
BPVOP-848205-2017 | BPV-095999-2014 | 6/29/2017 3:35:02 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Feed_pump.png Both feed water pumps cannot produce enough pressure to rise above the safety valve setting. If this high pressure steam boiler was to go full fire without control, the safety relief valve could pop open and relieve pressure but the feed pumps cannot maintain the water level due to their lack of pumping pressure. This would cause the boiler to gradually steam dry with the risk of overheating exposed metal not covered in water. The risk is an explosive release of energy damaging equipment and injury to personnel in close proximity. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Feed_pump.png | file://x:/photopub/docs/0000000623/ce59d1fc-a2b7-4d41-ba77-78b0184d7ef9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c01cdb3e_9eb9_4171_a880_487e884f5d72
ELIN-864276-2017 | EL-554327-2017 | 7/28/2017 1:37:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #In_terminated_conductors.png Load side conductors , including the Bare bond conductor, from the disconnect breaker for a combination meter disconnect switch, are not terminated and are resting inside the meter base area. In order to connect the conductors the would need to be removed from the meter base area, and terminated to the energized circuit breaker. The available fault current has the potential to be very high in the event of a fault. High shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | In_terminated_conductors.png | file://x:/photopub/docs/0000000637/7464b681-25c1-40ff-947e-224c07f0905b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5eb19de_5419_4afd_aa07_1d3cb36ff0b9
ELIN-814554-2017 | UW-531269-2017 | 5/12/2017 9:02:59 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #AC90_terminated_incorrectly.png Armoured cable installed by unqualified individual who did not understand the special installation requirements for this wiring method. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | AC90_terminated_incorrectly.png | file://x:/photopub/docs/0000000600/4480a1dc-fa21-45dd-b07b-e8854fceaf17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563014b0_ea51_47e1_846f_0943bc9382e8
ELIN-843525-2017 | EL-487271-2017 | 7/5/2017 4:01:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Loose_locknuts_on_rigid_metal_and_cable_connectors1.png,Loose_locknuts_on_rigid_metal_and_cable_connectors2.png,Loose_locknuts_on_rigid_metal_and_cable_connectors3.png,Loose_locknuts_on_rigid_metal_and_cable_connectors4.png,Loose_locknuts_on_rigid_metal_and_cable_connectors5.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and to prevent metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 600A 120/240V 1 phase service and sub-service equipment for a agricultural poultry building. The service equipment and sub-service equipmen | 3 | Continuity Bonding; method for equipment is not adequate. | Loose_locknuts_on_rigid_metal_and_cable_connectors2.png | file://x:/photopub/docs/0000000625/c09f1139-8605-4664-ac2f-6acecad95536.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811a534d_e660_4b93_bd75_8a73b6f3a731
GAIN-844597-2017 | GA-494486-2017 | 7/10/2017 10:18:15 AM | ASSESS: GA: Final | png | #asFound | GA148 | Over fired equipment | 4 | 4 | #Overheated_burner.png,Overheated_burner_2.png Gas range top is overheating and discolouring the metal surrounding the burners. This could lead to a fire. | 4 | Over fired equipment | Overheated_burner.png | file://x:/photopub/docs/0000000628/22377fa3-350c-45be-b286-ec92ba965fb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__530881a1_ccc8_40fc_aeba_ed06bb0e3023
GAIN-844597-2017 | GA-494486-2017 | 7/10/2017 10:18:15 AM | ASSESS: GA: Final | png | #asFound | GA148 | Over fired equipment | 4 | 4 | #Overheated_burner.png,Overheated_burner_2.png Gas range top is overheating and discolouring the metal surrounding the burners. This could lead to a fire. | 4 | Over fired equipment | Overheated_burner_2.png | file://x:/photopub/docs/0000000628/7f0f2d14-a551-4b69-8ec6-dd6e00206ad4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__530881a1_ccc8_40fc_aeba_ed06bb0e3023
BPVIN-820212-2017 | BPV-536707-2017 | 6/5/2017 4:30:37 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | #Coalescing_pre-filter.png Upon assessment of a coalescing pre filter with a maximum working pressure of 260 psig and a maximum working temperature of 200 degrees Fahrenheit, there was no pressure relief device installed. This may result in over pressurizing the pressure vessel in event of an incident. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Coalescing_pre-filter.png | file://x:/photopub/docs/0000000611/1e5418ae-a7f1-4e06-b608-8e86adcdd635.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d904cdc0_5f8d_4b90_840e_dac692c74292
ELHE-854325-2017 | HE-556509-2017 | 7/10/2017 12:30:06 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #Overloaded_fuses.png 240 volt 60 amp fused disconnect switches used to supply suites in a motel have fuses that appear to have been overloaded. This is a thermal effect. Picture attached. | 3 | Protection and control Loading of distribution equipment exceeded | Overloaded_fuses.png | file://x:/photopub/docs/0000000628/3bc0cb2e-3022-4f0e-a74d-995ca8df3afa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1609ea4a_2f4c_43b7_88c2_e5f77465a71b
GAHE-852796-2017 | HE-555796-2017 | 7/7/2017 10:06:05 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Water heater gas piping uncapped after manual shut-off | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open_gas_line.png When an appliance is not connected to a gas system the piping ran to the appliance shall remain capped or plugged till the appliance is connected. If the shut-off valve in this situation were to be accidentally opened or were to fail a un controlled release of gas could occur, causing property damage, explosion or injury. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000627/a31593e9-3bad-4e03-943a-8aa43ade238c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e61252a_4d6b_4b41_80df_6b21ea51e80b
AMIN-844149-2017 | AM-542328-2017 | 6/26/2017 4:38:28 PM | ASSESS: AM IN: Construction | png | #asFound Swaged fork end of cable has been removed from the eye | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 2 | #Eye_which_engages_fork_fitting.png On an elevated platform, a horizontal overhead wire rope is utilized as a anchoring point for the attendants fall protection system. A swaged fork fitting at the end of the horizontal cable which engages into an eye mounted into the platform structure is binding with the eye. (no internal clearance between fork and eye) this results in a cross loading of the fork. Cross loading of fork (spreading the fork) is a load for which a swaged fork is not intended. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Eye_which_engages_fork_fitting.png | file://x:/photopub/docs/0000000622/ef1afe17-b92d-4681-9af7-0a640f809526.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cfe1b3c_258e_4103_a78a_dc6586477cd8
ELIN-841667-2017 | EL-483841-2016 | 6/27/2017 3:46:04 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Dryer_outlet_inaccessible_due_to_counter_space_no_picrture_available_of_counter_plug_no_gif.png Kitchen counter receptacles rated 20 amps and 120 volts within 1.5 meters of sinks in both a main residence and the suite are not gfi protected. This can lead to injury to persons. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Dryer_outlet_inaccessible_due_to_counter_space_no_picrture_available_of_counter_plug_no_gif.png | file://x:/photopub/docs/0000000622/529fff21-b3dc-410f-b678-2d27a7e160aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37977e8f_c3fe_42a0_924e_e3ab08d27d6e
AMOP-844751-2017 | 3559651 | 6/27/2017 3:50:24 PM | ASSESS: AM OP: Periodic | png | #asFound | AM043 | Wear or defects that are Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Zipline_cable_crosby_clips1.png,Zipline_cable_crosby_clips2.png Crosby clips have distorted zipline cable, integrity of cable could be affected. | 2 | Wear or defects that are Reasonably detectable by maintenance program Likely to propagate | Zipline_cable_crosby_clips2.png | file://x:/photopub/docs/0000000622/caa495f6-bb60-42dc-a1ea-44fb5c458968.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79c73b06_2bf3_4edc_9d52_8ca82f81010f
BPVOP-868830-2017 | UW-565385-2017 | 5/6/2017 | ASSESS: BPV OP: Compliance REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Data_plate.png,Relief_valve.png During site assessment, I found the 49 years old air receiver mounted with machine. It is non-compliant to Safety Order requirements. Due to long period of cyclic loading service, there is a greater possibility that the shell thickness may have been reduced below design metal thickness due to corrosion order time. There is also possibility of pitting and cracking on all welded joints. Both these conditions may cause catastrophic failure of the air receiver, resulting in release of energy which will cause damage to nearby personnel and property. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Data_plate.png | file://x:/photopub/docs/0000000638/4f149068-84f0-4af8-9043-82b364f50f30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c2637d1_2aa2_40fc_8fcf_a12a1bc2c98f
BPVOP-868830-2017 | UW-565385-2017 | 5/6/2017 | ASSESS: BPV OP: Compliance REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Data_plate.png,Relief_valve.png During site assessment, I found the 49 years old air receiver mounted with machine. It is non-compliant to Safety Order requirements. Due to long period of cyclic loading service, there is a greater possibility that the shell thickness may have been reduced below design metal thickness due to corrosion order time. There is also possibility of pitting and cracking on all welded joints. Both these conditions may cause catastrophic failure of the air receiver, resulting in release of energy which will cause damage to nearby personnel and property. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Relief_valve.png | file://x:/photopub/docs/0000000638/ad96f8e3-5550-403e-9651-6499208ab309.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c2637d1_2aa2_40fc_8fcf_a12a1bc2c98f
GAUP-833897-2017 | UW-545039-2017 | 6/9/2017 4:27:07 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Uncapped_gas_line1.png,Uncapped_gas_line2.png,Uncapped_gas_line3.png While assessing an unpermitted gas installation I found two gas shut off valves that had been valved off, however were neither plugged nor capped off, the main shut off at the meter was also turned off. Should the main gas be turned on and one of the valves accidentally opened, raw gas could be released into the occupied space. If this gas found a source of ignition it would result in a fire or explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_gas_line1.png | file://x:/photopub/docs/0000000614/34505e5b-d2bf-40e4-b20e-e360099795f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87c10c2c_1e44_4feb_b30c_3acf51f7ea82
GAUP-833897-2017 | UW-545039-2017 | 6/9/2017 4:27:07 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Uncapped_gas_line1.png,Uncapped_gas_line2.png,Uncapped_gas_line3.png While assessing an unpermitted gas installation I found two gas shut off valves that had been valved off, however were neither plugged nor capped off, the main shut off at the meter was also turned off. Should the main gas be turned on and one of the valves accidentally opened, raw gas could be released into the occupied space. If this gas found a source of ignition it would result in a fire or explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_gas_line2.png | file://x:/photopub/docs/0000000614/7bd1020f-c5d2-40d5-8184-1bc57531b93d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87c10c2c_1e44_4feb_b30c_3acf51f7ea82
GAUP-833897-2017 | UW-545039-2017 | 6/9/2017 4:27:07 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Meter in as found condition | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Uncapped_gas_line1.png,Uncapped_gas_line2.png,Uncapped_gas_line3.png While assessing an unpermitted gas installation I found two gas shut off valves that had been valved off, however were neither plugged nor capped off, the main shut off at the meter was also turned off. Should the main gas be turned on and one of the valves accidentally opened, raw gas could be released into the occupied space. If this gas found a source of ignition it would result in a fire or explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_gas_line3.png | file://x:/photopub/docs/0000000614/f0028270-bf74-498a-9192-2435f20e66ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87c10c2c_1e44_4feb_b30c_3acf51f7ea82
GAIN-830092-2017 | GA-497822-2017 | 6/9/2017 11:22:55 AM | ASSESS: GA: Final | png | #asFound Uncapped gas line | GA000 | No Created Hazard Identified | 0 | 0 | #Open_gas_line1.png,Open_gas_line2.png,Open_gas_line3.png While assessing a commercial piping installation I found two gas lines valved off without caps or plugs installed in the open end of the valve, the meter shut off valve was turned off as well. Should one of the open ended valves get bumped open and the meter shut off get turned on, raw gas would flow into the space. Should that gas find a source of ignition a fire or explosion could result. | 0 | No Created Hazard Identified | Open_gas_line1.png | file://x:/photopub/docs/0000000613/91f73ef9-e070-4912-b31f-59091233aeb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ca6a0f9_b9c7_4f73_9b78_37f4950db413
GAIN-830092-2017 | GA-497822-2017 | 6/9/2017 11:22:55 AM | ASSESS: GA: Final | png | #asFound Meter in as found condition with shut off valve in the off position. | GA000 | No Created Hazard Identified | 0 | 0 | #Open_gas_line1.png,Open_gas_line2.png,Open_gas_line3.png While assessing a commercial piping installation I found two gas lines valved off without caps or plugs installed in the open end of the valve, the meter shut off valve was turned off as well. Should one of the open ended valves get bumped open and the meter shut off get turned on, raw gas would flow into the space. Should that gas find a source of ignition a fire or explosion could result. | 0 | No Created Hazard Identified | Open_gas_line3.png | file://x:/photopub/docs/0000000613/73c79e24-5557-4ce6-9695-10b680ff41b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ca6a0f9_b9c7_4f73_9b78_37f4950db413
GAIN-830092-2017 | GA-497822-2017 | 6/9/2017 11:22:55 AM | ASSESS: GA: Final | png | #asFound Uncapped gas line | GA000 | No Created Hazard Identified | 0 | 0 | #Open_gas_line1.png,Open_gas_line2.png,Open_gas_line3.png While assessing a commercial piping installation I found two gas lines valved off without caps or plugs installed in the open end of the valve, the meter shut off valve was turned off as well. Should one of the open ended valves get bumped open and the meter shut off get turned on, raw gas would flow into the space. Should that gas find a source of ignition a fire or explosion could result. | 0 | No Created Hazard Identified | Open_gas_line2.png | file://x:/photopub/docs/0000000613/30238749-b0c5-49d5-9197-0aa07d05f73b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ca6a0f9_b9c7_4f73_9b78_37f4950db413
ELIN-858127-2017 | EL-558616-2017 | 7/17/2017 11:00:31 AM | ASSESS: EL: Service Connection | png | #asFound Rigid service mast without adequate supports | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast.png Over head mast not supported | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast.png | file://x:/photopub/docs/0000000631/78749eb1-9bf4-4c00-bbb6-113059401136.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58c60880_01d7_401e_a626_827f11ca5af7
ELIN-858127-2017 | EL-558616-2017 | 7/17/2017 11:00:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast.png Over head mast not supported | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast.png | file://x:/photopub/docs/0000000631/2974b805-1304-4a3b-8470-e7436b991ec3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58c60880_01d7_401e_a626_827f11ca5af7
GAIN-830986-2017 | GA-540152-2017 | 6/9/2017 2:24:06 PM | ASSESS: GA: Rough-In | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #L_p_5.png Corrugated stainless steel tubing missing bond connection. Corrugated stainless steel tubing is highly susceptible to electrical fault damage which could lead to the uncontrolled release of gas. Risk of fire and or explosion. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | L_p_5.png | file://x:/photopub/docs/0000000614/1465e826-14c9-44a3-b130-261280e06452.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68bcdfe6_a95b_4e7c_84af_053044d300f2
AMOP-844751-2017 | 3559651 | 6/27/2017 3:50:24 PM | ASSESS: AM OP: Periodic | png | #asFound | AM043 | Wear or defects that are Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Zipline_cable_crosby_clips1.png,Zipline_cable_crosby_clips2.png Crosby clips have distorted zipline cable, integrity of cable could be affected. | 2 | Wear or defects that are Reasonably detectable by maintenance program Likely to propagate | Zipline_cable_crosby_clips1.png | file://x:/photopub/docs/0000000622/919a04ef-27e7-46b2-9c23-ac9722cc2106.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79c73b06_2bf3_4edc_9d52_8ca82f81010f
AMOP-844752-2017 | 3559647 | 6/26/2017 8:45:50 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Rider_clearance_to_trees.png Trees are growing into rider envelope, rider could brush a tree while travelling zipline. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Rider_clearance_to_trees.png | file://x:/photopub/docs/0000000622/c071d208-87e9-4972-9603-e8193eba6802.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c027fb8_6ab3_44c6_ad59_5b5e40690459
AMOP-844750-2017 | 3559643 | 6/26/2017 7:16:54 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Turnbuckles_with_no_seizing.png Turnbuckles do not have lock nuts or seizing, could become loose and loose required tension. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Turnbuckles_with_no_seizing.png | file://x:/photopub/docs/0000000622/d485c5e7-61b2-4747-bf13-b8948d0983ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d21ea24_e07f_4ac8_88e0_6ef93d7e3033
AMOP-844754-2017 | 3559653 | 6/27/2017 4:40:38 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Landing_in_need_of_railing.png Missing railing on top landing of zipline launch area, staff or guests could fall off landing | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Landing_in_need_of_railing.png | file://x:/photopub/docs/0000000622/7bb3a778-4cf8-484f-8848-b45447dd037d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b8287df_68ac_4e8b_9cd9_8a05bc69610b
BPVOP-832041-2017 | BPV 00000077487-2013 | 7/11/2017 9:07:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound There are several issues that cause concern with this boiler. First the boiler safety valve is beyond its maximum service interval which could result in the valve failing to operate in an overpressure condition. Second there is considerable rust and scale around the hand hole which which maybe an indication of a previous leak and the possibility of this area now being below the minimum thickness due to rusting. The boiler has also apparently never been properly anchored which could allow it to move in the event of an earthquake or some other unforeseen event. Some of these issues could not be seen on the previous inspection due to the condition of the boiler room caused by the failure of the hot water tank. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Issues1.png,Issues2.png,Issues3.png,Issues4.png The safety valve is beyond its maximum service interval. The boiler requires proper anchoring. There is considerable rust and scale buildup around the lower hand hole. The gage glass is leaking. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Issues1.png | file://x:/photopub/docs/0000000631/446857df-5d0d-48b0-942c-fbee20b9ef1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26c16064_d1ff_4a52_b359_40d3398667ec
BPVOP-832041-2017 | BPV 00000077487-2013 | 7/11/2017 9:07:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Issues1.png,Issues2.png,Issues3.png,Issues4.png The safety valve is beyond its maximum service interval. The boiler requires proper anchoring. There is considerable rust and scale buildup around the lower hand hole. The gage glass is leaking. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Issues4.png | file://x:/photopub/docs/0000000631/c5964970-8430-47e5-a982-eb6594078413.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26c16064_d1ff_4a52_b359_40d3398667ec
BPVOP-832041-2017 | BPV 00000077487-2013 | 7/11/2017 9:07:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Issues1.png,Issues2.png,Issues3.png,Issues4.png The safety valve is beyond its maximum service interval. The boiler requires proper anchoring. There is considerable rust and scale buildup around the lower hand hole. The gage glass is leaking. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Issues3.png | file://x:/photopub/docs/0000000631/6aa28f88-9ba2-4209-84a7-2fdb612a3bd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26c16064_d1ff_4a52_b359_40d3398667ec
BPVOP-832041-2017 | BPV 00000077487-2013 | 7/11/2017 9:07:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Issues1.png,Issues2.png,Issues3.png,Issues4.png The safety valve is beyond its maximum service interval. The boiler requires proper anchoring. There is considerable rust and scale buildup around the lower hand hole. The gage glass is leaking. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Issues2.png | file://x:/photopub/docs/0000000631/62d9f8cb-6af8-45ef-ade8-8a457af86ce0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26c16064_d1ff_4a52_b359_40d3398667ec
GAHE-836359-2017 | HE-546488-2017 | 6/14/2017 2:29:16 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Yellow highlighted "X" indicates that unit has failed pressure test. "Closed "refers to 2lb system and "Open" refers to low pressure side of gas system. | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | #PressureTestSheet.png Pressure tests not being completed in large town house project, resulting in 4 occupied units detecting the smell of natural gas in their home. Upon further testing of all units, they identified 12 more unoccupied units that failed pressure test. Potential for leaking gas to build up and ignite causing serious fire and health hazards. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | PressureTestSheet.png | file://x:/photopub/docs/0000000616/8c53d7a3-8dac-4037-817b-bf328f9133b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b618d9f7_aefe_44a9_9491_857f5d44964b
ELIN-852818-2017 | EL-555835-2017 | 7/19/2017 3:49:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_1.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_2.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_3.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_4.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_5.png Cables are required to be entered into boxes, cabinets, and fittings with approved connectors. This is required to protect the cable and conductor insulation from damage by sharp edges on boxes, equipment, and fixtures, and to protect the terminal connections from strain if the cable is pulled on. This installation in a mobile home addition has non-metallic sheathed cable entered into an exterior lighting box without a connector. The cable is installed pinched between the outlet box and the light fixture. Left uncorrected this is a potential shock and fire hazard if the cable jacket and conductor insulation gets damaged and equipment becomes energize | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_5.png | file://x:/photopub/docs/0000000632/a77946bd-5968-4cdb-a0f6-97b5ac0a5d23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9cfe91b_da53_42e5_a065_9403a2930c3c
ELIN-852818-2017 | EL-555835-2017 | 7/19/2017 3:49:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_1.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_2.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_3.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_4.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_5.png Cables are required to be entered into boxes, cabinets, and fittings with approved connectors. This is required to protect the cable and conductor insulation from damage by sharp edges on boxes, equipment, and fixtures, and to protect the terminal connections from strain if the cable is pulled on. This installation in a mobile home addition has non-metallic sheathed cable entered into an exterior lighting box without a connector. The cable is installed pinched between the outlet box and the light fixture. Left uncorrected this is a potential shock and fire hazard if the cable jacket and conductor insulation gets damaged and equipment becomes energize | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_2.png | file://x:/photopub/docs/0000000632/d0d1ad13-09cb-40af-a6cf-9ade829fb4ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9cfe91b_da53_42e5_a065_9403a2930c3c
ELIN-852818-2017 | EL-555835-2017 | 7/19/2017 3:49:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_1.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_2.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_3.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_4.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_5.png Cables are required to be entered into boxes, cabinets, and fittings with approved connectors. This is required to protect the cable and conductor insulation from damage by sharp edges on boxes, equipment, and fixtures, and to protect the terminal connections from strain if the cable is pulled on. This installation in a mobile home addition has non-metallic sheathed cable entered into an exterior lighting box without a connector. The cable is installed pinched between the outlet box and the light fixture. Left uncorrected this is a potential shock and fire hazard if the cable jacket and conductor insulation gets damaged and equipment becomes energize | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_4.png | file://x:/photopub/docs/0000000632/5d5c9e10-7497-45ea-9867-36aa9e52ff71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9cfe91b_da53_42e5_a065_9403a2930c3c
ELIN-852818-2017 | EL-555835-2017 | 7/19/2017 3:49:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_1.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_2.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_3.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_4.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_5.png Cables are required to be entered into boxes, cabinets, and fittings with approved connectors. This is required to protect the cable and conductor insulation from damage by sharp edges on boxes, equipment, and fixtures, and to protect the terminal connections from strain if the cable is pulled on. This installation in a mobile home addition has non-metallic sheathed cable entered into an exterior lighting box without a connector. The cable is installed pinched between the outlet box and the light fixture. Left uncorrected this is a potential shock and fire hazard if the cable jacket and conductor insulation gets damaged and equipment becomes energize | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_1.png | file://x:/photopub/docs/0000000632/2de78d82-be1b-4e63-bcd2-f23a66437047.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9cfe91b_da53_42e5_a065_9403a2930c3c
ELIN-832298-2017 | EL-468647-2016 | 6/12/2017 11:48:33 AM | ASSESS: EL: Service Connection | png | #asFound The neutral (white) conductor on the right is not stood off from the metal case of the meter base. | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | #Meter_base.png Service connection for new wood frame apartment building. The meter base used for the house load has had its neutral conductor connected improperly so that in a case of an electrical fault the fault may not clear as overcurrent devices may not function. Shock and fire hazard. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Meter_base.png | file://x:/photopub/docs/0000000614/bc7d3b7e-9876-400e-9b75-72e7fca158b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__743d2b6e_c612_4113_98a2_1d951a576fde
ELIN-858127-2017 | EL-558616-2017 | 7/17/2017 11:00:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast.png Over head mast not supported | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast.png | file://x:/photopub/docs/0000000631/20a9d5e3-0eec-4a40-aabe-a0161306c439.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58c60880_01d7_401e_a626_827f11ca5af7
ELIN-832116-2017 | EL-416376-2016 | 6/13/2017 8:22:23 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #Overloading_Neutral.png This assessment found a three wire with to hots being used on a tandem breaker. This can overload the Neutral and a risk of fire exists. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Overloading_Neutral.png | file://x:/photopub/docs/0000000615/5707df39-a6aa-425d-82ff-acb4e141acee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38b90676_00d3_4e8c_b1b4_f777c50de9b5
ELIN-833858-2017 | EL-526160-2017 | 6/13/2017 8:03:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #GFCIs_required.png This assessment found GFCI receptacles are needed for temporary outlets during construction to protect workers from shock hazards due to failure of equipment or damaged cords. | 3 | Conductors Equipment is not approved for the specific use. | GFCIs_required.png | file://x:/photopub/docs/0000000615/aeda48b5-5404-4e57-9890-90106ef56c1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09db2208_8834_43fe_a889_fd35311336ce
BPVIN-840735-2017 | UW-548623-2017 | 6/19/2017 7:15:16 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | #Sideways_safet_valve.png Found boiler with safety relief valve installed sideways in outlet header. Safety relief valve needs to be installed vertical so any mud or debris will not block or impair the function of the safety relief valve as it has to move in order to relieve pressure. Safety relief valve's that do not function will cause the boiler to go over pressure and may fail with an explosive release of hot water with equipment damage and injury to personnel in close proximity. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Sideways_safet_valve.png | file://x:/photopub/docs/0000000620/4cfe9a55-6288-4ae8-bcbc-66ef02228091.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ebc8e47_9fff_4265_a728_12498d9d1ada
EDRI-827892-2017 | ED-539355-2017 | 5/29/2017 | ASSESS: ED RI: Initial | png | #asFound | ED009 | Defects that are: Detected by Maintenance program Likely to progress | 2 | 2 | #Sills_making_contact.png Sill on hoist making contact with landing sill. Hoist could catch gate and pull it from building over time. | 2 | Defects that are: Detected by Maintenance program Likely to progress | Sills_making_contact.png | file://x:/photopub/docs/0000000609/a453092e-f282-4658-89e4-f729bbeb1439.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3b51ce0_27f1_4a81_a22f_6e3b24b5eaa5
GAHE-850551-2017 | HE-554544-2017 | 7/4/2017 9:21:13 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Open Gas line Shop 1 Gas Generator | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open_Gas_Line_11.png,Open_Gas_Line_12.png Found Gas Line in Shop 1 valved off but only a plastic cap taped onto outlet, if anyone had hit or opened valve gas, it would have leaked out and possibly caused extreme danger and destruction. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_Gas_Line_11.png | file://x:/photopub/docs/0000000625/554f474d-6d10-4b49-9a03-007d422a909c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a523cd76_97df_4b49_937b_f42860ff6e3c
GAHE-850551-2017 | HE-554544-2017 | 7/4/2017 9:21:13 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open_Gas_Line_11.png,Open_Gas_Line_12.png Found Gas Line in Shop 1 valved off but only a plastic cap taped onto outlet, if anyone had hit or opened valve gas, it would have leaked out and possibly caused extreme danger and destruction. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_Gas_Line_12.png | file://x:/photopub/docs/0000000625/60170f93-ef83-406b-ba3d-daea1c235283.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a523cd76_97df_4b49_937b_f42860ff6e3c
ELIN-852818-2017 | EL-555835-2017 | 7/19/2017 3:49:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_1.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_2.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_3.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_4.png,Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_5.png Cables are required to be entered into boxes, cabinets, and fittings with approved connectors. This is required to protect the cable and conductor insulation from damage by sharp edges on boxes, equipment, and fixtures, and to protect the terminal connections from strain if the cable is pulled on. This installation in a mobile home addition has non-metallic sheathed cable entered into an exterior lighting box without a connector. The cable is installed pinched between the outlet box and the light fixture. Left uncorrected this is a potential shock and fire hazard if the cable jacket and conductor insulation gets damaged and equipment becomes energize | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_pinched_between_an_outlet_box_edge_and_a_sharp_fixture_edge_3.png | file://x:/photopub/docs/0000000632/c7963fd2-eb0b-400c-9768-61d96cba20f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9cfe91b_da53_42e5_a065_9403a2930c3c
ELIN-543666-2016 | EL-301436-2015 | 5/16/2017 8:18:57 PM | ASSESS: EL: Service Connection | png | #asFound Grounding conductor entering meter-base . | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #15790_Rose_Prairie_Road1.png,15790_Rose_Prairie_Road2.png,15790_Rose_Prairie_Road3.png Service conductors do not enter the service box. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 15790_Rose_Prairie_Road2.png | file://x:/photopub/docs/0000000601/93b6acb1-7523-438d-9a0d-928a96e81bf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acab0af5_2b9d_4821_8760_e3c3c427d210
GAIN-823016-2017 | GA-498849-2017 | 5/30/2017 10:49:38 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_termination.png The vent termination of an on demand water heater was too close to an opening window. This could lead to exhaust gasses being recirculated into the home. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination.png | file://x:/photopub/docs/0000000607/fb50cc93-3088-45d5-8d04-d07fa37f71a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc16dadb_0404_4a5e_87d6_25acb33fcd80
ELIN-821009-2017 | EL-497268-2017 | 5/30/2017 1:40:27 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #receptacles1.png,receptacles2.png,receptacles3.png Arc-fault protection is required on new branch circuits or modified existing branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp/125V receptacles were added to existing branch circuits in the basement without adding arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | receptacles3.png | file://x:/photopub/docs/0000000607/9d6f746a-e534-4d0e-bef3-13ddf4c0d7d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e96e7f1_d4fd_4a4c_9d13_af4ed8e0a8af
ELIN-821009-2017 | EL-497268-2017 | 5/30/2017 1:40:27 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #receptacles1.png,receptacles2.png,receptacles3.png Arc-fault protection is required on new branch circuits or modified existing branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp/125V receptacles were added to existing branch circuits in the basement without adding arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | receptacles1.png | file://x:/photopub/docs/0000000607/c8bb4a3b-b8ec-40ac-944e-29bd44c71d7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e96e7f1_d4fd_4a4c_9d13_af4ed8e0a8af
ELIN-821009-2017 | EL-497268-2017 | 5/30/2017 1:40:27 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #receptacles1.png,receptacles2.png,receptacles3.png Arc-fault protection is required on new branch circuits or modified existing branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation in an existing single family dwelling, new 15 amp/125V receptacles were added to existing branch circuits in the basement without adding arc-fault protection. If a series or parallel arc was to occur in one of the branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | receptacles2.png | file://x:/photopub/docs/0000000607/7f9b76b3-3cc2-4a5c-97ac-5a275c3bb8eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e96e7f1_d4fd_4a4c_9d13_af4ed8e0a8af
BPVIN-833237-2017 | BPV-251606-2015 | 6/29/2017 10:35:48 AM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Nameplate.png | 0 | No Created Hazard Identified | Nameplate.png | file://x:/photopub/docs/0000000623/4acc6c09-0c3a-45a9-802c-17ba746ccba3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3379b986_1e31_49be_8114_097f3e8aa55d
ELIN-851111-2017 | EL-554856-2017 | 7/10/2017 11:42:43 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Bond_cut_at_cable_entry_found_throughout_basement.png Standard household wiring in the basement of a dwelling operating at 120 V and 15 apps for a number of circuits was installed lacking grounding to the device boxes and receptacles. This can lead to the failure of an over current device to react in a fault or short circuit which can result in property damage or injury to persons. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Bond_cut_at_cable_entry_found_throughout_basement.png | file://x:/photopub/docs/0000000628/ec3ef90d-1eb4-4d62-9282-6b55d4334a04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c8c1d91_e86d_47fb_9206_d4ce0d13e8f6
GAHE-831340-2017 | HE-543337-2017 | 6/6/2017 2:21:17 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting.png The product of combustion for the water heater are being exhausted via a kitchen exhaust system instead of a proper venting system. If the water heater is being used when the kitchen exhaust fan is not running, product of combustion could accumulate in the kitchen and create a risk for carbon monoxide poisoning to the occupants. | 3 | Unapproved venting material | Venting.png | file://x:/photopub/docs/0000000612/e4de7be4-b4f7-414d-94a8-ee6edae7068b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__703d9384_954b_403d_ba9c_a9085bcd1d51
AMOP-821585-2017 | 2053183 | 5/24/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #indications_of_cracking1.png,indications_of_cracking2.png,indications_of_cracking3.png,indications_of_cracking4.png,indications_of_cracking5.png Multiple indications of cracking and corrosion on ride; trolley's, sweeps, track and decking all have discontinuities | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | indications_of_cracking4.png | file://x:/photopub/docs/0000000606/316b2c09-9ba7-4e1a-83a5-803b3669adf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b339e9cb_d512_486c_9b9b_5bf456379025
ELIN-817789-2017 | EL-535125-2017 | 5/18/2017 12:15:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #No_cover.png The 15 amp 120 volt receptacle does not include a cover plate or insulated protection to prevent accidental contact by persons. This is a shock hazard | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | No_cover.png | file://x:/photopub/docs/0000000603/fd699817-9dfc-4363-8b5f-2c5c5fdee370.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76927ac9_eee1_481f_9f33_208c480d1dc1
ELIN-815838-2017 | EL-465984-2016 | 5/16/2017 11:56:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL136 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | 3 | 3 | #Box_fill_11.png,Box_fill_12.png,Box_fill_13.png Pan boxes do not have sufficient depth for number of conductors installed. | 3 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | Box_fill_11.png | file://x:/photopub/docs/0000000601/f6bd3d03-6dcc-4690-b710-d8a05b8c46e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5829b9be_b99e_4384_8beb_dd4e41713c9a
ELIN-815838-2017 | EL-465984-2016 | 5/16/2017 11:56:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL136 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | 3 | 3 | #Box_fill_11.png,Box_fill_12.png,Box_fill_13.png Pan boxes do not have sufficient depth for number of conductors installed. | 3 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | Box_fill_13.png | file://x:/photopub/docs/0000000601/de8222ae-63ce-4797-bead-7bfdda2e2852.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5829b9be_b99e_4384_8beb_dd4e41713c9a
ELIN-815838-2017 | EL-465984-2016 | 5/16/2017 11:56:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL136 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | 3 | 3 | #Box_fill_11.png,Box_fill_12.png,Box_fill_13.png Pan boxes do not have sufficient depth for number of conductors installed. | 3 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | Box_fill_12.png | file://x:/photopub/docs/0000000601/f6009d0a-ced5-46ca-b1ae-df77fe67d1b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5829b9be_b99e_4384_8beb_dd4e41713c9a
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png | file://x:/photopub/docs/0000000603/1c8c3bce-c1f3-4224-9966-9d2bedd42b0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png | file://x:/photopub/docs/0000000603/4c354573-8143-4f4f-8731-0fb5150fa4d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png | file://x:/photopub/docs/0000000603/05ba1fdc-b18f-4937-9967-96795fa7e37f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png | file://x:/photopub/docs/0000000603/84dea07e-6482-47a4-af21-7d7abbbc4f6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png | file://x:/photopub/docs/0000000603/f5b56d76-dc48-4a30-9d08-6e28cbe5d411.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png | file://x:/photopub/docs/0000000603/fc9b4ae0-7a80-4722-b37d-5f051a1dc46c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit11.png | file://x:/photopub/docs/0000000603/9a2b4cef-0b6a-4a68-accd-b24236f86fbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit13.png | file://x:/photopub/docs/0000000603/5c0aed25-53eb-4083-b2d0-1ffcef3aa49d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png | file://x:/photopub/docs/0000000603/20488aae-d81b-4fa5-a1fe-89c6e0181e5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png | file://x:/photopub/docs/0000000603/a85d6e7d-4206-4817-aad7-6249eb1f2c1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png | file://x:/photopub/docs/0000000603/b6a8275b-79f4-4e95-b88e-899691e55254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit10.png | file://x:/photopub/docs/0000000603/4287c34e-6028-4c12-a9ba-655514cfa0e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELOP-811598-2017 | 5107112 | 5/18/2017 3:52:27 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit1.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit2.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit3.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit4.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit5.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit6.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit7.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit8.png,Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit9.png,Energized_wiring_exposed_at_recep | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_wiring_exposed_at_receptacle__switch__outlet_box_heater_refrigeration_compressors_and_fan_unit12.png | file://x:/photopub/docs/0000000603/eb71e631-60f0-4699-9cfe-80a323949cff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__683b3349_f4cf_44d3_bec7_016b22b00efa
ELIN-813825-2017 | EL-433646-2016 | 5/26/2017 1:06:40 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuits1.png,Incorrectly_terminated_three_wire_circuits2.png,Incorrectly_terminated_three_wire_circuits3.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had 15A 120/240V three wire branch circuits that had both conductors of the three wire circuits terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulation and terminations causing damage to electrical equipment and potentially a fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuits1.png | file://x:/photopub/docs/0000000606/a89d575b-cb9f-44e9-8fc3-fcea8792f551.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__302ccc07_da3c_4189_8042_279d7353f60e
EDIN-838478-2017 | ED-461586-2016 | 6/16/2017 8:27:20 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Roof_top_passage.png No permanent guardrails were provided on roof top passage to the machine room. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Roof_top_passage.png | file://x:/photopub/docs/0000000617/6d31a1f9-df2b-4907-9231-becf7a2a08ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31b58797_fe2c_4d0e_bf32_e209e7abe28a
EDIN-838480-2017 | ED-461562-2016 | 6/15/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Roof_top_passage1.png Guard rail not provided on Roof Top passage to the machine room. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Roof_top_passage1.png | file://x:/photopub/docs/0000000617/781dfbac-a62d-422c-b433-5823260292a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d63dc20_da25_42d3_a077_76a881553cc6
ELIN-854598-2017 | EL-556129-2017 | 7/11/2017 12:32:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #A.png Cables that rise for termination from underground must have mechanical protection. This is a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | A.png | file://x:/photopub/docs/0000000628/c9cbdea2-59a4-4382-9497-b87cb310f3bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3972d4ff_cc32_400b_8f04_bd857f1a2507
ELHE-863745-2017 | HE-562538-2017 | 7/21/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Conductors_buried_with_no_mechanical_protection_or_burial_tape.png 100 amp, 120/240 volt direct buried conductors installed with no mechanical protection and burial tape. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Conductors_buried_with_no_mechanical_protection_or_burial_tape.png | file://x:/photopub/docs/0000000634/0355d1ba-a725-427d-85ff-08ec07978fc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e299f0d_a5b7_4953_b57a_59ee72abfb5b
BPVIN-789707-2017 | BPV-516083-2017 | 6/27/2017 4:23:55 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_lockable_disconnect.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no remote shutdown switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_lockable_disconnect.png | file://x:/photopub/docs/0000000623/ebc0c237-6682-4749-8150-1a86432f87e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3838df57_050d_4525_893e_8dd16a5158c7
ELIN-813825-2017 | EL-433646-2016 | 5/26/2017 1:06:40 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuits1.png,Incorrectly_terminated_three_wire_circuits2.png,Incorrectly_terminated_three_wire_circuits3.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had 15A 120/240V three wire branch circuits that had both conductors of the three wire circuits terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulation and terminations causing damage to electrical equipment and potentially a fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuits2.png | file://x:/photopub/docs/0000000606/b36aa476-3119-4d87-a40a-88d8dd72cc47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__302ccc07_da3c_4189_8042_279d7353f60e
ELIN-813825-2017 | EL-433646-2016 | 5/26/2017 1:06:40 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuits1.png,Incorrectly_terminated_three_wire_circuits2.png,Incorrectly_terminated_three_wire_circuits3.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had 15A 120/240V three wire branch circuits that had both conductors of the three wire circuits terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulation and terminations causing damage to electrical equipment and potentially a fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuits3.png | file://x:/photopub/docs/0000000606/1120b055-2a0b-4102-a9d2-7a9dea19d19d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__302ccc07_da3c_4189_8042_279d7353f60e
ELIN-819399-2017 | EL-518211-2017 | 5/18/2017 2:38:38 PM | ASSESS: EL: Final | png | #asFound Cable is stressed between stud and cable connector. | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #P4.png Feeder cable for the shop sub panel is in stress between the stud and cable connector to the service panel. This may cause cable insulation failure causing fire. Fire could in turn cause property damage, injuries or death to occupants of this house. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | P4.png | file://x:/photopub/docs/0000000603/9e2969c4-72c5-426b-bc22-829db803effb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7124300_3e4a_4a7c_a8eb_3efa9a7df6e7
ELOP-840311-2017 | EL-057232-2013 | 6/19/2017 12:15:25 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | #Emergency_lighting1.png,Emergency_lighting2.png Multiple emergency lighting units with tags showing they no longer function. In the case of an emergency loss of power there would be inadequate lighting levels for safe egress from the premise. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Emergency_lighting2.png | file://x:/photopub/docs/0000000618/2d084f7e-caaa-4a0c-96ae-1d57dc22a839.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d4b73_ae24_4508_b9c5_1a66d605b63d
ELOP-840311-2017 | EL-057232-2013 | 6/19/2017 12:15:25 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | #Emergency_lighting1.png,Emergency_lighting2.png Multiple emergency lighting units with tags showing they no longer function. In the case of an emergency loss of power there would be inadequate lighting levels for safe egress from the premise. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Emergency_lighting1.png | file://x:/photopub/docs/0000000618/74c91761-bb64-4058-8da0-9c59f9689807.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__343d4b73_ae24_4508_b9c5_1a66d605b63d
ELOP-840313-2017 | EL-155857-2014 | 6/19/2017 2:30:40 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Outlet.png Surface box with a receptacle fed by armoured cable that has been damaged and pulled to expose the energized conductors creating a shock or fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Outlet.png | file://x:/photopub/docs/0000000618/76bcb62c-266f-448e-8c1b-f7bc0984bedd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__047f4f73_ce8e_4301_84f7_da9756c64891
ELIN-840635-2017 | EL-536474-2017 | 6/19/2017 6:34:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL056 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | 3 | 3 | #Temporary_Service_1.png,Temporary_Service_2.png The 100 amp 120/240 volt Temporary Service feeder cable is tapped directly off of the 400 amp 120-240 volt meterbase and is exposed in areas and does not include any overcurrent protection. This can lead to a thermal and shock hazard | 3 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | Temporary_Service_2.png | file://x:/photopub/docs/0000000618/5ec31aab-ad47-4d44-be69-bb9ba98445b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63976ff0_1dc9_4462_8920_b2ac3bbe05d3
ELIN-840635-2017 | EL-536474-2017 | 6/19/2017 6:34:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL056 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | 3 | 3 | #Temporary_Service_1.png,Temporary_Service_2.png The 100 amp 120/240 volt Temporary Service feeder cable is tapped directly off of the 400 amp 120-240 volt meterbase and is exposed in areas and does not include any overcurrent protection. This can lead to a thermal and shock hazard | 3 | Protection and control Overcurrent protection for transformer has not been provided, or is not properly rated | Temporary_Service_1.png | file://x:/photopub/docs/0000000618/6745359c-c33b-4eb7-a00a-a004e8381d20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63976ff0_1dc9_4462_8920_b2ac3bbe05d3
GAHE-845971-2017 | HE-551714-2017 | 6/26/2017 8:28:57 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Secondary_Emergency_shut_off.png Missing mandatory propane fuel safety shut-off's on the dispenser and tank. These shut-off's are in place in case of a failure of the system. If there were to be a uncontrolled release of propane liquid and no way to shut off this discharge a explosion, fire, property damage or injury could occur.. | 4 | Missing mandatory safety controls | Secondary_Emergency_shut_off.png | file://x:/photopub/docs/0000000625/d4e65d09-1b85-418d-bbf6-4417d54fa917.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2235139_a3bb_4fd1_8b2f_318ee358b02a
GAIN-814333-2017 | GA-486376-2017 | 5/23/2017 9:47:08 AM | ASSESS: GA: Final | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | #Hump_back1.png,Hump_back2.png Vent limiter equipped regulator installed in un ventilated space( wall enclosure) Failure of regulator would allow gas to accumulate in the wall space. Risk of fire if a source of ignition was present | 3 | Vent limiter style regulator not installed in a ventilated space | Hump_back2.png | file://x:/photopub/docs/0000000604/1bad45e2-caf7-4754-8fd4-a4f39a7725e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd160406_a230_47ab_aad3_b0dbaf3081ac
GAIN-814333-2017 | GA-486376-2017 | 5/23/2017 9:47:08 AM | ASSESS: GA: Final | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | #Hump_back1.png,Hump_back2.png Vent limiter equipped regulator installed in un ventilated space( wall enclosure) Failure of regulator would allow gas to accumulate in the wall space. Risk of fire if a source of ignition was present | 3 | Vent limiter style regulator not installed in a ventilated space | Hump_back1.png | file://x:/photopub/docs/0000000604/08b8a2ed-1f65-48f7-a849-404e344c78a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd160406_a230_47ab_aad3_b0dbaf3081ac
BPVIN-685724-2016 | BPV-450720-2016 | 5/29/2017 10:04:16 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Clearnaces.png | 0 | No Created Hazard Identified | Clearnaces.png | file://x:/photopub/docs/0000000606/4fbb670b-fb79-4617-9f5c-0c99e125ce65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a218eee4_c492_4cec_9343_894fa797bd4c
ELIN-818406-2017 | EL-508356-2017 | 5/19/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_receptacle_.png In dwellings, the electrical code requires that no point along the floor line of usable wall space be more than 1.8m from a receptacle. The intent of this requirement is to reduce the hazardous use of permanent extension cords and to ensure the safe use of electrical appliances. In a new single family dwelling under construction, a point along the exterior wall was found to be more than 1.8m from a receptacle. Once this dwelling is complete and the circuits are energized, the occupants may have to use an extension cord to connect an electrical appliance at this location. Extension cords are not rated for permanent connections to equipment and could be a potential fire hazard to persons in this dwelling. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_receptacle_.png | file://x:/photopub/docs/0000000603/29a88dc7-44f1-41dc-a3e1-ac991c828c04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06cd6a3d_3fca_41b9_af6e_d237cb7a770f
ELIN-832127-2017 | UW-543820-2017 | 6/7/2017 12:29:58 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound Close-up view of cable that was being used | EL000 | No Created Hazard Identified | 0 | 0 | #irrigation_control_valve_wiring1.png,irrigation_control_valve_wiring2.png,irrigation_control_valve_wiring3.png,irrigation_control_valve_wiring4.png,irrigation_control_valve_wiring5.png,irrigation_control_valve_wiring6.png Class 2 regulated work | 0 | No Created Hazard Identified | irrigation_control_valve_wiring6.png | file://x:/photopub/docs/0000000612/3350ecbf-93c7-4fa6-9b04-eafe9995ce86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe71cf86_811e_4283_82c3_a2b109728077
ELIN-832127-2017 | UW-543820-2017 | 6/7/2017 12:29:58 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound End of cable real | EL000 | No Created Hazard Identified | 0 | 0 | #irrigation_control_valve_wiring1.png,irrigation_control_valve_wiring2.png,irrigation_control_valve_wiring3.png,irrigation_control_valve_wiring4.png,irrigation_control_valve_wiring5.png,irrigation_control_valve_wiring6.png Class 2 regulated work | 0 | No Created Hazard Identified | irrigation_control_valve_wiring2.png | file://x:/photopub/docs/0000000612/25c5fd32-565b-4226-b282-2286358fed72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe71cf86_811e_4283_82c3_a2b109728077
ELIN-832127-2017 | UW-543820-2017 | 6/7/2017 12:29:58 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound Photo from Road showing one of the trenches | EL000 | No Created Hazard Identified | 0 | 0 | #irrigation_control_valve_wiring1.png,irrigation_control_valve_wiring2.png,irrigation_control_valve_wiring3.png,irrigation_control_valve_wiring4.png,irrigation_control_valve_wiring5.png,irrigation_control_valve_wiring6.png Class 2 regulated work | 0 | No Created Hazard Identified | irrigation_control_valve_wiring4.png | file://x:/photopub/docs/0000000612/e4e42389-8ef4-47fa-abc8-9f668cff4620.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe71cf86_811e_4283_82c3_a2b109728077
ELIN-832127-2017 | UW-543820-2017 | 6/7/2017 12:29:58 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound Markings on cable | EL000 | No Created Hazard Identified | 0 | 0 | #irrigation_control_valve_wiring1.png,irrigation_control_valve_wiring2.png,irrigation_control_valve_wiring3.png,irrigation_control_valve_wiring4.png,irrigation_control_valve_wiring5.png,irrigation_control_valve_wiring6.png Class 2 regulated work | 0 | No Created Hazard Identified | irrigation_control_valve_wiring3.png | file://x:/photopub/docs/0000000612/bdfb7119-93bb-4f15-8c69-a665937720b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe71cf86_811e_4283_82c3_a2b109728077
ELIN-832127-2017 | UW-543820-2017 | 6/7/2017 12:29:58 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound Irrigation and control valve wiring installed in trench | EL000 | No Created Hazard Identified | 0 | 0 | #irrigation_control_valve_wiring1.png,irrigation_control_valve_wiring2.png,irrigation_control_valve_wiring3.png,irrigation_control_valve_wiring4.png,irrigation_control_valve_wiring5.png,irrigation_control_valve_wiring6.png Class 2 regulated work | 0 | No Created Hazard Identified | irrigation_control_valve_wiring1.png | file://x:/photopub/docs/0000000612/1da3c81f-b495-441a-9248-a460c8a81bb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe71cf86_811e_4283_82c3_a2b109728077
ELIN-832127-2017 | UW-543820-2017 | 6/7/2017 12:29:58 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound Close-up view of cable that was being used | EL000 | No Created Hazard Identified | 0 | 0 | #irrigation_control_valve_wiring1.png,irrigation_control_valve_wiring2.png,irrigation_control_valve_wiring3.png,irrigation_control_valve_wiring4.png,irrigation_control_valve_wiring5.png,irrigation_control_valve_wiring6.png Class 2 regulated work | 0 | No Created Hazard Identified | irrigation_control_valve_wiring5.png | file://x:/photopub/docs/0000000612/8a8568d5-3bc6-49c3-9799-9dd460a8ed43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe71cf86_811e_4283_82c3_a2b109728077
ELIN-843930-2017 | EL-549480-2017 | 6/29/2017 9:48:49 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Not_to_minimum_depth.png A50 amp 240 volt hot tub feeder has not been buried to a minimum depth. Damage can occur to cables due to settling or work done in area that could lead to property damage or injury to persons | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Not_to_minimum_depth.png | file://x:/photopub/docs/0000000624/4d9f66f9-7046-43c7-8cd9-37ae2dcef292.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0f6265d_eae3_4d38_a847_41f8c7400f8e
ELIN-846159-2017 | EL-544376-2017 | 6/29/2017 11:23:27 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #Panel_too_high.png A 200 amp 240 volt panel board service upgrade in a single dwelling has been placed 35 cm higher than permissible. Panelboards when not easily accessible can lead to injury for operators or workers that require ladders to work on equipment | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_too_high.png | file://x:/photopub/docs/0000000624/8f0e3127-bc72-470e-869b-105eabd72eaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c376aa4_f852_4ea4_b41c_e95457774ad6
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Electrical circuit installed for dishwasher | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit5.png | file://x:/photopub/docs/0000000633/b376a27e-02b6-4a98-a8a5-318bd53a7beb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Junction box missing from ceiling luminaire, typical for lower floor bedrooms | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit3.png | file://x:/photopub/docs/0000000633/a83fd8ea-2e3d-4b22-addb-1c8f4e309020.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Cable splicing completed for pot lights in living room | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit9.png | file://x:/photopub/docs/0000000633/9822082f-658b-4526-9b51-b50175a129f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Existing 100 amp panel board | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit1.png | file://x:/photopub/docs/0000000633/5135c675-6dc2-4e49-81e5-6aec65084ac3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Electrical switch wiring installed for luminaire in the shower | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit7.png | file://x:/photopub/docs/0000000633/ee1c2741-88c6-4016-b492-523e9925f499.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Electrical wiring for luminaire located in shower, upstairs bathroom. Same as downstairs bathroom | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit8.png | file://x:/photopub/docs/0000000633/580bbdd2-a292-4334-bc5c-55268ce9d4ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Owners information | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit2.png | file://x:/photopub/docs/0000000633/7c9de305-9154-47bc-ba10-3a1a97482140.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound As found cable splice for pot lights | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit4.png | file://x:/photopub/docs/0000000633/4ce56190-33df-41fb-8dce-fc49c1b62804.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
ELIN-861907-2017 | UW-561177-2017 | 7/20/2017 10:07:16 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound Pot lights installed in kitchen | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Electrical_work_performed_without_inspections_or_permit1.png,Electrical_work_performed_without_inspections_or_permit2.png,Electrical_work_performed_without_inspections_or_permit3.png,Electrical_work_performed_without_inspections_or_permit4.png,Electrical_work_performed_without_inspections_or_permit5.png,Electrical_work_performed_without_inspections_or_permit6.png,Electrical_work_performed_without_inspections_or_permit7.png,Electrical_work_performed_without_inspections_or_permit8.png,Electrical_work_performed_without_inspections_or_permit9.png Electrical work performed without the necessary permit or inspection request. Unable to determine scope of work performed by either the electrical contractor or the other person the homeowner hired to complete the work. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Electrical_work_performed_without_inspections_or_permit6.png | file://x:/photopub/docs/0000000633/ae405169-48c4-4a1c-941d-12f330c2c79d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__298baa54_dbab_4b56_9e20_df62ea00c21e
AMOP-821616-2017 | 2045536 | 5/24/2017 3:02:42 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Flag_pole_safety_strap1.png,Flag_pole_safety_strap2.png Safety strap on tower flag pole is not installed. If mechanical fastener were to fail, flag pole could fall to the ground . | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Flag_pole_safety_strap1.png | file://x:/photopub/docs/0000000605/bf2809c7-0dae-4de7-8a44-068a98c73b17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac7cfe84_da27_40e9_9529_ec4793076dea
AMOP-821616-2017 | 2045536 | 5/24/2017 3:02:42 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Flag_pole_safety_strap1.png,Flag_pole_safety_strap2.png Safety strap on tower flag pole is not installed. If mechanical fastener were to fail, flag pole could fall to the ground . | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Flag_pole_safety_strap2.png | file://x:/photopub/docs/0000000605/90494219-b1f5-4131-8d67-aa772ad8f500.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac7cfe84_da27_40e9_9529_ec4793076dea
AMOP-821620-2017 | 2046710 | 5/24/2017 2:11:53 PM | ASSESS: AM OP: Periodic | png | #asFound | AM047 | Non-Safety critical monitoring bypassed or failed in manner not reasonably detectable by maintenance/operation program | 2 | 2 | #Monitor_not_functioning.png Passenger control monitor not functioning, passenger behaviour could be missed | 2 | Non-Safety critical monitoring bypassed or failed in manner not reasonably detectable by maintenance/operation program | Monitor_not_functioning.png | file://x:/photopub/docs/0000000605/684676b7-ef54-4ddf-b424-15d9665204ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb54fc91_2a92_4867_9c6b_c8edcf2c0fcc
GAIN-828998-2017 | GA-534444-2017 | 6/9/2017 12:27:37 PM | ASSESS: GA: Rough-In | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | #2ndstagereg_no1st_stage.png Propane systems require two stage regulation. First stage regulation was missing and second stage regulator was not rated for excessive inlet pressure which in turn could potentially cause appliances to work incorrectly causing Carbon Monoxide, property damage from fire or explosion. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 2ndstagereg_no1st_stage.png | file://x:/photopub/docs/0000000614/a7e38c8b-aaef-4aea-b9e0-4aa24ea23c9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68681a88_8565_4de5_ba93_74b8eb6999e3
ELIN-825353-2017 | EL-302800-2015 | 5/31/2017 10:23:19 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Devices1.png,Energized_Devices2.png,Energized_Devices3.png,Energized_Devices4.png Energized 120 volt 15 amp junction boxes, light boxes are open and have not been provided with cover plates, and switches and receptacles have not been provided with cover plates, in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Devices4.png | file://x:/photopub/docs/0000000608/0920036d-eba6-448b-8eb6-7ef87a08af23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e3dda0d_db2e_4895_b549_8015bb558290
ELIN-825353-2017 | EL-302800-2015 | 5/31/2017 10:23:19 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Devices1.png,Energized_Devices2.png,Energized_Devices3.png,Energized_Devices4.png Energized 120 volt 15 amp junction boxes, light boxes are open and have not been provided with cover plates, and switches and receptacles have not been provided with cover plates, in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Devices3.png | file://x:/photopub/docs/0000000608/5d8c653f-071f-4ec2-950a-c0a87f945ae2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e3dda0d_db2e_4895_b549_8015bb558290
ELIN-825353-2017 | EL-302800-2015 | 5/31/2017 10:23:19 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Devices1.png,Energized_Devices2.png,Energized_Devices3.png,Energized_Devices4.png Energized 120 volt 15 amp junction boxes, light boxes are open and have not been provided with cover plates, and switches and receptacles have not been provided with cover plates, in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Devices2.png | file://x:/photopub/docs/0000000608/3c57fb1b-b2f7-412c-93a9-1a611736c24b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e3dda0d_db2e_4895_b549_8015bb558290
ELIN-833728-2017 | EL-488071-2017 | 6/20/2017 7:23:45 PM | ASSESS: EL: Final | png | #asFound | EL252 | Category 2 Equipment is not approved for the specific use or location. | 3 | 3 | #EMT_in_poultry_barn1.png,EMT_in_poultry_barn2.png Area's inside a poultry barn are considered a Category 2 (Wet and Corrosive) location as determined in the BC Electrical Code unless the barn has been engineered for a different area classification. In this installation for a new poultry barn without an area classification, electrical metal tubing (conduit) was installed on the surface of the ceiling and walls with non-weatherproof fittings and boxes. When the barn is full of poultry, the corrosive nature of the manure could cause the metal conduit to deteriorate over time and cause equipment damage. Also, moisture could enter the junction boxes and fixtures which could cause oxidation and overheating of the conductor connections. This could cause conductor failure which has a potential to create a fire hazard inside this barn. | 3 | Category 2 Equipment is not approved for the specific use or location. | EMT_in_poultry_barn2.png | file://x:/photopub/docs/0000000619/7f85632e-c09e-4e80-aeef-663ab3c5d032.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e66c368_c0df_49d1_a467_6f9acc2a57fe
ELIN-833728-2017 | EL-488071-2017 | 6/20/2017 7:23:45 PM | ASSESS: EL: Final | png | #asFound | EL252 | Category 2 Equipment is not approved for the specific use or location. | 3 | 3 | #EMT_in_poultry_barn1.png,EMT_in_poultry_barn2.png Area's inside a poultry barn are considered a Category 2 (Wet and Corrosive) location as determined in the BC Electrical Code unless the barn has been engineered for a different area classification. In this installation for a new poultry barn without an area classification, electrical metal tubing (conduit) was installed on the surface of the ceiling and walls with non-weatherproof fittings and boxes. When the barn is full of poultry, the corrosive nature of the manure could cause the metal conduit to deteriorate over time and cause equipment damage. Also, moisture could enter the junction boxes and fixtures which could cause oxidation and overheating of the conductor connections. This could cause conductor failure which has a potential to create a fire hazard inside this barn. | 3 | Category 2 Equipment is not approved for the specific use or location. | EMT_in_poultry_barn1.png | file://x:/photopub/docs/0000000619/2e2a993e-9d8e-49f0-bc31-88b091feddae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e66c368_c0df_49d1_a467_6f9acc2a57fe
ELIN-860118-2017 | EL-427829-2016 | 7/19/2017 9:04:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #No_expansion_joint_2.png Service raceway entering pole mount meter base does not have an expansion joint. Possibility for settlement of earth around raceway stressing connection to meter base creating the hazard for damage to the meter base. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | No_expansion_joint_2.png | file://x:/photopub/docs/0000000632/ba7baa95-e0d1-43ca-95f1-b113ce3fee91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f387f5f_dff5_4ef5_a4f6_c3ece29ebaf7
BPVIN-847135-2017 | BPV-203395-2015 | 6/28/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Remote_Shutdown_Switch.png The remote shutdown button allows the boiler operator to shut the power of to the steam generator from a safe distance. Should the steam generator experience mechanical failure where high temperature steam and water is spraying from the unit. The remote switch reduces the risk of the boiler operator being seriously hurt or injured by the spraying steam and hot water. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_Shutdown_Switch.png | file://x:/photopub/docs/0000000622/fd2eb788-6aae-4e62-9b12-cf077909e723.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac6ec20_0e84_47a5_8f2f_f522062332a3
ELIN-825353-2017 | EL-302800-2015 | 5/31/2017 10:23:19 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Energized_Devices1.png,Energized_Devices2.png,Energized_Devices3.png,Energized_Devices4.png Energized 120 volt 15 amp junction boxes, light boxes are open and have not been provided with cover plates, and switches and receptacles have not been provided with cover plates, in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_Devices1.png | file://x:/photopub/docs/0000000608/4464e576-d62c-4682-b97b-9cc01ae05251.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e3dda0d_db2e_4895_b549_8015bb558290
ELIN-844153-2017 | EL-546734-2017 | 6/26/2017 2:28:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Ground_plate_electrode_buried_to_400_mm.png Currently grounding electrode is installed at 400mm measured depth. A depth of 600 mm is required. Inadequate burial depth may allow stray voltages to be felt in the case of a fault, as well as over current devices may not act as required to clear faults in the main service or branch circuitry. There is potential for damage to persons and property in these scenarios. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_plate_electrode_buried_to_400_mm.png | file://x:/photopub/docs/0000000621/9435d068-3bcc-4bfd-9af8-a767a633b0b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8c27e55_8af6_4ecd_96be_5098cf0b311c
GAIN-837866-2017 | GA-491046-2017 | 6/26/2017 1:35:38 PM | ASSESS: GA: Rough-In | JPG | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 4 | #IMG_0109.JPG Natural Gas Log Lighter installed in solid fuel burning enclosure with damper not removed or installed in the a fixed open position as per BCSA safety order SO-G5 051207. Potential for flue gas spillage into residence if log lighter is used with damper in closed position with potential for serious illness or death. More pictures in attachments. | 4 | Gas log set installed with damper not permanently secured in open position | IMG_0109.JPG | file://x:/photopub/docs/0000000623/e0f696b5-3e10-4057-80ea-4191cbf12f96.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5244012_2205_4c8c_9c9b_a5ffe42e19c4
GAWP-846965-2017 | GA-497177-2017 | 6/29/2017 8:24:02 AM | ASSESS: GA Work In Progress | JPG | #asFound Roof | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #IMG_0105.JPG Roof top unit installed above restaurant, unit has return air completely block off and has been converted to be used as a make up air unit. Appliance not approved or designed to be used as make up air unit. Potential for premature failure of heat exchanger/appliance, potentially allowing flue gases to enter premise. | 3 | Appliance not installed according to installation instructions | IMG_0105.JPG | file://x:/photopub/docs/0000000623/76296611-2536-4cf6-b0ab-02357e9a709b.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a98ae08_7aa1_4568_ac41_6b1f0bbcf69d
ELIN-843525-2017 | EL-487271-2017 | 7/5/2017 4:01:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Loose_locknuts_on_rigid_metal_and_cable_connectors1.png,Loose_locknuts_on_rigid_metal_and_cable_connectors2.png,Loose_locknuts_on_rigid_metal_and_cable_connectors3.png,Loose_locknuts_on_rigid_metal_and_cable_connectors4.png,Loose_locknuts_on_rigid_metal_and_cable_connectors5.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and to prevent metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 600A 120/240V 1 phase service and sub-service equipment for a agricultural poultry building. The service equipment and sub-service equipmen | 3 | Continuity Bonding; method for equipment is not adequate. | Loose_locknuts_on_rigid_metal_and_cable_connectors4.png | file://x:/photopub/docs/0000000625/7fa651b9-28ea-4630-a2d5-600d48fddce1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811a534d_e660_4b93_bd75_8a73b6f3a731
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated6.png | file://x:/photopub/docs/0000000623/b5be19c1-1970-4d11-a334-f38a4656e5a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated4.png | file://x:/photopub/docs/0000000623/13018e6c-8b93-4cd0-8d75-c5417c4bd30f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated2.png | file://x:/photopub/docs/0000000623/d289afad-abf7-43c9-8afa-47c4de72db00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated1.png | file://x:/photopub/docs/0000000623/75198599-7aaa-401a-9876-790c5b5d1837.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated3.png | file://x:/photopub/docs/0000000623/7586b18b-e30a-4c4a-b662-8a177d666f47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-845216-2017 | EL-205727-2015 | 6/14/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL104 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | 4 | 4 | #High_and_low_voltage_conductors_not_separated1.png,High_and_low_voltage_conductors_not_separated2.png,High_and_low_voltage_conductors_not_separated3.png,High_and_low_voltage_conductors_not_separated4.png,High_and_low_voltage_conductors_not_separated5.png,High_and_low_voltage_conductors_not_separated6.png,High_and_low_voltage_conductors_not_separated7.png 14,400 volt system conductors in contact and not separated from 120/240 volt system conductors in transformer enclosure 14,400 volt system conductors not separated from 120/240 volt system conductors in transformer enclosure may present a shock hazard if different voltage systems come in electrical contact with each other | 4 | Separation of circuits Conductors of high and low voltage systems are not suitably separated from one and another. | High_and_low_voltage_conductors_not_separated7.png | file://x:/photopub/docs/0000000623/8df40388-073c-4e88-8809-c3c0d49e479b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cc731cd_e6d5_4152_9d32_6460cfd6a531
ELIN-823161-2017 | EL-524665-2017 | 5/26/2017 10:37:21 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Improper receptacle spacing in basement on a finished wall. | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Receptacle_spacing.png Rough wire of the new single-family dwelling. Receptacle spacing in basement on a finished wall does not account for receptacle use in that room. This could lead to misuse of extension cords which could be both a shock and fire hazard. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacle_spacing.png | file://x:/photopub/docs/0000000606/580af8a9-b5ac-437d-9d01-2edc3ffb0443.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9a7adf7_9161_4c31_8efe_b3a00ca70d81
AMOP-806669-2017 | 4813707 | 5/1/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Bottle_jack_seized.png An elevating rotating feature which lift passengers requires a method of lowering it in the event of a power failure to allow evacuation of the passengers. In the event that the rotating feature is only at it 50% passenger load capacity a section of a counterweight need to be removed to allow the rotating feature to be lowered. Equipment required to remove the section of the counterweight was not operational (1 of the 2 bottle jacks was seized due to corrosion). The operator did indicate that it was policy not to operate the device for public with a load of less than 50% an therefore very unlikely that the procedure of removing a section of the counterweight would ever need to be implemented. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Bottle_jack_seized.png | file://x:/photopub/docs/0000000610/1d1ac82d-5cee-45aa-96db-79157096b0e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e81fd90_fe78_4218_8825_f710cdffb444
ELIN-866937-2017 | EL-563292-2017 | 7/28/2017 2:28:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #AC90_installed_in_an_unapproved_outlet_box.png 15 amp, 120/208 volt outlet box used not approved with the use of armoured cable. This is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | AC90_installed_in_an_unapproved_outlet_box.png | file://x:/photopub/docs/0000000637/a3dd6460-a646-4031-8435-ee2f8fbcdc7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccb71586_49e6_4c5e_ad87_48e03307fd27
ELIN-868082-2017 | EL-537140-2017 | 7/28/2017 12:09:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding1.png,Grounding2.png The #6 ground wire for a new 200 amp 120/240 volt electrical service has not been terminated in the correct area, this poses a hazard to persons and the equipment has the overcurrent devices may not operate as designed and unwanted fault current may be present on the ground wire. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding1.png | file://x:/photopub/docs/0000000638/b5ef6904-f4f6-4857-9a65-9f93ec95db66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15551e53_9fff_4098_beac_f3c4ce1659b9
ELIN-868082-2017 | EL-537140-2017 | 7/28/2017 12:09:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding1.png,Grounding2.png The #6 ground wire for a new 200 amp 120/240 volt electrical service has not been terminated in the correct area, this poses a hazard to persons and the equipment has the overcurrent devices may not operate as designed and unwanted fault current may be present on the ground wire. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding2.png | file://x:/photopub/docs/0000000638/3f8ca57a-a90c-41bf-90e8-154ed1f6d277.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15551e53_9fff_4098_beac_f3c4ce1659b9
ELIN-845290-2017 | EL-524279-2017 | 6/27/2017 1:15:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Shock_hazard.png This assessment found that no cover on the panel potentially causing a shock or fire hazard when energized. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shock_hazard.png | file://x:/photopub/docs/0000000622/5349d85e-ea54-4ad7-89a1-2e670ae4648b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf51ef29_2586_4de6_8729_678796434cf8
ELIN-843525-2017 | EL-487271-2017 | 7/5/2017 4:01:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Loose_locknuts_on_rigid_metal_and_cable_connectors1.png,Loose_locknuts_on_rigid_metal_and_cable_connectors2.png,Loose_locknuts_on_rigid_metal_and_cable_connectors3.png,Loose_locknuts_on_rigid_metal_and_cable_connectors4.png,Loose_locknuts_on_rigid_metal_and_cable_connectors5.png Lock nuts are installed on metal conduit nipples and cable connectors for bonding of metal enclosures and the electrical equipment they contain. In the case of rigid metal nipples lock nuts are required to be installed on both sides of enclosures and made up tight. This is required to facilitate the operation of over current devices and to prevent metal enclosures of equipment from becoming energized. This is achieved by ensuring there is a good bonding path for fault current to flow back to the service ground and grounded conductor if there is a fault on the system. This installation has a new 600A 120/240V 1 phase service and sub-service equipment for a agricultural poultry building. The service equipment and sub-service equipmen | 3 | Continuity Bonding; method for equipment is not adequate. | Loose_locknuts_on_rigid_metal_and_cable_connectors5.png | file://x:/photopub/docs/0000000625/b4bd74a8-11eb-4b36-8789-b73cc645a8c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811a534d_e660_4b93_bd75_8a73b6f3a731
BPVIN-760990-2017 | BPV-498582-2017 | 6/22/2017 10:13:32 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 3 | #Chiller_1.png,Chiller_2.png In the event of escaping refrigerant there shall be a means capable of exhausting the refrigerant to atmosphere. I found that there was no exhaust system in the machine room for a 240kw chiller containing group A1 refrigerant. Potential exists for exposure due to lack emergency exhaust control. | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | Chiller_1.png | file://x:/photopub/docs/0000000629/02635fb9-b538-4b7c-95f6-a83eb4fda23a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__767651e9_6269_42b9_beb9_c36126d2745d
BPVIN-760990-2017 | BPV-498582-2017 | 6/22/2017 10:13:32 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 3 | #Chiller_1.png,Chiller_2.png In the event of escaping refrigerant there shall be a means capable of exhausting the refrigerant to atmosphere. I found that there was no exhaust system in the machine room for a 240kw chiller containing group A1 refrigerant. Potential exists for exposure due to lack emergency exhaust control. | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | Chiller_2.png | file://x:/photopub/docs/0000000629/f772d02a-54b4-40f5-b245-91f697aaba52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__767651e9_6269_42b9_beb9_c36126d2745d
GAIN-838583-2017 | GA-546944-2017 | 6/20/2017 2:33:52 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Clearance_to_mechanical_airsupply.png -Found RTU installed with vent outlet too close to air intake feeding restaurant. This could lead to products of combustion being recirculated back into the building by way of the Make up air supply to the restaurant. This could result in the occupants being exposed to carbon monoxide gases which are present in the flue of the roof top unit. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Clearance_to_mechanical_airsupply.png | file://x:/photopub/docs/0000000619/7371cc67-5d99-4ca8-a2a6-f341510681c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b27565a2_208d_4087_9a87_4c5c45046854
BPVOP-805603-2017 | 2984926 | 7/13/2017 10:23:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_1.png,Safety_Relief_Valve_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was under the relief capacity required by the boiler. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_2.png | file://x:/photopub/docs/0000000631/9c98629c-6584-4d5d-9386-c8371418f51f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00896849_d6b7_4efc_af24_65ec019fc7e2
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png | file://x:/photopub/docs/0000000625/5144bd64-3cb4-49f8-9179-4b9602047ffe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
GAIN-843933-2017 | GA-014387-2013 | 6/27/2017 3:12:14 PM | ASSESS: GA: Final | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Fireplace.png Certified/Approved gas log set installed in an existing brick chimney. Homeowner verified that the chimney is clean and clear and chimney damper has been removed. Asked to leave appliance in operation while we assess work completed in workshop. When returning back into the house, noticed a very strong formaldehyde smell throughout the living area. Appliance was then shut off and front door opened for fresh air, detecting trace amounts of CO with detector several minutes after appliance was shut off. Formaldehyde's are toxic and a high level of CO could result in sickness or death. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Fireplace.png | file://x:/photopub/docs/0000000622/e4799072-c1e9-45a1-8d0d-96c3a911552d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16d29940_12e1_4fe2_8c6a_ac9a0d0793e6
EDIN-861092-2017 | ED-523187-2017 | 7/19/2017 12:14:13 PM | ASSESS: ED IN: Acceptance | png | #asFound Controller rated for 18A. Conductors to controller rated for a maximum of 12A. | ED021 | Electrical wires showing, some sign of external damage Damp/Wet/Outdoor Location | 3 | 3 | #_41559_Savaria_controller_rating.png Handicap elevating device is rated for 120V-60 Hz-18A. I found the conductors to the controller to be rated for a maximum of 12A. Overtime the overloaded conductor jacket will become brittle and loos its integrity. This could potentially lead to an electrical fault causing an entrapment and or potential fire. | 3 | Electrical wires showing, some sign of external damage Damp/Wet/Outdoor Location | _41559_Savaria_controller_rating.png | file://x:/photopub/docs/0000000632/2ce3f1cd-2240-4101-90f2-b94ab91312dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84f049c6_12ac_4fbd_8ea7_59cfe9b5e35c
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust7.png | file://x:/photopub/docs/0000000637/3c7ce79b-fdef-4627-be3a-d307699d7484.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust2.png | file://x:/photopub/docs/0000000637/3dd3d20d-2cf6-4714-9de1-84bcd03890ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
ELIN-812099-2017 | EL-504984-2017 | 5/15/2017 11:25:28 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | #No_AFCI_or_TR_rated_protection1.png,No_AFCI_or_TR_rated_protection2.png The new 15 amp 120 volt receptacles installed on the top floor of the residence does not include TR rated receptacles or AFCI protection, this is both a thermal and shock hazard | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_or_TR_rated_protection2.png | file://x:/photopub/docs/0000000601/dc72a2fa-29eb-4dd1-bf11-ab4078c6004e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38f507cd_ff55_4308_9ba8_d72a9ec16553
ELIN-812099-2017 | EL-504984-2017 | 5/15/2017 11:25:28 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | #No_AFCI_or_TR_rated_protection1.png,No_AFCI_or_TR_rated_protection2.png The new 15 amp 120 volt receptacles installed on the top floor of the residence does not include TR rated receptacles or AFCI protection, this is both a thermal and shock hazard | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_AFCI_or_TR_rated_protection1.png | file://x:/photopub/docs/0000000601/6fda83fe-28dc-48c4-a777-fa3c09bbac41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38f507cd_ff55_4308_9ba8_d72a9ec16553
GAIN-813430-2017 | GA-532586-2017 | 5/24/2017 1:55:35 PM | ASSESS: GA: Final | png | #asFound Gas connector installed and is a approved gas connector but is for wrong application. | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | #Gas_connector_wrong_application.png Gas connector is approved but used in the wrong application. This could potentially cause a gas leak leading to an explosion due to pre-mature failure. | 2 | Certified appliance connector installed but not approved for application | Gas_connector_wrong_application.png | file://x:/photopub/docs/0000000605/d09786d1-8240-42ea-8b89-71a4f3c4e791.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87311fea_8dd5_47d5_b6fc_40eee493176c
ELIN-825345-2017 | EL-457394-2016 | 5/29/2017 1:20:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Grounding21.png,Grounding22.png Grounding electrode has not been buried and the electrode conductor has been spliced with an unapproved connection. Possibility for non-equal potential plane resulting in a shock hazard. Service has been energized. | 4 | Installation Grounding; conductor is not continuous. | Grounding21.png | file://x:/photopub/docs/0000000607/bb61f38e-39b1-416c-a409-0c5129777fcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b99c562d_a3b1_4080_a788_a63e5e739221
ELIN-825345-2017 | EL-457394-2016 | 5/29/2017 1:20:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Grounding21.png,Grounding22.png Grounding electrode has not been buried and the electrode conductor has been spliced with an unapproved connection. Possibility for non-equal potential plane resulting in a shock hazard. Service has been energized. | 4 | Installation Grounding; conductor is not continuous. | Grounding22.png | file://x:/photopub/docs/0000000607/7a2ab49a-73a8-4e26-a12e-150b8cd32ce0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b99c562d_a3b1_4080_a788_a63e5e739221
ELIN-818188-2017 | EL-387567-2016 | 5/29/2017 1:31:15 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Protection_plates_missing.png In a new single family dwelling space, a 15amp 120volt circuit was found running through new frame construction without adequate mechanical protection in place. This can lead to a "Shock Hazard" situation. Pic attached. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Protection_plates_missing.png | file://x:/photopub/docs/0000000607/68056b53-94cd-40a6-bcb1-d0091f3e380e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e84bcd5d_89a9_46fd_8a44_e0a61944f328
ELHE-857328-2017 | HE-558502-2017 | 7/13/2017 2:32:18 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #From_front_yard.png The device that attaches the overhead utility conductors to the house has come disconnected. This will cause the strain of the over head conductors to be placed onto the conductors in the raceway on the house down to the meter. This may cause the conductors to be damaged and short circuit or be pulled out of the meter base. Either situation can cause a fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | From_front_yard.png | file://x:/photopub/docs/0000000630/6109e809-e976-4c0d-befc-1debf53e7d12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c4e2da5_8f19_460e_8ee7_53bf8b169cd9
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png | file://x:/photopub/docs/0000000625/a216629d-70c1-4587-b096-9862ec80a1d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
ELIN-817375-2017 | EL-516852-2017 | 5/18/2017 10:09:15 AM | ASSESS: EL: Final | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png Top of panel cover rendered in accessible by the ceiling renovation. Persons can not access the screws at the top of the panel. Electrical equipment needs to be accessible for inspection and maintenance. This is a fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | A3.png | file://x:/photopub/docs/0000000603/653de203-a745-410d-8ef6-cf39aefc20e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c0abe5_9aae_4294_ba78_63606cc2937b
ELIN-817375-2017 | EL-516852-2017 | 5/18/2017 10:09:15 AM | ASSESS: EL: Final | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png Top of panel cover rendered in accessible by the ceiling renovation. Persons can not access the screws at the top of the panel. Electrical equipment needs to be accessible for inspection and maintenance. This is a fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | A1.png | file://x:/photopub/docs/0000000603/69bb1c94-69f4-46d5-9070-f179fd9fa853.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c0abe5_9aae_4294_ba78_63606cc2937b
ELIN-817375-2017 | EL-516852-2017 | 5/18/2017 10:09:15 AM | ASSESS: EL: Final | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png Top of panel cover rendered in accessible by the ceiling renovation. Persons can not access the screws at the top of the panel. Electrical equipment needs to be accessible for inspection and maintenance. This is a fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | A4.png | file://x:/photopub/docs/0000000603/07b31303-980c-45ad-a516-5373f027493a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c0abe5_9aae_4294_ba78_63606cc2937b
ELIN-817375-2017 | EL-516852-2017 | 5/18/2017 10:09:15 AM | ASSESS: EL: Final | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png Top of panel cover rendered in accessible by the ceiling renovation. Persons can not access the screws at the top of the panel. Electrical equipment needs to be accessible for inspection and maintenance. This is a fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | A2.png | file://x:/photopub/docs/0000000603/6c81ac4a-8879-47c1-9811-76705a975add.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5c0abe5_9aae_4294_ba78_63606cc2937b
AMOP-844769-2017 | 3850144 | 6/29/2017 11:16:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Seize_shackle_pin_.png Shackle pins not seized, could inadvertently loosen. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Seize_shackle_pin_.png | file://x:/photopub/docs/0000000623/39ca3c52-1697-4ae4-8660-675e447581d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59a258e5_b8c8_487f_8ba2_b827d240243d
AMOP-844771-2017 | AM-019442-2013 | 6/29/2017 12:33:12 PM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #Deck_boards_repair_replace.png Deck boards on the access bridge are loose and rotten in some locations, potential for trip and fall hazard, from height. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Deck_boards_repair_replace.png | file://x:/photopub/docs/0000000623/d68b5717-580d-4c55-96c9-2c0ed07aeee7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d972f77_a93c_4ff8_b4d2_cd6d4dd03ce2
BPVOP-863593-2017 | 2289568 | 7/21/2017 | ASSESS: BPV OP: Re-Certification Boiler | pdf | #asFound UT report | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Jul_13-17_50_111385-UT-01.pdf A Hot Water Boiler with MAWP of 160 psig had a UT survey done on the fireside tubes. The results showed that the remaining thickness is just above the 50% nominal. This can contribute to the failure of the tubes and the boiler. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Jul_13-17_50_111385-UT-01.pdf | file://x:/photopub/docs/0000000635/c072664c-b615-4238-801a-5ddca0438315.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc83124_49f8_4829_ae9e_bdddf46cf58c
BPVOP-863596-2017 | 2289574 | 7/21/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #T_and_P_11.png,T_and_P_12.png During the inspection of a Domestic Hot Water Tank it was discovered that the Temperature and Pressure (T&P) relieve valve has a set point at 150 psig, while the Maximum Allowable Working Pressure of the vessel is 125 psig. In case of over-pressure the T&P will not protect the vessel. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | T_and_P_12.png | file://x:/photopub/docs/0000000635/244799bc-2774-4dc9-9752-bdcf4970afb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c79f5452_b40f_4b07_80fb_7134e0115434
BPVOP-863592-2017 | 2289567 | 7/21/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Data_plate_.png A Hot Water Boiler with MAWP of 160 psig showed corrosion and pitting on the fireside. This can contribute to the failure of the tubes and the boiler. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Data_plate_.png | file://x:/photopub/docs/0000000635/29fa8a43-6fd4-4a43-83f5-25b92a72511a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9154931f_ebba_48eb_a332_536357bf23d0
ELOP-807332-2017 | EL-524532-2017 | 6/26/2017 9:57:47 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL179 | General Construction Indoor: Inadequate spacing from walls for transformer. | 4 | 4 | #One_of_two_transformers_with_combustible_material_storage_close_to_walls_and_obstructing_panels_and_switches.png 2 600 volt 3 phase dry core transformers have been installed in an electrical room as close to the adjacent walls as was possible during the installation. Dry core transformers when mounted on a floor rely on proper separation from adjacent walls to allow for proper dispersion of heat and to make transformers perform the way they were manufactured and tested and to operate safely. When this type of equipment is not correctly installed in this regard, damage to structures or injury to persons can occur. | 4 | General Construction Indoor: Inadequate spacing from walls for transformer. | One_of_two_transformers_with_combustible_material_storage_close_to_walls_and_obstructing_panels_and_switches.png | file://x:/photopub/docs/0000000621/62397341-e25f-4fb6-9508-0c40c4e7c86d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87127491_1290_473D_8DBC_E16D6F8D8A8D
GAIN-760224-2017 | GA-448164-2016 | 6/26/2017 4:11:14 PM | ASSESS: GA: Final | png | #asFound Unit is installed in an area that requires make-up air | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Draft_hood_in_same_area_as_exhaust_fans.png For correct operation of this gas fired appliance, make-up air needs to be provided to correct a negative air situation causing appliance to back draft or spill into kitchen area. This may effect the combustion process of this appliance allowing the products of combustion to enter the kitchen area may cause personal injury if the appliance is not burning properly.. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Draft_hood_in_same_area_as_exhaust_fans.png | file://x:/photopub/docs/0000000622/f146552b-f6ea-410b-9be5-c7efaf5b374e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c2f0fbb_62d1_47e0_ace1_04266b0191d5
ELIN-865647-2017 | EL-340752-2016 | 7/27/2017 1:58:16 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #4_meters_to_panel__obstructed_by_planter_beds.png A 200 amp 240 volt sub distribution was placed in a greenhouse. The panel boards and subdistribution control equipment were placed at an elevation of approximately 4 meters above the level grade below the equipment. To service this equipment or to interact with the panel boards or control equipment a ladder would be required. In addition to the need for a ladder, the grade below the equipment was obstructed by plant beds which would preclude easy access in the event of an emergency. Basic safety requirements in the Canadian Electrical Code address this hazard with very specific access requirements and prohibit this type of equipment being installed so that it requires a ladder to access. Technical repairs by electrical personnel or adjustment of electrical equipment by operators standing on ladders has been demonstrated to lead to potential serious injury or fatalities to persons. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 4_meters_to_panel__obstructed_by_planter_beds.png | file://x:/photopub/docs/0000000637/4382b572-3311-47ed-a02b-358fe1df8bfb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c334794_375b_4e79_bb10_457ca3dd3455
BPVOP-863596-2017 | 2289574 | 7/21/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #T_and_P_11.png,T_and_P_12.png During the inspection of a Domestic Hot Water Tank it was discovered that the Temperature and Pressure (T&P) relieve valve has a set point at 150 psig, while the Maximum Allowable Working Pressure of the vessel is 125 psig. In case of over-pressure the T&P will not protect the vessel. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | T_and_P_11.png | file://x:/photopub/docs/0000000635/711105dd-06b4-4702-b222-97bc7ebf71e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c79f5452_b40f_4b07_80fb_7134e0115434
BPVOP-863597-2017 | 2289572 | 7/21/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #T_and_P_2.png During the inspection of a Domestic Hot Water Tank it was discovered that the Temperature and Pressure (T&P) relieve valve has aset point at 150 psig, while the Maximum Allowable Working Pressure of the vessel is 125 psig. In case of over-pressure the T&P will not protect the vessel. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | T_and_P_2.png | file://x:/photopub/docs/0000000635/0ed22b78-f18f-443f-a340-16a094efc26a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37f05c80_7739_44dd_9883_cfba389efdd6
ELIN-816623-2017 | EL-531663-2017 | 5/16/2017 10:44:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | #Standard_receptacle.png The 15 amp 120 volt duplex receptacle in remote shed on residential property does not include a Tamper Rated receptacle, this is both a shock and a thermal hazard. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Standard_receptacle.png | file://x:/photopub/docs/0000000601/9de4b2d5-164c-4bf0-889c-a3eddedd96ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3df6c7b4_18d4_4770_87e1_8b2fdab1771f
ELIN-844743-2017 | EL-468570-2016 | 7/4/2017 10:52:00 AM | ASSESS: EL: Final | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Main_Ground.png The ground wire for the new 100 amp 120/240 volt Service has been terminated under an existing lug that already has a ground wire in place, the lug is not rated for multiple wires. This poses a safety risk a possible shock hazard and equipment damage if the connection becomes loose or is not making a proper connection. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Main_Ground.png | file://x:/photopub/docs/0000000625/176307ed-54be-4c1a-b7ee-49ab4c1728be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff5658c2_b673_4ce5_86e8_34accddb3d03
ELIN-826634-2017 | EL-538515-2017 | 6/1/2017 11:22:02 AM | ASSESS: EL: Service Connection | png | #asFound 6x6 post depths not achieved. | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Temporary_Contruction_Service.png FSR has used pallets to decrease panel and meter heights. Pole not set into ground to correct distances, no gain mark found on post. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Temporary_Contruction_Service.png | file://x:/photopub/docs/0000000609/b8e3f00a-a77c-4570-9798-d6a6e023799e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebcad40e_02a2_49d8_86c0_d77b76ea9b2f
GAIN-842878-2017 | GA-540229-2017 | 6/28/2017 10:21:48 AM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Pool_boiler1.png,Pool_boiler2.png Use plastic clips instead of metal Vent from reg to close to source of ignition | 3 | Code prohibited practices or materials | Pool_boiler2.png | file://x:/photopub/docs/0000000623/f5c84910-5c1a-4303-9bab-ac5b556add8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a61f3f3_c511_41a0_a16e_0fc226f3ede6
GAIN-842878-2017 | GA-540229-2017 | 6/28/2017 10:21:48 AM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Pool_boiler1.png,Pool_boiler2.png Use plastic clips instead of metal Vent from reg to close to source of ignition | 3 | Code prohibited practices or materials | Pool_boiler1.png | file://x:/photopub/docs/0000000623/914dc5d4-a573-4759-9b57-85f3f369a3d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a61f3f3_c511_41a0_a16e_0fc226f3ede6
ELIN-845647-2017 | EL-540739-2017 | 7/6/2017 4:16:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #A1.png,A2.png Tech cable terminated into a PVC box meant for nonmetallic sheath cable. This is a shock hazard because the metal armour of the cable is not bonded. | 3 | Continuity Bonding; method for equipment is not adequate. | A2.png | file://x:/photopub/docs/0000000626/9f5a8542-8f1c-46bd-9e98-99314d38de41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__783bcb7f_8e28_481b_a94f_7a44c260917d
ELIN-845647-2017 | EL-540739-2017 | 7/6/2017 4:16:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #A1.png,A2.png Tech cable terminated into a PVC box meant for nonmetallic sheath cable. This is a shock hazard because the metal armour of the cable is not bonded. | 3 | Continuity Bonding; method for equipment is not adequate. | A1.png | file://x:/photopub/docs/0000000626/927d440b-622d-4526-8491-89201070e544.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__783bcb7f_8e28_481b_a94f_7a44c260917d
ELIN-851065-2017 | EL-523546-2017 | 7/7/2017 12:36:52 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Open_termination.png Dishwasher was not installed circuit was off but no box was protecting wires, if it was to become energized it would create a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Open_termination.png | file://x:/photopub/docs/0000000627/f4b62033-85a4-4d94-8ba6-f0bf6d55dbcb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__375afbeb_7407_4916_8a66_5512f69cdf35
ELIN-843907-2017 | UW-550578-2017 | 7/17/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Armoured_cable1.png,Armoured_cable2.png,Armoured_cable3.png Armoured cable feeder connected to main distribution centre with bare conductors exposed without a box or cover and without evidence of proper lockout. There was no indication that the conductors were energized at the time of inspection. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Armoured_cable2.png | file://x:/photopub/docs/0000000632/011faa41-0c52-44b0-a0c8-19711009baf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fef11a7_cab0_4ad8_9b7e_5be45d6745e1
ELIN-860365-2017 | UW-560312-2017 | 7/17/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #Electrical_area1.png,Electrical_area2.png Forklift charging electrical room blocked from safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Electrical_area1.png | file://x:/photopub/docs/0000000632/78a524a8-6bfb-4c19-8568-a87196ea3d40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcd605ec_bc64_455c_9a0e_7f8bc01ddcb2
ELIN-843907-2017 | UW-550578-2017 | 7/17/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Armoured_cable1.png,Armoured_cable2.png,Armoured_cable3.png Armoured cable feeder connected to main distribution centre with bare conductors exposed without a box or cover and without evidence of proper lockout. There was no indication that the conductors were energized at the time of inspection. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Armoured_cable1.png | file://x:/photopub/docs/0000000632/1d8992b7-f32b-4af0-b6be-6a317debe0ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fef11a7_cab0_4ad8_9b7e_5be45d6745e1
ELIN-860365-2017 | UW-560312-2017 | 7/17/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #Electrical_area1.png,Electrical_area2.png Forklift charging electrical room blocked from safe egress in the case of an emergency or outage. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Electrical_area2.png | file://x:/photopub/docs/0000000632/2cbd241c-00b7-47f6-b95b-666156b8c6a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcd605ec_bc64_455c_9a0e_7f8bc01ddcb2
ELIN-843907-2017 | UW-550578-2017 | 7/17/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL297 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Armoured_cable1.png,Armoured_cable2.png,Armoured_cable3.png Armoured cable feeder connected to main distribution centre with bare conductors exposed without a box or cover and without evidence of proper lockout. There was no indication that the conductors were energized at the time of inspection. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Armoured_cable3.png | file://x:/photopub/docs/0000000632/5d730272-c965-4179-b797-55071c969e4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fef11a7_cab0_4ad8_9b7e_5be45d6745e1
GAHE-815243-2017 | HE-533685-2017 | 5/19/2017 12:30:44 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #1.png Uncertified equipment installed with no protective glass or safety features. Potential for fire hazard from unapproved devices | 3 | Uncertified appliance connected to gas supply but not in service | 1.png | file://x:/photopub/docs/0000000603/68bccd71-2845-49f2-85a9-66e5d6e24103.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d448f35_f4a1_4312_a1c4_54af1f13b93e
ELIN-867969-2017 | EL-563826-2017 | 7/28/2017 12:56:03 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | #Non_identified_interactive_inverter.png In a single family dwelling, where a micro-hydropower system was installed, an inverter installed in an utility interactive system was not identified as interactive. This could result in a shock hazard situation. Picture attached. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | Non_identified_interactive_inverter.png | file://x:/photopub/docs/0000000638/b6b2e3e1-55e9-45a1-94c8-8f1a4b2cd201.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddaddfa1_a683_4a0e_8fe2_6cff61204c7f
ELIN-850444-2017 | EL-421860-2016 | 7/4/2017 5:04:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #B.png Conductors exposed to mechanical damage from vehicular traffic. This is a hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000625/23ee1a13-8694-44ba-883a-915c9d0adb79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59e5ab5c_aa93_456e_b7fc_e1e3ed228e74
ELIN-846313-2017 | EL-531340-2017 | 6/28/2017 1:28:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #25mm_of_space_required.png This assessment found insulation not present between the heating ducts and conductors, potentially causing overheating of conductors resulting in fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 25mm_of_space_required.png | file://x:/photopub/docs/0000000622/11282f0a-8d3b-4a2d-aadb-216d0f6991bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef064fb1_0b6b_4d8d_9a15_0b8315a94809
ELIN-815650-2017 | EL-467403-2016 | 5/16/2017 2:28:26 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Only_2_arc_fault_protected_circuits_.png Arc fault circuit interrupters have not been provided for receptacle circuits where they are required. This condition increases the chances of an electrical fire caused by an arc fault. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Only_2_arc_fault_protected_circuits_.png | file://x:/photopub/docs/0000000601/7fce8041-c875-4944-b921-aa7e2a1c775a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0836be3_4715_471a_a3dd_6988717a3a80
ELIN-850493-2017 | EL-532536-2017 | 7/25/2017 2:05:27 PM | ASSESS: EL: Final | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Cable_connector_undone.png At an existing modular home, the 100amp 120/240volt feeder cable connector had become dislodged and unconnected. This can lead to a further "Equipment Damage" scenario. Pic attached. | 4 | Installation of electrical equipment Fixtures without suitable support. | Cable_connector_undone.png | file://x:/photopub/docs/0000000635/c947ac23-ec54-40a9-a1d7-812b30c4c6b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74c541a2_be03_491b_a8d4_0ba94c7c8235
BPVOP-852776-2017 | 2282030 | 7/7/2017 9:46:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP019 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | 2 | 2 | #Boiler_supports1.png,Boiler_supports2.png | 2 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | Boiler_supports1.png | file://x:/photopub/docs/0000000630/e843436e-01fc-496d-afe6-00c9f5664de3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af213c81_6e5a_4f46_a53e_844bc671f7da
BPVOP-852776-2017 | 2282030 | 7/7/2017 9:46:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP019 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | 2 | 2 | #Boiler_supports1.png,Boiler_supports2.png | 2 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | Boiler_supports2.png | file://x:/photopub/docs/0000000630/5c6ab19b-8931-4d1f-90b5-89e416b4896e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af213c81_6e5a_4f46_a53e_844bc671f7da
ELIN-865960-2017 | EL-495856-2017 | 7/28/2017 7:25:44 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Kitchen_Receptacle1.png,Kitchen_Receptacle2.png,Kitchen_Receptacle3.png A 15 amp 120 volt receptacle has been installed on a 20 amp 120 volt branch circuit, this poses a risk of equipment damage to the outlet as the Branch Breaker does properly protect the receptacle, allowing the rating of the receptacle to be exceeded. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_Receptacle1.png | file://x:/photopub/docs/0000000637/845dda74-cd1b-4e18-a7ce-585196edeb73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d296540f_8990_4eb7_8b6d_cb16f07592f1
ELIN-865960-2017 | EL-495856-2017 | 7/28/2017 7:25:44 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Kitchen_Receptacle1.png,Kitchen_Receptacle2.png,Kitchen_Receptacle3.png A 15 amp 120 volt receptacle has been installed on a 20 amp 120 volt branch circuit, this poses a risk of equipment damage to the outlet as the Branch Breaker does properly protect the receptacle, allowing the rating of the receptacle to be exceeded. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_Receptacle2.png | file://x:/photopub/docs/0000000637/818c977c-04f4-4a69-bf36-68922b9b0b3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d296540f_8990_4eb7_8b6d_cb16f07592f1
ELIN-865960-2017 | EL-495856-2017 | 7/28/2017 7:25:44 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Kitchen_Receptacle1.png,Kitchen_Receptacle2.png,Kitchen_Receptacle3.png A 15 amp 120 volt receptacle has been installed on a 20 amp 120 volt branch circuit, this poses a risk of equipment damage to the outlet as the Branch Breaker does properly protect the receptacle, allowing the rating of the receptacle to be exceeded. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_Receptacle3.png | file://x:/photopub/docs/0000000637/8e4fc7b4-ec2f-47e2-86b9-e487b40a7a5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d296540f_8990_4eb7_8b6d_cb16f07592f1
ELIN-843892-2017 | EL-530739-2017 | 6/26/2017 2:24:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Nmsc_in_styrofoam_wall.png The nonmetallic sheet cable has not been installed far enough from the finished surface edge. There has been no mechanical protection provided over the wiring therefore the wire could be penetrated unknowingly and damaged. This could lead to a short-circuit scenario and a potential fire due to the conductor being damaged from a piercing of the wiring jacket. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Nmsc_in_styrofoam_wall.png | file://x:/photopub/docs/0000000621/3b3c9480-2762-48be-afdd-d3b2f73a591b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6621a9fb_a959_4f50_ba23_24228cfcaba5
ELOP-851227-2017 | EL-550597-2017 | 7/10/2017 7:48:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Panel_Filler_Missing.png In a 600 amp 347/600 volt electrical panel an opening in the cover has been left where a breaker would be installed, this exposes the interior energized bus to possible contact. This poses a shock hazard to persons and potential damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_Filler_Missing.png | file://x:/photopub/docs/0000000629/ff9683d1-e6c3-47f1-b022-9597c1967f58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6F844DF0_A702_4E9D_9BB2_D6B8D6BACF45
ELIN-824328-2017 | EL-534691-2017 | 6/6/2017 12:02:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | #No_overcurrent_for_feeder_to_house_panel.png A 55 amp rated cable is downstream from a 400 amp overcurrent device and is lacking effective overcurrent protection. This can result in damage to the conductor and result in property damage or injury to persons | 3 | Protection and control Low voltage protection damaged or not provided. | No_overcurrent_for_feeder_to_house_panel.png | file://x:/photopub/docs/0000000612/5c43b3d8-c910-403d-91c4-29598b351277.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cbe8f1ef_fe62_4f63_9bcb_f98d25f3fd25
GAIN-831139-2017 | GA-542688-2017 | 6/27/2017 9:52:55 AM | ASSESS: GA: Rough-In | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | #Gas_connectors.png Appliance connectors for commercial kitchen appliances are not certified for use with appliances with casters. If the appliances are moved several times the connectors may crack and leak. | 3 | Non-certified appliance connector | Gas_connectors.png | file://x:/photopub/docs/0000000622/cc2b9595-d4d2-4908-b180-0fba6acf2d77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d5a6b00_ebc8_4d1b_b94d_c1a1591f0cb2
ELIN-866698-2017 | EL-455169-2016 | 7/27/2017 2:30:03 PM | ASSESS: EL: Final | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | #Receptacle_located_inside_cabinet.png Receptacles located inside cabinetry with closed doors. In the case of a fault, high temperatures or even fire could occur at these receptacles. Location would not allow for visibility of situation in the case of a fault and could cause damage to property or persons. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Receptacle_located_inside_cabinet.png | file://x:/photopub/docs/0000000637/c801dc5b-00c5-4f16-8bce-943340c22771.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4fde772_7fbd_4a6c_abed_f9c7569ab1c3
ELIN-866261-2017 | EL-486515-2017 | 7/27/2017 12:12:06 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #A1.png,A2.png Lag style point of attachment. These are a hazard as the will fail over time. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | A1.png | file://x:/photopub/docs/0000000637/62e8c347-0c5d-4780-830e-06d2cac4c375.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c27d62f1_f148_4765_a701_2c83f9704ab3
ELIN-866261-2017 | EL-486515-2017 | 7/27/2017 12:12:06 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #A1.png,A2.png Lag style point of attachment. These are a hazard as the will fail over time. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | A2.png | file://x:/photopub/docs/0000000637/d98ab4c5-af02-4f98-a935-b329b8a58d95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c27d62f1_f148_4765_a701_2c83f9704ab3
EDIN-822253-2017 | ED-426134-2016 | 5/24/2017 9:43:52 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | #41067_As_Found.png Guiderail brackets and their fastenings (bolts) are used to mount guiderails to the walls. It is important the bolts are torqued to the proper tightness as this will ensure the rail system maintains its mechanical integrity during an event involving the activation of the elevator mechanical safety brakes. During the engagement of the safety brakes there are reactionary forces the rail system must be able to withstand. In addition, proper tightening of the bolts also ensures that seismic code is met for seismic conditions. During an acceptance inspection, it was found that many bolts were not tightened properly. This 4 stop traction, MRL elevator is located in a new commercial building. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 41067_As_Found.png | file://x:/photopub/docs/0000000605/f9bd0b57-3cd8-4f63-8fc6-7b9ddd4e9d76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65f7e183_1c21_48cb_899d_878991668ce1
GAIN-862244-2017 | GA-235634-2015 | 7/21/2017 4:05:12 AM | ASSESS: GA: Final | png | #asFound Water heater attached with CSST and not secured | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | #Water_heater_CSST_attached.png Found CSST connected to free standing water heater. It is possible that the water heater moves, dislodges CSST tubing and creates a hazardous situation leading to damage or injury. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Water_heater_CSST_attached.png | file://x:/photopub/docs/0000000634/6f10ba52-dd51-4387-8249-34f44d2ccaf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__234465aa_61aa_467e_9782_5c046a1af66b
BPVOP-831968-2017 | 2270755 | 6/7/2017 8:48:01 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound No sign of heat damage | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 | #Burner_throat_with_spalled_refractory.png | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Burner_throat_with_spalled_refractory.png | file://x:/photopub/docs/0000000613/0babe4b3-0a80-41ce-a625-547ad3813de2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c550526_e4f0_4d9b_9397_214d67a13e11
ELIN-827848-2017 | UW-541136-2017 | 6/1/2017 11:51:04 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Subpanel1.png,Subpanel2.png,Subpanel3.png An existing energized 100 amp 120/240 volt electrical subpanel has been relocated and used for outdoor construction power. The panel has numerous openings in the cover and the panel enclosure which allows access to the energized components inside, this panel is located in a yard of a single family home and is accessible by anyone. This poses a shock hazard to person and potential mechanical and electrical damage to the panel itself. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | SubPanel3.png | file://x:/photopub/docs/0000000609/f9d93bca-a34a-4de3-8b9f-70f9766fc612.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc85036f_f4bf_42ef_871d_a2d50eb47d07
ELIN-827848-2017 | UW-541136-2017 | 6/1/2017 11:51:04 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Subpanel1.png,Subpanel2.png,Subpanel3.png An existing energized 100 amp 120/240 volt electrical subpanel has been relocated and used for outdoor construction power. The panel has numerous openings in the cover and the panel enclosure which allows access to the energized components inside, this panel is located in a yard of a single family home and is accessible by anyone. This poses a shock hazard to person and potential mechanical and electrical damage to the panel itself. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | SubPanel2.png | file://x:/photopub/docs/0000000609/be5cd151-10e4-43bc-b186-b6e2477550b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc85036f_f4bf_42ef_871d_a2d50eb47d07
ELIN-828864-2017 | EL-506230-2017 | 6/7/2017 10:12:02 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Conductors_not_terminated_in_boxes_or_devices_at_final_request_.png Multiple locations where wiring has been left unterminated, either in devices or junction boxes with covers. Circuits are de-energized currently but can be energized by turning on overcurrent devices. If circuits are turned on, exposed conductor ends would have energized conductors present. This scenario would provide a risk of shock and arc flash, as well as a potential for fire. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_not_terminated_in_boxes_or_devices_at_final_request_.png | file://x:/photopub/docs/0000000612/f81f8aab-8cff-47ed-8f7d-2eb699a4a668.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1c8cf9c_456c_425d_9d97_92aec257997f
ELIN-828849-2017 | EL-505863-2017 | 6/6/2017 2:23:57 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMD90_unprotected_within_one_point_five_meters_from_grade.png NMD90 wiring found unprotected.Receptacle wiring in garage is NMD90 type, this type of wiring requires mechanical protection when installed within 1.5 meters of grade. Damage to the exterior jacket of this type of wiring may expose energized conductors and provide a risk of shock or fire to persons and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_unprotected_within_one_point_five_meters_from_grade.png | file://x:/photopub/docs/0000000612/e19cd17b-e114-418d-9999-e5a05bce405c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a375fc7e_4f79_404c_886c_41a20d97d56e
ELOP-867446-2017 | EL-240331-2015 | 7/27/2017 1:10:16 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_equipment1.png,Exposed_energized_equipment2.png,Exposed_energized_equipment3.png,Exposed_energized_equipment4.png,Exposed_energized_equipment5.png Exposed energized electrical parts with a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_equipment3.png | file://x:/photopub/docs/0000000637/f70f43e2-f17f-47e9-82ff-0ebac5bc5405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a3e609_2279_458a_9c17_2c9cc3c97254
ELOP-867446-2017 | EL-240331-2015 | 7/27/2017 1:10:16 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_equipment1.png,Exposed_energized_equipment2.png,Exposed_energized_equipment3.png,Exposed_energized_equipment4.png,Exposed_energized_equipment5.png Exposed energized electrical parts with a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_equipment1.png | file://x:/photopub/docs/0000000637/8e755b14-cdb7-4700-9894-e8407a84baf3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a3e609_2279_458a_9c17_2c9cc3c97254
ELOP-867446-2017 | EL-240331-2015 | 7/27/2017 1:10:16 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_equipment1.png,Exposed_energized_equipment2.png,Exposed_energized_equipment3.png,Exposed_energized_equipment4.png,Exposed_energized_equipment5.png Exposed energized electrical parts with a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_equipment4.png | file://x:/photopub/docs/0000000637/4869b652-ca41-46ee-baee-f624b0563464.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a3e609_2279_458a_9c17_2c9cc3c97254
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust3.png | file://x:/photopub/docs/0000000637/07b450cc-a09c-471b-a7a4-3fec3c041fb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust5.png | file://x:/photopub/docs/0000000637/9e9787d9-760d-488a-bbc8-d94d8ac2bdff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust4.png | file://x:/photopub/docs/0000000637/c92e4792-07b9-4504-bcfc-d78543293440.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust1.png | file://x:/photopub/docs/0000000637/6c5924f2-f120-4e5e-b70a-85589a2ab298.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
ELOP-867446-2017 | EL-240331-2015 | 7/27/2017 1:10:16 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_equipment1.png,Exposed_energized_equipment2.png,Exposed_energized_equipment3.png,Exposed_energized_equipment4.png,Exposed_energized_equipment5.png Exposed energized electrical parts with a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_equipment2.png | file://x:/photopub/docs/0000000637/d9302393-ec88-468b-a25a-fe2dfd591a0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a3e609_2279_458a_9c17_2c9cc3c97254
ELOP-867446-2017 | EL-240331-2015 | 7/27/2017 1:10:16 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Exposed_energized_equipment1.png,Exposed_energized_equipment2.png,Exposed_energized_equipment3.png,Exposed_energized_equipment4.png,Exposed_energized_equipment5.png Exposed energized electrical parts with a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_energized_equipment5.png | file://x:/photopub/docs/0000000637/1e393eea-df77-458b-81d3-c68a64634c91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6a3e609_2279_458a_9c17_2c9cc3c97254
ELOP-867443-2017 | EL-240331-2015 | 7/27/2017 1:10:32 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png,Wood_dust6.png,Wood_dust7.png Evidence that Safety Order SO-EL-GA 2013-02 has not been complied with. Wood dust accumulations in various locations beyond acceptable limits. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust6.png | file://x:/photopub/docs/0000000637/90417f50-60e1-4807-b719-77c72909601e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54da32ca_7863_4fa2_b474_eb20f12a773c
GAIN-780969-2017 | GA-515010-2017 | 6/23/2017 4:47:00 PM | ASSESS: GA: Final | png | #asFound Tandoor Oven not installed to instructions/clearances/securing | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Tandoor_oven_.png Manufacturers instructions were not used in installation of unit, there's no way to tell if appliance was installed to certified instructions. If for example, a clearance distance was not met, it is possible the unit could overheat itself and create a situation that could lead to damage of appliance or surrounding area. | 3 | Appliance not installed according to installation instructions | Tandoor_oven_.png | file://x:/photopub/docs/0000000622/b2419dff-6ab7-41aa-84cd-9a6ad114f29b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__569b988d_7268_4c30_84cf_2c3098e98dd7
EDIN-846457-2017 | ED-434996-2016 | 6/28/2017 2:00:18 AM | ASSESS: ED IN: Acceptance | png | #asFound | ED013 | Oil/Water/Other Debris found that: Is not affecting components or operation and not likely to progress | 2 | 2 | #Pit_water_from_the_wall.png Water seepage on the pit wall not likely to affect equipment in the short term. | 2 | Oil/Water/Other Debris found that: Is not affecting components or operation and not likely to progress | Pit_water_from_the_wall.png | file://x:/photopub/docs/0000000622/d2232f69-b703-4505-9436-bdeb7ab707ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c47b6b93_fdfe_4287_b234_da3a2472a16f
BPVOP-853306-2017 | BPV-556103-2017 | 6/20/2017 | ASSESS: BPV OP: Special Request Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Door_1.png,Door_2.png During boiler room assessment, I found that the Emergency shut down Switch (ESD switch) has not been installed at both boiler room exits. Potential exists that in case of an emergency, the absence of an ESD switch may cause extensive harm to operators/staff or property, since boiler fuel supply cannot be shut down from boiler room itself. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Door_1.png | file://x:/photopub/docs/0000000627/4a4f8e0d-af14-4e9b-8fba-ccf425462d76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fbff1c2_f4ca_4501_9333_5cee3a12cdb6
BPVOP-853306-2017 | BPV-556103-2017 | 6/20/2017 | ASSESS: BPV OP: Special Request Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Door_1.png,Door_2.png During boiler room assessment, I found that the Emergency shut down Switch (ESD switch) has not been installed at both boiler room exits. Potential exists that in case of an emergency, the absence of an ESD switch may cause extensive harm to operators/staff or property, since boiler fuel supply cannot be shut down from boiler room itself. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Door_2.png | file://x:/photopub/docs/0000000627/195c8495-a1ce-4ee5-8718-e492e92d4434.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fbff1c2_f4ca_4501_9333_5cee3a12cdb6
AMIN-845877-2017 | AM-548687-2017 | 6/28/2017 5:59:32 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM031 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | #In_line_GFCI_that_was_not_utilized.png It was observed that a blower operating from portable generator was operating from a none GFCI protected circuit. The operator did not realize that blower needs to be operated from a GFCI even when operated from a generator. Operating a blower without a GFCI protected circuit result in a shock hazard to riders and to people near by. | 3 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | In_line_GFCI_that_was_not_utilized.png | file://x:/photopub/docs/0000000622/8bff4f94-764d-441e-968b-b1b72edb4250.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1585d87_8f3f_4389_9d76_ba91e5967012
ELIN-827848-2017 | UW-541136-2017 | 6/1/2017 11:51:04 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Subpanel1.png,Subpanel2.png,Subpanel3.png An existing energized 100 amp 120/240 volt electrical subpanel has been relocated and used for outdoor construction power. The panel has numerous openings in the cover and the panel enclosure which allows access to the energized components inside, this panel is located in a yard of a single family home and is accessible by anyone. This poses a shock hazard to person and potential mechanical and electrical damage to the panel itself. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Subpanel3.png | file://x:/photopub/docs/0000000609/a3c18933-f2ab-4847-8265-2472df87a3eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc85036f_f4bf_42ef_871d_a2d50eb47d07
ELIN-827848-2017 | UW-541136-2017 | 6/1/2017 11:51:04 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Subpanel1.png,Subpanel2.png,Subpanel3.png An existing energized 100 amp 120/240 volt electrical subpanel has been relocated and used for outdoor construction power. The panel has numerous openings in the cover and the panel enclosure which allows access to the energized components inside, this panel is located in a yard of a single family home and is accessible by anyone. This poses a shock hazard to person and potential mechanical and electrical damage to the panel itself. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Subpanel1.png | file://x:/photopub/docs/0000000609/f090590c-3aee-47c3-91e8-c05177466196.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc85036f_f4bf_42ef_871d_a2d50eb47d07
ELIN-827848-2017 | UW-541136-2017 | 6/1/2017 11:51:04 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Subpanel1.png,Subpanel2.png,Subpanel3.png An existing energized 100 amp 120/240 volt electrical subpanel has been relocated and used for outdoor construction power. The panel has numerous openings in the cover and the panel enclosure which allows access to the energized components inside, this panel is located in a yard of a single family home and is accessible by anyone. This poses a shock hazard to person and potential mechanical and electrical damage to the panel itself. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Subpanel2.png | file://x:/photopub/docs/0000000609/45e39096-930e-443f-84c3-6976b01c499f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc85036f_f4bf_42ef_871d_a2d50eb47d07
ELIN-827848-2017 | UW-541136-2017 | 6/1/2017 11:51:04 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Subpanel1.png,Subpanel2.png,Subpanel3.png An existing energized 100 amp 120/240 volt electrical subpanel has been relocated and used for outdoor construction power. The panel has numerous openings in the cover and the panel enclosure which allows access to the energized components inside, this panel is located in a yard of a single family home and is accessible by anyone. This poses a shock hazard to person and potential mechanical and electrical damage to the panel itself. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | SubPanel1.png | file://x:/photopub/docs/0000000609/5fc746c6-4f38-48dd-8949-7b4519d64c0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc85036f_f4bf_42ef_871d_a2d50eb47d07
ELIN-859651-2017 | EL-558984-2017 | 7/26/2017 5:28:54 PM | ASSESS: EL: Final | png | #asFound | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png Electrical service conductors are required to be de-energized prior to working on them. This is required to prevent shock, arc flash, and fire hazards during the installation and to protect persons and property from these hazards after the installation is completed. During installation for a service upgrade from 70A 120/240V to 200A 120/240V a certified electrician completed work under a home owner's | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png | file://x:/photopub/docs/0000000637/63ef8262-75e7-4e4b-9e35-fb87f2835cb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02e8ee1c_7c0d_4340_9548_3c883efff8b6
GAIN-841057-2017 | GA-548981-2017 | 7/5/2017 1:31:39 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Meter1.png,Meter2.png Meter has no swing joint and is unsecured. | 2 | Physical protection of piping and tubing absent. | Meter1.png | file://x:/photopub/docs/0000000625/e0e0727b-fe55-4b9a-acae-c4a62e68fe6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1966c7f7_e7f6_4b3b_a873_4610a02e218c
GAIN-841057-2017 | GA-548981-2017 | 7/5/2017 1:31:39 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Meter1.png,Meter2.png Meter has no swing joint and is unsecured. | 2 | Physical protection of piping and tubing absent. | Meter2.png | file://x:/photopub/docs/0000000625/3104568f-c87b-45cd-8db1-89dd7c06c6c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1966c7f7_e7f6_4b3b_a873_4610a02e218c
ELIN-860766-2017 | EL-558607-2017 | 7/28/2017 2:16:52 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #NMD_90_jury_rigged_extension_cord_laying_on_tinder_dry_forest_floor_for_approximately_90_m_eters.png A permanent RV service rated 200 amps and 240 volts was installed with associated sub distribution and equipment including rv receptacles rated 30 amps and 120 volts. The receptacles for 6 of the lots were not located close enough to the permanent RV's for them to connect without the use of extension cords. At the time of this inspection a number of jury rigged cords and extension cords across roadways were found in a tinder dry forest. This condition can lead to forest interface fires, damage to property and potential injury to persons. | 4 | Conductors, Misuse of flexible cords. | NMD_90_jury_rigged_extension_cord_laying_on_tinder_dry_forest_floor_for_approximately_90_m_eters.png | file://x:/photopub/docs/0000000638/5dd80786-989b-4652-bc54-05c695f65430.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec7398e7_212c_4c27_9ce1_7927d501954a
ELIN-849868-2017 | EL-462360-2016 | 7/6/2017 8:02:51 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Range_plug_too_high.png This assessment found that the range receptacle is installed too high, potentially causing damage to range cable if forced against the wall. This can create a shock or fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Range_plug_too_high.png | file://x:/photopub/docs/0000000626/d8245d1b-501e-46e5-8774-d07626d99751.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0dfef79_114f_450a_8efa_0d6eb19e659b
ELIN-859651-2017 | EL-558984-2017 | 7/26/2017 5:28:54 PM | ASSESS: EL: Final | png | #asFound | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png Electrical service conductors are required to be de-energized prior to working on them. This is required to prevent shock, arc flash, and fire hazards during the installation and to protect persons and property from these hazards after the installation is completed. During installation for a service upgrade from 70A 120/240V to 200A 120/240V a certified electrician completed work under a home owner's | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png | file://x:/photopub/docs/0000000637/cc08d011-35ae-4440-9f64-981da9106a92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02e8ee1c_7c0d_4340_9548_3c883efff8b6
ELIN-859651-2017 | EL-558984-2017 | 7/26/2017 5:28:54 PM | ASSESS: EL: Final | png | #asFound | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png Electrical service conductors are required to be de-energized prior to working on them. This is required to prevent shock, arc flash, and fire hazards during the installation and to protect persons and property from these hazards after the installation is completed. During installation for a service upgrade from 70A 120/240V to 200A 120/240V a certified electrician completed work under a home owner's | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png | file://x:/photopub/docs/0000000637/05b24401-706c-4eb6-b08b-9edeb69da7e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02e8ee1c_7c0d_4340_9548_3c883efff8b6
ELIN-859651-2017 | EL-558984-2017 | 7/26/2017 5:28:54 PM | ASSESS: EL: Final | png | #asFound | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png Electrical service conductors are required to be de-energized prior to working on them. This is required to prevent shock, arc flash, and fire hazards during the installation and to protect persons and property from these hazards after the installation is completed. During installation for a service upgrade from 70A 120/240V to 200A 120/240V a certified electrician completed work under a home owner's | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png | file://x:/photopub/docs/0000000637/6460b249-658d-4d4f-a8b3-8f99d0ffe6f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02e8ee1c_7c0d_4340_9548_3c883efff8b6
ELIN-859651-2017 | EL-558984-2017 | 7/26/2017 5:28:54 PM | ASSESS: EL: Final | png | #asFound | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors1.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors3.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors4.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors5.png,Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors6.png Electrical service conductors are required to be de-energized prior to working on them. This is required to prevent shock, arc flash, and fire hazards during the installation and to protect persons and property from these hazards after the installation is completed. During installation for a service upgrade from 70A 120/240V to 200A 120/240V a certified electrician completed work under a home owner's | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Photos_of_service_change_completed_by_disconnecting_and_reconnecting_energized_service_conductors2.png | file://x:/photopub/docs/0000000637/43c0ca35-bc62-405c-903d-4816e8fc6450.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02e8ee1c_7c0d_4340_9548_3c883efff8b6
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A5.png | file://x:/photopub/docs/0000000611/c0cc07d9-40f2-46dc-9266-97380d30d198.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A2.png | file://x:/photopub/docs/0000000611/7c1576e7-b2b1-498e-9708-f9e5d7883c2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A3.png | file://x:/photopub/docs/0000000611/3ec53a12-aaac-4139-8fa5-afbba64f939f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A8.png | file://x:/photopub/docs/0000000611/de44a912-a97e-4003-a88b-d876e8a60159.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A9.png | file://x:/photopub/docs/0000000611/bbd13bfe-a5e6-450a-a030-6e3baa4a760c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A4.png | file://x:/photopub/docs/0000000611/630d3c69-febb-4734-b2ff-e5f8bde2a9e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A1.png | file://x:/photopub/docs/0000000611/d680c0f7-e89e-4bf2-a572-dff401e8697b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A7.png | file://x:/photopub/docs/0000000611/1cbf5c22-aa84-4daa-9b84-7c4bc6cfe3ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
ELIN-831347-2017 | EL-468328-2016 | 6/6/2017 4:16:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png,A7.png,A8.png,A9.png Cable laid on top on ground and covered with sand, not buried to proper depth. This is a shock and fire hazard. The substrate coving the cable is eroding, eventually the cable will be exposed to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | A6.png | file://x:/photopub/docs/0000000611/2218d570-415d-48b8-bd52-a00de7924dc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__355613df_ce28_4e1e_8207_98d349d48986
GAIN-819880-2017 | GA-528195-2017 | 5/23/2017 2:06:33 PM | ASSESS: GA: Final | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 4 | #Fryer.png Found a Deep Fat Fryer in a commercial kitchen with the burners operating incorrectly and flashing back. When the burner was cycled on and off, delayed ignition occurred. Through further investigation it was noted that the Deep Fat Fryer had been incorrectly converted in relation to the burner input indicated on the rating plate. Due to the lack of gas volume, which caused the flash back and delayed ignition condition, this would lead to damage of the unit or potential harm to the operator. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Fryer.png | file://x:/photopub/docs/0000000604/d166e03a-d466-4dac-93a9-f33605929038.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811a09e4_b823_4ce3_8d95_073bdbb2838a
GAIN-828471-2017 | GA-493444-2017 | 6/12/2017 2:01:06 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Regulator_location.png 2nd Stage regulator installed near mechanical air inlet for a Make up Air Unit. In an overpressure scenario the relief from regulator will release pressure and the Make up air unit could suck propane gas into appliance causing an explosion of gases in heat exchanger if burner is on. If burner is not on propane gas will be pushed into kitchen area of bunk house, causing a possible fire. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulator_location.png | file://x:/photopub/docs/0000000615/d90479f7-8894-416f-8eec-649656748f70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2aad3e7_f64e_432a_a804_0450dcffea89
GAIN-864129-2017 | GA-562370-2017 | 7/25/2017 11:19:10 AM | ASSESS: GA: Final | png | #asFound Clearance from regulator relief vent opening to appliance air intake is approximately 3 feet. | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #RElief_opening_to_appliance_air_intake.png Appliance air intake clearance to regulator relief vent opening is approximately 3 feet and does not meet the requirements of directive D-GA 2014 04 which calls for 10 feet of clearance. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | RElief_opening_to_appliance_air_intake.png | file://x:/photopub/docs/0000000636/d5716c11-88ff-4d45-a404-87e2facaf778.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73a5dc60_4d7f_4579_b222_aad76425ebd8
GAIN-834037-2017 | GA-538413-2017 | 7/17/2017 11:26:35 AM | ASSESS: GA: Final | png | #asFound Inducer | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Inducer.png At time of inspection safety officer could not confirm that air proving switch was electrically connected, this condition could cause products of combustion to enter pool pump room. | 3 | Appliance not installed according to installation instructions | Inducer.png | file://x:/photopub/docs/0000000631/9cc2f7e9-ad48-499b-9121-32b22efda986.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee524755_55b0_4d33_b5cd_7ae1c053cf75
ELIN-826555-2017 | EL-530153-2017 | 5/30/2017 5:38:03 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound No raceway installed for in floor heat. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #4.png There is no raceway installed for the heating cable leads of the in-floor heat in the bathroom. This is a fire hazard as a nail could damage the leads of the heating cables in the wall causing a arc and subsequent fire inside the wall cavity. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 4.png | file://x:/photopub/docs/0000000608/0978f901-731f-4ca9-b32f-629edd7bf8a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2597fc00_a753_470a_aeb4_bea2fda37615
ELIN-867554-2017 | EL-564777-2017 | 7/28/2017 3:17:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_conduit_with_nail.png - No mechanical protection was installed on outside sheathing of conduit. Nail was in conduit at time of inspection. Cables in this conduit are unprotected from BC Hydro creating high risk of arcing or shock. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_conduit_with_nail.png | file://x:/photopub/docs/0000000638/d9ea2af1-3bf6-4a1e-9da4-a587bab10a7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0920db57_623d_4d9b_be46_1841dc115754
ELIN-854474-2017 | EL-555544-2017 | 7/11/2017 2:16:05 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Seimens_breakers_in_Cutler_panel.png A 30 amp 240 volt circuit was installed to an air condition from a panel in a residence. The circuit breaker installed was not of a type rated or approved for use in the panel board. Equipment not specifically approved for use in electrical systems can fail unpredictably leading to a potential for damage to property or injury to persons. | 3 | Conductors Equipment is not approved for the specific use. | Seimens_breakers_in_Cutler_panel.png | file://x:/photopub/docs/0000000629/52b64b18-c124-4ed7-8c7b-39b7847575cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64b44aa0_af72_430a_9b1c_cc15f898e973
ELIN-834129-2017 | UW-545183-2017 | 6/12/2017 2:12:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png Fixtures hanging from conductors, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | B5.png | file://x:/photopub/docs/0000000614/61597806-8c4a-4cfd-a7f6-f540039d1ce8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8470c7_2120_408d_b860_910b3e3f2f27
ELIN-834129-2017 | UW-545183-2017 | 6/12/2017 2:12:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png Fixtures hanging from conductors, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | B3.png | file://x:/photopub/docs/0000000614/33e59c24-2a0d-4d49-8fc6-c5452704427a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8470c7_2120_408d_b860_910b3e3f2f27
ELIN-834129-2017 | UW-545183-2017 | 6/12/2017 2:12:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png Fixtures hanging from conductors, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | B1.png | file://x:/photopub/docs/0000000614/e97c9e22-659d-4050-83e6-382358cca1ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8470c7_2120_408d_b860_910b3e3f2f27
ELIN-834931-2017 | EL-424702-2016 | 6/12/2017 1:59:04 PM | ASSESS: EL: Final | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | #A1.png,A2.png,A3.png Receptacles installed above linear convection heaters. As per the manufactures instruction receptacles are not to be located in this manner. This is a fire and shock hazard, as these heaters are hot enough to melt electrical cords. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A2.png | file://x:/photopub/docs/0000000614/df91e617-2274-4882-88c3-6d11893da383.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf1b410a_eea6_49b8_ac1a_ce40ef55bea5
ELIN-834931-2017 | EL-424702-2016 | 6/12/2017 1:59:04 PM | ASSESS: EL: Final | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | #A1.png,A2.png,A3.png Receptacles installed above linear convection heaters. As per the manufactures instruction receptacles are not to be located in this manner. This is a fire and shock hazard, as these heaters are hot enough to melt electrical cords. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A3.png | file://x:/photopub/docs/0000000614/0cb5fb08-5942-42a5-ba5c-2e5f08ea7ee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf1b410a_eea6_49b8_ac1a_ce40ef55bea5
ELIN-834931-2017 | EL-424702-2016 | 6/12/2017 1:59:04 PM | ASSESS: EL: Final | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | #A1.png,A2.png,A3.png Receptacles installed above linear convection heaters. As per the manufactures instruction receptacles are not to be located in this manner. This is a fire and shock hazard, as these heaters are hot enough to melt electrical cords. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A1.png | file://x:/photopub/docs/0000000614/ed07cd47-49b4-4de3-bace-d861f17837b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf1b410a_eea6_49b8_ac1a_ce40ef55bea5
AMOP-860590-2017 | 2047700 | 7/19/2017 6:03:40 AM | ASSESS: AM OP: Periodic | png | #asFound | AM012 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | 3 | 3 | #Corrosion_protection1.png,Corrosion_protection2.png Corrosion protection on support structure footings was failing, corrosion could propagate. | 3 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | Corrosion_protection1.png | file://x:/photopub/docs/0000000632/1243a2d3-6b52-4192-9c97-107d5ad1b7d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e17f34f4_eaed_45bf_8fb9_4de36826c7d8
AMOP-860590-2017 | 2047700 | 7/19/2017 6:03:40 AM | ASSESS: AM OP: Periodic | png | #asFound | AM012 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | 3 | 3 | #Corrosion_protection1.png,Corrosion_protection2.png Corrosion protection on support structure footings was failing, corrosion could propagate. | 3 | Defects that: May not be reasonably detectable by maintenance program Are likely to propagate | Corrosion_protection2.png | file://x:/photopub/docs/0000000632/b7258bb8-d04c-4315-ba77-d1f7f0a1a30c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e17f34f4_eaed_45bf_8fb9_4de36826c7d8
ELIN-840019-2017 | EL-541867-2017 | 6/21/2017 3:45:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Work_not_complete_and_not_accessible_1.png,Work_not_complete_and_not_accessible_2.png,Work_not_complete_and_not_accessible_3.png Work is not complete and is not accessible for assessment. Potential for non compliant service work to be connected with request to BC Hydro resulting in a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Work_not_complete_and_not_accessible_2.png | file://x:/photopub/docs/0000000619/c328087c-f3c5-479d-a4c5-2ce0c7d36482.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed2a702_0cf3_4c45_86e4_5338c7f6f163
ELIN-840019-2017 | EL-541867-2017 | 6/21/2017 3:45:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Work_not_complete_and_not_accessible_1.png,Work_not_complete_and_not_accessible_2.png,Work_not_complete_and_not_accessible_3.png Work is not complete and is not accessible for assessment. Potential for non compliant service work to be connected with request to BC Hydro resulting in a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Work_not_complete_and_not_accessible_1.png | file://x:/photopub/docs/0000000619/3fd9fe42-1af8-49ec-9cda-225bf32cf600.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed2a702_0cf3_4c45_86e4_5338c7f6f163
ELIN-840019-2017 | EL-541867-2017 | 6/21/2017 3:45:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL290 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Work_not_complete_and_not_accessible_1.png,Work_not_complete_and_not_accessible_2.png,Work_not_complete_and_not_accessible_3.png Work is not complete and is not accessible for assessment. Potential for non compliant service work to be connected with request to BC Hydro resulting in a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Work_not_complete_and_not_accessible_3.png | file://x:/photopub/docs/0000000619/717135dc-e3ae-4da0-aa70-2d650577b385.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eed2a702_0cf3_4c45_86e4_5338c7f6f163
BPVOP-866158-2017 | 2270611 | 7/26/2017 11:03:49 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_valves.png Upon assessment of Hot Water Boiler with Heating surface area of 75 square meters, Maximum Allowable Working Pressure (MAWP) of 125psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valves have exceeded the interval for testing and servicing/replacement. Failure to have safety valves tested and serviced/replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valves.png | file://x:/photopub/docs/0000000636/28c9e939-565f-4633-bf09-2d2c582355c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ff7bbf0_217c_420c_a291_6e221584f232
ELIN-820247-2017 | EL-465407-2016 | 5/23/2017 12:55:31 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #A1.png,A2.png,A3.png,A4.png,A5.png,A6.png Are lamp fixture located in close closet, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A3.png | file://x:/photopub/docs/0000000604/db6a0a82-dd5b-4665-becd-ba1e42874c77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b0a9c24_4b4b_427e_b462_14821bd3934f
BPVOP-864227-2017 | 2271382 | 7/24/2017 11:20:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Valve_1.png,Safety_Valve_2.png Upon assessment of Low Pressure steam Boiler with Heating surface area of 237 square meters, it was determined that safety valves have exceeded the required 5year interval for servicing/replacement. Failure to have safety valves serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and/or steam and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Valve_1.png | file://x:/photopub/docs/0000000634/87057977-e808-4631-8779-3742bef3f492.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5dd7f1a_aaaa_476c_aff5_ea5f4966be33
ELHE-833372-2017 | HE-544715-2017 | 6/8/2017 4:53:08 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Z1.png,Z2.png 3C/#1 AWG ACWU has been installed in a trench without observing correct installation procedures. This conductor is approximately 6" below grade. This is a shock hazard to anyone working in the area. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Z2.png | file://x:/photopub/docs/0000000613/420e58cb-a852-4f3b-b645-7fd197b36bd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2bbaeca_d1fe_4255_8721_2ecee8609910
GAIN-849552-2017 | GA-554006-2017 | 7/17/2017 2:02:25 PM | ASSESS: GA: Final | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | #Meter_and_piping_no_protection.png Vehicle protection is required to prevent damage to meter and piping if not present could cause physical damage to system and a possible uncontrolled release of gas could occur causing an explosion, fire , property damage or injury. | 3 | No protection Low traffic | Meter_and_piping_no_protection.png | file://x:/photopub/docs/0000000631/a40d3800-f360-4769-8617-8984977e94fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61cb23ac_96f1_4ed1_9ca7_d5349c9e9b3e
ELIN-821245-2017 | EL-536564-2017 | 6/7/2017 10:57:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Image_1-31.png,Image_1-32.png,Image_1-33.png - live electrical panels with no covers. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Image_1-31.png | file://x:/photopub/docs/0000000612/0936dcf8-8748-4a59-bd4b-44040b671277.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe3a7a70_3c63_4c24_a1c6_de123160d5fa
ELIN-821245-2017 | EL-536564-2017 | 6/7/2017 10:57:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Image_1-31.png,Image_1-32.png,Image_1-33.png - live electrical panels with no covers. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Image_1-33.png | file://x:/photopub/docs/0000000612/6fee1e94-77a9-418f-b200-98f1f1cbf51f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe3a7a70_3c63_4c24_a1c6_de123160d5fa
ELIN-856928-2017 | EL-556817-2017 | 7/14/2017 10:47:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Exposed_energized_panel1.png,Exposed_energized_panel2.png A feeder conductor has been spliced into the main panel through the cover with the cover off. No mechanical connection has been made to the feeder for the subpanel. The main panel is energized with exposed conductors and bus resulting in the potential for fire or electric shock. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized_panel1.png | file://x:/photopub/docs/0000000630/8cef8900-1124-42b1-912c-b6db4569b03f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__826fc0ff_e32f_4825_9bc1_d2a602a247c8
ELIN-834129-2017 | UW-545183-2017 | 6/12/2017 2:12:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png Fixtures hanging from conductors, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | B2.png | file://x:/photopub/docs/0000000614/c9b7eaf7-7c74-4be1-bde7-7c9acf3972e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8470c7_2120_408d_b860_910b3e3f2f27
ELIN-834129-2017 | UW-545183-2017 | 6/12/2017 2:12:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #B1.png,B2.png,B3.png,B4.png,B5.png Fixtures hanging from conductors, this is a fire and shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | B4.png | file://x:/photopub/docs/0000000614/e02de3a5-a6fe-430b-b0ba-feaddd2731f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8470c7_2120_408d_b860_910b3e3f2f27
ELIN-830014-2017 | EL-505299-2017 | 6/6/2017 2:05:07 PM | ASSESS: EL: Final | png | #asFound Range receptacle fed from 30 amp breaker. | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | #Range_breaker_.png Final assessment on new single-family dwelling. The electrical range receptacle in the kitchen has been fed by a circuit breaker that is smaller than the required circuit breaker. Therefore, when an electric range is installed it will not be able to work as intended and cause the overcurrent device to trip repeatedly. This can lead to fire in the panel and damage to the electronics in a newer range. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Range_breaker_.png | file://x:/photopub/docs/0000000611/f6e5a236-4079-4ee2-b5fe-798fd7c57df3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f205c01e_8e2b_4efe_bd12_6afdad10e13f
BPVOP-864228-2017 | 2271383 | 7/24/2017 12:44:46 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valves.png Upon assessment of Low Pressure steam Boiler with Heating surface area of 237 square meters, it was determined that safety valves have exceeded the required 5year interval for servicing/replacement. Failure to have safety valves serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and/or steam and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valves.png | file://x:/photopub/docs/0000000634/c7a4dd34-020d-414e-b971-3bbc5f6114e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__634f5c03_b471_4eae_9c0a_1b1eeb72b01d
ELHE-833372-2017 | HE-544715-2017 | 6/8/2017 4:53:08 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Z1.png,Z2.png 3C/#1 AWG ACWU has been installed in a trench without observing correct installation procedures. This conductor is approximately 6" below grade. This is a shock hazard to anyone working in the area. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Z1.png | file://x:/photopub/docs/0000000613/39e8cba7-edcf-48d5-a3bb-1d0f1442ad6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2bbaeca_d1fe_4255_8721_2ecee8609910
BPVOP-839508-2017 | 2277519 | 7/26/2017 12:01:28 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD1.png,PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not legible and the NDT inspection not done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD2.png | file://x:/photopub/docs/0000000638/af09e850-12f2-426f-9b76-45b79dc2d67f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09caa6dc_1a8d_497d_8a9a_befac842cbc9
BPVOP-839500-2017 | 4072295 | 7/26/2017 11:30:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_1.png,T_and_P_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2003 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_1.png | file://x:/photopub/docs/0000000638/30632b12-2aa6-4f29-8927-62a389b259e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a6d1f4e_6a50_4bc8_bc89_db352512654f
BPVOP-839503-2017 | 2278706 | 7/26/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD_and_Air_Receiver1.png,PRD_and_Air_Receiver2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and the NDT testing was not performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety order not being followed. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD_and_Air_Receiver2.png | file://x:/photopub/docs/0000000638/ce7fd411-00c4-43d5-a0d0-af729a5baa70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82ce4d80_81d5_4f27_93d4_d8300fc14858
BPVOP-839508-2017 | 2277519 | 7/26/2017 12:01:28 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD1.png,PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not legible and the NDT inspection not done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD1.png | file://x:/photopub/docs/0000000638/15b3c001-4136-49ad-94f7-526f09d5814c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09caa6dc_1a8d_497d_8a9a_befac842cbc9
BPVOP-839503-2017 | 2278706 | 7/26/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #PRD_and_Air_Receiver1.png,PRD_and_Air_Receiver2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and the NDT testing was not performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety order not being followed. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD_and_Air_Receiver1.png | file://x:/photopub/docs/0000000638/696c3695-4d7f-4dd2-b7f2-6f69ee610e5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82ce4d80_81d5_4f27_93d4_d8300fc14858
BPVOP-839500-2017 | 4072295 | 7/26/2017 11:30:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #T_and_P_1.png,T_and_P_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in 2003 and was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_2.png | file://x:/photopub/docs/0000000638/335826ea-07a8-4d3b-b921-0ca2448cefee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a6d1f4e_6a50_4bc8_bc89_db352512654f
ELIN-821245-2017 | EL-536564-2017 | 6/7/2017 10:57:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Image_1-31.png,Image_1-32.png,Image_1-33.png - live electrical panels with no covers. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Image_1-32.png | file://x:/photopub/docs/0000000612/33dd9e38-1bc4-4daf-bc48-d0a0531d2ead.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe3a7a70_3c63_4c24_a1c6_de123160d5fa
ELIN-856928-2017 | EL-556817-2017 | 7/14/2017 10:47:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Exposed_energized_panel1.png,Exposed_energized_panel2.png A feeder conductor has been spliced into the main panel through the cover with the cover off. No mechanical connection has been made to the feeder for the subpanel. The main panel is energized with exposed conductors and bus resulting in the potential for fire or electric shock. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized_panel2.png | file://x:/photopub/docs/0000000630/678f4764-7c93-42ac-89e3-921a989e44e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__826fc0ff_e32f_4825_9bc1_d2a602a247c8
GAIN-862521-2017 | GA-512479-2017 | 7/24/2017 11:53:15 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | #Vent_limiter_RV48_maxitrol.png | 2 | Not installed according to certified installation instructions | Vent_limiter_RV48_maxitrol.png | file://x:/photopub/docs/0000000635/4e6ce46b-07f8-40f5-ba94-9606f3fb6fe6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75165795_eed0_4aa5_90ab_0aae31f300b2
ELIN-864797-2017 | EL-526808-2017 | 7/25/2017 2:57:04 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_inside_dwelling1.png,ACWU_inside_dwelling2.png,ACWU_inside_dwelling3.png,ACWU_inside_dwelling4.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_inside_dwelling1.png | file://x:/photopub/docs/0000000636/881f466c-1833-4afa-b32a-981251029d41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bc1d2fb_8159_4ec6_8661_156ca5119b77
ELIN-864796-2017 | EL-526808-2017 | 7/25/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_greater_than_1_5_m1.png,ACWU_greater_than_1_5_m2.png,ACWU_greater_than_1_5_m3.png,ACWU_greater_than_1_5_m4.png,ACWU_greater_than_1_5_m5.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_greater_than_1_5_m2.png | file://x:/photopub/docs/0000000636/af9ac13a-51fc-4cf6-aad0-18e8c1cedb07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624711a3_cd0f_49fe_a3c2_a09b50d4f7a0
ELIN-864796-2017 | EL-526808-2017 | 7/25/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_greater_than_1_5_m1.png,ACWU_greater_than_1_5_m2.png,ACWU_greater_than_1_5_m3.png,ACWU_greater_than_1_5_m4.png,ACWU_greater_than_1_5_m5.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_greater_than_1_5_m1.png | file://x:/photopub/docs/0000000636/f97ee26a-b10e-40a7-a6cc-922c6a8df69d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624711a3_cd0f_49fe_a3c2_a09b50d4f7a0
ELIN-864796-2017 | EL-526808-2017 | 7/25/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_greater_than_1_5_m1.png,ACWU_greater_than_1_5_m2.png,ACWU_greater_than_1_5_m3.png,ACWU_greater_than_1_5_m4.png,ACWU_greater_than_1_5_m5.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_greater_than_1_5_m3.png | file://x:/photopub/docs/0000000636/b5db19a7-1bae-4fb8-857a-45bb430d2112.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624711a3_cd0f_49fe_a3c2_a09b50d4f7a0
ELIN-864797-2017 | EL-526808-2017 | 7/25/2017 2:57:04 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_inside_dwelling1.png,ACWU_inside_dwelling2.png,ACWU_inside_dwelling3.png,ACWU_inside_dwelling4.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_inside_dwelling4.png | file://x:/photopub/docs/0000000636/dab2e1f5-5cef-4ab5-878a-52e03b5f63f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bc1d2fb_8159_4ec6_8661_156ca5119b77
ELIN-841676-2017 | EL-502511-2017 | 6/21/2017 3:39:38 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | #A.png Service cable not adequately protected. This is a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000619/59545240-3406-4c56-871f-43c786e2e830.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__411e1b3a_833a_48e0_a77d_5875bfa5f988
ELIN-867393-2017 | EL-563784-2017 | 7/31/2017 8:59:31 AM | ASSESS: EL: Service Connection | png | #asFound Grounding electrode not buried. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_electrode.png Grounding electrode is not buried. If a fault were to occur, A worker working on the electrical equipment would not be at the same equipotential and likely receive a severe shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_electrode.png | file://x:/photopub/docs/0000000638/34c56c0a-4df9-41d1-b642-eb067fd9cf63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6e7b274_5b71_4ecc_a867_fbe42ae06565
ELIN-837188-2017 | EL-462586-2016 | 6/15/2017 2:11:23 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #plastic_bushing.png ACWU is entered in a rigid coupling and then through a nipple this method does not assure effective bonding as ACWU is not tight or could easily be loosened. The addition of a bond bushing will effectively capture transient electrical currents that may occur. | 3 | Continuity Bonding; method for equipment is not adequate. | plastic_bushing.png | file://x:/photopub/docs/0000000617/d306990e-2951-4227-a490-0857375326a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18f99d6a_ea18_4a23_ae47_a8f4cfe12577
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png | file://x:/photopub/docs/0000000625/a6848c6c-a926-4c7b-810c-8276d6e11b62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png | file://x:/photopub/docs/0000000625/2afe5384-fad0-4786-ba42-49b86c0793f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
ELIN-837624-2017 | EL-458887-2016 | 7/4/2017 1:38:18 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuit1.png,Incorrectly_terminated_three_wire_circuit2.png,Incorrectly_terminated_three_wire_circuit3.png,Incorrectly_terminated_three_wire_circuit4.png,Incorrectly_terminated_three_wire_circuit5.png,Incorrectly_terminated_three_wire_circuit6.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had a 20A 120/240V three wire branch circuit that had both conductors of the three wire circuit terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulatio | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuit5.png | file://x:/photopub/docs/0000000625/85f91e05-a80d-4c89-a380-5a556b9143ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3305821d_f5e4_4481_83a5_9c6af3412bc0
ELIN-837624-2017 | EL-458887-2016 | 7/4/2017 1:38:18 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuit1.png,Incorrectly_terminated_three_wire_circuit2.png,Incorrectly_terminated_three_wire_circuit3.png,Incorrectly_terminated_three_wire_circuit4.png,Incorrectly_terminated_three_wire_circuit5.png,Incorrectly_terminated_three_wire_circuit6.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had a 20A 120/240V three wire branch circuit that had both conductors of the three wire circuit terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulatio | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuit6.png | file://x:/photopub/docs/0000000625/f0981366-8a0f-44d9-928d-08574e5127ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3305821d_f5e4_4481_83a5_9c6af3412bc0
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png | file://x:/photopub/docs/0000000625/cb1869b6-3375-41f3-b7de-360b9958971b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png | file://x:/photopub/docs/0000000625/9ae54bab-8408-4967-9a61-84656f68a5e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
ELIN-837624-2017 | EL-458887-2016 | 7/4/2017 1:38:18 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuit1.png,Incorrectly_terminated_three_wire_circuit2.png,Incorrectly_terminated_three_wire_circuit3.png,Incorrectly_terminated_three_wire_circuit4.png,Incorrectly_terminated_three_wire_circuit5.png,Incorrectly_terminated_three_wire_circuit6.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had a 20A 120/240V three wire branch circuit that had both conductors of the three wire circuit terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulatio | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuit1.png | file://x:/photopub/docs/0000000625/ccf14fe1-c1c4-4502-80bc-3f1af54a0b80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3305821d_f5e4_4481_83a5_9c6af3412bc0
ELIN-864796-2017 | EL-526808-2017 | 7/25/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_greater_than_1_5_m1.png,ACWU_greater_than_1_5_m2.png,ACWU_greater_than_1_5_m3.png,ACWU_greater_than_1_5_m4.png,ACWU_greater_than_1_5_m5.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_greater_than_1_5_m5.png | file://x:/photopub/docs/0000000636/b0dcc88f-e01d-45b1-bd23-0bdd33d14cdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624711a3_cd0f_49fe_a3c2_a09b50d4f7a0
ELIN-864797-2017 | EL-526808-2017 | 7/25/2017 2:57:04 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_inside_dwelling1.png,ACWU_inside_dwelling2.png,ACWU_inside_dwelling3.png,ACWU_inside_dwelling4.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_inside_dwelling3.png | file://x:/photopub/docs/0000000636/ed80866f-5d78-44bf-94a7-1bd689817ade.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bc1d2fb_8159_4ec6_8661_156ca5119b77
ELIN-864797-2017 | EL-526808-2017 | 7/25/2017 2:57:04 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_inside_dwelling1.png,ACWU_inside_dwelling2.png,ACWU_inside_dwelling3.png,ACWU_inside_dwelling4.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_inside_dwelling2.png | file://x:/photopub/docs/0000000636/97be2643-206e-4c1e-9b66-6213550715cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bc1d2fb_8159_4ec6_8661_156ca5119b77
ELIN-864796-2017 | EL-526808-2017 | 7/25/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_greater_than_1_5_m1.png,ACWU_greater_than_1_5_m2.png,ACWU_greater_than_1_5_m3.png,ACWU_greater_than_1_5_m4.png,ACWU_greater_than_1_5_m5.png Consumer service cables are to be run on the outside of the building except when entering the building to connect to the service panel or service switch. The maximum length of service cable allowed inside the building is 1.5 meters unless the cable is encased in minimum 50mm of concrete or located under a concrete slab that is a minimum 50mm thick. This requirement is to reduce the risk of fire because the consumer service cable lacks effective over current protection when connected to the supply authorities conductors. In this consumer service cable installation for a new service panel at a dwelling with a suite, the cable was installed a total length of 4 m inside the building without concrete encasement. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the service cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_greater_than_1_5_m4.png | file://x:/photopub/docs/0000000636/051efd69-6f09-4464-950d-b65bbf09c8a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624711a3_cd0f_49fe_a3c2_a09b50d4f7a0
BPVOP-825173-2017 | 2821342 | 5/29/2017 10:40:19 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2004_SRD.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s) for a hot water boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2004_SRD.png | file://x:/photopub/docs/0000000613/322e02e4-68ba-47b3-b80d-156bceb4cdc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a26207bd_64ed_40db_b8b4_f751b087a6c2
BPVOP-825210-2017 | 2821336 | 6/8/2017 1:16:01 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_releif_valve_2003.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s) for a hot water boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_releif_valve_2003.png | file://x:/photopub/docs/0000000613/285b84af-eb8d-4a31-9672-d103e790d56e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6d7f000_e343_4518_95a2_2a9e13c3db8f
BPVIN-851146-2017 | BPV-550774-2017 | 7/6/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Local_Disconnect_Switch_Missing_Lockout_Feture.png The local disconnect switch requires a means of being locked in the "OPEN" position. Without the lockout feature the switch maybe inadvertently turned on during a time when a person is servicing the unit or it is shutdown due to seasonal operation. This may lead to personnel and property damage if the unit is switched on at this time. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Local_Disconnect_Switch_Missing_Lockout_Feture.png | file://x:/photopub/docs/0000000626/f7b49608-04da-4f35-b3c1-2127adbfd2eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfdfb842_07d7_46d3_9350_816ef32b257d
BPVOP-805603-2017 | 2984926 | 7/13/2017 10:23:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #Safety_Relief_Valve_1.png,Safety_Relief_Valve_2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was under the relief capacity required by the boiler. This can contribute to the failure of the boiler safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_1.png | file://x:/photopub/docs/0000000631/d80a2542-962d-495c-940d-e9ff530f8963.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00896849_d6b7_4efc_af24_65ec019fc7e2
ELIN-837624-2017 | EL-458887-2016 | 7/4/2017 1:38:18 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuit1.png,Incorrectly_terminated_three_wire_circuit2.png,Incorrectly_terminated_three_wire_circuit3.png,Incorrectly_terminated_three_wire_circuit4.png,Incorrectly_terminated_three_wire_circuit5.png,Incorrectly_terminated_three_wire_circuit6.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had a 20A 120/240V three wire branch circuit that had both conductors of the three wire circuit terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulatio | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuit4.png | file://x:/photopub/docs/0000000625/4320fe14-eb1b-44d6-8996-0107c2513664.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3305821d_f5e4_4481_83a5_9c6af3412bc0
ELIN-837624-2017 | EL-458887-2016 | 7/4/2017 1:38:18 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuit1.png,Incorrectly_terminated_three_wire_circuit2.png,Incorrectly_terminated_three_wire_circuit3.png,Incorrectly_terminated_three_wire_circuit4.png,Incorrectly_terminated_three_wire_circuit5.png,Incorrectly_terminated_three_wire_circuit6.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had a 20A 120/240V three wire branch circuit that had both conductors of the three wire circuit terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulatio | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuit3.png | file://x:/photopub/docs/0000000625/46d2d30d-0b20-401d-81c7-48132d008129.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3305821d_f5e4_4481_83a5_9c6af3412bc0
ELIN-837624-2017 | EL-458887-2016 | 7/4/2017 1:38:18 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Incorrectly_terminated_three_wire_circuit1.png,Incorrectly_terminated_three_wire_circuit2.png,Incorrectly_terminated_three_wire_circuit3.png,Incorrectly_terminated_three_wire_circuit4.png,Incorrectly_terminated_three_wire_circuit5.png,Incorrectly_terminated_three_wire_circuit6.png Three wire circuits are required to be terminated properly in order to ensure that the neutral conductor is not over loaded. This is required so that the conductor insulation and terminations are not over heated causing damage to electrical equipment or a potential fire. This installation for a new house had a 20A 120/240V three wire branch circuit that had both conductors of the three wire circuit terminated to circuit breakers that were connected to the same bus in the electrical panel. Terminating three wire circuits in this way will cause the neutral conductor to carry the sum of both circuit currents rather that the difference or imbalanced current of the circuits. This can over heat and damage the neutral conductors insulatio | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Incorrectly_terminated_three_wire_circuit2.png | file://x:/photopub/docs/0000000625/e03ccd5d-c587-4e64-8b18-e6b575cad09b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3305821d_f5e4_4481_83a5_9c6af3412bc0
ELIN-825176-2017 | EL-233077-2015 | 7/4/2017 4:01:07 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses2.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses3.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses4.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses5.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses6.png,3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses7.png Feeder conductors for sub-distribution equipment that feeds power, lighting, and motor loads are required to be protected by over current devices that will open to prevent the conductors from becoming overloaded and potentially damaged by current that exceeds the rating of the cables. Th | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 3c_1_0_tapped_from_the_existing_600A_service_switch_and_terminated_in_a_200A_switch_with_200A_fuses1.png | file://x:/photopub/docs/0000000625/a9615da6-5ebe-41f9-b6ee-3709db6dacf5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__332fc9cf_d5a8_439b_9a51_f08a34836c24
GAIN-827379-2017 | GA-420517-2016 | 7/20/2017 10:45:51 AM | ASSESS: GA: Final | png | #asFound B vent serving make-up air | GA105 | Unapproved venting material | 3 | 3 | #Venting_material.png The as-found condition is that the venting material serving a make-up air unit does not comply with the manufacturer's venting requirements for positive pressure vent systems in indoor applications. The potential hazard is that the products of combustion will leak into the room, resulting in the release of harmful emissions such as carbon monoxide that could pose a risk to human health. | 3 | Unapproved venting material | Venting_material.png | file://x:/photopub/docs/0000000633/78239951-9dfa-4c88-8191-121a2987e837.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__244182f4_f557_4196_8501_655776cf31e9
GAIN-833093-2017 | GA-544529-2017 | 7/18/2017 3:42:04 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent.png The as-found condition is that the vent serving a patio heater is installed too close to combustible material. The potential hazard is that the high heat of the vent will cause the combustible material to catch fire. | 3 | Non compliant Type C Vent clearance | Vent.png | file://x:/photopub/docs/0000000633/e4e2167a-a186-49e1-a687-3e4511d36fe6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e889686c_2385_431d_894c_c7a5c52dfe40
ELIN-866140-2017 | EL-562340-2017 | 7/31/2017 3:01:46 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Rigid_bare_lamp_fixture_has_jb_covered_and_is_below_2_1m.png A bare lamp fixture is located below 2.1 meters and is not mechanically protected. The junction box is also not accessible. This condition could expose occupants to a shock or fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Rigid_bare_lamp_fixture_has_jb_covered_and_is_below_2_1m.png | file://x:/photopub/docs/0000000638/9774066c-d0ee-43f7-a358-bceef7505e2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db538664_3c03_4b4f_8daf_5e0b67b6fdf7
GAIN-859066-2017 | GA-504829-2017 | 7/31/2017 12:32:29 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #No_evidence_of_combustion_air_near_tube_heater.png Gas fired tube heater installed in a shop has no dedicated combustion air supplied for combustion. The flame may look for other sources of air outside of heat exchanger (Tube) possibly going back to controls of heater and causing a fire in control box. | 4 | Combustion air supply missing | No_evidence_of_combustion_air_near_tube_heater.png | file://x:/photopub/docs/0000000638/418533dc-c2fb-495d-b36b-97fe45908220.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897b997c_6502_4558_92d0_9e478be1c75b
BPVIN-877945-2017 | BPV-565602-2017 | 8/12/2017 8:21:41 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #DHW_Heater1.png,DHW_Heater2.png Upon the assessment of a Domestic Hot Water Heater with MAWP of 160 psig, was found that the Temperature and Pressure Valve was under-capacity as per CSA B51. This can contribute to the failure of the heater safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | DHW_Heater2.png | file://x:/photopub/docs/0000000644/127158e1-324e-43f7-a4b2-f4067a7505d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c99570_c4a9_4523_9c0e_a66496cc6560
BPVIN-877945-2017 | BPV-565602-2017 | 8/12/2017 8:21:41 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #DHW_Heater1.png,DHW_Heater2.png Upon the assessment of a Domestic Hot Water Heater with MAWP of 160 psig, was found that the Temperature and Pressure Valve was under-capacity as per CSA B51. This can contribute to the failure of the heater safeties. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | DHW_Heater1.png | file://x:/photopub/docs/0000000644/1c2511d8-da3e-4d2d-bbe3-f6fde3ab0c32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c99570_c4a9_4523_9c0e_a66496cc6560
GAIN-894858-2017 | GA-577500-2017 | 9/6/2017 12:59:52 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Regulator_vent_earls.png Potential for regulator to relief due to moisture entering regulator vent. Damage to regulator and release of gas. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Regulator_vent_earls.png | file://x:/photopub/docs/0000000658/9602b3d4-f9ef-4034-ba6f-eea542022baa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6632c42_a0df_4261_99fa_cad80b179625
EDIN-901508-2017 | ED-451880-2016 | 9/6/2017 4:41:23 PM | ASSESS: ED IN: Acceptance | png | #asFound Mainline disconnect | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Disconnect.png Incorrect main disconnect installed | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Disconnect.png | file://x:/photopub/docs/0000000658/ac61b001-cf2f-466b-a248-cf8ccaa617b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__469b85d1_db6a_4f34_836a_af44d6be34d7
EDMA-901507-2017 | ED-512526-2017 | 9/6/2017 4:21:03 PM | ASSESS: ED MA: Partial Acceptance | png | #asFound Air conditioning unit placed above elevator equipment | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | #HVAC.png Air conditioning unit placed above elevator equipment that may cause unexpected operation of the elevator thus contravening the B44-07 code | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | HVAC.png | file://x:/photopub/docs/0000000658/7286f606-f6b2-400d-8d39-ad415ddec005.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fb81a64_993c_4da8_91f4_c3c96d8c8bde
ELIN-855333-2017 | EL-275546-2015 | 7/28/2017 10:52:17 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Panelboards1.png,Panelboards2.png The residential sfd installation includes a main 200 amp service panel located in a shed and is missing a 2" knock out filler at the main breaker end of the panel plus the sub-distribution panel (with door) located in the residence is missing multiple breaker filler spaces. Both panels are accessible to persons and energized parts are accessible, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panelboards1.png | file://x:/photopub/docs/0000000646/1844de04-4544-4c7e-9d11-2861524dd6cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dec870ae_d665_45ca_bad6_78fdb654888c
GAUP-857233-2017 | UW-558411-2017 | 7/31/2017 2:30:31 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #StockPot.png Uncertified and unapproved kitchen equipment in use. Potential for failure of appliances causing injury or property damage. | 3 | Uncertified appliance connected to gas supply but not in service | StockPot.png | file://x:/photopub/docs/0000000638/42b6810f-225d-4948-8d9c-dfe241e86e2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1b90f80_f719_4dbb_8c5c_afc195effa91
EDIN-886569-2017 | ED-563885-2017 | 8/22/2017 5:57:40 PM | ASSESS: ED IN: Construction Use | png | #asFound Air conditioning unit located above elevator related equipment may cause erratic operation if the condensate from the unit leaked | ED024 | Accessible location Preventative measure show sign of excessive wear and/or damage Contact with Object/human possible Contact could result in some life &/or property damage | 4 | 4 | #Air_con.png | 4 | Accessible location Preventative measure show sign of excessive wear and/or damage Contact with Object/human possible Contact could result in some life &/or property damage | Air_con.png | file://x:/photopub/docs/0000000650/e8eba26a-1d4f-444d-9434-b8909e4ddb6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8cc2312_38c4_460e_9bd0_a33506cfa3bc
EDRI-878093-2017 | ED-544855-2017 | 8/11/2017 2:34:35 PM | ASSESS: ED RI: Final | png | #asFound | ED021 | Electrical wires showing, some sign of external damage Damp/Wet/Outdoor Location | 3 | 3 | #Disconnect_after_protection_installed.png The hoists main 480 Volt power is run through a disconnect that is not rated to withstand weather. This installation had the disconnects at the bottom landing where it was not protected from rain. Site installed the small roof and side shown in picture to protect the disconnect. | 3 | Electrical wires showing, some sign of external damage Damp/Wet/Outdoor Location | Disconnect_after_protection_installed.png | file://x:/photopub/docs/0000000645/85d9427c-bb7b-48c0-b580-921555abda0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__012d9f79_354b_4f4f_8ff0_fbb822701029
GAUP-867233-2017 | UW-549804-2017 | 7/31/2017 11:12:16 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Gas_hose1.png,Gas_hose2.png,Firepit.png Rubber gas hose used under ground in a conducted as a permanent piping system. The material used is not intended as a permanent piping system. As the hose is run in a conducted underground its condition could deteriorate and release gas. This could lead to a fire or explosion. | 3 | Non-compliant material/fittings installed | Gas_hose1.png | file://x:/photopub/docs/0000000638/abc82960-400f-4560-98a2-23fe58dd0dd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74844a3f_626f_4654_bab7_9b270b93ccf5
GAUP-867233-2017 | UW-549804-2017 | 7/31/2017 11:12:16 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Gas_hose1.png,Gas_hose2.png,Firepit.png Rubber gas hose used under ground in a conducted as a permanent piping system. The material used is not intended as a permanent piping system. As the hose is run in a conducted underground its condition could deteriorate and release gas. This could lead to a fire or explosion. | 3 | Non-compliant material/fittings installed | Gas_hose2.png | file://x:/photopub/docs/0000000638/ab5302c1-d04f-44c8-9d10-c6b9f24be206.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74844a3f_626f_4654_bab7_9b270b93ccf5
GAUP-867233-2017 | UW-549804-2017 | 7/31/2017 11:12:16 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Gas_hose1.png,Gas_hose2.png,Firepit.png Rubber gas hose used under ground in a conducted as a permanent piping system. The material used is not intended as a permanent piping system. As the hose is run in a conducted underground its condition could deteriorate and release gas. This could lead to a fire or explosion. | 3 | Non-compliant material/fittings installed | Firepit.png | file://x:/photopub/docs/0000000638/a472a640-881a-4740-89bf-cdd424fc2f27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74844a3f_626f_4654_bab7_9b270b93ccf5
ELIN-884234-2017 | EL-502144-2017 | 8/22/2017 2:27:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png,G5.png Welder hard wired into panel, no connectors used. This is a shock and fire hazard as the cable could be damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | G2.png | file://x:/photopub/docs/0000000650/ec1b9ca4-bb60-43c9-a8c9-6d2426410220.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54a4d301_96de_47b7_8e27_359f30c86cc4
ELIN-884234-2017 | EL-502144-2017 | 8/22/2017 2:27:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png,G5.png Welder hard wired into panel, no connectors used. This is a shock and fire hazard as the cable could be damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | G3.png | file://x:/photopub/docs/0000000650/8e9ca294-8473-4279-a563-320a7c445920.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54a4d301_96de_47b7_8e27_359f30c86cc4
ELIN-884234-2017 | EL-502144-2017 | 8/22/2017 2:27:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png,G5.png Welder hard wired into panel, no connectors used. This is a shock and fire hazard as the cable could be damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | G1.png | file://x:/photopub/docs/0000000650/b1e257b8-43f1-4962-80c1-3754fa7649ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54a4d301_96de_47b7_8e27_359f30c86cc4
ELIN-884234-2017 | EL-502144-2017 | 8/22/2017 2:27:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png,G5.png Welder hard wired into panel, no connectors used. This is a shock and fire hazard as the cable could be damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | G5.png | file://x:/photopub/docs/0000000650/23421bda-6f9d-404a-83c5-9c21197d53c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54a4d301_96de_47b7_8e27_359f30c86cc4
ELIN-884234-2017 | EL-502144-2017 | 8/22/2017 2:27:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png,G5.png Welder hard wired into panel, no connectors used. This is a shock and fire hazard as the cable could be damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | G4.png | file://x:/photopub/docs/0000000650/8fed7f17-5b72-4a1d-97fb-a32c885f09d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54a4d301_96de_47b7_8e27_359f30c86cc4
ELIN-885414-2017 | EL-573778-2017 | 8/22/2017 12:09:00 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | #A.png Roof top receptacle not provided. This is a hazard as technician will have to run extension cords. | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | A.png | file://x:/photopub/docs/0000000650/2dfa1cfb-6c69-4e8a-bb83-b109c22f2f96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d9189e7_6c89_4b4d_93f1_46e414971178
ELIN-855333-2017 | EL-275546-2015 | 7/28/2017 10:52:17 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Panelboards1.png,Panelboards2.png The residential sfd installation includes a main 200 amp service panel located in a shed and is missing a 2" knock out filler at the main breaker end of the panel plus the sub-distribution panel (with door) located in the residence is missing multiple breaker filler spaces. Both panels are accessible to persons and energized parts are accessible, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panelboards2.png | file://x:/photopub/docs/0000000646/a5f2cd5a-47ea-4b23-a654-a4dde8e8de69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dec870ae_d665_45ca_bad6_78fdb654888c
BPVOP-885121-2017 | 3155865 | 8/21/2017 11:35:50 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #ASME_plate_.png During the inspection of a Domestic Hot Water Boiler with MAWP of 160 psig was found that there is no Emergency Shut Down Switch located at the boiler room entrance. Without this emergency shut down switch located at the boiler room entrance, it would be difficult to shut down this equipment in an emergency situation. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | ASME_plate_.png | file://x:/photopub/docs/0000000650/2316d710-73b4-4d36-a9b0-b5690393f76a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1d53bcd_dc41_4142_8349_d5cb2a8f74cd
BPVOP-885118-2017 | 4024364 | 8/21/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Venting_1.png,Venting_2.png During the inspection on a hot water boiler with MAWP of 160 psig it was found that the venting from the boilers is corroded and has holes that can permit the flue gases in the boiler room. This can be dangerous to human life at the flue gases can vent in the boiler room. | 4 | 5.1.0 In service proc/process - Casing leakage | Venting_1.png | file://x:/photopub/docs/0000000650/13251a5e-ede4-4f15-9466-39ec7ba3b233.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c322a54c_3622_4053_82f6_43175d4a8867
BPVOP-885118-2017 | 4024364 | 8/21/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Venting_1.png,Venting_2.png During the inspection on a hot water boiler with MAWP of 160 psig it was found that the venting from the boilers is corroded and has holes that can permit the flue gases in the boiler room. This can be dangerous to human life at the flue gases can vent in the boiler room. | 4 | 5.1.0 In service proc/process - Casing leakage | Venting_2.png | file://x:/photopub/docs/0000000650/d3e16853-357b-4e64-abe4-8a69d644fb80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c322a54c_3622_4053_82f6_43175d4a8867
ELIN-872644-2017 | UW-136844-2014 | 8/3/2017 2:52:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Overhead service conductors damaged and under strain due to improper overhead service attachment device installation and conductors on supply side are in contact with building. Meterbase is fully covered and inaccessible to inside of meterbase and consumer's service raceway is covered in wall. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Overhead_service_conductors_damaged_and_under_strain1.png,Overhead_service_conductors_damaged_and_under_strain2.png Found 120/240 volt 200amp overhead service head and service conductors attachment device has been altered and service conductors are not properly installed, are under strain and are in contact with building structure. The service conductors are damaged and are not terminated properly due to strain on termination of service conductors at roof line and service head. There is no over-current protection to protect service conductors in event of fault condition on service conductors. When electrical equipment for overhead consumer's service conductors are damaged, strained and in contact with building structure while there is no over-current protection for protecting service conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Overhead_service_conductors_damaged_and_under_strain2.png | file://x:/photopub/docs/0000000641/03d4fb29-b1d6-4448-8f82-f430a5576154.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ece8bfd7_f4ee_49f0_b452_695ca1d9b627
ELIN-872644-2017 | UW-136844-2014 | 8/3/2017 2:52:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Overhead service conductors damaged and under strain due to improper overhead service attachment device installation and conductors on supply side are in contact with building | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Overhead_service_conductors_damaged_and_under_strain1.png,Overhead_service_conductors_damaged_and_under_strain2.png Found 120/240 volt 200amp overhead service head and service conductors attachment device has been altered and service conductors are not properly installed, are under strain and are in contact with building structure. The service conductors are damaged and are not terminated properly due to strain on termination of service conductors at roof line and service head. There is no over-current protection to protect service conductors in event of fault condition on service conductors. When electrical equipment for overhead consumer's service conductors are damaged, strained and in contact with building structure while there is no over-current protection for protecting service conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Overhead_service_conductors_damaged_and_under_strain1.png | file://x:/photopub/docs/0000000641/db9dafd8-b2bb-4b97-804d-f4603ddb2d05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ece8bfd7_f4ee_49f0_b452_695ca1d9b627
GAHE-877256-2017 | HE-569970-2017 | 8/10/2017 3:59:25 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA058 | Cathodic protection missing causing a hazard | 3 | 3 | #Pacific_forest_center1.png,Pacific_forest_center2.png Corroded underground propane line entering building below grade. Possible leak from piping if the integrity of the piping is breached.Soil conditions may scrub the odourant from the fuel making detection difficult. Possible fire and explosive risk if source of ignition was present | 3 | Cathodic protection missing causing a hazard | Pacific_forest_center1.png | file://x:/photopub/docs/0000000644/a5baf1e1-ee92-4f6f-8042-f083e4b6aa00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c31ba9e0_e0a4_457c_9e1e_0e267bf1344f
GAHE-877256-2017 | HE-569970-2017 | 8/10/2017 3:59:25 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA058 | Cathodic protection missing causing a hazard | 3 | 3 | #Pacific_forest_center1.png,Pacific_forest_center2.png Corroded underground propane line entering building below grade. Possible leak from piping if the integrity of the piping is breached.Soil conditions may scrub the odourant from the fuel making detection difficult. Possible fire and explosive risk if source of ignition was present | 3 | Cathodic protection missing causing a hazard | Pacific_forest_center2.png | file://x:/photopub/docs/0000000644/c82adf76-d2a5-4334-8b42-2fd599ae7f0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c31ba9e0_e0a4_457c_9e1e_0e267bf1344f
ELIN-881974-2017 | EL-570963-2017 | 8/23/2017 2:59:22 PM | ASSESS: EL: Service Connection | png | #asFound Enclosure not suitable for wet conditions. | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Temporary_Contruction_Service_Enclosure.png Enclosure not suitable for wet conditions. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_Contruction_Service_Enclosure.png | file://x:/photopub/docs/0000000650/cba9a90e-5cbb-44a9-bd62-19ec2b891ff6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0afc7582_6878_4c6d_a448_16dee2d44383
GAIN-895022-2017 | GA-401010-2016 | 9/6/2017 12:37:35 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent.png The as-found condition is that the vent material serving a make-up air is not rated for condensing vent applications. The potential hazard is that the corrosive nature of the flue gas condensate will corrode the vent, enabling flue gas and harmful products of combustion to escape into an occupied space. | 3 | Unapproved venting material | Vent.png | file://x:/photopub/docs/0000000658/317249fb-2bcc-471c-968c-934eb7529cc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__814bc703_1095_4c0e_9711_075269d12979
ELIN-877373-2017 | EL-554722-2017 | 8/14/2017 9:35:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Water_in_panel_.png The main electrical panel is not adequately protected from rain damage. This will lead to damage to circuit breakers at which time they may not work as designed. This is a possible shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Water_in_panel_.png | file://x:/photopub/docs/0000000645/805ec316-c746-4f80-b645-ea0403387777.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae1dce81_0514_4d57_92e7_1df30a394e52
GAIN-852172-2017 | GA-444785-2016 | 7/24/2017 1:38:56 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Joints.png The as-found condition is that the joints on threaded black iron pipe have not been sealed with an approved product. the potential hazard is that the joints will leak and allow gas to escape into an occupied space causing risk of fire and property damage. | 3 | Non-compliant material/fittings installed | Joints.png | file://x:/photopub/docs/0000000639/b986390e-0784-4caf-b0f1-391ba6da5657.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edeeda19_27b1_4b8c_a34f_91cc879e2724
ELIN-876951-2017 | EL-537026-2017 | 8/11/2017 10:28:16 AM | ASSESS: EL: Final | png | #asFound Transformer XO point not grounded | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Transformer_1.png,Transformer_2.png Transformer XO point is not grounded, fault current will not be able to facilitate an overcurent device because there is no return path. Should a fault occur electrical equipment will not have equal potentiality | 4 | Installation Grounding; conductor is not continuous. | Transformer_1.png | file://x:/photopub/docs/0000000644/9d1fd766-3b9b-46f2-abed-9c27e5085fea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3db4770_c5c8_49f3_8aee_03e47ff53a25
ELIN-876951-2017 | EL-537026-2017 | 8/11/2017 10:28:16 AM | ASSESS: EL: Final | png | #asFound 600-120/240 V-15 kVA transformer | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Transformer_1.png,Transformer_2.png Transformer XO point is not grounded, fault current will not be able to facilitate an overcurent device because there is no return path. Should a fault occur electrical equipment will not have equal potentiality | 4 | Installation Grounding; conductor is not continuous. | Transformer_2.png | file://x:/photopub/docs/0000000644/916705c1-979c-4df1-9a54-4c9a805ac197.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3db4770_c5c8_49f3_8aee_03e47ff53a25
ELHE-895361-2017 | HE-577812-2017 | 8/30/2017 7:53:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL210 | All Classes, All Zones Area is classified: wiring method is not suitable for area. | 4 | 4 | #Site.png The installation of this fuel dispensing facility has several non compliances, from bonding and use of unapproved equipment in a hazardous location. If not corrected site could result in catastrophic incident. | 4 | All Classes, All Zones Area is classified: wiring method is not suitable for area. | Site.png | file://x:/photopub/docs/0000000655/41fdba57-c181-4459-8e69-cf5d47ccaa13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3c94417_f216_43b1_be0d_18181d06acbb
GAIN-882877-2017 | GA-555513-2017 | 8/31/2017 1:28:04 PM | ASSESS: GA: Final | png | #asFound | GA111 | Power vent add-on not interlocked correctly with appliance | 5 | 5 | #Interlock_requirement.png The as found condition was power exhaust vent system located on a commercial oven vent did not have the fan operation interlocked with the appliance, allowing the oven to operate without the exhaust fan on. The as found hazard is if the appliance was functioning and the exhaust fan was not operating, products of combustion, including carbon monoxide, would vent into the building envelope creating a potentially fatal situation for inhabitants. | 5 | Power vent add-on not interlocked correctly with appliance | Interlock_requirement.png | file://x:/photopub/docs/0000000655/6ec317c6-862b-4e33-96b9-f86f5617f522.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca961764_4046_4a2e_bbd0_2d2c1e29405e
ELHE-873389-2017 | HE-568066-2017 | 8/4/2017 12:52:25 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_utility_conductors_.png The conduit which is intended to protect the BC hydro conductors from being exposed is separated and utility wires are accessible to general public. This is an extreme shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_utility_conductors_.png | file://x:/photopub/docs/0000000641/40136407-81c5-4022-b55b-af7f762d46b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8602973_7eda_4e5e_b896_bc18f7e6f9eb
ELIN-881246-2017 | EL-558774-2017 | 8/16/2017 8:22:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 4 | #Energized_counter_plug.png During a renovation numerous 15A 120 volt switches and receptacles were removed from outlet boxes and left with exposed energized terminals. This could lead to serious shock injury or fire. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_counter_plug.png | file://x:/photopub/docs/0000000647/83b1d09d-8522-45c2-b7fe-9626819e8f67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e32fbd5d_674c_4e68_96b5_199f91f407cd
GAHE-882624-2017 | HE-572259-2017 | 8/17/2017 8:19:19 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #3722_trunk_2.png Minor leak of fuel from inlet piping connection on system regulator. Risk of fire if a source of ignition was present. Leak would be classified as peach fuzz. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3722_trunk_2.png | file://x:/photopub/docs/0000000648/d1fe968a-2cfa-4b51-b318-1fdeff3b19e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4c3e558_4843_42a5_bc0b_fe410b8d0b2f
GAIN-880680-2017 | GA-559242-2017 | 8/17/2017 11:59:05 AM | ASSESS: GA: Final | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | #Wick_2.png 2 pound to inches regulator installed indoors without the required vent limiting orifice installed. Failure of the regulator could result in a release of fuel entering the occupied space. Risk of fire if source of ignition was present. | 3 | Line pressure regulator without required overpressure protection in place | Wick_2.png | file://x:/photopub/docs/0000000648/14c9e062-e629-4b2a-8871-62f73c6b4c85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5319214b_68a9_4599_9acf_6f14b2ce52af
ELIN-884749-2017 | EL-565023-2017 | 8/21/2017 3:31:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Ser.png Service conductors enter of the inside of the dwelling in excess of 1.5 m. In the event of fault the high current and the exposed conductor creates a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Ser.png | file://x:/photopub/docs/0000000649/0de0db67-dcb0-4f59-937e-27910d9fd6fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d668bf10_c341_441a_ad96_91a1d956e07e
BPVOP-870371-2017 | 2267325 | 8/1/2017 11:24:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valves.png Upon assessment of Low Pressure Steam Boiler with Heating surface area of 36 square meters, it was determined that safety valves have exceeded the interval for servicing/replacement. Failure to have safety valves serviced/replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water, and /or steam and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valves.png | file://x:/photopub/docs/0000000639/afcd32f2-3bd5-4309-8cad-2d7256d04d7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48d4e7f4_5e64_4467_b52c_7bb88f29483d
BPVOP-870285-2017 | 2290045 | 8/1/2017 11:09:01 AM | ASSESS: BPV OP: Compliance REF/PV | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 4 | #Ammonia_Gas_Vent_Line.png The ammonia gas discharge line that vents to the atmosphere needs to be extended. When the pressure relief valves discharge to the atmosphere due to over pressure conditions the ammonia gas is vented to the atmosphere. The outlet of the pipe is too low and may spray a person with ammonia gas if they are working next to the pipe. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | Ammonia_Gas_Vent_Line.png | file://x:/photopub/docs/0000000639/8210c9b8-7624-45a0-b239-43ab642fcf63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3c62c3c_5b05_4951_afed_9746fb9781cf
PROP-870971-2017 | 2224040 | 8/9/2017 | ASSESS: PR OP: RAP | png | #asFound Deck in contact with skip car | PR007 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | 4 | 4 | #Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck1.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck2.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck3.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck4.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck5.png At the return station a steel step plate was added to the deck. This raised the original deck height approximately 100mm. The additional height interferes with the pathway of the carrier. In the original build the carrier could enter the station and in the event of not coming to stop would engage with a spring buffer. The spring buffer has an internal limit switch which actuated a stop upon over compression of the spring. Because of the additional height of the deck, in the event that the carrier does not stop prior to engaging the the end buffer the carrier would collide with the edge of the deck prior to the spring buffer switch ac | 4 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck4.png | file://x:/photopub/docs/0000000644/14c9437f-28c0-426a-a3c4-c9b4f98ec862.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__432881AB_B0F4_4D4B_AFE9_0F6F2E346609
PROP-870971-2017 | 2224040 | 8/9/2017 | ASSESS: PR OP: RAP | png | #asFound Skip car in contact with the edge of decking | PR007 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | 4 | 4 | #Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck1.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck2.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck3.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck4.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck5.png At the return station a steel step plate was added to the deck. This raised the original deck height approximately 100mm. The additional height interferes with the pathway of the carrier. In the original build the carrier could enter the station and in the event of not coming to stop would engage with a spring buffer. The spring buffer has an internal limit switch which actuated a stop upon over compression of the spring. Because of the additional height of the deck, in the event that the carrier does not stop prior to engaging the the end buffer the carrier would collide with the edge of the deck prior to the spring buffer switch ac | 4 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck5.png | file://x:/photopub/docs/0000000644/0cc400ce-a88e-4062-88fc-65d6051cd028.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__432881AB_B0F4_4D4B_AFE9_0F6F2E346609
PROP-870971-2017 | 2224040 | 8/9/2017 | ASSESS: PR OP: RAP | png | #asFound View of carriage and buffer. Carriage approximately .15m from engaging buffer. Skip car is in contact with deck in this photo. | PR007 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | 4 | 4 | #Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck1.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck2.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck3.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck4.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck5.png At the return station a steel step plate was added to the deck. This raised the original deck height approximately 100mm. The additional height interferes with the pathway of the carrier. In the original build the carrier could enter the station and in the event of not coming to stop would engage with a spring buffer. The spring buffer has an internal limit switch which actuated a stop upon over compression of the spring. Because of the additional height of the deck, in the event that the carrier does not stop prior to engaging the the end buffer the carrier would collide with the edge of the deck prior to the spring buffer switch ac | 4 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck3.png | file://x:/photopub/docs/0000000644/1bb79bbf-5ce4-4af3-8fb5-7215d26dc4f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__432881AB_B0F4_4D4B_AFE9_0F6F2E346609
PROP-870971-2017 | 2224040 | 8/9/2017 | ASSESS: PR OP: RAP | png | #asFound Decking | PR007 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | 4 | 4 | #Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck1.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck2.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck3.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck4.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck5.png At the return station a steel step plate was added to the deck. This raised the original deck height approximately 100mm. The additional height interferes with the pathway of the carrier. In the original build the carrier could enter the station and in the event of not coming to stop would engage with a spring buffer. The spring buffer has an internal limit switch which actuated a stop upon over compression of the spring. Because of the additional height of the deck, in the event that the carrier does not stop prior to engaging the the end buffer the carrier would collide with the edge of the deck prior to the spring buffer switch ac | 4 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck2.png | file://x:/photopub/docs/0000000644/9a692924-c2a7-4206-8165-8619482cb3a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__432881AB_B0F4_4D4B_AFE9_0F6F2E346609
PROP-870971-2017 | 2224040 | 8/9/2017 | ASSESS: PR OP: RAP | png | #asFound Raised deck | PR007 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | 4 | 4 | #Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck1.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck2.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck3.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck4.png,Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck5.png At the return station a steel step plate was added to the deck. This raised the original deck height approximately 100mm. The additional height interferes with the pathway of the carrier. In the original build the carrier could enter the station and in the event of not coming to stop would engage with a spring buffer. The spring buffer has an internal limit switch which actuated a stop upon over compression of the spring. Because of the additional height of the deck, in the event that the carrier does not stop prior to engaging the the end buffer the carrier would collide with the edge of the deck prior to the spring buffer switch ac | 4 | Misalignment has resulted with significant wear such that required deropement prevention may no longer exist. Maintenance and sensing systems have failed to prevent or detect progressing deterioration. | Carrier_clearance_to_newly_installed_step_plating_on_the_existing_deck1.png | file://x:/photopub/docs/0000000644/d2751c2e-6550-4d67-a023-47a1203dd199.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__432881AB_B0F4_4D4B_AFE9_0F6F2E346609
EDOP-882054-2017 | 2045064 | 8/9/2017 | ASSESS: ED OP: Call | png | #asFound Worn anti friction material exposing metal on skirt panel | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | #Skirt_panel.png The skirt panels are located next to the steps of the escalator. It is required that an anti-friction surface be provided on the skirt panel to allow free flow of clothing or shoes. | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Skirt_panel.png | file://x:/photopub/docs/0000000649/4cd34d8e-f5e6-48a3-98e0-e0711c410d56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edc14e06_7f2e_4af8_a03a_3733337a7546
ELIN-876177-2017 | EL-558101-2017 | 8/10/2017 2:01:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_energized_panel.png Bare live electrical parts are required to be guarded against accidental contact by means of an approved cabinet or enclosure. This is to keep persons from contacting the energized electrical equipment and to contain the electrical energy if there is a fault. During a home owner electrical assessment of a new basement suite in an existing residential dwelling, an energized 100A, 120/240 volt electrical panel was found with no panel cover installed. Only the home owners family was on site at the time of the inspection. The open electrical panel is a potential shock hazard for any person that makes accidental contact with with the energized bus bars inside the panel. There is also a potential for an arc fault hazard if metal was to come in contact with the energized bus bars or conductors inside the panel. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_energized_panel.png | file://x:/photopub/docs/0000000645/4d426af8-1524-46c6-b5df-7dbf4853ba3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb0c452f_bb9d_4412_aaf3_ec2bf39c6632
ELIN-868832-2017 | EL-549398-2017 | 7/31/2017 10:00:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 3 | #M1.png,M2.png A 15 Amp receptacle has been installed on a 20 Amp branch circuit. This is a shock and fire hazard as the over-current device does not properly protect the receptacle that has been installed. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | M1.png | file://x:/photopub/docs/0000000638/ffc05adf-9aa8-4af5-aa26-50050c119faa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4efe2bea_448f_4949_83b0_5b38f904cd38
ELIN-868832-2017 | EL-549398-2017 | 7/31/2017 10:00:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 3 | #M1.png,M2.png A 15 Amp receptacle has been installed on a 20 Amp branch circuit. This is a shock and fire hazard as the over-current device does not properly protect the receptacle that has been installed. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | M2.png | file://x:/photopub/docs/0000000638/e88dcdb9-9126-4d62-bf8e-eb90a6b233cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4efe2bea_448f_4949_83b0_5b38f904cd38
ELOP-888029-2017 | EL-567172-2017 | 8/25/2017 11:55:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 3 | #A1.png,A2.png A dry type open core transformer has been installed within 300mm of a combustible surface (plywood wall). This is a fire hazard as these types of transformers can create a substantial amount of heat under heavy loads. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | A1.png | file://x:/photopub/docs/0000000653/57998996-e38b-478a-a0d5-f039a81217d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D172D0BE_7B44_463A_A422_AFC67493185A
ELOP-888029-2017 | EL-567172-2017 | 8/25/2017 11:55:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound Dry type transformer installed within 300mm of a combustible material | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 3 | #A1.png,A2.png A dry type open core transformer has been installed within 300mm of a combustible surface (plywood wall). This is a fire hazard as these types of transformers can create a substantial amount of heat under heavy loads. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | A2.png | file://x:/photopub/docs/0000000653/fec670d4-494c-44dd-b09a-f5974ccc005c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D172D0BE_7B44_463A_A422_AFC67493185A
GAWP-879375-2017 | GA-568057-2017 | 8/14/2017 10:40:41 AM | ASSESS: GA Work In Progress | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Setchfield.png Mechanical air intake for category 4 appliance Installed with less than the mimimim required clearance to regulator relief. Failure of regulator on meter set would result in the release of high pressure gas. Risk of fuel being drawn into appliance intake resulting in over fire condition. Possible risk of risk of fire or the production of carbon monoxide. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Setchfield.png | file://x:/photopub/docs/0000000645/f92c7ea8-321d-409e-9e8d-08cfaea07767.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d5f7a71_765f_4a81_a34c_c009351565e2
GAIN-874637-2017 | GA-566316-2017 | 8/14/2017 12:41:43 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Murcury_5.png Mechanical appliance intake located with less than the required 10 foot separation from meter regulator vent. Failure of meter regulator would allow the release of high pressure gas. Risk of fuel being drawn into appliance causing over fire condition. Risk of fire and or the production of carbon monoxide. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Murcury_5.png | file://x:/photopub/docs/0000000645/1ba25f0a-8fc9-435e-8b65-039af7e38acb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ac5faf8_7db5_4d8a_b47f_92f3ce31b426
ELIN-854960-2017 | UW-556871-2017 | 7/11/2017 9:14:17 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Live_condutors_exposed_multiple_location_in_occupied_seniors_center__not_locked.png Live exposed conductors operating at 240 volts and up to 30 amps were found in an area that was accessible to seniors in an operating seniors facility. This condition could have created potential for electric shock or electrocution. A senior was seen entering the area at the time of the assessment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Live_condutors_exposed_multiple_location_in_occupied_seniors_center__not_locked.png | file://x:/photopub/docs/0000000648/3dfc7297-c66f-4c7d-b4e9-8469e092d6a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7debafd7_e4f9_419a_91de_1656abdbc705
GAIN-882649-2017 | GA-327059-2015 | 8/18/2017 10:55:06 AM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Gas_entry.png The as-found condition is that a gas line enters a building below grade. The potential hazard is that, in the event of a gas leak on the underground piping, the gas will navigate inside the building, causing a fire and explosion hazard | 3 | Underground piping entering a building below grade (unapproved) | Gas_entry.png | file://x:/photopub/docs/0000000648/8f189a1a-8063-4d2e-9e6c-a1f5fb358021.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee47b924_9695_4a09_9547_d066c7f60d18
EDOP-882035-2017 | 2050978 | 8/14/2017 | ASSESS: ED OP: Call | png | #asFound Tiller access covered by ceramic flooring | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Cab_flooring_tiller_rope_access.png When work is performed by contractors not licensed, errors can be made which may affect the operations of the elevator system. In this case, important access point to the elevator safety mechanism was covered by a ceramic floor tile. If there was a emergency which required access to this access point it would be very difficult for authorized personnel to proceed which a repair. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Cab_flooring_tiller_rope_access.png | file://x:/photopub/docs/0000000649/39fe803d-cd7f-4cf4-b061-eb5d08871cea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18fe0630_67fc_4783_b091_0aa71378d694
EDOP-882068-2017 | 2045063 | 8/9/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound The skirt panel should have an anti-friction material which is worn to the metal | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 3 | #Worn_skirt_panel.png The skirt panels are next to the steps of an escalator. The normally have an anti-friction material which has been worn off to the metal. | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Worn_skirt_panel.png | file://x:/photopub/docs/0000000649/57df24e4-00c0-496b-8f62-a7e3464516aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8f0e524_b830_4454_aee7_e956c958f5b0
EDOP-882042-2017 | 2050979 | 8/14/2017 | ASSESS: ED OP: Call | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Ceramic_tile_covering_tiller_safety.png Non licensed contractor did alteration and covered elevator safety component in elevator floor with ceramic tiles | 3 | Defects that are: Not detected by maintenance program Likely to progress | Ceramic_tile_covering_tiller_safety.png | file://x:/photopub/docs/0000000649/f3544a9b-ac8c-4088-8642-3b82051b5ffa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89b2653b_4d55_4583_a248_5f6a1c3fb37e
GAIN-859078-2017 | GA-507294-2017 | 8/29/2017 3:14:08 PM | ASSESS: GA: Final | png | #asFound Relieve is pipe with 90 pointing down right side of photo | GA018 | Venting of pressure relief device indoors where source of ignition is present | 5 | 5 | #Regulator_Relief_installed_inside_parkade.png Natural Gas regulator has a built in overpressure device. If pressure upstream of Regulator were to go above rated pressure the relief port (overpressure device) will Relief gas out of piping system. The relief port shall be piped outdoors, leaving no trace of natural gas inside building should over-pressurization occur. Relief port has been piped to underground parkade, if over-pressurization occurs, natural gas will enter the parkade where sources of ignition are present (car ignition etc). This could cause a fire or explosion. | 5 | Venting of pressure relief device indoors where source of ignition is present | Regulator_Relief_installed_inside_parkade.png | file://x:/photopub/docs/0000000653/1b4915b8-16b9-4267-b277-9af09350406d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f051b0bf_0d20_44d8_86cc_0a1662f9fd46
ELIN-880899-2017 | EL-426091-2016 | 8/16/2017 1:37:06 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | #Arc_Faults_Missing.png This assessment found that Arc fault protection was missed, which has a potential fire hazard. | 3 | Conductors Equipment is not approved for the specific use. | Arc_Faults_Missing.png | file://x:/photopub/docs/0000000647/66011c03-789c-4d93-9e91-ced69201ee26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e005cf_0768_49c6_81c8_e15c1e99e3f5
BPVOP-875299-2017 | 2286490 | 8/9/2017 5:01:55 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP077 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | 3 | 3 | #Crack_repair_rear_of_fire_tube.png,Rear_bottom_morrision_tube_repair_area_.png Crack repairs were completed by contractor. Further NDE found other indications of surface cracks. Hydrostatic test was completed with no indication of leaks. Remaining surface cracks can grow and open with continued service. Fitness for service evaluation required. | 3 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | Rear_bottom_morrision_tube_repair_area_.png | file://x:/photopub/docs/0000000656/b75adb40-fba6-4974-af37-ef91ddaee189.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084593b2_c8bb_4603_8884_e05c2ac1dcdb
ELIN-877873-2017 | UW-570213-2017 | 8/11/2017 11:23:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Wiring_exiting_garage.png Flexible cord has been installed and left on the ground to feed power to a security system at a neighbouring property. Cord is not mechanicaly protected and is susceptible to mechanical damage. Mechanical damage could expose energized conductor and lead to shock or fire to persons or property. | 3 | Conductors Equipment is not approved for the specific use. | Wiring_exiting_garage.png | file://x:/photopub/docs/0000000645/4f37b47e-9526-414d-9f9a-abc4e6a483fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__767d820a_1461_45fe_95ad_3c00e728377e
GAIN-868403-2017 | GA-565263-2017 | 8/2/2017 11:00:19 AM | ASSESS: GA: Final | png | #asFound Under slab piping | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Under_slab_piping.png At Time of inspection copper tubing was installed under the building, if a gas leak developed underground , the gas could enter the building. | 3 | Underground piping entering a building below grade (unapproved) | Under_slab_piping.png | file://x:/photopub/docs/0000000640/813a2581-2004-4e42-9f7d-b29ff86ba1d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a45f42e7_5457_400f_941c_168c2f7c5d3a
GAIN-864005-2017 | GA-562617-2017 | 8/2/2017 11:53:13 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting.png At time of inspection chimney liner wasn't terminated properly, chimney liners are not compatible to be installed in an open space. | 3 | Unapproved venting material | Venting.png | file://x:/photopub/docs/0000000640/94396673-9baf-4434-8d22-391328d5bfe9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__514fb750_5093_4241_aa03_144c07f316db
EDMA-873657-2017 | ED-526150-2017 | 8/4/2017 | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #Hardware1.png,Hardware2.png All car door hardware to be installed. | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Hardware1.png | file://x:/photopub/docs/0000000642/28fb4e65-d1c7-451a-a76b-c6868ebfe3b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5d15f16_990c_4f51_9e92_b3f353b10ad4
EDMA-873657-2017 | ED-526150-2017 | 8/4/2017 | ASSESS: ED MA: Partial Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #Hardware1.png,Hardware2.png All car door hardware to be installed. | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Hardware2.png | file://x:/photopub/docs/0000000642/a0de4677-4426-4076-b44b-af07661a0b33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5d15f16_990c_4f51_9e92_b3f353b10ad4
ELIN-893930-2017 | EL-564351-2017 | 8/31/2017 12:14:03 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #1750_Dicken1.png,1750_Dicken2.png,1750_Dicken3.png,1750_Dicken4.png Loose main connections. service is energized | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 1750_Dicken3.png | file://x:/photopub/docs/0000000655/4650cd2a-dd59-4b4f-8e77-b4ad86b0b394.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74870be4_c9b6_4f43_a7ac_565a6bc7a6b0
ELIN-893930-2017 | EL-564351-2017 | 8/31/2017 12:14:03 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #1750_Dicken1.png,1750_Dicken2.png,1750_Dicken3.png,1750_Dicken4.png Loose main connections. service is energized | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 1750_Dicken2.png | file://x:/photopub/docs/0000000655/4397d4af-4fab-44fa-ad7d-bb175db025b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74870be4_c9b6_4f43_a7ac_565a6bc7a6b0
ELIN-893930-2017 | EL-564351-2017 | 8/31/2017 12:14:03 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound Energized | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #1750_Dicken1.png,1750_Dicken2.png,1750_Dicken3.png,1750_Dicken4.png Loose main connections. service is energized | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 1750_Dicken4.png | file://x:/photopub/docs/0000000655/5655ca01-0e24-4d17-be4e-3dfc9311ff88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74870be4_c9b6_4f43_a7ac_565a6bc7a6b0
ELIN-893930-2017 | EL-564351-2017 | 8/31/2017 12:14:03 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound All three main service conductors are completely loose and free to move in the terminal. Service is energized | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #1750_Dicken1.png,1750_Dicken2.png,1750_Dicken3.png,1750_Dicken4.png Loose main connections. service is energized | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 1750_Dicken1.png | file://x:/photopub/docs/0000000655/0abc15ae-8974-49ba-afbe-b9b8265b65fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74870be4_c9b6_4f43_a7ac_565a6bc7a6b0
GAHE-873443-2017 | HE-568092-2017 | 8/4/2017 2:54:13 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Open Lines on tank after disconnect | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open_Lines.png Found Propane tank disconnected and three separate lines on a header attached to the first stage regulator had valves with no caps or plugs. It is hazardous because anyone or anything could hit those valves causing a high pressure propane leak, which could lead to injury or death | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_Lines.png | file://x:/photopub/docs/0000000641/ad97d187-d64b-4ce3-9c03-d7fcdd65c238.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6a49fb4_eb60_4819_aaf8_3bf4f5a9347d
GAHE-873443-2017 | HE-568092-2017 | 8/4/2017 2:54:13 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Open Gas Lines | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | #Open_Lines.png Found Propane tank disconnected and three separate lines on a header attached to the first stage regulator had valves with no caps or plugs. It is hazardous because anyone or anything could hit those valves causing a high pressure propane leak, which could lead to injury or death | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_lines.png | file://x:/photopub/docs/0000000641/5186790b-df7e-4d1e-89d1-8b676caac7c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6a49fb4_eb60_4819_aaf8_3bf4f5a9347d
GAIN-869644-2017 | GA-127107-2014 | 8/29/2017 8:15:32 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Non_compliant_vent_arrangment.png Non compliant venting arrangement. A type B vent passing through an exterior wall and terminating adjacent to the wall will be unable to naturally draft under adverse conditions and can be affected by air pressure on the outside wall possible causing is to spill flue products into the space. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Non_compliant_vent_arrangment.png | file://x:/photopub/docs/0000000653/1f600b51-2944-4a6f-ac92-282530bfb4c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31ef6be6_7b07_4777_b9d4_7799e0fda19d
ELIN-885094-2017 | EL-568327-2017 | 8/22/2017 1:35:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Grounding conductor terminated incorrectly | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #grounding_conductor1.png,grounding_conductor2.png Grounding conductor incorrectly terminated onto bonding bus of circuit breaker compartment. Should a ground fault occurs, fault current will not travel into the ground, thereby not permitting an equipotential environment. | 4 | Installation Grounding; conductor is not continuous. | Grounding_conductor2.png | file://x:/photopub/docs/0000000650/cf8364c8-af24-41ae-9c3c-bdf007630217.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab0b0e47_e21d_4265_a215_e7758944ad56
ELIN-885094-2017 | EL-568327-2017 | 8/22/2017 1:35:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Grounding conductor not terminated in the service compartment | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #grounding_conductor1.png,grounding_conductor2.png Grounding conductor incorrectly terminated onto bonding bus of circuit breaker compartment. Should a ground fault occurs, fault current will not travel into the ground, thereby not permitting an equipotential environment. | 4 | Installation Grounding; conductor is not continuous. | grounding_conductor2.png | file://x:/photopub/docs/0000000650/28567d51-3995-47bf-9b6e-049fa14d85e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab0b0e47_e21d_4265_a215_e7758944ad56
ELIN-885094-2017 | EL-568327-2017 | 8/22/2017 1:35:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Grounding conductor incorrectly terminated | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #grounding_conductor1.png,grounding_conductor2.png Grounding conductor incorrectly terminated onto bonding bus of circuit breaker compartment. Should a ground fault occurs, fault current will not travel into the ground, thereby not permitting an equipotential environment. | 4 | Installation Grounding; conductor is not continuous. | Grounding_conductor1.png | file://x:/photopub/docs/0000000650/f6ac71ed-ba33-4755-adf4-9205b06486d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab0b0e47_e21d_4265_a215_e7758944ad56
ELIN-885094-2017 | EL-568327-2017 | 8/22/2017 1:35:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Grounding conductor terminated in the incorrect location | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #grounding_conductor1.png,grounding_conductor2.png Grounding conductor incorrectly terminated onto bonding bus of circuit breaker compartment. Should a ground fault occurs, fault current will not travel into the ground, thereby not permitting an equipotential environment. | 4 | Installation Grounding; conductor is not continuous. | grounding_conductor1.png | file://x:/photopub/docs/0000000650/6ffbd605-fed5-49e7-85f3-eca0bcff94bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab0b0e47_e21d_4265_a215_e7758944ad56
ELIN-868961-2017 | EL-541428-2017 | 8/2/2017 11:44:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #No_cover_on_panelboard.png Missing cover on equipment requested to be energized | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | No_cover_on_panelboard.png | file://x:/photopub/docs/0000000639/9e65be66-ee7c-48db-9649-ec7a6285240a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c75572ab_4b69_42cc_ada2_68d33e744b35
ELIN-869623-2017 | EL-461607-2016 | 8/2/2017 10:51:42 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #Exposed_insulated_conductors.png Conductors are intended to be installed in a raceway, to limit exposure to unqualified persons. The lack of a raceway over these conductor presents exposure risk | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_insulated_conductors.png | file://x:/photopub/docs/0000000639/a3f3ea06-f13f-4d62-b775-5e2cb37ac820.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac379413_97a0_44c9_acee_23547d585bb4
ELIN-897554-2017 | EL-574679-2017 | 9/1/2017 8:32:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL110 | Conductors Conductors are not suitably identified. | 3 | 3 | #Conductors_not_colour_identified.png 200 amp, 120/240 volt service rated cable is terminated in the meter base and main distribution without the proper colour markings of each individual phase conductor. This could lead to a system interruption. | 3 | Conductors Conductors are not suitably identified. | Conductors_not_colour_identified.png | file://x:/photopub/docs/0000000657/61464151-7789-439a-91a8-dd64a9cba160.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__804ca815_19ab_476a_8e7c_29ff2e16a7f9
GAIN-885436-2017 | GA-539255-2017 | 9/2/2017 8:22:34 AM | ASSESS: GA: Final | png | #asFound | GA117 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | 2 | 2 | #System_636.png Multiple system 636 fittings not glued on combustion air side, Dislodged or disconnected venting could cause lack of combustion air to furnace or create a negative in the building | 2 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | System_636.png | file://x:/photopub/docs/0000000656/ad0b5c3d-708c-409b-8ef9-aa7605436d66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3dcb7136_07a6_4b5d_bf3a_15f5b963bf20
ELIN-887621-2017 | EL-534615-2017 | 8/24/2017 11:11:19 AM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #RTU_switch_cover.png At a new commercial building, a 208volt 40amp rooftop unit was observed with an unapproved weatherproof cover over top the disconnecting switch. This can lead to a shock hazard condition. Pic is attached. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | RTU_switch_cover.png | file://x:/photopub/docs/0000000651/be3e8876-dc76-446b-9e4b-dd17c73ddd49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb88bbf7_ac0e_4dfb_9737_6bd3e32b335e
ELHE-901199-2017 | HE-580883-2017 | 9/6/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #hazard1.png,hazard2.png Panel covers removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | hazard2.png | file://x:/photopub/docs/0000000660/d411470e-9e01-444a-9e5f-f414d6aeb7fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3bafe2b_87f6_4523_be63_32330c7bf82c
ELIN-891044-2017 | UW-576960-2017 | 8/28/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Energized_and_exposed1.png,Energized_and_exposed2.png,Energized_and_exposed3.png Energized receptacles did not have protective cover plates installed. This condition could lead to accidental contact of the energized terminals resulting in an electrical shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_and_exposed2.png | file://x:/photopub/docs/0000000653/8801eaf4-2df9-4cc6-9d23-14b98ba9a25e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd837d50_e2df_4781_8cbb_c906a0607fd3
ELIN-891044-2017 | UW-576960-2017 | 8/28/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Energized_and_exposed1.png,Energized_and_exposed2.png,Energized_and_exposed3.png Energized receptacles did not have protective cover plates installed. This condition could lead to accidental contact of the energized terminals resulting in an electrical shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_and_exposed3.png | file://x:/photopub/docs/0000000653/d863e63d-a943-4c83-8a82-1e65ddc9930c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd837d50_e2df_4781_8cbb_c906a0607fd3
ELIN-891044-2017 | UW-576960-2017 | 8/28/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Energized_and_exposed1.png,Energized_and_exposed2.png,Energized_and_exposed3.png Energized receptacles did not have protective cover plates installed. This condition could lead to accidental contact of the energized terminals resulting in an electrical shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_and_exposed1.png | file://x:/photopub/docs/0000000653/51a27230-c27a-43df-a8d0-7c529f857912.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd837d50_e2df_4781_8cbb_c906a0607fd3
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures8.png | file://x:/photopub/docs/0000000648/f688210c-e50d-4dbc-8e41-d5da824ee5e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures2.png | file://x:/photopub/docs/0000000648/045b46bb-c2ae-4ddb-9157-eb134b7afb2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELIN-883550-2017 | EL-520425-2017 | 9/5/2017 1:30:16 PM | ASSESS: EL: Service Connection | png | #asFound Connection point twisted due to stress of conductor. Cap screw(removed for photo) is stripped and results in poor electrical contact between lug and neutral bar. This can result in overheating, arcing and over-voltages between circuits | EL020 | Damage to equipment may result in overheating. | 4 | 4 | #Stressed_neutral_lug_connection.png Stressed terminal lugs can result in poor connections and resulting overheating and or arcing. | 4 | Damage to equipment may result in overheating. | Stressed_neutral_lug_connection.png | file://x:/photopub/docs/0000000657/8c4ceecc-9be0-4451-bf0b-6afe5b3f688f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__818667c5_a3c0_4ef6_b160_398c89f668ef
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures7.png | file://x:/photopub/docs/0000000648/87d21653-6b7d-4702-8fc1-a35371c9227b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures16.png | file://x:/photopub/docs/0000000648/f8f9a4bf-e917-49ea-a008-e4f7eef903f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures9.png | file://x:/photopub/docs/0000000648/91cd4e14-6e5c-44b0-8232-e7b5ba4fd971.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures14.png | file://x:/photopub/docs/0000000648/2034b9bc-f5c0-4775-adb6-3b2ec95ea37f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. Electrical equipment adjacent to vehicle fuel tank. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures1.png | file://x:/photopub/docs/0000000648/e9c01c85-6bd6-4b38-b6a7-ef92a88b7800.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures18.png | file://x:/photopub/docs/0000000648/3ffdb862-7e35-44dd-bac8-41955ab56d97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures4.png | file://x:/photopub/docs/0000000648/eed977c6-5784-4347-a299-c0d700d26cec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures3.png | file://x:/photopub/docs/0000000648/66c3d61f-860f-461f-834c-d69373c6441c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures17.png | file://x:/photopub/docs/0000000648/9e7bcf0b-5f53-4fec-bb1d-69cce97e0557.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures15.png | file://x:/photopub/docs/0000000648/ea255abe-ad2d-4666-b238-b20c23f428a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures6.png | file://x:/photopub/docs/0000000648/db995b3c-8f4a-4589-9d29-5164b20792be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
GAUP-884266-2017 | UW-573222-2017 | 8/28/2017 2:38:36 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | #Leg_support.png Propane tank has bent and broken support, tank is full of fuel and in service. Propane tank could fall over due to no support and damage gas line or service valves and cause uncontrollable release of propane vapour or liquid causing a fire or explosion | 4 | Tank saddles/support failing | Leg_support.png | file://x:/photopub/docs/0000000653/1cf68d5e-a1ce-48e6-98b7-263b67c4d4d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__febd0126_4482_4c00_a93a_f5a695d59c62
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures12.png | file://x:/photopub/docs/0000000648/f896e20a-003d-497b-8165-74767e39a665.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures10.png | file://x:/photopub/docs/0000000648/fae53623-76cb-4eda-9854-0aa49636a82a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures13.png | file://x:/photopub/docs/0000000648/c410d688-b6ef-4391-b938-7f9b75d0220b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELIN-885259-2017 | EL-544045-2017 | 8/21/2017 12:09:42 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #Non_compliant_underground_cable_installation1.png,Non_compliant_underground_cable_installation2.png In a new multi family dwelling construction, 100 amp 120/240 volt consumer service cables were found to not meet the requirements of underground installation codes with regards to fill, depth and burial tape. This could cause an equipment damage condition. Pictures attached. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Non_compliant_underground_cable_installation1.png | file://x:/photopub/docs/0000000649/5f54bd7d-3c73-43eb-aa18-8e8b5c6bd216.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfa23f30_3be6_43ba_8648_7907360a21e4
ELIN-885259-2017 | EL-544045-2017 | 8/21/2017 12:09:42 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #Non_compliant_underground_cable_installation1.png,Non_compliant_underground_cable_installation2.png In a new multi family dwelling construction, 100 amp 120/240 volt consumer service cables were found to not meet the requirements of underground installation codes with regards to fill, depth and burial tape. This could cause an equipment damage condition. Pictures attached. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Non_compliant_underground_cable_installation2.png | file://x:/photopub/docs/0000000649/b1e480ce-635f-4bc1-8469-a4ae6af7b622.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfa23f30_3be6_43ba_8648_7907360a21e4
ELIN-893931-2017 | EL-278177-2015 | 9/7/2017 4:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #D1.png,D2.png,D3.png,D4.png,D5.png,D6.png Receptacle located within 3m of a hot tub. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | D6.png | file://x:/photopub/docs/0000000659/e528790f-3a30-4025-b9d9-fcd4f5a86546.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdd6430_5d2d_4503_8a03_a2ce8dfecaf4
ELIN-893931-2017 | EL-278177-2015 | 9/7/2017 4:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #D1.png,D2.png,D3.png,D4.png,D5.png,D6.png Receptacle located within 3m of a hot tub. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | D2.png | file://x:/photopub/docs/0000000659/21cb1c6c-40bf-4973-87e6-2bc744f89384.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdd6430_5d2d_4503_8a03_a2ce8dfecaf4
ELIN-893931-2017 | EL-278177-2015 | 9/7/2017 4:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #D1.png,D2.png,D3.png,D4.png,D5.png,D6.png Receptacle located within 3m of a hot tub. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | D1.png | file://x:/photopub/docs/0000000659/03a57c54-99c3-461a-81de-f329491c0819.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdd6430_5d2d_4503_8a03_a2ce8dfecaf4
ELIN-893931-2017 | EL-278177-2015 | 9/7/2017 4:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #D1.png,D2.png,D3.png,D4.png,D5.png,D6.png Receptacle located within 3m of a hot tub. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | D3.png | file://x:/photopub/docs/0000000659/81639435-bc22-4215-b806-9a77293c9156.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdd6430_5d2d_4503_8a03_a2ce8dfecaf4
ELIN-893931-2017 | EL-278177-2015 | 9/7/2017 4:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #D1.png,D2.png,D3.png,D4.png,D5.png,D6.png Receptacle located within 3m of a hot tub. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | D4.png | file://x:/photopub/docs/0000000659/5339af58-c732-49ea-9e84-2a10777f8675.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdd6430_5d2d_4503_8a03_a2ce8dfecaf4
ELIN-893931-2017 | EL-278177-2015 | 9/7/2017 4:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #D1.png,D2.png,D3.png,D4.png,D5.png,D6.png Receptacle located within 3m of a hot tub. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | D5.png | file://x:/photopub/docs/0000000659/5e4b9564-10d1-4adf-8f58-309aba41ed5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcdd6430_5d2d_4503_8a03_a2ce8dfecaf4
ELHE-902151-2017 | HE-581400-2017 | 9/7/2017 12:52:28 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Panel_Cover1.png,Panel_Cover2.png In the 200 amp 120/240 volt Main Panel located in a Power Shack, the panel cover has branch breaker spaces which are open and have not been provided with covers or fillers. This poses a shock hazard to persons and potential mechanical and electrical damage to the Main Panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_Cover1.png | file://x:/photopub/docs/0000000659/070c7cd0-1013-4b06-8fc8-b9fbd9559051.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8ed650_17ae_472b_8fe7_d8d410f23ff9
ELHE-902151-2017 | HE-581400-2017 | 9/7/2017 12:52:28 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Panel_Cover1.png,Panel_Cover2.png In the 200 amp 120/240 volt Main Panel located in a Power Shack, the panel cover has branch breaker spaces which are open and have not been provided with covers or fillers. This poses a shock hazard to persons and potential mechanical and electrical damage to the Main Panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_Cover2.png | file://x:/photopub/docs/0000000659/96043f4c-d7b2-43f8-a4dc-80d9931d3b11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc8ed650_17ae_472b_8fe7_d8d410f23ff9
BPVOP-880812-2017 | 4460401 | 8/15/2017 1:47:00 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that horizontal machine mounted air receiver (0.90m long and 0.50m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000646/549a68c2-e120-44e4-a306-1007fb0046dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac597925_af78_4fc3_8995_937b63cef47b
GAIN-866280-2017 | GA-497404-2017 | 7/31/2017 9:46:54 AM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #As_found.png The as found condition is two propane second stage regulators installed with their vents within the minimum 10 foot clearance from a source of ignition (appliance vent terminations). The as found hazard is in the event of a regulator failure, high pressure propane gas can migrate into the combustion chamber of the appliance and ignite leading to an explosion. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | As_found.png | file://x:/photopub/docs/0000000638/a950bb17-c4b1-442a-8895-ac063bf8f975.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6462a3b_dab6_4d9b_b40a_c955f9be6895
GAUP-873384-2017 | UW-568065-2017 | 8/9/2017 2:37:13 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Fireplace1.png Uncertified fireplace installed and connected for use. No evidence of data tag with certification found. Red tagged appliance. Potential for failure of unapproved appliances creating higher risk of property damage or injury | 3 | Uncertified appliance connected to gas supply but not in service | Fireplace1.png | file://x:/photopub/docs/0000000644/e71affd0-c2b0-4ad2-a625-0376ba291e4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6d71087_6b14_434c_92b3_0566370c2102
ELOP-841613-2017 | EL-503972-2017 | 8/22/2017 7:09:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exterior_conduits_and_lighting1.png,Exterior_conduits_and_lighting2.png,Exterior_conduits_and_lighting3.png,Exterior_conduits_and_lighting4.png,Exterior_conduits_and_lighting5.png,Exterior_conduits_and_lighting6.png Unprotected underground raceways in non-vehicular areas are required to to be installed a minimum of 450mm below grade and to have marker tape installed half way between the installed conduit and top of grade. The conductors installed in the raceway must also be suitable for the condition of use (wet location) During an operating permit assessment at a hotel, the underground PVC conduits for new exterior lighting in the garden area's beside the sidewalks were found to be at a depth of approximately 150mm and did not have marker tape above the conduit. The conductors inside the raceways was non-metallic sheathed cable rated for dry location. The shallow depth of the unmarked conduit has the potential to be damaged by persons working in the garden and could create a shock hazard if the conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_conduits_and_lighting3.png | file://x:/photopub/docs/0000000650/2fcb708e-54a5-4bd4-be0e-576775e64c4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C93F1D94_C619_487D_9D1E_9F95B751F1B3
ELOP-841613-2017 | EL-503972-2017 | 8/22/2017 7:09:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exterior_conduits_and_lighting1.png,Exterior_conduits_and_lighting2.png,Exterior_conduits_and_lighting3.png,Exterior_conduits_and_lighting4.png,Exterior_conduits_and_lighting5.png,Exterior_conduits_and_lighting6.png Unprotected underground raceways in non-vehicular areas are required to to be installed a minimum of 450mm below grade and to have marker tape installed half way between the installed conduit and top of grade. The conductors installed in the raceway must also be suitable for the condition of use (wet location) During an operating permit assessment at a hotel, the underground PVC conduits for new exterior lighting in the garden area's beside the sidewalks were found to be at a depth of approximately 150mm and did not have marker tape above the conduit. The conductors inside the raceways was non-metallic sheathed cable rated for dry location. The shallow depth of the unmarked conduit has the potential to be damaged by persons working in the garden and could create a shock hazard if the conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_conduits_and_lighting6.png | file://x:/photopub/docs/0000000650/e8f603ac-da22-4995-8621-4816de56f596.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C93F1D94_C619_487D_9D1E_9F95B751F1B3
ELIN-882750-2017 | EL-544006-2017 | 8/21/2017 1:02:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Service_1.png,Service_2.png,Service_3.png,Service_4.png The BC electrical code requires PVC conduit inside a wall for supply service conductors to be mechanically protected if subject to damage and not to be installed were the the conduit will be covered with thermal insulation. BC Hydro requires underground supply conduits inside a wall for a residential service to be encased in a minimum of 50mm of concrete. During an assessment for a service inspection of a new single family dwelling, the 3" PVC conduit for the supply service was found in an exterior wall against the exterior sheathing. There was no mechanical protection for this conduit. When the exterior siding is installed on this dwelling, there is the potential for a nail or screw to puncture this conduit and damage the service cables. When the cables are energized, a fault condition on the service cables could create a potential fire hazard inside the dwelling or damage electrical equipment connected to this service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_4.png | file://x:/photopub/docs/0000000650/88d4fcee-f776-41ed-8186-6af66c349072.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a2b78ce_8343_4b0d_a00e_5ca77848f09d
ELIN-879635-2017 | EL-560907-2017 | 8/15/2017 9:49:18 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Main_Panel_Location1.png,Main_Panel_Location2.png A 200 amp 120/240 volt Electrical Panel has been mounted in an outdoor location and the panel is not rated for the environment, it is not of weatherproof construction. This could result in a shock hazard to persons and will result in permanent mechanical damage to the panel, causing it to fail at a later date. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_Panel_Location1.png | file://x:/photopub/docs/0000000646/bd8a4870-0ae1-4b6e-af32-992941291f90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3a77672_3b15_4d83_bb76_43db76224548
ELIN-879635-2017 | EL-560907-2017 | 8/15/2017 9:49:18 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Main_Panel_Location1.png,Main_Panel_Location2.png A 200 amp 120/240 volt Electrical Panel has been mounted in an outdoor location and the panel is not rated for the environment, it is not of weatherproof construction. This could result in a shock hazard to persons and will result in permanent mechanical damage to the panel, causing it to fail at a later date. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_Panel_Location2.png | file://x:/photopub/docs/0000000646/340053fa-6261-4615-bf31-ba3e9e9f64e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3a77672_3b15_4d83_bb76_43db76224548
ELIN-861585-2017 | EL-294077-2015 | 7/31/2017 1:03:13 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Flexible_cord_to_permanent_refrigerator_and_microwave.png Flexible cord, or extension cords been run through a cabinet to provide power to a permanent refrigerator. 2 conductor extension cord with no ground has been used to provide power to kitchen counter microwave that needs a ground to operate safely. Either of these 2 conditions can lead to property damage or injury to persons | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_to_permanent_refrigerator_and_microwave.png | file://x:/photopub/docs/0000000639/92a87d80-22d1-430a-83a4-df9035f5fde8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9b3da53_0fc5_45b3_922c_453690b3f2d7
ELIN-882750-2017 | EL-544006-2017 | 8/21/2017 1:02:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Service_1.png,Service_2.png,Service_3.png,Service_4.png The BC electrical code requires PVC conduit inside a wall for supply service conductors to be mechanically protected if subject to damage and not to be installed were the the conduit will be covered with thermal insulation. BC Hydro requires underground supply conduits inside a wall for a residential service to be encased in a minimum of 50mm of concrete. During an assessment for a service inspection of a new single family dwelling, the 3" PVC conduit for the supply service was found in an exterior wall against the exterior sheathing. There was no mechanical protection for this conduit. When the exterior siding is installed on this dwelling, there is the potential for a nail or screw to puncture this conduit and damage the service cables. When the cables are energized, a fault condition on the service cables could create a potential fire hazard inside the dwelling or damage electrical equipment connected to this service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_3.png | file://x:/photopub/docs/0000000650/b973b7e1-5a3e-48cc-903f-31fb233adcc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a2b78ce_8343_4b0d_a00e_5ca77848f09d
ELIN-882750-2017 | EL-544006-2017 | 8/21/2017 1:02:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Service_1.png,Service_2.png,Service_3.png,Service_4.png The BC electrical code requires PVC conduit inside a wall for supply service conductors to be mechanically protected if subject to damage and not to be installed were the the conduit will be covered with thermal insulation. BC Hydro requires underground supply conduits inside a wall for a residential service to be encased in a minimum of 50mm of concrete. During an assessment for a service inspection of a new single family dwelling, the 3" PVC conduit for the supply service was found in an exterior wall against the exterior sheathing. There was no mechanical protection for this conduit. When the exterior siding is installed on this dwelling, there is the potential for a nail or screw to puncture this conduit and damage the service cables. When the cables are energized, a fault condition on the service cables could create a potential fire hazard inside the dwelling or damage electrical equipment connected to this service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_2.png | file://x:/photopub/docs/0000000650/026e036c-6f59-4c22-a4ee-cc22c182a16d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a2b78ce_8343_4b0d_a00e_5ca77848f09d
ELOP-841613-2017 | EL-503972-2017 | 8/22/2017 7:09:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exterior_conduits_and_lighting1.png,Exterior_conduits_and_lighting2.png,Exterior_conduits_and_lighting3.png,Exterior_conduits_and_lighting4.png,Exterior_conduits_and_lighting5.png,Exterior_conduits_and_lighting6.png Unprotected underground raceways in non-vehicular areas are required to to be installed a minimum of 450mm below grade and to have marker tape installed half way between the installed conduit and top of grade. The conductors installed in the raceway must also be suitable for the condition of use (wet location) During an operating permit assessment at a hotel, the underground PVC conduits for new exterior lighting in the garden area's beside the sidewalks were found to be at a depth of approximately 150mm and did not have marker tape above the conduit. The conductors inside the raceways was non-metallic sheathed cable rated for dry location. The shallow depth of the unmarked conduit has the potential to be damaged by persons working in the garden and could create a shock hazard if the conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_conduits_and_lighting4.png | file://x:/photopub/docs/0000000650/54ae9b05-d45e-4bfd-a649-4f3208fdbf5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C93F1D94_C619_487D_9D1E_9F95B751F1B3
ELOP-841613-2017 | EL-503972-2017 | 8/22/2017 7:09:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exterior_conduits_and_lighting1.png,Exterior_conduits_and_lighting2.png,Exterior_conduits_and_lighting3.png,Exterior_conduits_and_lighting4.png,Exterior_conduits_and_lighting5.png,Exterior_conduits_and_lighting6.png Unprotected underground raceways in non-vehicular areas are required to to be installed a minimum of 450mm below grade and to have marker tape installed half way between the installed conduit and top of grade. The conductors installed in the raceway must also be suitable for the condition of use (wet location) During an operating permit assessment at a hotel, the underground PVC conduits for new exterior lighting in the garden area's beside the sidewalks were found to be at a depth of approximately 150mm and did not have marker tape above the conduit. The conductors inside the raceways was non-metallic sheathed cable rated for dry location. The shallow depth of the unmarked conduit has the potential to be damaged by persons working in the garden and could create a shock hazard if the conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_conduits_and_lighting1.png | file://x:/photopub/docs/0000000650/07fe211c-af89-486d-92fd-f6fe36b113c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C93F1D94_C619_487D_9D1E_9F95B751F1B3
ELIN-882750-2017 | EL-544006-2017 | 8/21/2017 1:02:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Service_1.png,Service_2.png,Service_3.png,Service_4.png The BC electrical code requires PVC conduit inside a wall for supply service conductors to be mechanically protected if subject to damage and not to be installed were the the conduit will be covered with thermal insulation. BC Hydro requires underground supply conduits inside a wall for a residential service to be encased in a minimum of 50mm of concrete. During an assessment for a service inspection of a new single family dwelling, the 3" PVC conduit for the supply service was found in an exterior wall against the exterior sheathing. There was no mechanical protection for this conduit. When the exterior siding is installed on this dwelling, there is the potential for a nail or screw to puncture this conduit and damage the service cables. When the cables are energized, a fault condition on the service cables could create a potential fire hazard inside the dwelling or damage electrical equipment connected to this service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_1.png | file://x:/photopub/docs/0000000650/ad88a9f2-a629-46f1-b94c-51d3918a40d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a2b78ce_8343_4b0d_a00e_5ca77848f09d
ELOP-841613-2017 | EL-503972-2017 | 8/22/2017 7:09:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exterior_conduits_and_lighting1.png,Exterior_conduits_and_lighting2.png,Exterior_conduits_and_lighting3.png,Exterior_conduits_and_lighting4.png,Exterior_conduits_and_lighting5.png,Exterior_conduits_and_lighting6.png Unprotected underground raceways in non-vehicular areas are required to to be installed a minimum of 450mm below grade and to have marker tape installed half way between the installed conduit and top of grade. The conductors installed in the raceway must also be suitable for the condition of use (wet location) During an operating permit assessment at a hotel, the underground PVC conduits for new exterior lighting in the garden area's beside the sidewalks were found to be at a depth of approximately 150mm and did not have marker tape above the conduit. The conductors inside the raceways was non-metallic sheathed cable rated for dry location. The shallow depth of the unmarked conduit has the potential to be damaged by persons working in the garden and could create a shock hazard if the conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_conduits_and_lighting2.png | file://x:/photopub/docs/0000000650/889b2405-d70d-470d-b170-08f1a72b86d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C93F1D94_C619_487D_9D1E_9F95B751F1B3
EDOP-804931-2017 | 2050527 | 8/24/2017 11:22:20 AM | ASSESS: ED OP: RAP | png | #asFound | ED009 | Defects that are: Detected by Maintenance program Likely to progress | 2 | 2 | #Emergency_light_and_stop_switch1.png,Emergency_light_and_stop_switch2.png Emergency light broken / stop switch broken | 2 | Defects that are: Detected by Maintenance program Likely to progress | Emergency_light_and_stop_switch1.png | file://x:/photopub/docs/0000000651/f3ca6fe9-d7f8-409e-a578-6d4e41e2a9db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EF967BF1_0D55_4A5F_8EE5_CD11D2939363
ELIN-887864-2017 | UW-575297-2017 | 8/24/2017 10:43:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Electrical equipment located in a corrosive environment. Equipment is damaged from the corrosive chlorine environment. Live conductors are exposed. This is a shock and fire hazard. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | A2.png | file://x:/photopub/docs/0000000651/95ce99c7-cea6-4137-807e-0badacd49b34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c094069e_6eb8_49fb_a032_ec65c3dd8c63
ELIN-887864-2017 | UW-575297-2017 | 8/24/2017 10:43:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Electrical equipment located in a corrosive environment. Equipment is damaged from the corrosive chlorine environment. Live conductors are exposed. This is a shock and fire hazard. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | A5.png | file://x:/photopub/docs/0000000651/a65b149f-9f9e-41a2-a607-167099d534f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c094069e_6eb8_49fb_a032_ec65c3dd8c63
ELIN-887864-2017 | UW-575297-2017 | 8/24/2017 10:43:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Electrical equipment located in a corrosive environment. Equipment is damaged from the corrosive chlorine environment. Live conductors are exposed. This is a shock and fire hazard. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | A1.png | file://x:/photopub/docs/0000000651/d9d0415b-f5cf-4161-b021-6377bca75fbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c094069e_6eb8_49fb_a032_ec65c3dd8c63
ELIN-887864-2017 | UW-575297-2017 | 8/24/2017 10:43:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Electrical equipment located in a corrosive environment. Equipment is damaged from the corrosive chlorine environment. Live conductors are exposed. This is a shock and fire hazard. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | A3.png | file://x:/photopub/docs/0000000651/3da0ff30-89e1-4aa3-b76a-c706e652b1b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c094069e_6eb8_49fb_a032_ec65c3dd8c63
ELIN-887864-2017 | UW-575297-2017 | 8/24/2017 10:43:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | #A1.png,A2.png,A3.png,A4.png,A5.png Electrical equipment located in a corrosive environment. Equipment is damaged from the corrosive chlorine environment. Live conductors are exposed. This is a shock and fire hazard. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | A4.png | file://x:/photopub/docs/0000000651/7b5a5de9-7a95-4897-8b13-e10dd9db7c4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c094069e_6eb8_49fb_a032_ec65c3dd8c63
ELIN-890833-2017 | EL-544278-2017 | 8/29/2017 10:21:30 AM | ASSESS: EL: Service Connection | png | #asFound Connectors are not tightened, concentric knock outs are broken | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Loose_connectors_and_broken_conncentrics.png Consumer service cables are not made up tight in connectors and concentric knock out in meter base is broken | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Loose_connectors_and_broken_conncentrics.png | file://x:/photopub/docs/0000000653/4ce805e7-061f-4f6a-8b7c-689c4fd2c633.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f61c27_0b0e_42f6_870d_1ca94bbe0e49
ELIN-890833-2017 | EL-544278-2017 | 8/29/2017 10:21:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Loose_connectors_and_broken_conncentrics.png Consumer service cables are not made up tight in connectors and concentric knock out in meter base is broken | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Loose_connectors_and_broken_conncentrics.png | file://x:/photopub/docs/0000000653/27a6cc85-b570-4593-b643-a05810929a69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f61c27_0b0e_42f6_870d_1ca94bbe0e49
ELIN-890833-2017 | EL-544278-2017 | 8/29/2017 10:21:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Loose_connectors_and_broken_conncentrics.png Consumer service cables are not made up tight in connectors and concentric knock out in meter base is broken | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Loose_connectors_and_broken_conncentrics.png | file://x:/photopub/docs/0000000653/c59c0cd1-6a00-4608-be8c-1be6cdc10d37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f61c27_0b0e_42f6_870d_1ca94bbe0e49
ELIN-869655-2017 | EL-565860-2017 | 8/1/2017 3:59:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | #A1.png,A2.png Type 1 panel installed in a wet location. This is a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | A1.png | file://x:/photopub/docs/0000000639/08d96591-1ae9-42e8-94f6-da978b447279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25cf25db_a057_43d6_9387_e6321d1897bc
ELIN-868329-2017 | EL-564655-2017 | 8/1/2017 4:46:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #B1.png,B2.png Panel located in area that is not readily accessible nor has proper working clearances or head room. This is a shock and fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | B1.png | file://x:/photopub/docs/0000000639/0b9bd7da-a067-447b-a390-7647bf2b26c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b70f7e60_a4ee_4255_9923_d28475a32599
ELIN-869655-2017 | EL-565860-2017 | 8/1/2017 3:59:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | #A1.png,A2.png Type 1 panel installed in a wet location. This is a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | A2.png | file://x:/photopub/docs/0000000639/00cf9e7b-c5f0-4ce1-b045-8d04c186216c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25cf25db_a057_43d6_9387_e6321d1897bc
ELIN-868329-2017 | EL-564655-2017 | 8/1/2017 4:46:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #B1.png,B2.png Panel located in area that is not readily accessible nor has proper working clearances or head room. This is a shock and fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | B2.png | file://x:/photopub/docs/0000000639/a7ebac15-42e3-4514-8326-5fc251aa98d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b70f7e60_a4ee_4255_9923_d28475a32599
ELIN-874765-2017 | EL-537117-2017 | 8/11/2017 8:12:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Bonding_Jumper.png A 200 amp 120/240 volt Subpanel located in a new home has the bonding jumper from the neutral bar to the panel enclosure still in place. This jumper is to be removed on all equipment downstream of the Service Main Panel or Switch. With the jumper still in place the correct path for any possible fault current is not in place, and unwanted circulating currents may be present at the panel and on the bonding conductors. This poses a shock hazard to persons and potential damage to the equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding_Jumper.png | file://x:/photopub/docs/0000000644/c479fc8e-8af8-4d8f-b2a7-affe42f0ed83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6c646c9_febc_4f46_984e_f6e881571927
ELIN-876743-2017 | EL-569248-2017 | 8/11/2017 1:04:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_Panel.png A 100 amp 120/240 volt energized electrical panel has numerous openings in the cover exposing the energized components inside. This poses a shock hazard to persons and potential damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_Panel.png | file://x:/photopub/docs/0000000644/4e0cad95-00d3-4f34-8e12-17f176fdcda6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55a51b67_08a3_4fe9_abcb_b6a7e600161a
ELIN-871549-2017 | EL-565453-2017 | 8/3/2017 3:09:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #2_gang_box_in_entry.png Energized parts | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 2_gang_box_in_entry.png | file://x:/photopub/docs/0000000641/0293343c-42b3-44cd-b40d-9042dfb11f7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23473e86_018c_4fb4_bf46_ef0bd4e30dfe
GAUP-867237-2017 | UW-549803-2017 | 8/2/2017 9:28:01 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Firplace21.png,Firplace22.png,Firplace23.png A gas fireplace was found to be installed with a wood trim and mantel within the manufactures clearance requirements. Over time heat produced by the fireplace can course the combustible material to reach a point of combustion causing a fire. | 3 | Clearance to combustible not met | Firplace21.png | file://x:/photopub/docs/0000000639/610971f7-2393-4943-9a0e-7dc291896576.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6eb1baa1_fe94_4d6d_8aff_1841831163a7
GAUP-867237-2017 | UW-549803-2017 | 8/2/2017 9:28:01 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Firplace21.png,Firplace22.png,Firplace23.png A gas fireplace was found to be installed with a wood trim and mantel within the manufactures clearance requirements. Over time heat produced by the fireplace can course the combustible material to reach a point of combustion causing a fire. | 3 | Clearance to combustible not met | Firplace22.png | file://x:/photopub/docs/0000000639/3d4f421c-ddcb-4b8c-be25-462f8b200454.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6eb1baa1_fe94_4d6d_8aff_1841831163a7
GAUP-867237-2017 | UW-549803-2017 | 8/2/2017 9:28:01 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Firplace21.png,Firplace22.png,Firplace23.png A gas fireplace was found to be installed with a wood trim and mantel within the manufactures clearance requirements. Over time heat produced by the fireplace can course the combustible material to reach a point of combustion causing a fire. | 3 | Clearance to combustible not met | Firplace23.png | file://x:/photopub/docs/0000000639/e057b809-a9b0-4834-bc95-3719f657a0ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6eb1baa1_fe94_4d6d_8aff_1841831163a7
ELIN-868129-2017 | EL-549466-2017 | 8/3/2017 1:53:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_incorrect.png This assessment found that the grounding has been done incorrectly, potentially causing a shock hazard if the bonding jumper was removed or damaged. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_incorrect.png | file://x:/photopub/docs/0000000641/9205928e-42e2-41c9-a591-a92dcf16178d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66712358_3653_43ec_83e2_a12e0b3ff484
ELIN-860543-2017 | EL-540038-2017 | 8/3/2017 10:03:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #tandem_breaker_with_3-wire_circuit_.png This assessment found that the red and black wire from a three phase circuit share the same phase, this can overload the neutral conductor. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | tandem_breaker_with_3-wire_circuit_.png | file://x:/photopub/docs/0000000641/9ca24dac-1030-4a97-84f2-a1d886189e59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f85772a4_e649_45f9_8890_d27cf74c18bf
GAIN-879577-2017 | GA-141015-2014 | 8/15/2017 10:11:19 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_termination.png Two commercial water heaters were found installed and running with vents terminated too close to a window that could be opened for an apartment suite. In the event that the window was left open, flue gases could make their way into the living space and expose occupants to the negative effects of carbon monoxide in the flue gases. It is important that all flue gases make their way to the outdoors at a safe location. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination.png | file://x:/photopub/docs/0000000646/b8e472b5-71c7-45cd-bb8e-d27a754a17f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c6c73df_326a_409a_8322_292ee4a9c13c
EDRI-889281-2017 | ED-426308-2016 | 8/25/2017 9:24:37 AM | ASSESS: ED RI: Extension | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | #Scaffold_report_example.png When exiting the hoist, some landings are supported by scaffolding. The scaffolding is engineered and inspected to ensure it is of sufficient strength. One of the requirements in the engineers report for these suspended landings is that the scaffolding is checked daily to ensure it has not come loose. These inspections are not being performed. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | Scaffold_report_example.png | file://x:/photopub/docs/0000000652/5839abf8-2fae-458d-a3d6-92ca7682d966.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14916f4f_cb8a_4943_bd09_e559d7abe444
BPVIN-883256-2017 | UW-572616-2017 | 8/17/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve_.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000648/ffe60f35-2c07-4079-b0d5-eb37a2eec167.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__181f5936_c5ee_4e91_aaf5_701c705e93ae
BPVOP-877838-2017 | 2263510 | 8/17/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #ASME_plate_.png During the inspection of a Hot Water Boiler with MAWP of 160 psig was found that there is no Emergency Shut Down Switch located at the boiler room entrance. Without this emergency shut down switch located at the boiler room entrance, it would be difficult to shut down this equipment in an emergency situation. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | ASME_plate_.png | file://x:/photopub/docs/0000000648/7892d9ee-26bd-44be-90c1-bae269afdf39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8237e3ce_953a_49ca_9cd9_145e2241d25a
EDIN-878253-2017 | ED-563899-2017 | 8/11/2017 7:58:44 PM | ASSESS: ED IN: Acceptance | png | #asFound Fire control panel | ED031 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | 4 | 4 | #Final_Panel.png Fire panel not installed for final acceptance inspection | 4 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | Final_Panel.png | file://x:/photopub/docs/0000000645/f072bfa7-9825-4450-9d11-a5e04508c4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20b93503_dae8_4799_9f24_b757a8c76b39
EDOP-847053-2017 | 2048226 | 6/19/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound The elevator pit contains a large amount of debris which must be removed to prevent fire and tripping hazards. | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Debris_in_pit.png | 3 | Defects that are: Not detected by maintenance program Likely to progress | Debris_in_pit.png | file://x:/photopub/docs/0000000647/b9788a4a-a7f5-4045-a094-92f74df72ffc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb053985_e534_4b5a_be94_a3b9166e6170
ELIN-870385-2017 | UW-241931-2015 | 8/1/2017 12:57:59 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound 120 volt rated bed or table is unapproved not certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_medical_table_or_bed_electrical_product1.png,Unapproved_medical_table_or_bed_electrical_product2.png,Unapproved_medical_table_or_bed_electrical_product3.png Electrical product 120 volt rated medical table or bed has no recognized approval or certification mark or label attached to electrical equipment as identified in INFORMATION BULLETIN No. B-E3 071019 3 APPROVED CERTIFICATION MARKS FOR ELECTRICAL PRODUCTS. Electrical equipment/products above which are not approved or certified as required by regulations are not authorized to be used or to be connected to power supply system and may be a possible electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_medical_table_or_bed_electrical_product1.png | file://x:/photopub/docs/0000000639/931ac793-c550-438a-be51-b8ca8d55f2bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7a82c57_9e3e_4c89_b400_186e6b177934
ELIN-870385-2017 | UW-241931-2015 | 8/1/2017 12:57:59 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound 120 volt rated bed or table is unapproved not certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_medical_table_or_bed_electrical_product1.png,Unapproved_medical_table_or_bed_electrical_product2.png,Unapproved_medical_table_or_bed_electrical_product3.png Electrical product 120 volt rated medical table or bed has no recognized approval or certification mark or label attached to electrical equipment as identified in INFORMATION BULLETIN No. B-E3 071019 3 APPROVED CERTIFICATION MARKS FOR ELECTRICAL PRODUCTS. Electrical equipment/products above which are not approved or certified as required by regulations are not authorized to be used or to be connected to power supply system and may be a possible electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_medical_table_or_bed_electrical_product3.png | file://x:/photopub/docs/0000000639/3488f095-d124-4bf8-85c3-8c41038110cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7a82c57_9e3e_4c89_b400_186e6b177934
ELIN-870385-2017 | UW-241931-2015 | 8/1/2017 12:57:59 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound 120 volt rated bed or table is unapproved not certified | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_medical_table_or_bed_electrical_product1.png,Unapproved_medical_table_or_bed_electrical_product2.png,Unapproved_medical_table_or_bed_electrical_product3.png Electrical product 120 volt rated medical table or bed has no recognized approval or certification mark or label attached to electrical equipment as identified in INFORMATION BULLETIN No. B-E3 071019 3 APPROVED CERTIFICATION MARKS FOR ELECTRICAL PRODUCTS. Electrical equipment/products above which are not approved or certified as required by regulations are not authorized to be used or to be connected to power supply system and may be a possible electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_medical_table_or_bed_electrical_product2.png | file://x:/photopub/docs/0000000639/626b7802-95a5-48ab-be72-cc9f671a02e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7a82c57_9e3e_4c89_b400_186e6b177934
ELIN-869713-2017 | EL-101995-2014 | 8/1/2017 7:38:01 AM | ASSESS: EL: Final | jpg | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Car_Charger_-_view_inside_locker_-_20140327_172806.jpg Locker enclosure being utilized for electrical bonding purposes does not appear to be approved electrical equipment. Approved electrical equipment would be tested for the purpose intended. Proper bonding methods help to maintain an equipotential plain and prevent dangerous potential (voltage) differences. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Car_Charger_-_view_inside_locker_-_20140327_172806.jpg | file://x:/photopub/docs/0000000639/c3dbe3cd-8774-4cb3-b4c0-07da650161ab.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c59485ca_3c9e_402b_bb04_e7f532b90dab
ELIN-869713-2017 | EL-101995-2014 | 8/1/2017 7:38:01 AM | ASSESS: EL: Final | jpg | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Car_Charger_-_view_inside_locker_-_20140327_172806.jpg Locker enclosure being utilized for electrical bonding purposes does not appear to be approved electrical equipment. Approved electrical equipment would be tested for the purpose intended. Proper bonding methods help to maintain an equipotential plain and prevent dangerous potential (voltage) differences. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Car_Charger_-_view_inside_locker_-_20140327_172806.jpg | file://x:/photopub/docs/0000000639/4f38b37d-5a1a-4ffa-b097-92680070b949.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c59485ca_3c9e_402b_bb04_e7f532b90dab
GAIN-871195-2017 | GA-553806-2017 | 8/14/2017 10:56:39 AM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #CSST_bend.png Corrugated stainless steel tubing installed with tight bends beyond the manufacturers recommended radius. This could lead to damaged tubing the release of propane gas. | 3 | Code prohibited practices or materials | CSST_bend.png | file://x:/photopub/docs/0000000645/4658484e-42be-493a-8737-f52d878f5835.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2cc3054_ee33_41a9_88c4_dfabcdf8884a
GAIN-871195-2017 | GA-553806-2017 | 8/14/2017 10:56:39 AM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #CSST_bend.png Corrugated stainless steel tubing installed with tight bends beyond the manufacturers recommended radius. This could lead to damaged tubing the release of propane gas. | 3 | Code prohibited practices or materials | CSST_bend.png | file://x:/photopub/docs/0000000645/0c6ba976-5436-403c-a954-e6056b40fcb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2cc3054_ee33_41a9_88c4_dfabcdf8884a
EDIN-883377-2017 | ED-445071-2016 | 8/17/2017 | ASSESS: ED IN: Acceptance | png | #asFound Safety arm jammed | ED007 | Defects found where the required strength may no longer exist | 4 | 4 | #River_Bend_seniors_411061.png,River_Bend_seniors_411062.png Mechanical safeties on an elevator provide a safe stop for the passengers in the event of an overspeeding descending elevator car. During an acceptance inspection it was found the safeties functioned properly in the down direction, but did not release also the Speed governor did not function properly, centrifugal dawgs stuck in extended position. This would cause the safeties to operate erratically, potentially causing injury to passengers due to sudden stopping of the elevator. | 4 | Defects found where the required strength may no longer exist | River_Bend_seniors_411061.png | file://x:/photopub/docs/0000000649/06ac8ed3-fe28-4251-ada3-b1618385248b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__825db3a7_dd69_47ac_bd63_03217f1d2aea
EDIN-883377-2017 | ED-445071-2016 | 8/17/2017 | ASSESS: ED IN: Acceptance | png | #asFound Governor stuck in activated position | ED007 | Defects found where the required strength may no longer exist | 4 | 4 | #River_Bend_seniors_411061.png,River_Bend_seniors_411062.png Mechanical safeties on an elevator provide a safe stop for the passengers in the event of an overspeeding descending elevator car. During an acceptance inspection it was found the safeties functioned properly in the down direction, but did not release also the Speed governor did not function properly, centrifugal dawgs stuck in extended position. This would cause the safeties to operate erratically, potentially causing injury to passengers due to sudden stopping of the elevator. | 4 | Defects found where the required strength may no longer exist | River_Bend_seniors_411062.png | file://x:/photopub/docs/0000000649/3d8e3df1-0469-49bf-bbf0-021c17efe839.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__825db3a7_dd69_47ac_bd63_03217f1d2aea
GAIN-846916-2017 | GA-527402-2017 | 8/3/2017 10:05:37 AM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Combustion_air_inlet.png The as-found condition is that a mechanical air inlet serving a boiler is installed within 10 feet of a full-relief gas regulator. The potential hazard is that the regulator will release raw gas into the atmosphere which will be drawn into the boiler via the mechanical air inlet, causing poor combustion and the production of harmful emissions such as carbon monoxide | 3 | insufficient mechanical air intake clearance to gas regulator relief | Combustion_air_inlet.png | file://x:/photopub/docs/0000000640/5211116b-96d4-46ed-8821-d15ee446af97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8121c1c5_c9c6_45a5_a3f3_84b4fe01cb31
ELIN-881237-2017 | EL-571672-2017 | 8/16/2017 9:17:19 AM | ASSESS: EL: Service Connection | png | #asFound Photo showing that there are two openings where panel fillers are required at the bottom of the service entrance panel. | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Panel_fillers_.png Service connection for new single family dwelling. Two openings have no been closed in the service entrance panel in an open garage. Panel fillers are required to close the opens to make it safe after the service is connected. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_fillers_.png | file://x:/photopub/docs/0000000647/989cea6b-5737-40f2-be80-57f7a475beda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4ff2d32_4210_4a0f_b813_84afce030c17
ELIN-871469-2017 | EL-564324-2017 | 8/11/2017 8:57:26 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Need_GFCI.png This assessment found that receptacles located within 1.5m of the sink are not ground fault protected. This could result in a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Need_GFCI.png | file://x:/photopub/docs/0000000644/25c0f0a3-276e-4bdd-b3be-72904ac50843.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e71185c_91ae_4a8d_bde5_5f8b4593173d
ELIN-889750-2017 | EL-576390-2017 | 8/29/2017 3:57:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #32mm.png The code requires cables and wire be installed with a minimum Cables installed in wood construction should be protected with a minimum of 32 mm of wood or approved steel protection plates.This protects the cables from being damaged during the instalation of wall finishes.During the inspection it was observed that cables had not been installed with adequate protection.this presents a possible shock hazard to the installer of the wall finishes and or a short circuit that could cause a fire.12-616 | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 32mm.png | file://x:/photopub/docs/0000000654/5fbd5b36-43ce-48f0-9259-f433728d8b50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac724205_e1f6_4139_8041_df595d48c8d0
ELIN-881821-2017 | EL-570838-2017 | 8/22/2017 1:57:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Conductors_.png Service conductors not protected from mechanical damage. These conductors are unprotected from utility and have higher risk of arcing if carpenter/drywallers were to put a nail through. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Conductors_.png | file://x:/photopub/docs/0000000650/b696a87e-9b98-415d-a5b1-4d6647ec0cbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b2e7957_bdf9_4cd4_8bb6_1af8ad1298ba
ELIN-875065-2017 | EL-452950-2016 | 8/8/2017 3:00:00 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Copper_water_lines.png In a new commercial micro brewery installation with a 600volt 100amp main service, exposed copper water lines were found not to have bonding provided. This could result in a shock hazard situation. Picture attached. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Copper_water_lines.png | file://x:/photopub/docs/0000000643/22aa0c89-8bdc-4091-9516-51679b11a2cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfd9ee56_c488_41d2_8328_a9b8ab8593c4
GAIN-831513-2017 | GA-543469-2017 | 8/1/2017 2:32:09 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #Water_heater.png The as-found condition is that a water heater has been installed without a combustion air supply. The potential hazard is that the water heater will not have enough air supply for proper combustion, resulting in the production of harmful emissions such as carbon monoxide, that pose a threat to human health. | 4 | Combustion air supply missing | Water_heater.png | file://x:/photopub/docs/0000000639/f1642c76-7783-4ec0-86b6-a5676077aacb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96e24cc6_f981_405e_82c1_b4abd59999ac
ELIN-883943-2017 | UW-540678-2017 | 8/17/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #Triplex_into_mobile_home.png Overhead secondary feeder conductors supplying mobile home installed on home made pole line and run directly into the mobile home service equipment Overhead secondary feeder conductors supplying mobile home installed on home made pole line and run directly into the mobile home service equipment | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Triplex_into_mobile_home.png | file://x:/photopub/docs/0000000648/aa136371-5304-4c27-9104-360a3d1c3b1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb314481_ffa5_43f3_a26f_28d33c1290bc
ELIN-869039-2017 | EL-512489-2017 | 8/3/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #REceptacle_behind_sink_location1.png,REceptacle_behind_sink_location2.png Receptacles in dwelling units are prohibited from areas behind and directly in front of the kitchen sink because the receptacles are subject to water splashing. Other water-related hazards include the risk of attachment cords lying or falling in the water or attachment plugs being inserted and removed by people with wet hands. During a rough wire assessment for a new basement suite in an existing family dwelling, a device box was observed directly over the drain pipe for the future kitchen sink. The owner of the dwelling confirmed that this was the location of the new sink. Once work was completed in the kitchen and this receptacle was energized, there would a potential shock hazard for persons using this device. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | REceptacle_behind_sink_location1.png | file://x:/photopub/docs/0000000642/4a17b485-4b8b-4bd2-831a-cc57e9b56453.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a21d6a6_dacc_4013_8b06_eaf907541ca8
ELIN-869039-2017 | EL-512489-2017 | 8/3/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #REceptacle_behind_sink_location1.png,REceptacle_behind_sink_location2.png Receptacles in dwelling units are prohibited from areas behind and directly in front of the kitchen sink because the receptacles are subject to water splashing. Other water-related hazards include the risk of attachment cords lying or falling in the water or attachment plugs being inserted and removed by people with wet hands. During a rough wire assessment for a new basement suite in an existing family dwelling, a device box was observed directly over the drain pipe for the future kitchen sink. The owner of the dwelling confirmed that this was the location of the new sink. Once work was completed in the kitchen and this receptacle was energized, there would a potential shock hazard for persons using this device. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | REceptacle_behind_sink_location2.png | file://x:/photopub/docs/0000000642/6d896bbb-3898-4728-a177-8568a8cf2921.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a21d6a6_dacc_4013_8b06_eaf907541ca8
ELIN-867103-2017 | EL-467066-2016 | 8/4/2017 4:43:52 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacles_not_on_AFCI_protection1.png,Receptacles_not_on_AFCI_protection2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation for new bedrooms and a family area in an existing single family dwelling, one receptacles in the bedroom and two receptacles in the common area were installed without arc-fault protection. If a series or parallel arc was to occur in one of the unprotected branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacles_not_on_AFCI_protection1.png | file://x:/photopub/docs/0000000642/89e2ed7b-62f0-489e-90c3-b62eb437b756.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58611389_8071_4980_9b92_d0a880c14427
ELIN-867103-2017 | EL-467066-2016 | 8/4/2017 4:43:52 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacles_not_on_AFCI_protection1.png,Receptacles_not_on_AFCI_protection2.png Arc-fault protection is required on new branch circuits for receptacles 20 amps or less installed in residential dwellings. An arc-fault device recognizes both series and parallel arc faults and de-energizing the circuit when an arc -fault is detected. In this installation for new bedrooms and a family area in an existing single family dwelling, one receptacles in the bedroom and two receptacles in the common area were installed without arc-fault protection. If a series or parallel arc was to occur in one of the unprotected branch circuits, the circuit may not de-energize. The arc produced in the branch circuit may reach temperatures high enough to create a fire or smoke hazard to persons and property. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacles_not_on_AFCI_protection2.png | file://x:/photopub/docs/0000000642/7a2d118d-f978-4a61-9bd3-367c089a6cd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58611389_8071_4980_9b92_d0a880c14427
EDOP-800079-2017 | ED -0000326336-2015 | 8/24/2017 1:07:34 PM | ASSESS: ED OP: RAP | png | #asFound | ED009 | Defects that are: Detected by Maintenance program Likely to progress | 2 | 2 | #Emergency_light.png Alarm bell and emergency light not working | 2 | Defects that are: Detected by Maintenance program Likely to progress | Emergency_light.png | file://x:/photopub/docs/0000000651/5a3b21d4-3ec3-4f65-ba3a-51d07ea07cfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08CD7EC1_4AAC_42A9_AFF7_07A0AE5CB901
EDOP-804931-2017 | 2050527 | 8/24/2017 11:22:20 AM | ASSESS: ED OP: RAP | png | #asFound | ED009 | Defects that are: Detected by Maintenance program Likely to progress | 2 | 2 | #Emergency_light_and_stop_switch1.png,Emergency_light_and_stop_switch2.png Emergency light broken / stop switch broken | 2 | Defects that are: Detected by Maintenance program Likely to progress | Emergency_light_and_stop_switch2.png | file://x:/photopub/docs/0000000651/a57782b6-7a98-4e69-99af-52c8c45f9f77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EF967BF1_0D55_4A5F_8EE5_CD11D2939363
EDIN-873625-2017 | ED-483687-2016 | 8/4/2017 7:37:57 PM | ASSESS: ED IN: Construction Use | png | #asFound Cutouts in the fascia | ED010 | Small Defects that are: Detected by maintenance program Unlikely to progress | 1 | 1 | #Fascia_1.png Cutouts in the fascia | 1 | Small Defects that are: Detected by maintenance program Unlikely to progress | Fascia_1.png | file://x:/photopub/docs/0000000641/b63f5040-e8e0-44f0-b64c-03aeb70d0c38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89facd2f_88d8_47e1_82a0_4aba6c47717d
ELIN-872473-2017 | EL-352056-2016 | 8/8/2017 8:24:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Space_required_1.png,Space_required_2.png,Space_required_3.png This assessment found that cables are installed without the 25mm space between heating ducts and conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Space_required_2.png | file://x:/photopub/docs/0000000642/ebd7361b-d23f-4073-a82d-4e1b02c2a476.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__946749ac_672f_471d_a116_2fcb34490535
ELIN-872473-2017 | EL-352056-2016 | 8/8/2017 8:24:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Space_required_1.png,Space_required_2.png,Space_required_3.png This assessment found that cables are installed without the 25mm space between heating ducts and conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Space_required_3.png | file://x:/photopub/docs/0000000642/be791796-3237-4311-ad3a-897fbba1ff50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__946749ac_672f_471d_a116_2fcb34490535
ELIN-872473-2017 | EL-352056-2016 | 8/8/2017 8:24:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Space_required_1.png,Space_required_2.png,Space_required_3.png This assessment found that cables are installed without the 25mm space between heating ducts and conductors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Space_required_1.png | file://x:/photopub/docs/0000000642/2f953d95-cf15-4761-9643-8130774e7461.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__946749ac_672f_471d_a116_2fcb34490535
ELIN-868463-2017 | EL-518871-2017 | 8/1/2017 11:42:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMD90_1.png,NMD90_2.png Two 120 volt 15 & 20 amp non metallic sheathed cables have been installed in an underground plumbing pipe which also has a Hot and cold water line installed inside of it. The wiring is not rated to be installed underground or in contact with hot water lines, this could lead to failure of the wire's protective jacket and insulation, resulting in a possible shock hazard to persons and equipment failure. | 3 | Conductors Equipment is not approved for the specific use. | NMD90_2.png | file://x:/photopub/docs/0000000639/24918633-8fa7-4b3f-903d-8dcfc993aba7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d58af39_353e_40a2_be72_855b2c9a2d3d
ELIN-871426-2017 | EL-566631-2017 | 8/16/2017 3:27:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Pump_service_panel1.png,Pump_service_panel2.png The 100 amp 120/240 volt pole mounted weather-proof lockable (unlocked) service is de-energized awaiting service connection but is missing 2 breaker filler plates. Once this service is connected and the issue has not been corrected this can become a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Pump_service_panel2.png | file://x:/photopub/docs/0000000647/fec946a7-de17-469a-8bd1-8ccabd6959f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0d253dd_655a_434c_bcc8_8d430acf42b3
ELIN-871426-2017 | EL-566631-2017 | 8/16/2017 3:27:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Pump_service_panel1.png,Pump_service_panel2.png The 100 amp 120/240 volt pole mounted weather-proof lockable (unlocked) service is de-energized awaiting service connection but is missing 2 breaker filler plates. Once this service is connected and the issue has not been corrected this can become a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Pump_service_panel1.png | file://x:/photopub/docs/0000000647/5434466b-0d00-4ce5-82ab-3cc257ecc4ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0d253dd_655a_434c_bcc8_8d430acf42b3
ELIN-882354-2017 | EL-545237-2017 | 8/17/2017 10:02:24 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | #Consumer_service_conductor_without_mechanical_protection1.png,Consumer_service_conductor_without_mechanical_protection2.png In a new single family dwelling the 200 amp 240 volt consumer service conductor cable was found not to have adequate mechanical protection. This could result in an equipment damage condition. Picture attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Consumer_service_conductor_without_mechanical_protection1.png | file://x:/photopub/docs/0000000647/7a3fe02d-408a-4786-a823-02131b81c062.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e53d0d_b7df_47f8_a4bb_bac4018b494e
ELIN-882354-2017 | EL-545237-2017 | 8/17/2017 10:02:24 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | #Consumer_service_conductor_without_mechanical_protection1.png,Consumer_service_conductor_without_mechanical_protection2.png In a new single family dwelling the 200 amp 240 volt consumer service conductor cable was found not to have adequate mechanical protection. This could result in an equipment damage condition. Picture attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Consumer_service_conductor_without_mechanical_protection2.png | file://x:/photopub/docs/0000000647/813c46fc-489f-4d75-aa81-224e5eac2763.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e53d0d_b7df_47f8_a4bb_bac4018b494e
BPVOP-879529-2017 | 2297443 | 8/18/2017 12:08:02 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #ASME_plate_and_PRD1.png,ASME_plate_and_PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and no NDT was performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety order not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | ASME_plate_and_PRD2.png | file://x:/photopub/docs/0000000648/36a75068-e755-4f7f-9e84-1c46db892c7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__199a1c80_903d_4129_9629_1365b1a31ecd
BPVOP-879529-2017 | 2297443 | 8/18/2017 12:08:02 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #ASME_plate_and_PRD1.png,ASME_plate_and_PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and no NDT was performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety order not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | ASME_plate_and_PRD1.png | file://x:/photopub/docs/0000000648/b0ef1ef7-2bd6-4127-beeb-becb43818d74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__199a1c80_903d_4129_9629_1365b1a31ecd
BPVOP-705434-2016 | 4006595 | 8/15/2017 4:36:41 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP114 | 3.0.1 Safeties will not function - Pressure Relief Device valve nameplate not legible, and not traceable | 3 | 3 | #PRD1.png,PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device with no markings. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device valve nameplate not legible, and not traceable | PRD2.png | file://x:/photopub/docs/0000000647/8882a0c0-af72-4f0d-9b3b-f10a6a61ec0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff6f500b_0209_4471_aa0e_2bf6aca76b59
ELIN-875749-2017 | EL-554104-2017 | 8/17/2017 | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Main_distribution_mounted_on_pole.png Distribution panel for permanent installation has been mounted on pole. Distribution equipment for a residence must be located in the building being served. This allows for proper operation and access in case of emergency. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Main_distribution_mounted_on_pole.png | file://x:/photopub/docs/0000000648/60e1a4de-d457-4e44-b421-07e2a1ee84b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76b4b160_2bd0_4ba1_b8a7_6e27858cdfb4
ELIN-871067-2017 | EL-566647-2017 | 8/17/2017 1:18:21 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Flexible_cord_used_as_permanent_wiring.png 15 amp, 120 volt branch circuit has flexible cord used as permanent wiring. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Flexible_cord_used_as_permanent_wiring.png | file://x:/photopub/docs/0000000648/1b10b4f1-32ad-47e8-afdf-b553cc3ccd6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1729968_02cc_4e23_bbac_2d6f539d967b
ELIN-871068-2017 | EL-556426-2017 | 8/17/2017 1:38:44 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Flexible_cord_running_thru_wall.png Flexible cord used on 15 amp, 120 volt branch circuit for permanent wiring. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Flexible_cord_running_thru_wall.png | file://x:/photopub/docs/0000000648/126ac279-821a-4881-a9f1-7ca6fffe314d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19486dbb_313b_4fdc_9c9d_ed34507d275b
BPVOP-705434-2016 | 4006595 | 8/15/2017 4:36:41 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP114 | 3.0.1 Safeties will not function - Pressure Relief Device valve nameplate not legible, and not traceable | 3 | 3 | #PRD1.png,PRD2.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device with no markings. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device valve nameplate not legible, and not traceable | PRD1.png | file://x:/photopub/docs/0000000647/b74b8694-3f82-471b-adfb-663103e4cefd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff6f500b_0209_4471_aa0e_2bf6aca76b59
EDOP-897398-2017 | 2044207 | 8/31/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | #Elevator_pit.png A clean and dry pit provides a safe running elevator for passengers. During a regular inspection it was found that an elevator pit was full of water mixed with oil/debris. This could cause a fire hazard and affect components are operation making it unsafe for passengers riding the elevator. | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Elevator_pit.png | file://x:/photopub/docs/0000000657/8f581f24-1ab7-465a-af73-8615d03a657f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__372cc780_cf92_46ca_b41d_fedf73202237
ELIN-865132-2017 | EL-562587-2017 | 8/15/2017 3:41:08 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | #Microwave.png In an existing modular home , a 120volt 15amp built-in microwave unit was found connected to the area lighting circuit. This can lead to a "Thermal Effect" condition. Pic attached. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Microwave.png | file://x:/photopub/docs/0000000646/1140e866-1e56-40f8-b3cc-dca411454663.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__296b43a6_9190_4e01_af08_4f52636cadb9
GAIN-894287-2017 | GA-427757-2016 | 8/29/2017 3:06:55 PM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 2 | #E_and_S.png Small peach fuzz fuel leak on control valve serving gas furnace. Risk of fire if lower explosive limits and source of ignition was to occur. Leak found by GSO at shut off at valve. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | E_and_S.png | file://x:/photopub/docs/0000000654/dab0eab8-9289-4ec1-830e-1ddb48bb3634.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9da48340_cdb2_4b5d_8416_1e52498ee150
ELIN-888571-2017 | EL-574731-2017 | 8/28/2017 12:58:17 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | #Missing_receptacle.png This assessment found that a receptacle has not been provided for 1m from a bathroom sink, creating a shock hazard to run extension cords. | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Missing_receptacle.png | file://x:/photopub/docs/0000000653/f81caa8c-3f0e-405a-a719-5afe7effa236.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78841b2b_9e6a_4617_aee2_f224b53ae34a
ELIN-889336-2017 | EL-515067-2017 | 8/28/2017 12:09:30 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Incomplete_outlet_boxes1.png,Incomplete_outlet_boxes2.png General lighting and receptacle outlets are incomplete. This could be a potential shock hazard to people if they were to touch potentially live wires located within these outlets. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Incomplete_outlet_boxes2.png | file://x:/photopub/docs/0000000653/96f309f2-1d8d-451f-9190-3d65a3ccb8bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc947f33_db2f_40d5_b1e8_bb0d3f62a25d
ELIN-889336-2017 | EL-515067-2017 | 8/28/2017 12:09:30 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Incomplete_outlet_boxes1.png,Incomplete_outlet_boxes2.png General lighting and receptacle outlets are incomplete. This could be a potential shock hazard to people if they were to touch potentially live wires located within these outlets. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Incomplete_outlet_boxes1.png | file://x:/photopub/docs/0000000653/2111437f-dd4a-4f68-b440-362db2a36e6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc947f33_db2f_40d5_b1e8_bb0d3f62a25d
ELIN-890325-2017 | EL-371858-2016 | 8/29/2017 12:05:54 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #No_afci_new_dwelling.png In a new dwelling six branch circuits which feed standard receptacle equipment have not been provided arc fault current interruption. These receptacles which operate at 15 A or 20 amps and 120 V when not properly protected can lead to property damage or injury to persons. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_afci_new_dwelling.png | file://x:/photopub/docs/0000000654/f3f3c3be-ccf6-447a-acff-f3e5b0f95a24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86b59f23_3d3b_461e_8d61_5e41c8c93cf1
ELIN-891058-2017 | EL-572016-2017 | 8/29/2017 10:10:00 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | #No_ceing_fan_rated_boxes.png A 15 amp 120 V receptacle was provided on an upper floor deck and a new residential dwelling. This receptacle was connected to the grade level receptacles which are supposed to be on their own circuit so they provide robust power for electrical equipment typically used outdoors for gardening and yard maintenance. When an upper floor receptacle or other devices are connected to the circuit circuit becomes less robust and less likely to function as required for use in the dwelling this can lead to overloading of the exterior branch circuit causing potential for damage to property | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | No_ceing_fan_rated_boxes.png | file://x:/photopub/docs/0000000654/911c390d-c9cf-4162-9eea-3b668e748972.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c3a36d3_bd55_4734_a9df_0a0f41a247f4
ELIN-870438-2017 | EL-477088-2016 | 9/6/2017 11:04:27 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #2_service_panels1.png,2_service_panels2.png A new residential home built with a basement suite includes a 200 amp service for main residence and a 100 amp service for the suite. In both services there are 15 amp 120 volt branch circuits and outlets that do not include any AFCI protection as required, this can lead to a Thermal hazard | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 2_service_panels1.png | file://x:/photopub/docs/0000000658/7565e448-6f01-484b-8685-d0ab6b7008b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0329652d_745f_49d2_a7d3_b64e5bd636bc
ELIN-870438-2017 | EL-477088-2016 | 9/6/2017 11:04:27 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #2_service_panels1.png,2_service_panels2.png A new residential home built with a basement suite includes a 200 amp service for main residence and a 100 amp service for the suite. In both services there are 15 amp 120 volt branch circuits and outlets that do not include any AFCI protection as required, this can lead to a Thermal hazard | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 2_service_panels2.png | file://x:/photopub/docs/0000000658/cd7883df-f938-416f-bb38-775b3bd5c0f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0329652d_745f_49d2_a7d3_b64e5bd636bc
ELIN-881595-2017 | EL-550580-2017 | 8/28/2017 3:14:44 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Bond_connection.png In an existing modular home, the 100amp 120/240volt electrical distribution equipment system does not effectively bond to the unit chassis. This can lead to a "Shock" scenario. Pic attached. | 3 | Continuity Bonding; method for equipment is not adequate. | Bond_connection.png | file://x:/photopub/docs/0000000653/a312b38d-49c4-4eb0-b428-71478c93d812.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65238e7a_a093_435f_9c7c_93642d7e8ac6
BPVIN-894246-2017 | BPV-545537-2017 | 9/1/2017 2:41:36 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnects.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. Potential exists for an incident due to no lockable disconnects. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnects.png | file://x:/photopub/docs/0000000656/817bfade-50d4-4306-a585-4fc3220c1036.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db0438f6_1183_4bf7_abc5_93a7c78975f5
ELIN-880233-2017 | UW-571120-2017 | 8/14/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Electrical_Panel1.png,Electrical_Panel2.png,Electrical_Panel3.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 70A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Electrical_Panel1.png | file://x:/photopub/docs/0000000647/1ee66f0b-c1bf-48b9-b3b3-b0c075135736.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d46e1e8f_e165_43de_ae06_e3dfd37037fb
ELIN-880233-2017 | UW-571120-2017 | 8/14/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Electrical_Panel1.png,Electrical_Panel2.png,Electrical_Panel3.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 70A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Electrical_Panel2.png | file://x:/photopub/docs/0000000647/26669559-5bb7-4d55-8688-a39547f56828.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d46e1e8f_e165_43de_ae06_e3dfd37037fb
ELIN-880233-2017 | UW-571120-2017 | 8/14/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Electrical_Panel1.png,Electrical_Panel2.png,Electrical_Panel3.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 70A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Electrical_Panel3.png | file://x:/photopub/docs/0000000647/04d0537d-25cf-42c4-99bb-a4240653cc69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d46e1e8f_e165_43de_ae06_e3dfd37037fb
BPVOP-888581-2017 | 2295816 | 8/24/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_Relief_Device_-_Air_Receiver.png The pressure relief device provides over pressure protection to the air receiver. Overtime the pressure relief device may fail to operate (seize shut) as an example. In such a case the air receiver may fail or burst if it encounters a overpressure situation. Annual testing and replacing the pressure relief device on a fixed time basis will help to eliminate the potential of the device from failing. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_Relief_Device_-_Air_Receiver.png | file://x:/photopub/docs/0000000651/0be77b25-217b-4098-bebe-7fae2c3e377c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fa8d766_70ad_41ef_af89_2ec6140f467e
ELIN-887498-2017 | EL-551575-2017 | 8/24/2017 2:57:50 PM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_installed.png Imported electrical equipment has been installed and does not bear a mark of approval for use in the province. Unapproved equipment poses a risk of fire and shock to persons and property, unapproved equipment may not function or provide safety measures required to ensure safe operation. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_installed.png | file://x:/photopub/docs/0000000651/cf3fd928-e444-4b8c-b300-41074106dc87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf695ebc_3565_43a8_8c4b_70a62b581f7f
BPVOP-900780-2017 | BPV-100651-2014 | 9/5/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound Lifted pre-maturely at 130 psi. Valve set pressure is 150 psi. Valve replaced with one rebuild by B&B Valves. | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #As_found_Safety_Valve.png Safety valve lifted at a pre-mature pressure setting of 130 psi and failed to close. If this boiler is inservice and the safety valve lifted and did not re-close an added load would be created on the boiler combustion system which could lead to an over-firing event. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | As_found_Safety_Valve.png | file://x:/photopub/docs/0000000658/d427dc6e-8328-4f3c-af66-4c3e873cb7c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44bb49ef_1920_48bf_9f7b_78bed35e9681
BPVOP-900307-2017 | 2269732 | 9/5/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Boiler_relief_valve1.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Boiler_relief_valve1.png | file://x:/photopub/docs/0000000658/0079eff8-7e86-451c-bd07-003c13d51c91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75c8bc53_f5f1_4630_87ef_dd31eae15918
BPVOP-900294-2017 | 2301308 | 9/5/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Boiler_relief_valve2.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Boiler_relief_valve2.png | file://x:/photopub/docs/0000000658/d3a7f0e4-dedc-4e39-aec7-6b11f94a93cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae1c01ec_e974_4a6d_b549_bb8a95c99176
BPVOP-901081-2017 | 2270267 | 9/5/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Relief_valve.png All pressure relief devices require periodic inspection, testing and service. I found no records of service or replacement of relief valve on this hot water boiler. Potential exists for a relief valve not functioning properly in a critical situation due to being inadequately serviced/replaced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Relief_valve.png | file://x:/photopub/docs/0000000658/65d368c1-c6b2-4567-9466-0701d5c2edd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4aabaffd_41e7_4ca9_9316_15b34af7f58a
ELIN-881593-2017 | UW-571802-2017 | 8/16/2017 1:04:13 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Cable_with_recently_downed_tree_one_of_two_locations.png An armoured cable operating at 120 volts and 15 amps was installed to provide power to a communications tower in a forest. The cable was found laying on a driveway, not buried and run through a tinder dry field and forest for approximately 600 meters. Damage to the cable had already been sustained in two locations due to downed trees on this cable. When cables are not properly buried or other wise protected from damage injury to persons or in this case the potential for a forest interface fire are a real potential | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_with_recently_downed_tree_one_of_two_locations.png | file://x:/photopub/docs/0000000647/7b882e31-908c-4969-906f-3cb5a51fbc44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d958b90e_5141_4bc1_b307_400ce5900450
GAHE-888748-2017 | HE-575846-2017 | 8/25/2017 8:51:29 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA080 | Line pressure regulator without required overpressure protection in place | 3 | 3 | #OARA.png 10 psi gas supplied to a system regulator rated for a 2 psi inlet pressure. Downstream pressure on regulator would exceed maximum safe inlet pressure of installed appliances. Risk of fire and damage to downstream components resulting in over fire condition and the production of carbon monoxide. | 3 | Line pressure regulator without required overpressure protection in place | OARA.png | file://x:/photopub/docs/0000000652/d4afb058-920d-47e6-b3eb-615e49e8b3ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9833e375_10b4_42cd_b8ff_e7c0dd2da6d7
GAHE-888535-2017 | HE-575613-2017 | 8/24/2017 2:59:30 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Kitchener.png Small fuel leak on flare fitting.(peach fuzz) Risk of fire should source of ignition be present. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Kitchener.png | file://x:/photopub/docs/0000000652/092f6d38-730c-4d3b-8ae2-734f0343a057.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c21496b_2dd6_459e_ae51_7968368af1da
EDRI-905935-2017 | ED-544833-2017 | 9/12/2017 9:38:09 AM | ASSESS: ED RI: Extension | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Missing_handrails1.png,Missing_handrails2.png,Missing_handrails3.png,Missing_handrails4.png Handrails have been removed from the hoist deck and been left off. This is a 20" difference between levels where a worker could fall or trip and become injured. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Missing_handrails1.png | file://x:/photopub/docs/0000000661/78a4d7e7-851d-45f1-876c-3ed3ecfb786c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b02eecf8_a677_4d75_bb66_a03fc8593b52
EDRI-905935-2017 | ED-544833-2017 | 9/12/2017 9:38:09 AM | ASSESS: ED RI: Extension | png | #asFound Handrail removed from ramp. 20" Rise. | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Missing_handrails1.png,Missing_handrails2.png,Missing_handrails3.png,Missing_handrails4.png Handrails have been removed from the hoist deck and been left off. This is a 20" difference between levels where a worker could fall or trip and become injured. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Missing_handrails3.png | file://x:/photopub/docs/0000000661/247499e3-33a6-4428-8605-44a0d382f7d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b02eecf8_a677_4d75_bb66_a03fc8593b52
EDRI-905935-2017 | ED-544833-2017 | 9/12/2017 9:38:09 AM | ASSESS: ED RI: Extension | png | #asFound Handrail removed from ramp, also being used to access door to building. | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Missing_handrails1.png,Missing_handrails2.png,Missing_handrails3.png,Missing_handrails4.png Handrails have been removed from the hoist deck and been left off. This is a 20" difference between levels where a worker could fall or trip and become injured. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Missing_handrails4.png | file://x:/photopub/docs/0000000661/22f4e29c-0941-4cff-ac2a-2ac8a482dee2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b02eecf8_a677_4d75_bb66_a03fc8593b52
EDRI-905935-2017 | ED-544833-2017 | 9/12/2017 9:38:09 AM | ASSESS: ED RI: Extension | png | #asFound Handrail removed to access door from hoist deck. 18" from door to deck. | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Missing_handrails1.png,Missing_handrails2.png,Missing_handrails3.png,Missing_handrails4.png Handrails have been removed from the hoist deck and been left off. This is a 20" difference between levels where a worker could fall or trip and become injured. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Missing_handrails2.png | file://x:/photopub/docs/0000000661/256a2050-5b04-4943-bdce-4349f4ed6f9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b02eecf8_a677_4d75_bb66_a03fc8593b52
ELIN-903089-2017 | EL-552514-2017 | 9/8/2017 7:41:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #One_of_2_panel_boards_no_lockable_covers.png Temporary connection to 2 panel boards in a new residential building was authorized by an electrical contractor for a 200 and a 100 amp 240 volt panel boards. The panels were left accessible to unauthorized operation in an area with neighbouring residences. Persons may interfere with this equipment causing a potential for injury to persons or damage to structures | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | One_of_2_panel_boards_no_lockable_covers.png | file://x:/photopub/docs/0000000660/31537af6-9b50-4612-ae57-e7b490d7b87f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8267e30_8b3f_4c8b_9cbb_dc8a37d52ffb
ELIN-903861-2017 | EL-582823-2017 | 9/11/2017 2:27:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Outlet_boxes_over_100mm_1_support1.png,Outlet_boxes_over_100mm_1_support2.png The larger electrical device boxes are not adequately supported and may be subject to breakage and exposed electrical parts creating a shock hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Outlet_boxes_over_100mm_1_support1.png | file://x:/photopub/docs/0000000660/7dcffaee-8c11-4a0d-884d-925e6011ded3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe95dcf6_a163_4d2c_8006_9e96cd00c04e
EDIN-885532-2017 | ED-484440-2016 | 8/22/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED000 | No Created Hazard Identified | 0 | 0 | #As_found1.png,As_found2.png | 0 | No Created Hazard Identified | As_found1.png | file://x:/photopub/docs/0000000652/1c6b206e-0c65-4c57-a986-f3410aae638f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e18472fb_5a43_4945_acab_7b1b5c912dcb
EDIN-885532-2017 | ED-484440-2016 | 8/22/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED000 | No Created Hazard Identified | 0 | 0 | #As_found1.png,As_found2.png | 0 | No Created Hazard Identified | As_found2.png | file://x:/photopub/docs/0000000652/0188eb0c-1516-41a6-9d39-6cc5fe163e2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e18472fb_5a43_4945_acab_7b1b5c912dcb
ELIN-869607-2017 | EL-535072-2017 | 8/1/2017 10:18:18 AM | ASSESS: EL: Final | png | #asFound Only one arc fault breaker has been installed. | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #One_arc_fault.png Renovation to existing dwelling consisting of three floors in the rear middle. Arc fault circuit interrupters have not been installed where they are required. This means that there is no arc fault protection for the new circuits of receptacles. Possible fire hazard if there is a wiring fault. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | One_arc_fault.png | file://x:/photopub/docs/0000000639/0953578f-b0e3-4cfa-93b4-748087716c07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac3f14e2_c0af_43df_98c1_aefa13477b03
EDIN-903886-2017 | ED-483084-2016 | 9/8/2017 9:46:42 PM | ASSESS: ED IN: Construction Use | png | #asFound Construction material being stored at elevator lobby | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Obstruction.png Construction materials located at elevator lobby causing safe egress and ingress to and from the elevator. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Obstruction.png | file://x:/photopub/docs/0000000660/e817c2b9-fc87-480b-bf64-d7595047d2cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb9275a8_5609_4a94_832f_fc548457f251
GAUP-887152-2017 | UW-574833-2017 | 8/23/2017 12:07:08 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_vent.png Common venting used to vent flue gases of Furnace and Water Heater. Common vent is 6 inches in diameter. Furnace venting has been removed from common vent leaving a 4 inch vent connected to 6 inch common vent. Venting of the hot water heater is now oversized and under certain conditions flue gases could cool down too quickly inside vent and spill through draft hood of water heater into home possibly causing CO poisoning to occupants | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_vent.png | file://x:/photopub/docs/0000000650/22c329bc-bb47-4e64-91a9-80527b954af3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__391cb561_337e_40a5_8d61_7e6781aefe6a
ELIN-872704-2017 | EL-541188-2017 | 8/8/2017 4:23:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #PVC_Service_conduit_inside_wall1.png,PVC_Service_conduit_inside_wall2.png The BC electrical code requires PVC conduit inside a wall for supply service conductors to be mechanically protected if subject to damage and not to be installed were the the conduit will be covered with thermal insulation. BC Hydro requires underground supply conduits inside a wall for a residential service to be encased in a minimum of 50mm of concrete. During an assessment for a rough-wire inspection of a new single family dwelling, the 3" PVC conduit for the supply service was found in an exterior wall against the exterior sheathing. The service was energized and there was no mechanical protection for this conduit. When the exterior siding is installed on this dwelling, there is the potential for a nail or screw to puncture this conduit and damage the energized service cables. A fault condition on the service cables could create a potential fire hazard inside the dwelling or damage electrical equipment connected to this service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | PVC_Service_conduit_inside_wall2.png | file://x:/photopub/docs/0000000644/3531b872-c8b0-4c30-85a8-41b71d4d7be3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93823568_0e20_44c2_b0b9_b8dceaff78c9
ELIN-872704-2017 | EL-541188-2017 | 8/8/2017 4:23:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #PVC_Service_conduit_inside_wall1.png,PVC_Service_conduit_inside_wall2.png The BC electrical code requires PVC conduit inside a wall for supply service conductors to be mechanically protected if subject to damage and not to be installed were the the conduit will be covered with thermal insulation. BC Hydro requires underground supply conduits inside a wall for a residential service to be encased in a minimum of 50mm of concrete. During an assessment for a rough-wire inspection of a new single family dwelling, the 3" PVC conduit for the supply service was found in an exterior wall against the exterior sheathing. The service was energized and there was no mechanical protection for this conduit. When the exterior siding is installed on this dwelling, there is the potential for a nail or screw to puncture this conduit and damage the energized service cables. A fault condition on the service cables could create a potential fire hazard inside the dwelling or damage electrical equipment connected to this service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | PVC_Service_conduit_inside_wall1.png | file://x:/photopub/docs/0000000644/ca2401f9-0851-47e6-be3c-7ff4ec2cd4a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93823568_0e20_44c2_b0b9_b8dceaff78c9
BPVIN-874217-2017 | BPV-568322-2017 | 8/14/2017 10:06:39 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound PSV | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PSVa.png There are no records available to determine when the relief valve was last serviced. Failure to service relief valves at the appropriate interval could lead to valve malfunction and possible overpressure and failure of the pressure vessel in the event of an overpressure situation. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PSVa.png | file://x:/photopub/docs/0000000646/3b2cc261-f00d-4ae4-8f9b-410665a916a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3a77a43_a6e4_4cdd_b5e3_7f27dd7f7385
BPVIN-871803-2017 | BPV-086465-2014 | 8/16/2017 11:36:48 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP112 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping under size | 3 | 3 | #Pressure_Relief_Valve.png The pressure relief valve discharge pipe cross sectional area must be equal to the pressure relief valve outlet area. By installing a discharge pipe with a smaller area than what is required will reduce the relieving capacity of the pressure relief valve and may cause the system pressure to increase instead and ultimately lead to pressure vessel failure / rupture. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping under size | Pressure_Relief_Valve.png | file://x:/photopub/docs/0000000647/26cd4a6b-aa54-4233-a9fa-f6d5528e7e5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f45f9f8c_e755_47c7_82cf_0ed268925888
GAWP-882706-2017 | GA-570412-2017 | 8/17/2017 12:23:07 PM | ASSESS: GA Work In Progress | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Regulator.png Regulator relief terminates too close to a mechanical air intake. If the regulator was to relieve gas, it could be drawn into the gas appliance causing an explosion or fire. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulator.png | file://x:/photopub/docs/0000000647/cd46bca8-9b71-41b6-a4a8-1733c9b40a95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c773399_5da1_4975_927f_709a3305e514
ELIN-872929-2017 | EL-534704-2017 | 8/4/2017 2:14:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_panel_covers1.png,Missing_panel_covers2.png,Missing_panel_covers3.png - 3 electrical panels located in house were missing there panel cover leaving exposed electrical buss. If service was connected by utility these panels would become live and present shock risk to all trades people working on project. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_panel_covers1.png | file://x:/photopub/docs/0000000642/95593c0c-d2a0-4a76-b650-e6300edf8463.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d39d46f_1196_4f19_8286_b71d5a64e9d2
ELIN-872929-2017 | EL-534704-2017 | 8/4/2017 2:14:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_panel_covers1.png,Missing_panel_covers2.png,Missing_panel_covers3.png - 3 electrical panels located in house were missing there panel cover leaving exposed electrical buss. If service was connected by utility these panels would become live and present shock risk to all trades people working on project. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_panel_covers3.png | file://x:/photopub/docs/0000000642/4dab7ca7-c191-4cb9-91bd-85f6ae8ed312.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d39d46f_1196_4f19_8286_b71d5a64e9d2
ELIN-872929-2017 | EL-534704-2017 | 8/4/2017 2:14:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_panel_covers1.png,Missing_panel_covers2.png,Missing_panel_covers3.png - 3 electrical panels located in house were missing there panel cover leaving exposed electrical buss. If service was connected by utility these panels would become live and present shock risk to all trades people working on project. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_panel_covers2.png | file://x:/photopub/docs/0000000642/7fb60203-4360-47f9-96c4-3b72dede0eda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d39d46f_1196_4f19_8286_b71d5a64e9d2
ELIN-876141-2017 | EL-561709-2017 | 8/30/2017 8:34:07 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Temp_wiring.png - unapproved cords used to energize branch circuits with no all connections exposed to public. Connections could easily become loose causing possible shock risk or arcing and fire risk. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Temp_wiring.png | file://x:/photopub/docs/0000000654/b37173a0-5a8c-47e2-a382-af2e6ecb6613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8702bb1_e948_4af5_87b4_3486045036a2
ELIN-893916-2017 | EL-573985-2017 | 8/30/2017 11:41:24 AM | ASSESS: EL: Service Connection | png | #asFound Grounding electrode not buried | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_electrode_not_buried.png Rounding conductor not buried. Should someone be working on or near the electrical equipment and a fault occur, that person will not be at equal potential to the electrical equipment and receive a shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_electrode_not_buried.png | file://x:/photopub/docs/0000000654/10b00dc5-4afc-48a3-b926-73d58882992d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5da320e8_7ccf_4e8c_9d34_67d8e657a192
ELIN-873173-2017 | UW-567869-2017 | 8/4/2017 9:44:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Subpanel1.png,Subpanel2.png A energized 225 amp 120/208 volt rated electrical panel has had the cover removed exposing the interior energized components to possible contact by persons. This poses a shock hazard and possible damage to the electrical components and system. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Subpanel2.png | file://x:/photopub/docs/0000000642/651d287c-e321-4bab-b62d-17b544a80df9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb8673d8_44c4_47cf_ab9f_56bb298aecf2
ELIN-873173-2017 | UW-567869-2017 | 8/4/2017 9:44:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Subpanel1.png,Subpanel2.png A energized 225 amp 120/208 volt rated electrical panel has had the cover removed exposing the interior energized components to possible contact by persons. This poses a shock hazard and possible damage to the electrical components and system. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Subpanel1.png | file://x:/photopub/docs/0000000642/8b3be7c2-fcfb-4dea-85f0-5dc782da4dfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb8673d8_44c4_47cf_ab9f_56bb298aecf2
BPVIN-905136-2017 | BPV-583550-2017 | 9/12/2017 3:27:46 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Custom_burning_superior_propane1.png,Custom_burning_superior_propane2.png,Custom_burning_superior_propane3.png Outside mounted Propane tanks connected on a supply manifold are exposed to the elements and show substantial corrosion and original parent metal loss. without corrosion removal or painting for a significant amount of time, propane tanks are at risk of winning below the corrosion allowance which reduces the overall pressure retaining ability. This corrosion left unchecked will eventually corrode right through the shell and allow propane to escape to atmosphere causing a fire or explosion and risk of injury to personnel or damage to buildings and equipment. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Custom_burning_superior_propane2.png | file://x:/photopub/docs/0000000661/250e8413-80a9-471d-9d84-a7408827c6cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f40d04_7eb1_451f_a829_d878087faf66
ELIN-877372-2017 | EL-541727-2017 | 8/11/2017 9:30:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #Cable_in_shallow_groove_in_styrofoam_insulation.png At the rough wire stage of a residential installation, the branch circuit wiring run in the styrofoam of the exterior basement walls was found to be very near the surface. During drywall installation, and after completion, these cables would be vulnerable to damage from nails, screws etc. Such damage could cause personal shock injury or thermal damage to the cable as well as the surrounding structure. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable_in_shallow_groove_in_styrofoam_insulation.png | file://x:/photopub/docs/0000000644/2315b605-61b7-44ef-8672-3f692713ad09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__460626ae_446d_4fc0_9a4f_3eb326a6d9f0
EDOP-307708-2015 | 2037821 | 8/21/2017 12:28:21 AM | ASSESS: ED OP: RAP | png | #asFound Access panel for pit access is required to have a lock to prevent public from entering hoistway | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Pit_access_panel1.png | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Pit_access_panel1.png | file://x:/photopub/docs/0000000652/1b637460-d74c-426e-92ee-5e37b15c7cac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BF39AA1A_453B_4EB8_A4FE_289DA9544B66
ELIN-869159-2017 | EL-515055-2017 | 8/2/2017 10:43:59 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #Multiple_locations__multiple_locations_receptacle_spacing_incorrect_throughout_dwelling_but_in_particular_kitchen.png 120 V 20 amp receptacles have not been provided at minimum intervals of launch kitchen counter wall lying nor at kitchen island. This can lead to the owners of these dwellings using extension cord's to power kitchen appliances this can lead to property damage and or injury to persons | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Multiple_locations__multiple_locations_receptacle_spacing_incorrect_throughout_dwelling_but_in_particular_kitchen.png | file://x:/photopub/docs/0000000641/81155aa3-79b2-4ed5-bd6f-4a22e2017db0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__197f0b45_0b26_47c9_ab49_7a4141b85098
BPVOP-890429-2017 | 2270755 | 8/21/2017 | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP052 | 1.2.1 Vessell characteristics - Mechanical Internal or External damage such as dents or gouges which exceed code allowable limits for size and depth | 4 | 3 | #Front_tubesheet_with_welded_ring.png Upon assessment it is determined that hole drilled in the tubesheet compromises pressure boundary integrity of boiler. Operation of boiler without repair to restore pressure boundary integrity as per original code of construction can cause irreparable damage of tubesheet and costly downtime. | 4 | 1.2.1 Vessell characteristics - Mechanical Internal or External damage such as dents or gouges which exceed code allowable limits for size and depth | Front_tubesheet_with_welded_ring.png | file://x:/photopub/docs/0000000655/e9557fa2-411f-4f9e-9475-62568622afbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c34657b5_e289_4ec4_b4f3_33fcba4b455b
ELIN-899839-2017 | EL-349224-2016 | 9/8/2017 9:10:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Picture show's that the sub-feeder cable is installed two close to the edge of the 2x4 stud without mechanical protection. | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Hazard.png Wiring installed to close to the edge of the studs or structural members that are not protected from mechanical damage can be punctured by a fastener (drywall screws, nails, drywall anchors) during or after installation which may cause a fire and energy hazard by puncturing the conductor or the conductor insulation. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Hazard.png | file://x:/photopub/docs/0000000659/1bebb5e3-d914-497c-9997-2af65326753b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddf95bfb_81a8_4eed_b99d_ad04361626ce
GAIN-898986-2017 | GA-464610-2016 | 9/12/2017 12:03:05 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Return_air_duct_.png Return air ducting provides a pathway for circulating air back to the furnace. Return air is typically sealed, the furnace is using a 1-pipe vent system and has combustion air in the same room as the furnace. The return air is not sealed and could affect the combustion air for the furnace. This could cause the overall poor operation of the furnace. | 3 | Appliance not installed according to installation instructions | Return_air_duct_.png | file://x:/photopub/docs/0000000661/5ea23818-44d4-4997-8325-639d5d16304a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ba238f5_1cea_49ca_b8e6_d2676eaab907
GAIN-867370-2017 | GA-525769-2017 | 7/31/2017 10:55:58 AM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Vent_terminations.png Two concentric vent terminations are installed incorrectly blocking off the air intakes. This could lead to incomplete combustion and the production of carbon monoxide. | 2 | Side wall vent termination not compliant with installation instructions | Vent_terminations.png | file://x:/photopub/docs/0000000638/0b3dc73e-ce9f-4b30-863a-a37d015b2b45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3d4f105_af49_4262_86f9_1fec67884b62
EDRI-902090-2017 | ED-539353-2017 | 9/7/2017 9:52:56 AM | ASSESS: ED RI: Extension | png | #asFound | ED025 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | 3 | 3 | #Loose_cable.png A power cable was run adjacent to where the hoist runs. There was slack in the cable, making it possible for the cable to swing into the path of the hoist where the hoist could catch the cable and pull it from the building. | 3 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | Loose_cable.png | file://x:/photopub/docs/0000000659/d1055b0d-6314-430d-b920-762b26fb2929.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59925518_738f_4314_a269_b12dca3a0900
ELIN-898531-2017 | EL-572318-2017 | 9/11/2017 1:06:21 PM | ASSESS: EL: Final | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #Shelving_in-front_of_panel.png In an existing modular home recertification, a 200amp 120/240volt combination panel was found with shelving built in front of panel area. This will impede on system operations when access is required. Pic attached. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Shelving_in-front_of_panel.png | file://x:/photopub/docs/0000000660/72b1266f-4545-4e52-9956-79ace591287b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cc28080_00bb_48e4_81b3_7c6a7c0b9ab2
ELHE-883019-2017 | HE-572495-2017 | 8/17/2017 2:23:23 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound Dryer receptacle | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #T.png Cover plates on receptacles are missing and receptacles are not secured to junction boxes. This is a shock hazard to individuals living in the dwelling. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | T.png | file://x:/photopub/docs/0000000647/81870d07-be11-4bb9-886b-7c92f31bfac7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c9efa75_a43a_4558_8c48_8ce5d30172da
ELIN-857187-2017 | EL-414459-2016 | 7/25/2017 | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_closer_than_32_mm_from_edge.png Non-metallic sheathed cable is exposed to damage when installed too close to the surface where drywall screws or nails may penetrate and cause a short circuit. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_closer_than_32_mm_from_edge.png | file://x:/photopub/docs/0000000638/d7ce823f-d29e-41da-b1d5-51c5f46ba318.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73fc6389_fa27_478d_bf70_e8fcc9941206
ELIN-857187-2017 | EL-414459-2016 | 7/25/2017 | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_closer_than_32_mm_from_edge.png Non-metallic sheathed cable is exposed to damage when installed too close to the surface where drywall screws or nails may penetrate and cause a short circuit. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_closer_than_32_mm_from_edge.png | file://x:/photopub/docs/0000000638/02c799b0-18cf-440a-90bd-dc56f73639d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73fc6389_fa27_478d_bf70_e8fcc9941206
GAIN-862141-2017 | GA-558209-2017 | 8/15/2017 8:04:00 AM | ASSESS: GA: Rough-In | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Bbq.png Built in barbecue installed in an enclosure made from combustible material. This could lead to a potential fire. | 3 | Clearance to combustible not met | Bbq.png | file://x:/photopub/docs/0000000646/1659017e-bc38-4931-bb16-30515871e669.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92249492_b4f0_4d14_a87f_1f6bacd6f348
GAIN-862141-2017 | GA-558209-2017 | 8/15/2017 8:04:00 AM | ASSESS: GA: Rough-In | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Bbq.png Built in barbecue installed in an enclosure made from combustible material. This could lead to a potential fire. | 3 | Clearance to combustible not met | Bbq.png | file://x:/photopub/docs/0000000646/80e21bc0-2f53-40da-b7a1-1a3a0f12ae9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92249492_b4f0_4d14_a87f_1f6bacd6f348
ELIN-882997-2017 | EL-550949-2017 | 8/21/2017 2:55:56 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | #Plywood_over_box__no_connectorsharp_edge_box__2_boxes_behind_wall_finish_like_this.png Junction boxes containing 120 volt 15 amp conductors have been rendered inaccessible with building materials. One of the boxes was covered with plywood with single conductors entering the light fixture through abrasive opening. This condition ca lead to property damage or injury to persons | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Plywood_over_box__no_connectorsharp_edge_box__2_boxes_behind_wall_finish_like_this.png | file://x:/photopub/docs/0000000650/0efd4073-de55-4f08-99a7-60a892041e6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13a6e076_fffe_4d8d_9c3d_066353c20569
ELIN-875944-2017 | EL-049166-2013 | 8/21/2017 10:09:24 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Makeshift_neutral_lug.png A subpanel operating at 240 volts and 100 amps has had the neutral conductor connected using a makeshift lug in the panel feeding the subpanel. Neutral lugs are to be approved for the purpose to prevent potential loosening and subsequent arc fault damage, which can lead to property damage or injury to persons | 3 | General Equipment is not approved for the specific use | Makeshift_neutral_lug.png | file://x:/photopub/docs/0000000650/ca28c0ed-e916-4273-8445-297b57721404.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1951e38_49f9_46ee_954c_95785c95cd21
GAHE-873633-2017 | HE-568239-2017 | 8/8/2017 11:11:35 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Regulators1.png,Regulators2.png Propane regulator with 10 PSI inlet installed by source of ignition and air stream on 2 construction heaters | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulators1.png | file://x:/photopub/docs/0000000642/5a0bd44d-7e58-414a-bf26-121e73d04814.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b348f7be_d16c_4d7b_9a15_22aef63b9b8f
GAHE-873618-2017 | HE-568234-2017 | 8/8/2017 11:28:42 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Removed1.png,Removed2.png Power damper motor on commercial propane water heater found removed during inspection and water heater in service. Having motor removed has nothing to prove the safety's that the damper is in the open position before firing of the water and ensuring a path to the outdoors for the products of combustion. Products of combustion could enter the building causing carbon monoxide poising to the workers causing sickness or death. | 4 | Missing mandatory safety controls | Removed2.png | file://x:/photopub/docs/0000000642/ae2ccae1-76a8-46f3-85c0-8aeeca2ddccb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d25606c_4da7_4782_94d1_8414d9e3c5ad
GAHE-873633-2017 | HE-568239-2017 | 8/8/2017 11:11:35 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Regulators1.png,Regulators2.png Propane regulator with 10 PSI inlet installed by source of ignition and air stream on 2 construction heaters | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulators2.png | file://x:/photopub/docs/0000000642/0e2fe091-4e52-4fd1-9ca4-7a3055656397.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b348f7be_d16c_4d7b_9a15_22aef63b9b8f
GAHE-873618-2017 | HE-568234-2017 | 8/8/2017 11:28:42 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Removed1.png,Removed2.png Power damper motor on commercial propane water heater found removed during inspection and water heater in service. Having motor removed has nothing to prove the safety's that the damper is in the open position before firing of the water and ensuring a path to the outdoors for the products of combustion. Products of combustion could enter the building causing carbon monoxide poising to the workers causing sickness or death. | 4 | Missing mandatory safety controls | Removed1.png | file://x:/photopub/docs/0000000642/2c8bbc45-620b-4fc8-88ab-087b4d25e145.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d25606c_4da7_4782_94d1_8414d9e3c5ad
EDIN-900116-2017 | ED-418741-2016 | 9/5/2017 1:27:52 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED049 | Suspected wear or defects that are: Unlikely to progress Contractor is aware of condition | 1 | 1 | #Loose_governor_rope_securing_fist_grip__.png The fist grip securing the governor rope was loose. This is one of the two securing the rope. | 1 | Suspected wear or defects that are: Unlikely to progress Contractor is aware of condition | Loose_governor_rope_securing_fist_grip__.png | file://x:/photopub/docs/0000000657/c0c71dc7-f723-4732-9b39-143f60b5f44d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42460ecb_9e16_4246_8881_a8c3beacfce8
BPVIN-905136-2017 | BPV-583550-2017 | 9/12/2017 3:27:46 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Custom_burning_superior_propane1.png,Custom_burning_superior_propane2.png,Custom_burning_superior_propane3.png Outside mounted Propane tanks connected on a supply manifold are exposed to the elements and show substantial corrosion and original parent metal loss. without corrosion removal or painting for a significant amount of time, propane tanks are at risk of winning below the corrosion allowance which reduces the overall pressure retaining ability. This corrosion left unchecked will eventually corrode right through the shell and allow propane to escape to atmosphere causing a fire or explosion and risk of injury to personnel or damage to buildings and equipment. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Custom_burning_superior_propane1.png | file://x:/photopub/docs/0000000661/4cb60305-1c74-4213-8703-56d19bbdb499.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f40d04_7eb1_451f_a829_d878087faf66
BPVIN-905136-2017 | BPV-583550-2017 | 9/12/2017 3:27:46 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #Custom_burning_superior_propane1.png,Custom_burning_superior_propane2.png,Custom_burning_superior_propane3.png Outside mounted Propane tanks connected on a supply manifold are exposed to the elements and show substantial corrosion and original parent metal loss. without corrosion removal or painting for a significant amount of time, propane tanks are at risk of winning below the corrosion allowance which reduces the overall pressure retaining ability. This corrosion left unchecked will eventually corrode right through the shell and allow propane to escape to atmosphere causing a fire or explosion and risk of injury to personnel or damage to buildings and equipment. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Custom_burning_superior_propane3.png | file://x:/photopub/docs/0000000661/83dec042-734e-4cc9-87e0-b38919519fa1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f40d04_7eb1_451f_a829_d878087faf66
PROP-864299-2017 | 2224022 | 7/26/2017 | ASSESS: PR OP: Annual | png | #asFound Brake linkage and counterweight | PR020 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | 3 | 3 | #Evacuation_car_winch1.png,Evacuation_car_winch2.png An evacuation car winch is utilized in moving an evacuation/rescue car up and down the ropeway track rope. The winch utilizes 2 types of brakes. One electrical lifted shoe type brake (shoes apply to the outside of a rotating drum) which applies to the input end of a gearbox which drives the winch drum. Another band type brake applies directly to the winch drum. The design intent is that the band brake requires constant physical effort (foot pedal) from the winch operator to hold the brake open. It was found that after the band brake was opened that it would not apply when physical effort was removed (foot lifted off of pedal). This was likely due to excessive friction in band brake linkage pivot points as a result of lack of lubrication and corrosion (corrosion was observed around pivot point). This results in an operating condition in which there is no redundant brake and a potential scenario in which a failure of the shoe brake or the failure of the d | 3 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | Evacuation_car_winch1.png | file://x:/photopub/docs/0000000639/310e5039-6184-42b2-9203-33cdf2f0988b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f980cae2_b319_48e7_bc03_d1a53ef7976f
PROP-864299-2017 | 2224022 | 7/26/2017 | ASSESS: PR OP: Annual | png | #asFound Brake peddle on lower left side | PR020 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | 3 | 3 | #Evacuation_car_winch1.png,Evacuation_car_winch2.png An evacuation car winch is utilized in moving an evacuation/rescue car up and down the ropeway track rope. The winch utilizes 2 types of brakes. One electrical lifted shoe type brake (shoes apply to the outside of a rotating drum) which applies to the input end of a gearbox which drives the winch drum. Another band type brake applies directly to the winch drum. The design intent is that the band brake requires constant physical effort (foot pedal) from the winch operator to hold the brake open. It was found that after the band brake was opened that it would not apply when physical effort was removed (foot lifted off of pedal). This was likely due to excessive friction in band brake linkage pivot points as a result of lack of lubrication and corrosion (corrosion was observed around pivot point). This results in an operating condition in which there is no redundant brake and a potential scenario in which a failure of the shoe brake or the failure of the d | 3 | Defect that impairs performance: Performance is outside of limitations or is degenerative Reasonably detectable by the maintenance or operation program | Evacuation_car_winch2.png | file://x:/photopub/docs/0000000639/03b2041b-3df9-4846-9bec-e7f0bfb188bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f980cae2_b319_48e7_bc03_d1a53ef7976f
AMOP-872517-2017 | 3581399 | 8/17/2017 | ASSESS: AM OP: Periodic | png | #asFound | AM037 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | #Loose_corrosion_debris.png Loose and flaking material loss corrosion debris on the flume structural support member. The sharp debris falls into the flume and onto sliding path when becoming detached. This sharp debris whether on the flume or collected into the splashdown lane exposes the user to injury. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Loose_corrosion_debris.png | file://x:/photopub/docs/0000000650/5dd273b5-e7db-45c3-aeff-d006feb9849f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5eaa618_461c_48ea_ba57_54a61507211b
GAIN-900152-2017 | GA-577983-2017 | 9/6/2017 10:35:00 AM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Valve.png Unplugged ball valve connected to an active gas piping system. Potential for the release of natural gas if ball valves opened. Building is under construction with several power tools being used within 10 feet of the ball valve. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Valve.png | file://x:/photopub/docs/0000000658/546e8964-f243-4749-a9a5-3881f41f5430.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__325cd3ee_3db4_467d_a768_35cd0715e5ab
BPVOP-890348-2017 | 3810538 | 8/25/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that horizontal machine mounted air receiver (0.90m long and 0.40m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000652/bb424e1e-5705-4895-886c-b27a6043656e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1750851b_1361_40cb_ae08_4ac2bf688051
EDIN-883148-2017 | ED-408296-2016 | 8/17/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED004 | Wear of defects that are: Likely to progress and affects a non-safety critical component | 2 | 2 | #Twist.png Power to the hoist is supplied through a travel cable, which is guided by a 'basket' that keeps tension on the cable. This basket is guided by the drive and safety steel cables. If the basket spins it causes the travel cable to twist with the steel cables which will eventually cut the travel cable and cause a power short. | 2 | Wear of defects that are: Likely to progress and affects a non-safety critical component | Twist.png | file://x:/photopub/docs/0000000658/9639db5d-5793-474a-8106-86ab6fb7a6b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d4f4b8_f798_4aff_9fb0_5766898c4ed0
ELHE-869295-2017 | HE-476430-2016 | 8/1/2017 9:56:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png Found high voltage overhead conductors 14.4 Kv are located too close to trees and structures and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png | file://x:/photopub/docs/0000000639/d143eaf5-b7a8-483f-84af-a81684d4a6d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485319da_87b0_4be7_9927_b7c3f1f72cb1
ELHE-869295-2017 | HE-476430-2016 | 8/1/2017 9:56:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png Found high voltage overhead conductors 14.4 Kv are located too close to trees and structures and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png | file://x:/photopub/docs/0000000639/52ce30f0-c10d-4499-9e8c-88103d8f7e2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485319da_87b0_4be7_9927_b7c3f1f72cb1
ELHE-869295-2017 | HE-476430-2016 | 8/1/2017 9:56:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png Found high voltage overhead conductors 14.4 Kv are located too close to trees and structures and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png | file://x:/photopub/docs/0000000639/b7102792-b987-4165-9a85-112349d07fc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485319da_87b0_4be7_9927_b7c3f1f72cb1
ELHE-869295-2017 | HE-476430-2016 | 8/1/2017 9:56:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png Found high voltage overhead conductors 14.4 Kv are located too close to trees and structures and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png | file://x:/photopub/docs/0000000639/19e3718d-e5b4-4bdd-845f-5152fbf2ba49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485319da_87b0_4be7_9927_b7c3f1f72cb1
ELHE-869295-2017 | HE-476430-2016 | 8/1/2017 9:56:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png Found high voltage overhead conductors 14.4 Kv are located too close to trees and structures and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png | file://x:/photopub/docs/0000000639/5b256f91-3bf1-43e8-b2b7-eda2fc5dbaf9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485319da_87b0_4be7_9927_b7c3f1f72cb1
ELHE-869295-2017 | HE-476430-2016 | 8/1/2017 9:56:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site1.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site2.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site4.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site5.png,High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site6.png Found high voltage overhead conductors 14.4 Kv are located too close to trees and structures and do not have conductors located and spaced away from other structures as required by code standards. When high voltage electrical equipment and conductors are not located properly and not spaced away with proper spacing from other structures, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | High_Voltage_Overhead_electrical_equipment_poles_and_service_and_feeders_on_site3.png | file://x:/photopub/docs/0000000639/038d1f54-af4d-4235-9e7a-9a41c31a3b19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485319da_87b0_4be7_9927_b7c3f1f72cb1
ELOP-871621-2017 | 3900093 | 8/2/2017 2:09:08 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png Wood Dust Accumulations at the time of inspection are a risk for explosion if ignited. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust3.png | file://x:/photopub/docs/0000000643/7d12527c-fddd-4d73-a5cb-36dd76856403.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__275ebd63_76e8_428e_ad9b_ddb8699a93a6
ELOP-871630-2017 | 3900093 | 8/2/2017 2:08:44 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Motor_conductors1.png,Motor_conductors2.png,Motor_conductors3.png Band saw & compressor feeders without box to protect issuing conductors exposing the conductors to mechanical damage which could lead to an unconfined fire or explosion. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Motor_conductors2.png | file://x:/photopub/docs/0000000643/86f50ff1-7b18-4e8b-a25a-0cf769565635.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__134107d3_d954_4312_a73e_a1e3da35232b
ELOP-871630-2017 | 3900093 | 8/2/2017 2:08:44 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Motor_conductors1.png,Motor_conductors2.png,Motor_conductors3.png Band saw & compressor feeders without box to protect issuing conductors exposing the conductors to mechanical damage which could lead to an unconfined fire or explosion. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Motor_conductors1.png | file://x:/photopub/docs/0000000643/720abe07-b65f-4ddf-88a3-88dbcb886f71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__134107d3_d954_4312_a73e_a1e3da35232b
ELOP-871621-2017 | 3900093 | 8/2/2017 2:09:08 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png Wood Dust Accumulations at the time of inspection are a risk for explosion if ignited. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust5.png | file://x:/photopub/docs/0000000643/d056a41e-4af9-4810-92f3-af5c6ea1a6c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__275ebd63_76e8_428e_ad9b_ddb8699a93a6
ELOP-871621-2017 | 3900093 | 8/2/2017 2:09:08 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png Wood Dust Accumulations at the time of inspection are a risk for explosion if ignited. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust2.png | file://x:/photopub/docs/0000000643/04e6aff6-4e63-4238-a2d9-16ff8819c24b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__275ebd63_76e8_428e_ad9b_ddb8699a93a6
ELOP-871630-2017 | 3900093 | 8/2/2017 2:08:44 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Motor_conductors1.png,Motor_conductors2.png,Motor_conductors3.png Band saw & compressor feeders without box to protect issuing conductors exposing the conductors to mechanical damage which could lead to an unconfined fire or explosion. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Motor_conductors3.png | file://x:/photopub/docs/0000000643/e5d1a1f5-06ba-4541-9396-edfe19ea74b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__134107d3_d954_4312_a73e_a1e3da35232b
ELOP-871621-2017 | 3900093 | 8/2/2017 2:09:08 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png Wood Dust Accumulations at the time of inspection are a risk for explosion if ignited. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust4.png | file://x:/photopub/docs/0000000643/195eaf61-976c-43b4-8c8c-d07adf627b25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__275ebd63_76e8_428e_ad9b_ddb8699a93a6
ELOP-871621-2017 | 3900093 | 8/2/2017 2:09:08 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | #Wood_dust1.png,Wood_dust2.png,Wood_dust3.png,Wood_dust4.png,Wood_dust5.png Wood Dust Accumulations at the time of inspection are a risk for explosion if ignited. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Wood_dust1.png | file://x:/photopub/docs/0000000643/2d4458cc-dc9e-4e2b-8b2c-4fba210f10ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__275ebd63_76e8_428e_ad9b_ddb8699a93a6
BPVOP-882143-2017 | 2296627 | 8/16/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_Relief_Valve.png The pressure relief valve provides protection to the air compressor receiver from being over pressurized with compressed air. The air receiver has a maximum allowable working pressure and if this pressure is exceeded the pressure relief valve will vent the air to atmosphere to prevent the air receiver from failing / bursting. The pressure relief valve requires replacement or servicing when it exceeds the time frame as specified in CSA B51. The valve was more than 5 years old with no service record and requires replacement. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_Relief_Valve.png | file://x:/photopub/docs/0000000647/d9bd5bca-fa10-47ed-9c3a-0572d8f3880a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72ca1868_ee8d_4d7f_98ff_162bd578ca13
ELIN-878055-2017 | EL-434358-2016 | 8/10/2017 | ASSESS: EL: Final | png | #asFound | EL294 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Relocated_panel_and_ccts.png Homeowner has relocated and energized a 200 amp service panel and relocated and energized new unauthorized and existing branch wiring without inspection or acceptance from BCCA A thermal hazard may occur when a homeowner has relocated and energized a 200 amp service panel and relocated and energized new unauthorized and existing branch wiring without inspection or acceptance from BCCA | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Relocated_panel_and_ccts.png | file://x:/photopub/docs/0000000645/b20b3fb4-cb7d-4f06-a678-c1b6b7bfe631.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbc2bb24_e625_413c_a03a_5583f5f23102
GAHE-877788-2017 | HE-570170-2017 | 8/11/2017 11:24:58 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Relief_port_open_inside.png A Gas regulator has a relief port on it to vent gas in an overpressure scenario. The Relief port is vented to the outside to release the over pressurized gas to the atmosphere. The relief port is not piped to the outside and in an over pressure situation the regulator could release gas into the indoor space, possible filling room with gas and causing an explosive atmosphere inside the room. | 5 | Relief style regulator/device allowed to vent within building/confined space | Relief_port_open_inside.png | file://x:/photopub/docs/0000000644/e56ae51d-5f66-429a-87bc-db2327c58533.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2bc69e9c_13ec_4b38_b5b3_c7720d3e7983
EDMA-905392-2017 | ED-574750-2017 | 9/11/2017 5:36:13 PM | ASSESS: ED MA: Acceptance | png | #asFound Car Rooftop. Distance to hoistway wall exceeds 12". | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Car_Rooftop.png During a major alteration inspection of the car rooftop, a section of railing required to prevent a fall hazard from the car rooftop was not installed. The distance from the perimeter of the car rooftop to the hoistway wall exceeds 12" | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Car_Rooftop.png | file://x:/photopub/docs/0000000661/6830e532-fc63-4e90-a932-f8f6cdf394f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be44607e_29c6_4840_956f_b305a404fd1a
ELIN-903861-2017 | EL-582823-2017 | 9/11/2017 2:27:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Outlet_boxes_over_100mm_1_support1.png,Outlet_boxes_over_100mm_1_support2.png The larger electrical device boxes are not adequately supported and may be subject to breakage and exposed electrical parts creating a shock hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Outlet_boxes_over_100mm_1_support2.png | file://x:/photopub/docs/0000000660/071d8192-668e-4dd9-9f18-3461e43df417.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe95dcf6_a163_4d2c_8006_9e96cd00c04e
GAHE-903767-2017 | HE-582968-2017 | 9/11/2017 2:19:10 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Notice the close proximity of the 80 gallon propane tank in relation to the heat pump | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_locations.png An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device installed in the tank begins to vent, and explosion or fire could occur if the heat pump cycled on causing an arc and providing a source of ignition to the propane. | 4 | Ignition sources present with-in minimum distance required | Tank_locations.png | file://x:/photopub/docs/0000000660/bee2dbb9-e429-4ce4-b199-fd280cfa7208.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9198c9e_8bb9_4df7_84aa_5ec2dcd8625e
GAHE-903723-2017 | HE-582938-2017 | 9/8/2017 3:18:38 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Source_of_ignition.png An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device installed in the tank begins to vent, an explosion or fire could occur if the heat pump cycled on simultaneously causing and arc and providing ignition to the propane. | 4 | Ignition sources present with-in minimum distance required | Source_of_ignition.png | file://x:/photopub/docs/0000000660/e025031f-42d5-4bc2-a07e-8379ea49d885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed55bf2c_987b_4506_8c27_5a5aa44d4ca4
GAHE-903566-2017 | HE-582842-2017 | 9/11/2017 10:28:01 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_location.png An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device installed in the tank begins to vent, and explosion or fire could occur if the heat pump cycled on simultaneously causing an arc and providing ignition. | 4 | Ignition sources present with-in minimum distance required | Tank_location.png | file://x:/photopub/docs/0000000660/8bd49bcb-d4ba-43be-80d4-1a5ad221d9ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feae2fbd_0016_41f6_ba01_6e695e03c080
ELIN-898745-2017 | EL-579704-2017 | 9/5/2017 10:46:07 AM | ASSESS: EL: Service Connection | png | #asFound Service raceway not bonded | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | #No_bonding.png Reconnection of a service for building being renovated as a bakery. Service conduits and cables have not been bonded. Shock hazard if a cable was to fault. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | No_bonding.png | file://x:/photopub/docs/0000000657/729e7180-acf3-4259-8dec-221346c08f9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__887c17c8_21f7_408e_addd_2924f6bfae67
GAIN-869678-2017 | GA-513827-2017 | 8/1/2017 11:27:12 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Dfma.png The as-found condition is that a full relief regulator terminates within 10 feet of a mechanical air inlet. The potential hazard is that the regulator will relieve and release raw gas into the atmosphere which will be drawn into the mechanical air inlet to a building, dispersing raw gas into the air of an occupied space. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Dfma.png | file://x:/photopub/docs/0000000639/65e1dfed-95cd-41b8-acd0-02df3ff204aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90c710c8_21f8_41d8_bf9f_9a2c94b1edd9
ELIN-883089-2017 | UW-572534-2017 | 7/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Damaged_conduit1.png,Damaged_conduit2.png,Damaged_conduit3.png,Damaged_conduit4.png,Damaged_conduit5.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a new single family home under construction, electrical underground conduits for hydro and telephone were installed without an electrical permit and without a request for inspections. The underground conduits are required to be installed 915mm deep with marking tape installed half way between the conduit and top of grade. When Fortis went to install the underground gas line in the driveway of the dwelling, the gas crew hit the underground conduits for for the hydro and telephone. The underground Hydro conduit was 400mm below grade and the telephone conduit was 300mm below grade. No marking tape was found over the conduits. The hydro conduit co | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Damaged_conduit5.png | file://x:/photopub/docs/0000000647/8399db9f-a75d-487e-afa0-86f7b3f96cc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bc60add_4f09_4e0c_885d_a77177ef8f6a
AMIN-868358-2017 | AM-558761-2017 | 8/1/2017 1:19:32 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Anchor_points_requiring_ballast1.png,Anchor_points_requiring_ballast2.png,Anchor_points_requiring_ballast3.png Anchor points on inflatable device did not have ballast attached, device could possibly move unexpectantly while in operation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Anchor_points_requiring_ballast1.png | file://x:/photopub/docs/0000000639/c3dbdad6-8ecc-48d2-bd0b-b0ceb4134d7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d8f204c_3ac3_4200_b3b9_0054856ae105
AMIN-868358-2017 | AM-558761-2017 | 8/1/2017 1:19:32 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Anchor_points_requiring_ballast1.png,Anchor_points_requiring_ballast2.png,Anchor_points_requiring_ballast3.png Anchor points on inflatable device did not have ballast attached, device could possibly move unexpectantly while in operation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Anchor_points_requiring_ballast3.png | file://x:/photopub/docs/0000000639/ced4d638-a21f-46b3-97d4-c1bade043045.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d8f204c_3ac3_4200_b3b9_0054856ae105
AMIN-868358-2017 | AM-558761-2017 | 8/1/2017 1:19:32 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | #Anchor_points_requiring_ballast1.png,Anchor_points_requiring_ballast2.png,Anchor_points_requiring_ballast3.png Anchor points on inflatable device did not have ballast attached, device could possibly move unexpectantly while in operation. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Anchor_points_requiring_ballast2.png | file://x:/photopub/docs/0000000639/e25bbdb1-c402-43c1-b191-b3879003a269.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d8f204c_3ac3_4200_b3b9_0054856ae105
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures19.png | file://x:/photopub/docs/0000000648/d59f6a7d-9486-4a11-8606-b61852f6cc0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELIN-876660-2017 | EL-549916-2017 | 8/11/2017 2:02:43 PM | ASSESS: EL: Final | png | #asFound Grounding electrode not installed | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_electrode.png Grounding electrode not installed, should an electrical fault occur while someone is working on the equipment they will not be at equal potential to the equipment and thereby receive a shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_electrode.png | file://x:/photopub/docs/0000000644/aee50f02-77a4-4715-8d6b-000d0c50c195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8916632_7540_4c7d_9d53_b6bd40e152b8
BPVIN-477714-2015 | UW-312620-2015 | 7/17/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound Vessel is not supported with anchor bolts. | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 3 | #support.png,Unsupported_vessel.png Air receiver support legs are not anchored to the floor, only sitting in position. If the vessel were to be struck by equipment or move from earthquake forces or possibly process flow forces, it could move. This could cause other damage to piping and potentially cause a rupture and release. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | Unsupported_vessel.png | file://x:/photopub/docs/0000000639/4ee10149-3789-4db8-a559-b3d2117084fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bde0893_6816_4926_a88e_57a4fe215d18
AMOP-900851-2017 | AM-158617-2014 | 9/11/2017 8:46:07 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #Control_arm_hardware1.png,Control_arm_hardware2.png Control arm hardware connecting the train cars, were not tightened , or were missing hardware. Connection could fail, causing train car to be freed from the rest of the train. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Control_arm_hardware2.png | file://x:/photopub/docs/0000000660/3b7adea9-b57a-465e-a767-2c9bf80f8697.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f387e5fd_9a93_46e8_8ad3_eac2c9e5f4ad
ELIN-883089-2017 | UW-572534-2017 | 7/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Damaged_conduit1.png,Damaged_conduit2.png,Damaged_conduit3.png,Damaged_conduit4.png,Damaged_conduit5.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a new single family home under construction, electrical underground conduits for hydro and telephone were installed without an electrical permit and without a request for inspections. The underground conduits are required to be installed 915mm deep with marking tape installed half way between the conduit and top of grade. When Fortis went to install the underground gas line in the driveway of the dwelling, the gas crew hit the underground conduits for for the hydro and telephone. The underground Hydro conduit was 400mm below grade and the telephone conduit was 300mm below grade. No marking tape was found over the conduits. The hydro conduit co | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Damaged_conduit3.png | file://x:/photopub/docs/0000000647/66ca0bf5-7110-415b-8d6e-53a3ed1db61f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bc60add_4f09_4e0c_885d_a77177ef8f6a
ELIN-883089-2017 | UW-572534-2017 | 7/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Damaged_conduit1.png,Damaged_conduit2.png,Damaged_conduit3.png,Damaged_conduit4.png,Damaged_conduit5.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a new single family home under construction, electrical underground conduits for hydro and telephone were installed without an electrical permit and without a request for inspections. The underground conduits are required to be installed 915mm deep with marking tape installed half way between the conduit and top of grade. When Fortis went to install the underground gas line in the driveway of the dwelling, the gas crew hit the underground conduits for for the hydro and telephone. The underground Hydro conduit was 400mm below grade and the telephone conduit was 300mm below grade. No marking tape was found over the conduits. The hydro conduit co | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Damaged_conduit4.png | file://x:/photopub/docs/0000000647/9ac35560-8cd7-4895-9492-9b7778541f7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bc60add_4f09_4e0c_885d_a77177ef8f6a
ELIN-883089-2017 | UW-572534-2017 | 7/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Damaged_conduit1.png,Damaged_conduit2.png,Damaged_conduit3.png,Damaged_conduit4.png,Damaged_conduit5.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a new single family home under construction, electrical underground conduits for hydro and telephone were installed without an electrical permit and without a request for inspections. The underground conduits are required to be installed 915mm deep with marking tape installed half way between the conduit and top of grade. When Fortis went to install the underground gas line in the driveway of the dwelling, the gas crew hit the underground conduits for for the hydro and telephone. The underground Hydro conduit was 400mm below grade and the telephone conduit was 300mm below grade. No marking tape was found over the conduits. The hydro conduit co | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Damaged_conduit2.png | file://x:/photopub/docs/0000000647/b86af3d7-faf3-4a5b-bfbc-41bcde08d12e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bc60add_4f09_4e0c_885d_a77177ef8f6a
ELIN-883089-2017 | UW-572534-2017 | 7/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Damaged_conduit1.png,Damaged_conduit2.png,Damaged_conduit3.png,Damaged_conduit4.png,Damaged_conduit5.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a new single family home under construction, electrical underground conduits for hydro and telephone were installed without an electrical permit and without a request for inspections. The underground conduits are required to be installed 915mm deep with marking tape installed half way between the conduit and top of grade. When Fortis went to install the underground gas line in the driveway of the dwelling, the gas crew hit the underground conduits for for the hydro and telephone. The underground Hydro conduit was 400mm below grade and the telephone conduit was 300mm below grade. No marking tape was found over the conduits. The hydro conduit co | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Damaged_conduit1.png | file://x:/photopub/docs/0000000647/f4ff8a8a-4c47-4455-98e7-bd5f48283120.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bc60add_4f09_4e0c_885d_a77177ef8f6a
ELIN-885382-2017 | EL-573075-2017 | 8/25/2017 12:48:20 PM | ASSESS: EL: Service Connection | png | #asFound Grounding electrode not buried. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #ground_plate_not_buried.png Grounding electrode not buried, should someone be working on the electrical equipment when a fault occurs, the worker will not be at equal potential to the equipment there by receiving an electrical shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | ground_plate_not_buried.png | file://x:/photopub/docs/0000000652/8d7c0331-b3d2-481a-920d-fe4e9f2ca9c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b531d95d_9c2d_4091_ae54_b14830538825
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures11.png | file://x:/photopub/docs/0000000648/4aa5e441-581e-4f52-aa30-fa754897000d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
ELOP-881590-2017 | EL-551399-2017 | 8/17/2017 | ASSESS: EL OP: Acceptance | png | #asFound Unapproved electrical equipment for unapproved/uncertified relocatable structures. | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Unapproved_electrical_equipment_for_relocatable_structures1.png,Unapproved_electrical_equipment_for_relocatable_structures2.png,Unapproved_electrical_equipment_for_relocatable_structures3.png,Unapproved_electrical_equipment_for_relocatable_structures4.png,Unapproved_electrical_equipment_for_relocatable_structures5.png,Unapproved_electrical_equipment_for_relocatable_structures6.png,Unapproved_electrical_equipment_for_relocatable_structures7.png,Unapproved_electrical_equipment_for_relocatable_structures8.png,Unapproved_electrical_equipment_for_relocatable_structures9.png,Unapproved_electrical_equipment_for_relocatable_structures10.png,Unapproved_electrical_equipment_for_relocatable_structures11.png,Unapproved_electrical_equipment_for_relocatable_structures12.png,Unapproved_electrical_equipment_for_relocatable_structures13.png,Unapproved_electrical_equipment_for_relocatable_structures14.png,Unapproved_electrical_equipment_for_relocatable_structures15.png,Unapproved_electrical_equipment_for_relocatable_structure | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Unapproved_electrical_equipment_for_relocatable_structures5.png | file://x:/photopub/docs/0000000648/682341a9-ce32-4436-aa85-0edc46ef933c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658fa13a_08bf_4902_8cd9_554974c107cd
GAUP-880889-2017 | UW-571434-2017 | 8/19/2017 8:34:06 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Venting1.png,Venting2.png,Venting3.png Commercial water heaters installed in a fire camp occupied wash area. The venting system has not been terminated to the outdoors, allowing products of combustion to enter the space. Products of combustion in occupied area could cause individuals to get sick or die from carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Venting2.png | file://x:/photopub/docs/0000000648/0dedf2d3-3a2d-474a-94a1-f08bf0e85663.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e785c063_0915_4617_bca5_2391ad3db75c
GAUP-880889-2017 | UW-571434-2017 | 8/19/2017 8:34:06 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Venting1.png,Venting2.png,Venting3.png Commercial water heaters installed in a fire camp occupied wash area. The venting system has not been terminated to the outdoors, allowing products of combustion to enter the space. Products of combustion in occupied area could cause individuals to get sick or die from carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Venting3.png | file://x:/photopub/docs/0000000648/7cb16f3f-c6a4-4d88-a29b-cb8f01ec4a4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e785c063_0915_4617_bca5_2391ad3db75c
GAUP-880889-2017 | UW-571434-2017 | 8/19/2017 8:34:06 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Venting1.png,Venting2.png,Venting3.png Commercial water heaters installed in a fire camp occupied wash area. The venting system has not been terminated to the outdoors, allowing products of combustion to enter the space. Products of combustion in occupied area could cause individuals to get sick or die from carbon monoxide poisoning. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Venting1.png | file://x:/photopub/docs/0000000648/82c0545c-a56b-4732-a71a-d55f2adcfedb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e785c063_0915_4617_bca5_2391ad3db75c
ELIN-896217-2017 | EL-559825-2017 | 9/5/2017 2:29:22 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Db2_no_encasement_alleyway.png An 800 amp 240 volt single phase service is being changed to an underground feed to eliminate overhead service in an alleyway. The service raceways emerge from grade as very lightwall pipe that is easily damaged when not encased in concrete. Subsequent damage to property or injury to persons can occur under this condition | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Db2_no_encasement_alleyway.png | file://x:/photopub/docs/0000000658/f0fab55d-284d-4744-b408-6438739ad9db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9275d2b8_56f5_4e6d_ac43_a28584c952a1
AMOP-900851-2017 | AM-158617-2014 | 9/11/2017 8:46:07 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #Control_arm_hardware1.png,Control_arm_hardware2.png Control arm hardware connecting the train cars, were not tightened , or were missing hardware. Connection could fail, causing train car to be freed from the rest of the train. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Control_arm_hardware1.png | file://x:/photopub/docs/0000000660/4568be8f-505b-4480-93d3-e9e137e8b1ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f387e5fd_9a93_46e8_8ad3_eac2c9e5f4ad
AMOP-897348-2017 | AM-567320-2017 | 9/11/2017 9:14:31 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #Pillow_block_hardware_missing.png Pillow block hardware connecting the hub to the structure was found to be missing, loose, or oversized locking washers were utilized. Ferris wheel could fall off its support if remaining connections were to fail. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Pillow_block_hardware_missing.png | file://x:/photopub/docs/0000000660/3cb62834-5bae-46fe-898c-bb807aae73d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a2f96c6_4f55_4093_81ed_aa99a111234f
EDIN-889939-2017 | ED-496173-2017 | 8/25/2017 9:00:17 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED046 | Defects found where the required strength may no longer exist. | 4 | 4 | #missing_key_way_on_safety_sytem_.png I found the key way missing on the activation arm for the safety system. In an overspeed situation the safety arm may slip on the activation bar. | 4 | Defects found where the required strength may no longer exist. | missing_key_way_on_safety_sytem_.png | file://x:/photopub/docs/0000000653/213e7fe2-945a-4506-a78d-caddd4066e43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__325b1676_aa22_4b07_9650_aec13a2fb70c
ELIN-900862-2017 | EL-567771-2017 | 9/7/2017 2:18:24 PM | ASSESS: EL: Final | png | #asFound Grounding conductor termination. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #grounding_conductor_termination.png Grounding conductor not terminated in the correct location. Should a ground fault occur, the fault current will not make its way back to the utility. Main overcurrent device may not facilitate if a ground fault were to occur in the electrical system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | grounding_conductor_termination.png | file://x:/photopub/docs/0000000659/1a5a650f-73f3-4a70-963c-bb19b305a8e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c46699d5_43b6_47cd_aa5c_1df7aeae2c72
BPVOP-887841-2017 | 3676147 | 8/25/2017 11:07:04 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Gas_plate.png During the inspection of a Hot Water Boiler with MAWP of 160 psig was found that there is no Emergency Shut Down Switch located at the boiler room entrance. Without this emergency shut down switch located at the boiler room entrance, it would be difficult to shut down this equipment in an emergency situation. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Gas_plate.png | file://x:/photopub/docs/0000000652/0d9db50b-04fc-46c0-87f6-7cac6bfebe55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94554e58_325e_46c1_bfeb_0a3354a6dcb7
BPVOP-887839-2017 | 3676150 | 8/25/2017 11:21:43 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Gas_plate_.png During the inspection of a Hot Water Boiler with MAWP of 160 psig was found that there is no Emergency Shut Down Switch located at the boiler room entrance. Without this emergency shut down switch located at the boiler room entrance, it would be difficult to shut down this equipment in an emergency situation. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Gas_plate_.png | file://x:/photopub/docs/0000000652/502771db-af1f-4b82-a5ea-f236837a34d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ba8e371_eb18_42d8_9e0c_8bf3a1fb442e
ELIN-888542-2017 | UW-575610-2017 | 8/24/2017 12:28:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #Damaged_feeder_cables1.png,Damaged_feeder_cables2.png,Damaged_feeder_cables3.png In a new multi family dwelling construction, 200 amp 120/240 volt feeder cables were found to be damaged. This is an equipment damage condition. Pictures attached. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Damaged_feeder_cables2.png | file://x:/photopub/docs/0000000651/6166fe16-5fa2-464b-b0a8-13a6132c84c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__840b471e_61ad_42c2_9e7b_38f4c8eece13
ELIN-888542-2017 | UW-575610-2017 | 8/24/2017 12:28:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #Damaged_feeder_cables1.png,Damaged_feeder_cables2.png,Damaged_feeder_cables3.png In a new multi family dwelling construction, 200 amp 120/240 volt feeder cables were found to be damaged. This is an equipment damage condition. Pictures attached. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Damaged_feeder_cables3.png | file://x:/photopub/docs/0000000651/846634aa-e65c-4ab5-bf02-06b5be28ca00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__840b471e_61ad_42c2_9e7b_38f4c8eece13
ELIN-888542-2017 | UW-575610-2017 | 8/24/2017 12:28:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #Damaged_feeder_cables1.png,Damaged_feeder_cables2.png,Damaged_feeder_cables3.png In a new multi family dwelling construction, 200 amp 120/240 volt feeder cables were found to be damaged. This is an equipment damage condition. Pictures attached. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Damaged_feeder_cables1.png | file://x:/photopub/docs/0000000651/d8825b90-b7fc-43f3-8a06-45ade7ae6009.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__840b471e_61ad_42c2_9e7b_38f4c8eece13
ELIN-885943-2017 | EL-563208-2017 | 8/29/2017 11:40:00 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Two_cables_per_entry__jacket_damage.png Cables must be entered in box in a manner which does not damage outer jacket | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Two_cables_per_entry__jacket_damage.png | file://x:/photopub/docs/0000000654/5a82af96-92fe-42aa-a464-13e5a30dad70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4753d4d1_e39c_4a3b_8499_371e4c3f6dd1
ELIN-894324-2017 | EL-502504-2017 | 8/31/2017 1:18:18 PM | ASSESS: EL: Final | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Open_breaker_space_as_found1.png,Open_breaker_space_as_found2.png Open breaker spaces on an energized panel leaving exposed electrical parts and a potential shock hazard. Panel cover is closed and open breaker space is at the top of the panel. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Open_breaker_space_as_found2.png | file://x:/photopub/docs/0000000656/e0f8851d-dcd8-4cd9-a906-d897a42dcf47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78845eeb_e534_4266_9800_1a4d49bc96c4
ELHE-896104-2017 | HE-578356-2017 | 8/31/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png,As_found3.png,As_found4.png,As_found5.png Ground floor master bathroom hanging light fixture not approved for damp or wet locations and is in close proximity (48 inches) to bath tub plumbing fixture creating potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | As_found3.png | file://x:/photopub/docs/0000000656/1c260851-1cb8-4402-ac3e-70a143732fc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab33301e_3191_479e_92ac_729fedff5080
ELIN-890720-2017 | EL-576745-2017 | 8/31/2017 8:44:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found_hazards1.png,As_found_hazards2.png,As_found_hazards3.png,As_found_hazards4.png Energized temporary construction panels are without internal barriers creating a potential shock hazard if opened by site workers or persons entering the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found_hazards4.png | file://x:/photopub/docs/0000000656/76df1ea6-4c7a-4c66-bd73-8b26225bc71d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bef99e2_b4de_417d_994d_a7e6b2c1a775
ELHE-896104-2017 | HE-578356-2017 | 8/31/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png,As_found3.png,As_found4.png,As_found5.png Ground floor master bathroom hanging light fixture not approved for damp or wet locations and is in close proximity (48 inches) to bath tub plumbing fixture creating potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | As_found2.png | file://x:/photopub/docs/0000000656/7e4f73f4-ade0-4282-abbe-7660eaab4b68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab33301e_3191_479e_92ac_729fedff5080
ELIN-890720-2017 | EL-576745-2017 | 8/31/2017 8:44:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found_hazards1.png,As_found_hazards2.png,As_found_hazards3.png,As_found_hazards4.png Energized temporary construction panels are without internal barriers creating a potential shock hazard if opened by site workers or persons entering the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found_hazards1.png | file://x:/photopub/docs/0000000656/44d4010e-18d3-42ee-827c-7c69508f6b80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bef99e2_b4de_417d_994d_a7e6b2c1a775
ELHE-896104-2017 | HE-578356-2017 | 8/31/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png,As_found3.png,As_found4.png,As_found5.png Ground floor master bathroom hanging light fixture not approved for damp or wet locations and is in close proximity (48 inches) to bath tub plumbing fixture creating potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | As_found5.png | file://x:/photopub/docs/0000000656/6ba437f8-8416-454f-9e95-84a057a3df52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab33301e_3191_479e_92ac_729fedff5080
ELIN-894324-2017 | EL-502504-2017 | 8/31/2017 1:18:18 PM | ASSESS: EL: Final | png | #asFound | EL292 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Open_breaker_space_as_found1.png,Open_breaker_space_as_found2.png Open breaker spaces on an energized panel leaving exposed electrical parts and a potential shock hazard. Panel cover is closed and open breaker space is at the top of the panel. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Open_breaker_space_as_found1.png | file://x:/photopub/docs/0000000656/da45f798-a57f-491a-b9f1-ff2b6d20a9d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78845eeb_e534_4266_9800_1a4d49bc96c4
ELHE-896104-2017 | HE-578356-2017 | 8/31/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png,As_found3.png,As_found4.png,As_found5.png Ground floor master bathroom hanging light fixture not approved for damp or wet locations and is in close proximity (48 inches) to bath tub plumbing fixture creating potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | As_found1.png | file://x:/photopub/docs/0000000656/ebda5527-26c4-4b69-ac42-cc6084cb31e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab33301e_3191_479e_92ac_729fedff5080
ELHE-896104-2017 | HE-578356-2017 | 8/31/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png,As_found3.png,As_found4.png,As_found5.png Ground floor master bathroom hanging light fixture not approved for damp or wet locations and is in close proximity (48 inches) to bath tub plumbing fixture creating potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | As_found4.png | file://x:/photopub/docs/0000000656/87e0ae0c-ca54-4e3d-9c91-b9c094827d3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab33301e_3191_479e_92ac_729fedff5080
ELIN-900844-2017 | EL-579222-2017 | 9/7/2017 2:01:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #KO_Filler_Needed.png This assessment found that a knock out hole at the main breaker compartment missing, with a potential for a rodent to enter, creating a fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | KO_filler_needed.png | file://x:/photopub/docs/0000000659/6b22341e-bf0b-4262-885c-18a154377e59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f37db7a1_f61d_4f55_be65_aaae0f0343da
ELIN-900844-2017 | EL-579222-2017 | 9/7/2017 2:01:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | #KO_Filler_Needed.png This assessment found that a knock out hole at the main breaker compartment missing, with a potential for a rodent to enter, creating a fire hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | KO_Filler_Needed.png | file://x:/photopub/docs/0000000659/01f3815f-a7ba-41ec-b9f7-413e63b64019.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f37db7a1_f61d_4f55_be65_aaae0f0343da
ELIN-894543-2017 | EL-574348-2017 | 9/6/2017 11:03:06 AM | ASSESS: EL: Service Connection | png | #asFound Grounding conductor not buried | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #grounding_conductor1.png,grounding_conductor2.png Grounding electrode not buried, Should a ground fault occur when someone is walking near the electrical equipment, that person will not be at equal potential to the fault and will receive a shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | grounding_conductor2.png | file://x:/photopub/docs/0000000658/807647c2-949f-47ec-91ae-6c868c7be258.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c54447c_9579_4bf7_b574_08571765fa96
ELIN-894543-2017 | EL-574348-2017 | 9/6/2017 11:03:06 AM | ASSESS: EL: Service Connection | png | #asFound Who is Bluestar electrical Limited | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #grounding_conductor1.png,grounding_conductor2.png Grounding electrode not buried, Should a ground fault occur when someone is walking near the electrical equipment, that person will not be at equal potential to the fault and will receive a shock | 3 | Installation Grounding; Electrode or grounding conductor are not present. | grounding_conductor1.png | file://x:/photopub/docs/0000000658/f7e07c29-92b3-40da-bcd0-a9a879cbbc06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c54447c_9579_4bf7_b574_08571765fa96
EDIN-882167-2017 | ED-532702-2017 | 8/16/2017 4:02:17 PM | ASSESS: ED IN: Acceptance | png | #asFound Lighting at lower landing measured with light meter | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | #Lower_landing.png Lack of adequate lighting at lower landing and on the platform of lift | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Lower_landing.png | file://x:/photopub/docs/0000000647/9d5f1a07-ae39-4d68-baaa-7dfb2fd6e1d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ac4385c_28d2_4019_ab0f_e34cf4982917
EDIN-809460-2017 | ED-408346-2016 | 8/30/2017 | ASSESS: ED IN: Incident | png | #asFound | ED029 | Defect that is: • undetectable by maintenance program • Likely to progress | 3 | 3 | #Travel_cable_snag.png A nylon strip along the entire bottom edge of the hoist is used to keep the travel cable from catching on the bottom of the hoist. This strip was missing a section and the travel cable was catching on the corner of the strip. This will lead to damage to the travel cable, and the cable could short out to the hoist. | 3 | Defect that is: • undetectable by maintenance program • Likely to progress | Travel_cable_snag.png | file://x:/photopub/docs/0000000658/b6ae7d97-4842-4d41-b47b-840157d0a4eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47fa6cc2_265b_4fd6_b597_d54745d8db5d
ELIN-903745-2017 | EL-501082-2017 | 9/11/2017 1:34:45 PM | ASSESS: EL: Final | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | #Limited_headroom.png Working space in front of electrical service has been limited by a unapproved lighting guard. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Limited_headroom.png | file://x:/photopub/docs/0000000660/df2e87e1-530d-4761-947b-ab0b00d4a46f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a1de6e_7a1e_423e_bc13_bc2a7b8a53a8
BPVIN-902173-2017 | UW-581475-2017 | 9/7/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | #Pressure_vessels1.png,Pressure_vessels2.png,Pressure_vessels3.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of multiple pressure vessels, I found that not every pressure vessels is protected by a Pressure Relief Device. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Pressure_vessels2.png | file://x:/photopub/docs/0000000660/759439d2-f1b4-40cb-b2d2-db1cabd39647.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f551578_e8b5_44f8_b552_6eabc421fe9c
BPVIN-902173-2017 | UW-581475-2017 | 9/7/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | #Pressure_vessels1.png,Pressure_vessels2.png,Pressure_vessels3.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of multiple pressure vessels, I found that not every pressure vessels is protected by a Pressure Relief Device. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Pressure_vessels3.png | file://x:/photopub/docs/0000000660/631de0b4-6eff-4437-8e9d-a2521be3705f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f551578_e8b5_44f8_b552_6eabc421fe9c
ELIN-890720-2017 | EL-576745-2017 | 8/31/2017 8:44:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found_hazards1.png,As_found_hazards2.png,As_found_hazards3.png,As_found_hazards4.png Energized temporary construction panels are without internal barriers creating a potential shock hazard if opened by site workers or persons entering the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found_hazards2.png | file://x:/photopub/docs/0000000656/1857898b-7bb1-4523-8a8d-1db97328bc31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bef99e2_b4de_417d_994d_a7e6b2c1a775
ELIN-890720-2017 | EL-576745-2017 | 8/31/2017 8:44:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found_hazards1.png,As_found_hazards2.png,As_found_hazards3.png,As_found_hazards4.png Energized temporary construction panels are without internal barriers creating a potential shock hazard if opened by site workers or persons entering the site. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found_hazards3.png | file://x:/photopub/docs/0000000656/82347229-2b11-4e37-aeb7-75fe4e8f9a23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bef99e2_b4de_417d_994d_a7e6b2c1a775
GAIN-898021-2017 | GA-578383-2017 | 9/5/2017 1:00:36 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Venting.png The as found condition is exhaust venting from a high efficient furnace has some sections of uncertified venting material installed. The as found hazard is uncertified material can break down prematurely leading to an exhaust leaking, potentially subjecting building inhabitants to deadly carbon monoxide by-products. | 3 | Unapproved venting material | Venting.png | file://x:/photopub/docs/0000000657/9b5e20be-78e6-432a-9cf6-1160723f33ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65b5eb06_4337_467f_b485_395e4cbf2ef1
GAIN-884202-2017 | GA-573195-2017 | 8/30/2017 10:15:38 AM | ASSESS: GA: Final | png | #asFound Close nipple | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Close_nipple.png The as-found condition is that a prohibited fitting has been used on a gas piping system. The potential hazard is that thin walled material of the prohibited fitting will break under stress and cause a gas leak in an occupied space, resulting in a fire and explosion hazard | 3 | Non-compliant material/fittings installed | Close_nipple.png | file://x:/photopub/docs/0000000654/a68a7f0a-965f-4b9e-ba83-7c03894090db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3fa74b6_699d_41e8_bf6b_b2b7414ef240
GAIN-884202-2017 | GA-573195-2017 | 8/30/2017 10:15:38 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Close_nipple.png The as-found condition is that a prohibited fitting has been used on a gas piping system. The potential hazard is that thin walled material of the prohibited fitting will break under stress and cause a gas leak in an occupied space, resulting in a fire and explosion hazard | 3 | Non-compliant material/fittings installed | Close_nipple.png | file://x:/photopub/docs/0000000654/1a2a6d3c-e54a-4869-af36-e21a56320219.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3fa74b6_699d_41e8_bf6b_b2b7414ef240
EDIN-895090-2017 | ED-515029-2017 | 8/29/2017 4:59:57 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | #Handrail-1.png Safety zone violation | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Handrail-1.png | file://x:/photopub/docs/0000000654/7a1c3264-0369-47ea-9d44-d96549f44b7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5865f30_7dfe_48b3_84b3_1a8033fc845b
ELIN-903593-2017 | EL-540339-2017 | 9/11/2017 11:44:53 AM | ASSESS: EL: Final | png | #asFound This photo shows an outlet box inset too far into the wall. It will not be able to contain an internal fire. An extension ring is required. | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Counter.png Final assessment on new dental clinic. Counter receptacles in a mechanical room have their boxes inset into the wall too far so that the receptacles can not be secured properly. Potential fire hazard if there is a fault in the receptacle which can not be contained by the outlet box. Receptacle would be close to surrounding combustiblesin wall. | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Counter.png | file://x:/photopub/docs/0000000660/c06e4ba5-4805-4658-ae48-a8c819df5c9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fcfabf9_2255_496b_9b84_46fb0ea94f80
BPVIN-902173-2017 | UW-581475-2017 | 9/7/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | #Pressure_vessels1.png,Pressure_vessels2.png,Pressure_vessels3.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of multiple pressure vessels, I found that not every pressure vessels is protected by a Pressure Relief Device. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Pressure_vessels1.png | file://x:/photopub/docs/0000000660/6b55be9a-4885-4081-810b-71000b560b3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f551578_e8b5_44f8_b552_6eabc421fe9c
BPVIN-904863-2017 | BPV-583371-2017 | 9/11/2017 3:08:07 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Data_plate.png During site assessment, I found the 23 years old in-service air receiver mounted with machine. It is non-compliant to Boiler Safety Order SO-B6 050530 3. Due to long period of cyclic loading service and internal corrosion, there is a greater possibility that the shell thickness may have been reduced below design metal thickness due to corrosion over time. There is also possibility of pitting and cracking on all welded joints. Both these conditions may cause catastrophic failure of the air receiver, resulting in release of energy which will cause damage to nearby personnel and property. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Data_plate.png | file://x:/photopub/docs/0000000660/e465efd8-9cbb-42b8-98ff-db4e95ca7137.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__153eb21c_9a20_4302_af9a_5d129e9940b9
EDIN-896032-2017 | ED-479148-2016 | 8/30/2017 2:26:45 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED042 | Wear/Defects resulting in the brake to stop car/step unsafely. Likely to progress additional means of deceleration are functional. Risk Reg ED-02 | 3 | 3 | #Speed_governor.png A speed governor is used to regulate the speed at which the elevator safety brakes are applied to stop the elevator in the downward direction in an emergency situation. The elevator safety brakes are engaged during an emergency when the elevator travels above the calibrated governor speed. During an acceptance assessment it was found the governor was unable to engage the elevator safety brakes. The governor Pull value was such that it was too low and unable to apply the doubled-up Hollister Whitney safeties. | 3 | Wear/Defects resulting in the brake to stop car/step unsafely. Likely to progress additional means of deceleration are functional. Risk Reg ED-02 | Speed_governor.png | file://x:/photopub/docs/0000000654/bcb457e1-7bde-459b-a03c-e35ab723bbf0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ac653dd_3982_4a5f_addb_eb87ac4eaebd
GAHE-898754-2017 | HE-579707-2017 | 9/5/2017 10:42:27 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Clearance.png Propane tank installed beside commercial motel where BBQ is installed. Source of ignition near propane tank could cause fire or explosion if tank leaking or when filling with liquid spit valve. | 4 | Ignition sources present with-in minimum distance required | Clearance.png | file://x:/photopub/docs/0000000657/a5038945-90a3-4d2c-a86b-171f6dbb6b84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__105f2417_ebf8_4f0f_8cd3_5e3ba15a59cc
ELIN-904641-2017 | EL-403333-2016 | 9/11/2017 11:50:33 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | #A.png Tamper resistant receptacle not provided. This is a shock hazard as young children can access the energized parts. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | A.png | file://x:/photopub/docs/0000000661/cb8c99dd-4e34-4adc-b444-2c6f28f0ebc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__88b7b9e5_a9f7_488d_86bc_2dc891b942ba
ELHE-905236-2017 | HE-583613-2017 | 9/12/2017 1:46:57 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound An energized meter base caused by removal of the BC Hydro meter. Strips of metal siding have been inserted to keep power on to the structure. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_meter_base.png Respond to complaints on unsafe wiring on an agricultural property. A BC Hydro meter has been removed and jumped out to allow a power diversion by using strips of metal siding. The energized strips of siding are hanging out of the meter base and it is accessible to anyone on the property. A child lives in the attic of the barn this meter base is attached to. It is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_meter_base.png | file://x:/photopub/docs/0000000661/57003498-5d3c-4c64-b1a8-4bc27a73968a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0447540_e79b_4ae5_836b_a6ca2aebe913
GAHE-906156-2017 | HE-584130-2017 | 9/12/2017 1:54:30 PM | ASSESS: GA HE: Hazard Elimination | JPG | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #image1.JPG Liquefaction of propane can create a hazard. First-stage and integral two-stage propane vapour regulators that are not installed directly on a propane container can be subjected to liquid propane due to no-flow conditions and/or changes in ambient temperatures if they are installed below the liquid level of the supply container. Vapour service regulators are not designed to regulate propane liquid, and may be damaged by it, or may pass liquid leading to hazardous conditions downstream. These regulators must be installed above the maximum liquid level of the supply container(s), and have the supply connection oriented to allow for any liquid to drain back to the container. Second-stage regulators installed in areas of the province where the ambient temperature may permit reliquification at the supplied intermediate pressure are to be installed in such a manner preventing the accumulation of liquid at the regulatorâ€™s inlet. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | image1.JPG | file://x:/photopub/docs/0000000661/1b6e6ff1-c6f5-4343-a914-84edcd907ae8.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9871a14_4a26_4b8e_8aee_2128b07a1d26
GAHE-906169-2017 | HE-584144-2017 | 9/12/2017 1:27:00 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane_.png An 80 gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device installed in the tank begins to vent, and explosion or fire could occur if the heat pump cycled on, causing and arc and providing and ignition source to the propane. | 4 | Ignition sources present with-in minimum distance required | Propane_.png | file://x:/photopub/docs/0000000661/af141e47-dbfd-4081-a138-26bb53301a4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0cb6fc4d_8e52_4b3f_9530_50b8e591999f
GAHE-906168-2017 | HE-584142-2017 | 9/12/2017 1:37:56 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_location.png An 80 gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device in the tank begins to vent, an explosion or fire could occur if the heat pump cycled , causing and arc and providing an ignition source for the propane. | 4 | Ignition sources present with-in minimum distance required | Tank_location.png | file://x:/photopub/docs/0000000661/9b4665f1-dfa1-4358-896a-931d1dc752f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42fd3da5_af1b_4a43_b339_a2d273dabab6
BPVOP-875299-2017 | 2286490 | 8/9/2017 5:01:55 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP077 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | 3 | 3 | #Crack_repair_rear_of_fire_tube.png,Rear_bottom_morrision_tube_repair_area_.png Crack repairs were completed by contractor. Further NDE found other indications of surface cracks. Hydrostatic test was completed with no indication of leaks. Remaining surface cracks can grow and open with continued service. Fitness for service evaluation required. | 3 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | Crack_repair_rear_of_fire_tube.png | file://x:/photopub/docs/0000000650/749bca94-66e8-4055-a2f9-06d20f678392.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084593b2_c8bb_4603_8884_e05c2ac1dcdb
ELIN-903715-2017 | EL-572106-2017 | 9/8/2017 3:05:17 PM | ASSESS: EL: Final | png | #asFound Main 125 amp combination panel. The rating of the bus was 125amp. This panel board is being used as the utility -interconnected point of connection for the two solar photovoltaic systems. | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Pic11.png,Pic12.png - New 20amp 2pole breaker source circuits solar photovoltaic utility-interconnected breaker has been installed and now exceeds the main 125 amp rated bus of the combination panel board located within attached garage of dwelling. | 3 | Protection and control Loading of distribution equipment exceeded. | Pic12.png | file://x:/photopub/docs/0000000661/9796bccb-b0b5-425f-b141-e11ac69ae156.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7284a7a_950b_4d35_9e35_af0cd6a9a47b
ELIN-903715-2017 | EL-572106-2017 | 9/8/2017 3:05:17 PM | ASSESS: EL: Final | png | #asFound -two X 20amp 2pole photovoltaic source circuits installed in | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Pic11.png,Pic12.png - New 20amp 2pole breaker source circuits solar photovoltaic utility-interconnected breaker has been installed and now exceeds the main 125 amp rated bus of the combination panel board located within attached garage of dwelling. | 3 | Protection and control Loading of distribution equipment exceeded. | Pic11.png | file://x:/photopub/docs/0000000661/f5dd3abb-79c1-4a4c-a82d-a3cef34df70b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7284a7a_950b_4d35_9e35_af0cd6a9a47b
ELIN-888485-2017 | EL-508567-2017 | 8/28/2017 2:45:20 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Improper_staple_1.png,Improper_staple_2.png,Improper_staple_3.png Multiple cables were installed under an improper (too small) staple support. Use of staple too small for cables could damage the insulation and and cause arcing leading to fire risk. | 3 | Conductors Equipment is not approved for the specific use. | Improper_staple_3.png | file://x:/photopub/docs/0000000653/3d8ec4d0-6002-4bf9-95c8-52c33a814ca6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e326740_5c55_4dcc_bdc3_6342c86e35e7
ELIN-888485-2017 | EL-508567-2017 | 8/28/2017 2:45:20 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Improper_staple_1.png,Improper_staple_2.png,Improper_staple_3.png Multiple cables were installed under an improper (too small) staple support. Use of staple too small for cables could damage the insulation and and cause arcing leading to fire risk. | 3 | Conductors Equipment is not approved for the specific use. | Improper_staple_2.png | file://x:/photopub/docs/0000000653/01d696fd-b9c3-402b-9cc3-0fb7c41aed1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e326740_5c55_4dcc_bdc3_6342c86e35e7
ELIN-887482-2017 | EL-572017-2017 | 8/25/2017 12:50:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Backfed_distribution_from_service_conductor_from_meterbase1.png,Backfed_distribution_from_service_conductor_from_meterbase2.png,Backfed_distribution_from_service_conductor_from_meterbase3.png,Backfed_distribution_from_service_conductor_from_meterbase4.png,Backfed_distribution_from_service_conductor_from_meterbase5.png,Backfed_distribution_from_service_conductor_from_meterbase6.png Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in type ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other branch circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker thinking main breaker is off could unknowingly come in contact with energized conductors i | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Backfed_distribution_from_service_conductor_from_meterbase4.png | file://x:/photopub/docs/0000000652/e458b467-89a8-4ae9-97cd-96cfac2b3a09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3acff245_2886_4afe_be93_bae75c7b9085
ELIN-896283-2017 | EL-551234-2017 | 9/5/2017 11:57:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Gas_range_receptacle_with_Dishwasher_and_hood_fan.png This assessment found that the gas range receptacle circuit also shared the dishwasher and hood fan, potentially causing overloading of the circuit with a fire hazard in a fault condition. | 3 | Conductors Equipment is not approved for the specific use. | Gas_range_receptacle_with_Dishwasher_and_hood_fan.png | file://x:/photopub/docs/0000000657/f9304d33-833b-4f6f-81ef-99a398d22530.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bb6a130_7ba1_4e14_a46b_4fb797c67ea6
ELIN-900659-2017 | EL-537989-2017 | 9/11/2017 2:49:49 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 3 | #M1.png,M2.png A panel cover on a energized 100 Amp sub panel is not installed. This is a shock hazard to anyone in the dwelling. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | M1.png | file://x:/photopub/docs/0000000661/fff23411-f401-4b08-8b6f-3a560f472e62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__593c4e3e_e7f6_483d_99f3_1baba05eb316
ELIN-900659-2017 | EL-537989-2017 | 9/11/2017 2:49:49 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 3 | #M1.png,M2.png A panel cover on a energized 100 Amp sub panel is not installed. This is a shock hazard to anyone in the dwelling. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | M2.png | file://x:/photopub/docs/0000000661/f9e13e1f-b0ef-4d4c-b412-45c4df8e6099.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__593c4e3e_e7f6_483d_99f3_1baba05eb316
ELHE-900189-2017 | HE-580258-2017 | 9/6/2017 10:07:16 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Photo showing combustible dust at a height. The dust is building up. | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Dust_.png Hazard elimination on cabinet shop. Respond to complaints from WorkSafe BC. There is an accumulation of combustible dust in this cabinet shop at a height. The equipment is not rated for combustible dust. Therefore, a combustible dust management plan has to be developed. And electrical operating permit must also be in place. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Dust_.png | file://x:/photopub/docs/0000000658/cd1a6988-df32-4b71-9166-4c448d1848bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0aec53a_46ec_4a71_ac8d_c65d55f2c7d6
GAIN-890607-2017 | GA-576193-2017 | 9/5/2017 4:28:49 PM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_vent.png Vent on replacement hot water tank is using an oversized chimney, chimney is too large and may cause back drafting/draft hood spillage into the room causing carbon monoxide to be present into the mechanical room. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_vent.png | file://x:/photopub/docs/0000000657/c4dd2e2c-9649-4288-98df-0abf324f05ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e35a984a_b702_47fb_a7b3_b2bf127dcff1
GAHE-884394-2017 | HE-573230-2017 | 8/19/2017 7:36:22 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 4 | #Within_structure.png Propane tank and pressure relief valve at commercial general store installed beside and with in a structure. If pressure relief valve discharged or when filling the propane tank vapour propane gas could ignite due to work shop and source of ignition and could cause a fire or explosion | 3 | Clearance to combustibles not maintained | Within_structure.png | file://x:/photopub/docs/0000000648/d48f286c-5eb6-4d7d-9a67-b20cacb782d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e19ca1a8_d312_4999_b8b8_452676406397
ELIN-897188-2017 | 3918110 | 9/8/2017 10:17:06 AM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | #No_mechanical_protection_on_feeder_to_garden_shed.png In a single family dwelling a detached garden shed 120/240 volt 15 amp feeder cable was found to exit the earth without mechanical protection. This could result in an equipment damage condition. Picture attached. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | No_mechanical_protection_on_feeder_to_garden_shed.png | file://x:/photopub/docs/0000000660/d0e1d1bb-364f-407c-a07d-8991366248a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1631bdb4_a510_4c22_9e87_ba704efff473
ELIN-901522-2017 | EL-528088-2017 | 9/8/2017 2:11:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Conductor_of_insufficient_size_for_200_amp_service.png In a new residential single family dwelling a 200 amp 120/240 volt cable was found to be of insufficient size for intended use. This could cause a thermal effect condition. Picture attached. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Conductor_of_insufficient_size_for_200_amp_service.png | file://x:/photopub/docs/0000000660/e5ea9ce6-36d7-46a7-8539-201aef3b8bb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__595ad12c_b5ee_4f70_a347_2d7e5ceb063c
BPVOP-877053-2017 | 4881162 | 8/10/2017 2:44:54 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that horizontal machine mounted air receiver (0.90m long and 0.50m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000645/7e5a3a3a-dab8-4317-aca7-98afd1453a37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd89816f_990e_4062_928e_b78d6e27183e
BPVOP-905289-2017 | 3298889 | 9/11/2017 3:42:03 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound PSV set pressure | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #PSV.png The pressure relief valve installed on this vessel has a set pressure that exceeds the maximum allowable pressure for the vessel. The vessel is designed for 200 PSIG maximum and the valve is set at 325 PSIG. This could lead to overpressure, damage and possibly a failure of the vessel if the pressure switch failed to stop the compressor in time. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | PSV.png | file://x:/photopub/docs/0000000660/1c595b4d-12d6-40ec-9a50-87bd61e76854.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13af5fc9_b0f0_443c_a90b_68ced9ed2f58
ELIN-895552-2017 | EL-575277-2017 | 8/31/2017 8:24:31 AM | ASSESS: EL: Service Connection | png | #asFound Grounding electrode not buried | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #grounding_electrode_not_buried.png Grounding electrode not buried, should a ground fault occur when someone is within proximity of the electrical service, that person will not be at equal potential to the electrical equipment and will receive an electrical shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | grounding_electrode_not_buried.png | file://x:/photopub/docs/0000000655/66d85017-f8d5-4fde-b8c9-6f60cf28c2d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8101d190_fc4c_416b_ace5_f96c936387f9
GAWP-865008-2017 | GA-555680-2017 | 8/15/2017 10:07:35 AM | ASSESS: GA Work In Progress | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Clearance_to_combustible_material_not_met1.png,Clearance_to_combustible_material_not_met2.png Clearance to combustible material not met. Combustible material inside the area outlined by the manufacturer as the clearance to combustible material may start on fire. | 3 | Clearance to combustible not met | Clearance_to_combustible_material_not_met1.png | file://x:/photopub/docs/0000000646/103e6b19-af9b-4524-9410-fec554b415aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed97b990_1861_4ab4_ba5b_7a340afbde06
GAWP-865008-2017 | GA-555680-2017 | 8/15/2017 10:07:35 AM | ASSESS: GA Work In Progress | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Clearance_to_combustible_material_not_met1.png,Clearance_to_combustible_material_not_met2.png Clearance to combustible material not met. Combustible material inside the area outlined by the manufacturer as the clearance to combustible material may start on fire. | 3 | Clearance to combustible not met | Clearance_to_combustible_material_not_met2.png | file://x:/photopub/docs/0000000646/8b73fbc0-2ae6-45a0-b8a9-61f10cfd3c72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed97b990_1861_4ab4_ba5b_7a340afbde06
GAIN-846744-2017 | GA-504817-2017 | 8/15/2017 10:55:02 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_venting11.png,Oversized_venting12.png,Oversized_venting13.png Oversized venting for natural draft appliance. Appliance vents in ideal conditions but spills flue products to space under other than ideal conditions. Possible exposure of building occupant to flue products when appliance is spilling flue products into the space. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_venting13.png | file://x:/photopub/docs/0000000646/d3946d47-8d70-4b6c-b0d8-66e516711d32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81520e94_fb04_4582_a2fc_6d5d99b272c7
GAIN-846744-2017 | GA-504817-2017 | 8/15/2017 10:55:02 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_venting11.png,Oversized_venting12.png,Oversized_venting13.png Oversized venting for natural draft appliance. Appliance vents in ideal conditions but spills flue products to space under other than ideal conditions. Possible exposure of building occupant to flue products when appliance is spilling flue products into the space. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_venting12.png | file://x:/photopub/docs/0000000646/25a98fd9-0051-4bdb-a7cc-3517c9ee9597.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81520e94_fb04_4582_a2fc_6d5d99b272c7
GAIN-846744-2017 | GA-504817-2017 | 8/15/2017 10:55:02 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_venting11.png,Oversized_venting12.png,Oversized_venting13.png Oversized venting for natural draft appliance. Appliance vents in ideal conditions but spills flue products to space under other than ideal conditions. Possible exposure of building occupant to flue products when appliance is spilling flue products into the space. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_venting11.png | file://x:/photopub/docs/0000000646/26c9ca47-debe-4d81-a361-66b97585edb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81520e94_fb04_4582_a2fc_6d5d99b272c7
BPVOP-894027-2017 | 2259143 | 8/31/2017 9:07:39 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Casing_holes1.png,Casing_holes2.png During the inspection of a HP Steam boiler with MAWP of 150 psig it was found that the casing had cracks and holes. This can lead to flue gases to escape in the boiler room and endanger the human life. | 4 | 5.1.0 In service proc/process - Casing leakage | Casing_holes1.png | file://x:/photopub/docs/0000000656/82e25340-ea7f-4eec-9d89-25009e6f64e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a55c3016_ae71_4b4b_9e60_5a8364f23193
BPVOP-894027-2017 | 2259143 | 8/31/2017 9:07:39 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Casing_holes1.png,Casing_holes2.png During the inspection of a HP Steam boiler with MAWP of 150 psig it was found that the casing had cracks and holes. This can lead to flue gases to escape in the boiler room and endanger the human life. | 4 | 5.1.0 In service proc/process - Casing leakage | Casing_holes2.png | file://x:/photopub/docs/0000000656/37bb5d35-ffaf-46d4-9421-2fb983fbc6ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a55c3016_ae71_4b4b_9e60_5a8364f23193
ELOP-866488-2017 | EL-548206-2017 | 8/3/2017 11:38:06 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #G.png An AC90 cable is not enclosed in a junction box. This is a shock and fire hazard to the people in this building. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | G.png | file://x:/photopub/docs/0000000640/7cd2a3b1-765e-46c9-9bd4-3c957562a11f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F326F962_AF8A_4C88_8E25_3DB9661EFA95
ELIN-881952-2017 | EL-572020-2017 | 8/21/2017 1:03:59 PM | ASSESS: EL: Final | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Bath_fan.png The existing 15 amp 120 volt bathroom fan located in the main washroom of a mobile home (was unplugged) was tested and found to be seized. This fan if left energized is a thermal hazard | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Bath_fan.png | file://x:/photopub/docs/0000000649/655d8afe-c085-498d-bf00-628358dd9df3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7e04fa_0576_48bd_b6a3_e4dc28fc0bc9
GAIN-876950-2017 | GA-569790-2017 | 8/23/2017 2:03:57 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Vent.png Insufficient clearances between appliance vent and mechanical air intake. Potential for flue gas to enter the intake and enter occupied working space creating a hazardous situation where CO might be present. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Vent.png | file://x:/photopub/docs/0000000651/43108a29-d2aa-4062-b66f-499888a40d3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d99829e2_e30e_4dfd_ab3e_27066d2bb367
ELHE-887721-2017 | HE-575236-2017 | 8/22/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Badly rusted and damaged combination panelboard and it branch circuit breakers have had water entering circuit breakers and is not approved for the use or connection to power supply system | EL294 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Feeder_still_connected_and_not_de-energized_to_damaged_rusted_panelboard1.png,Feeder_still_connected_and_not_de-energized_to_damaged_rusted_panelboard2.png Found severely rusted and damaged combination panelboard and it branch circuit breakers have had water entering circuit breakers and panelboard. When electrical distribution equipment becomes wet, rusted and damaged the electrical equipment is an electrical fire or shock hazard to people and property and is not approved and is not authorized for the use or for connection to power supply system. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Feeder_still_connected_and_not_de-energized_to_damaged_rusted_panelboard2.png | file://x:/photopub/docs/0000000651/6081f706-4559-4000-8a32-2af2e147ac22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50aca6f2_4ce8_4231_8cff_be83bf2a3510
ELIN-870152-2017 | EL-503146-2017 | 8/9/2017 4:04:34 PM | ASSESS: EL: Final | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Emergency_Lighting.png A 150 watt 12 volt Emergency Lighting Pack has been installed to power various 12 volt 5 watt remote Emergency Heads through out the building, but the EM Pack has not been fed from the lighting circuit in the area that it serves. This poses a safety risk as the general lighting could fail and the Emergency Lighting for that area may not come on because it's fed from a different lighting circuit. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Emergency_Lighting.png | file://x:/photopub/docs/0000000643/3a5474ed-98d5-4711-af02-7aa225c10f4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e504b148_dabf_4cf0_ba53_22f8b516dcc5
BPVOP-851297-2017 | 2255317 | 7/31/2017 2:16:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Certificate_of_qualification.png A Hot Water boiler with a maximum allowable working pressure of 125 psig and a maximum allowable working temperature of 250 degrees Fahrenheit, it was determined there was no continuous supervision by qualified operators during after hours. Potential exists to lead to damage of equipment or injury to personnel. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Certificate_of_qualification.png | file://x:/photopub/docs/0000000638/f4b6305e-adbe-4ada-bb7d-5935982ccee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__459846a5_05bd_4a31_8383_1aa84d480433
GAIN-873188-2017 | GA-565438-2017 | 8/4/2017 10:14:51 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Fire.png,FireDisplay1.png,FireDisplay2.png,FireDisplay3.png,FireDisplay4.png Uncertified fire displays installed and connected for use. Potential for failure of an unapproved appliance causing injury or damage. | 0 | No Created Hazard Identified | FireDisplay1.png | file://x:/photopub/docs/0000000641/642c0143-a3c7-44b1-b0f8-9cb30a353a27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e81237c8_7745_42e5_9e38_b034546d3bec
GAIN-873188-2017 | GA-565438-2017 | 8/4/2017 10:14:51 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Fire.png,FireDisplay1.png,FireDisplay2.png,FireDisplay3.png,FireDisplay4.png Uncertified fire displays installed and connected for use. Potential for failure of an unapproved appliance causing injury or damage. | 0 | No Created Hazard Identified | Fire.png | file://x:/photopub/docs/0000000641/a30c25dc-0d9e-4bc7-b9c9-5e6126be8732.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e81237c8_7745_42e5_9e38_b034546d3bec
GAIN-873188-2017 | GA-565438-2017 | 8/4/2017 10:14:51 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Fire.png,FireDisplay1.png,FireDisplay2.png,FireDisplay3.png,FireDisplay4.png Uncertified fire displays installed and connected for use. Potential for failure of an unapproved appliance causing injury or damage. | 0 | No Created Hazard Identified | FireDisplay4.png | file://x:/photopub/docs/0000000641/72f9592d-adb3-4b70-894c-6833c4f9d564.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e81237c8_7745_42e5_9e38_b034546d3bec
GAIN-873188-2017 | GA-565438-2017 | 8/4/2017 10:14:51 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Fire.png,FireDisplay1.png,FireDisplay2.png,FireDisplay3.png,FireDisplay4.png Uncertified fire displays installed and connected for use. Potential for failure of an unapproved appliance causing injury or damage. | 0 | No Created Hazard Identified | FireDisplay2.png | file://x:/photopub/docs/0000000641/d105f163-9ef6-4601-a272-603136d83bf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e81237c8_7745_42e5_9e38_b034546d3bec
GAIN-873188-2017 | GA-565438-2017 | 8/4/2017 10:14:51 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Fire.png,FireDisplay1.png,FireDisplay2.png,FireDisplay3.png,FireDisplay4.png Uncertified fire displays installed and connected for use. Potential for failure of an unapproved appliance causing injury or damage. | 0 | No Created Hazard Identified | FireDisplay3.png | file://x:/photopub/docs/0000000641/0fb2e324-49cf-48ad-9e67-014bf6ba6697.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e81237c8_7745_42e5_9e38_b034546d3bec
AMOP-878187-2017 | AM-272611-2015 | 8/12/2017 10:58:28 AM | ASSESS: AM OP: Operational | ocx | #asFound Slide the City Collision Protection Plan | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Slide_the_City_Collision_Prevention_Plan.docx The operators Collision Protection Plan requires that managers (attendant) that are required to monitor the slide along it length be carrying a radio that allows for communication to the manager (attendant) at the top of the slide. The manager (attendant) at the top of the slide is responsible for dispatching riders at a safe intervals and must be in communication with managers monitoring the length of the slide to ensure safe intervals are maintained. A manager (attendant) at the midsection of the slide was not carrying a radio and therefore would make it challenging to communicate with the top of the slide. This would likely result in an increased risk in rider collisions. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Slide_the_City_Collision_Prevention_Plan.docx | file://x:/photopub/docs/0000000645/b67eb34d-1f02-454b-86f4-4f1bb03dff4edocx | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9737f7fd_31a6_46bf_a2eb_3a7aba765f6f
AMOP-878187-2017 | AM-272611-2015 | 8/12/2017 10:58:28 AM | ASSESS: AM OP: Operational | ocx | #asFound Slide the City Collision Prevention Plan | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | #Slide_the_City_Collision_Prevention_Plan.docx The operators Collision Protection Plan requires that managers (attendant) that are required to monitor the slide along it length be carrying a radio that allows for communication to the manager (attendant) at the top of the slide. The manager (attendant) at the top of the slide is responsible for dispatching riders at a safe intervals and must be in communication with managers monitoring the length of the slide to ensure safe intervals are maintained. A manager (attendant) at the midsection of the slide was not carrying a radio and therefore would make it challenging to communicate with the top of the slide. This would likely result in an increased risk in rider collisions. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Slide_the_City_Collision_Prevention_Plan.docx | file://x:/photopub/docs/0000000645/1a5a0d1a-0fc8-4a24-969c-f961e458715adocx | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9737f7fd_31a6_46bf_a2eb_3a7aba765f6f
ELHE-887721-2017 | HE-575236-2017 | 8/22/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Badly rusted and damaged combination panelboard and it branch circuit breakers have had water entering circuit breakers and is not approved for the use or connection to power supply system | EL294 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Feeder_still_connected_and_not_de-energized_to_damaged_rusted_panelboard1.png,Feeder_still_connected_and_not_de-energized_to_damaged_rusted_panelboard2.png Found severely rusted and damaged combination panelboard and it branch circuit breakers have had water entering circuit breakers and panelboard. When electrical distribution equipment becomes wet, rusted and damaged the electrical equipment is an electrical fire or shock hazard to people and property and is not approved and is not authorized for the use or for connection to power supply system. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Feeder_still_connected_and_not_de-energized_to_damaged_rusted_panelboard1.png | file://x:/photopub/docs/0000000651/db552580-fc57-410d-b6d9-20cb87ddb697.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50aca6f2_4ce8_4231_8cff_be83bf2a3510
ELHE-895661-2017 | HE-577970-2017 | 8/30/2017 1:17:39 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Flexible_cord_used_for_permanent_wiring.png 15 amp, 120 volt branch circuit has flexible cord used for permanent wiring and running through structures. This is a thermal issue. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_permanent_wiring.png | file://x:/photopub/docs/0000000654/607940e2-a609-4e5c-bd16-f452c915468c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d6da915_5562_4867_9f59_8206a1b39fed
ELIN-891162-2017 | EL-458543-2016 | 8/29/2017 2:59:09 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #GFCI_not_operational_with_circuit_turned_on_.png GFCI type receptacles have been installed in kitchen counter area. Overcurrent devices protecting these receptacles have the handles in the on position. When receptacles are tested they do not indicate that they are on,but the green light on the front of the receptacle is on. ESO is unable to confirm if the receptacles are wired correctly or if the receptacles are defective. Leakage currents associated with the location of these receptacles requires GFCI protection, without this protection a risk of shock and fire could occur. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | GFCI_not_operational_with_circuit_turned_on_.png | file://x:/photopub/docs/0000000653/45f5eb6e-3e4c-4140-a905-d36ff0e9d0ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74faa053_b579_4d02_a389_9700d604d612
GAIN-883170-2017 | GA-511919-2017 | 8/22/2017 2:08:47 PM | ASSESS: GA: Final | png | #asFound Relief 4" from roof | GA013 | Regulator relief buried in snow ice or dirt | 4 | 4 | #Regulator_relief.png Regulator installed four inches from roof, if it becomes frozen from ice or snow in winter in will not regulate gas properly to units being served in store, which could lead to dangerous situation leading to damage or injury. | 4 | Regulator relief buried in snow ice or dirt | Regulator_relief.png | file://x:/photopub/docs/0000000650/a144347c-f9a6-4b8e-bcbf-0b9464dae655.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4a118e0_89d3_491b_aa04_0dbe297c2ff3
ELIN-869000-2017 | EL-565410-2017 | 8/14/2017 3:22:36 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | #Dishwasher.png In a single wide modular home, a 15amp 120volt dishwasher was found connected to the existing kitchen counter receptacle. This can lead to "Thermal Effect" condition. Pic attached | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Dishwasher.png | file://x:/photopub/docs/0000000646/abc618e4-f13a-43b9-87ef-22526ad9f440.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb647ff7_6362_47b7_892a_f5cfc9f8245b
ELIN-882801-2017 | EL-568809-2017 | 8/21/2017 11:01:43 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | #A.png Non metallic sheathed cable left coiled up in cabinet above stove for microwave/range hood. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000649/477ea816-941f-4673-a21a-a6dd65476c9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c182235d_e027_410e_89b2_4c0a481dfb76
EDIN-888648-2017 | ED-549127-2017 | 8/24/2017 2:04:42 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED009 | Defects that are: Detected by Maintenance program Likely to progress | 2 | 2 | #Sharp_edges1.png,Sharp_edges2.png Sheet metal used as part of the hoistway walls was cut in a manner that left sharp edges and corners. Riders would be exposed to these cut hazards. | 2 | Defects that are: Detected by Maintenance program Likely to progress | Sharp_edges1.png | file://x:/photopub/docs/0000000652/cc17176f-eb87-4754-b694-bade74762543.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e840bb7_507a_44d3_9b63_18ebeabb5e64
EDIN-888648-2017 | ED-549127-2017 | 8/24/2017 2:04:42 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED009 | Defects that are: Detected by Maintenance program Likely to progress | 2 | 2 | #Sharp_edges1.png,Sharp_edges2.png Sheet metal used as part of the hoistway walls was cut in a manner that left sharp edges and corners. Riders would be exposed to these cut hazards. | 2 | Defects that are: Detected by Maintenance program Likely to progress | Sharp_edges2.png | file://x:/photopub/docs/0000000652/8a2041ca-0b5a-4191-b005-7ab5fbfc2abe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e840bb7_507a_44d3_9b63_18ebeabb5e64
GAIN-875751-2017 | GA-327059-2015 | 8/15/2017 8:48:14 AM | ASSESS: GA: Rough-In | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Regulator_.png The as-found condition is that three line pressure regulators with internal relief are not vented to the outdoors. The potential hazard is if the regulator vents it will relieve a large amount of raw gas into a confined space, creating a significant fire and explosion hazard. | 5 | Relief style regulator/device allowed to vent within building/confined space | Regulator_.png | file://x:/photopub/docs/0000000646/2c5ad2e9-3253-4939-8804-8c63d1be3c2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84667d8f_1ab6_4e9a_85ee_2b84ca15f09a
GAIN-871275-2017 | GA-547468-2017 | 8/14/2017 1:05:32 PM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Regulator.png The as-found condition is that the regulators serving commercial kitchen appliances are not rated for the gas delivery pressure. The potential hazard is that the excessive delivery pressure will cause the regulators to allow excessive pressure to the appliances causing them to over fire, resulting in a risk of fire and explosion. | 4 | Appliance regulator not installed, incorrect delivery pressure | Regulator.png | file://x:/photopub/docs/0000000646/ed08065f-84be-413a-83c1-2419f6801f3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96432d2a_e15a_4fbd_9f80_dc4f8ad5a538
ELOP-879750-2017 | 6560 | 8/14/2017 12:50:08 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Bonding_hm1.png,Bonding_hm2.png,Bonding_hm3.png Bonding not continuous for Quadplex Delta Overhead Wiring to HOG area which could result in a potential voltage difference and possible shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_hm1.png | file://x:/photopub/docs/0000000647/1ed8cfa2-daff-4f37-b0ae-c119eea82a49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e1443d7_5932_42d1_801f_bafca4a98359
ELOP-879750-2017 | 6560 | 8/14/2017 12:50:08 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Bonding_hm1.png,Bonding_hm2.png,Bonding_hm3.png Bonding not continuous for Quadplex Delta Overhead Wiring to HOG area which could result in a potential voltage difference and possible shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_hm2.png | file://x:/photopub/docs/0000000647/ceb599dc-54dd-431f-8be5-7baaeb3fe9f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e1443d7_5932_42d1_801f_bafca4a98359
ELOP-879750-2017 | 6560 | 8/14/2017 12:50:08 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Bonding_hm1.png,Bonding_hm2.png,Bonding_hm3.png Bonding not continuous for Quadplex Delta Overhead Wiring to HOG area which could result in a potential voltage difference and possible shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_hm3.png | file://x:/photopub/docs/0000000647/9e13d534-6ec0-4091-8255-225ef3b286d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e1443d7_5932_42d1_801f_bafca4a98359
ELIN-874000-2017 | EL-543121-2017 | 8/9/2017 2:18:10 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 2 | #H.png Exterior receptacles were missing in use weather proof cover plates. This is a shock hazard to individuals using these receptacles. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | H.png | file://x:/photopub/docs/0000000643/6de5dcfe-39de-42ec-bb31-7182c3a59a9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3b01504_1d41_4338_9a9f_a9e8b9cd8ab5
ELIN-880541-2017 | EL-570058-2017 | 8/23/2017 2:00:34 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Grounding2.png,Grounding3.png,Generator_disconnect.png The installation of a secondary 'grounding' conductor with mechanical connection point to existing main ground system located in the 400 amp rated generator disconnect (200 amp 120/240 volt supply) in a commercial poultry barn provides a secondary path for current to flow in parallel with the identified conductor. This can lead to a shock hazard | 3 | Continuity Bonding; method for equipment is not adequate. | Grounding2.png | file://x:/photopub/docs/0000000651/f4be3d94-fef1-4883-91e2-4f4f2925ebc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46b25697_7364_476e_9bf9_966bd8f577cf
ELIN-880541-2017 | EL-570058-2017 | 8/23/2017 2:00:34 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Grounding2.png,Grounding3.png,Generator_disconnect.png The installation of a secondary 'grounding' conductor with mechanical connection point to existing main ground system located in the 400 amp rated generator disconnect (200 amp 120/240 volt supply) in a commercial poultry barn provides a secondary path for current to flow in parallel with the identified conductor. This can lead to a shock hazard | 3 | Continuity Bonding; method for equipment is not adequate. | Generator_disconnect.png | file://x:/photopub/docs/0000000651/159a1bc2-b297-4ffd-b2ac-a92efef178b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46b25697_7364_476e_9bf9_966bd8f577cf
ELIN-868463-2017 | EL-518871-2017 | 8/1/2017 11:42:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMD90_1.png,NMD90_2.png Two 120 volt 15 & 20 amp non metallic sheathed cables have been installed in an underground plumbing pipe which also has a Hot and cold water line installed inside of it. The wiring is not rated to be installed underground or in contact with hot water lines, this could lead to failure of the wire's protective jacket and insulation, resulting in a possible shock hazard to persons and equipment failure. | 3 | Conductors Equipment is not approved for the specific use. | NMD90_1.png | file://x:/photopub/docs/0000000639/2f88f681-ca4d-46d7-b78f-3a7d0aa1bff7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d58af39_353e_40a2_be72_855b2c9a2d3d
ELIN-882903-2017 | EL-572311-2017 | 8/21/2017 1:15:56 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_Cover_Plates1.png,Missing_Cover_Plates2.png This assessment found that cover plates missing in dwelling unit, creating a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_Cover_Plates1.png | file://x:/photopub/docs/0000000649/09f5df50-dfdb-4a71-a05b-05f0bbb8fe03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b047b277_6b95_4a3c_8b42_0e87787174c9
ELIN-882903-2017 | EL-572311-2017 | 8/21/2017 1:15:56 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Missing_Cover_Plates1.png,Missing_Cover_Plates2.png This assessment found that cover plates missing in dwelling unit, creating a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_Cover_Plates2.png | file://x:/photopub/docs/0000000649/bf595fad-c7fd-4956-8f77-7d6ef26a91c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b047b277_6b95_4a3c_8b42_0e87787174c9
ELHE-883053-2017 | HE-572511-2017 | 8/17/2017 4:35:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_service_equipment_reinstalled_on_new_siding1.png,Existing_service_equipment_reinstalled_on_new_siding2.png,Existing_service_equipment_reinstalled_on_new_siding3.png The existing 200 amp 120/240 volt residential service equipment (consumer service conduits/conductors, meterbase and utility overhead point of attachment) on the exterior of residence were loosened from wall to remove old siding and re-mounted on new siding all while energized without utility disconnect/reconnect requirements. This is both a shock and thermal hazard. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Existing_service_equipment_reinstalled_on_new_siding1.png | file://x:/photopub/docs/0000000648/02f405e4-1521-462b-afaf-c5c581f84789.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91ee4c3a_699c_442a_a60f_e748980fd81f
ELIN-877047-2017 | EL-519249-2017 | 8/10/2017 1:44:16 PM | ASSESS: EL: Service Connection | png | #asFound Servicemaster covered by builder | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #Service_mast_covered.png Consumer service mast located inside wall which is not concrete encased, consumer service conductors are not adequately protected should A fault or fire occur. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_mast_covered.png | file://x:/photopub/docs/0000000644/3cfa1318-8ef2-4d11-8140-55c9849baeba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__342f77e4_a0b4_4ace_b4df_5eb505efcfda
GAIN-842098-2017 | GA-456751-2016 | 8/14/2017 12:45:27 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #Propaneregulator.png | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Propaneregulator.png | file://x:/photopub/docs/0000000645/c3958310-6964-4cfb-8538-f1629ac6b2f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__335ec770_6972_4562_83fe_a460a251ac77
GAIN-867399-2017 | GA-534945-2017 | 8/10/2017 3:29:08 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #No_combustion_air.png Combustion air is required to provide a gas burner with the appropriate amount of air to safely burn. Combustion air is not present on this install. The gas burner will starve itself of air and the flame may source out air from another source ie, outside of the combustion chamber or it can soot up and block chimney. This can cause possible fire damage to surrounding area as well as appliance. | 4 | Combustion air supply missing | No_combustion_air.png | file://x:/photopub/docs/0000000644/b865712e-36d9-4610-9aba-d6e188399777.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3cc3d165_fee2_432c_a2ff_c1f5f2b8e2f2
GAIN-867397-2017 | GA-489125-2017 | 8/10/2017 2:53:18 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | #Vertical_reg.png 2psi to Low Pressure Regulator installed vertically. Vent limiting device on relief of Regulator will not vent gas out properly in an overpressure scenario. Vent limiting device has a ball bearing inside it which does not sit over relief port when installed vertically. Possible gas leak can happen if Regulator was to fail in the installed position. | 3 | Regulator vent not terminated as per manufacturers instruction | Vertical_reg.png | file://x:/photopub/docs/0000000644/8e51af93-2dc6-43aa-b213-4cb503a15e50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96ab1f5a_f7e7_4231_b61f_135ffe909c31
ELOP-841613-2017 | EL-503972-2017 | 8/22/2017 7:09:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exterior_conduits_and_lighting1.png,Exterior_conduits_and_lighting2.png,Exterior_conduits_and_lighting3.png,Exterior_conduits_and_lighting4.png,Exterior_conduits_and_lighting5.png,Exterior_conduits_and_lighting6.png Unprotected underground raceways in non-vehicular areas are required to to be installed a minimum of 450mm below grade and to have marker tape installed half way between the installed conduit and top of grade. The conductors installed in the raceway must also be suitable for the condition of use (wet location) During an operating permit assessment at a hotel, the underground PVC conduits for new exterior lighting in the garden area's beside the sidewalks were found to be at a depth of approximately 150mm and did not have marker tape above the conduit. The conductors inside the raceways was non-metallic sheathed cable rated for dry location. The shallow depth of the unmarked conduit has the potential to be damaged by persons working in the garden and could create a shock hazard if the conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exterior_conduits_and_lighting5.png | file://x:/photopub/docs/0000000650/56a37770-1703-45bb-8fca-2639252fe75b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__C93F1D94_C619_487D_9D1E_9F95B751F1B3
ELIN-880541-2017 | EL-570058-2017 | 8/23/2017 2:00:34 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Grounding2.png,Grounding3.png,Generator_disconnect.png The installation of a secondary 'grounding' conductor with mechanical connection point to existing main ground system located in the 400 amp rated generator disconnect (200 amp 120/240 volt supply) in a commercial poultry barn provides a secondary path for current to flow in parallel with the identified conductor. This can lead to a shock hazard | 3 | Continuity Bonding; method for equipment is not adequate. | Grounding3.png | file://x:/photopub/docs/0000000651/d4f1b310-5f21-425e-bebf-a36a0e617ba4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46b25697_7364_476e_9bf9_966bd8f577cf
GAIN-874781-2017 | GA-521165-2017 | 8/10/2017 3:34:32 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Unit.png The as-found condition is that the exhaust from a direct-fired make-up air unit terminates too close to a building air supply inlet. The potential hazard is that the exhaust from the make-up air will enter the building air supply and circulate harmful products of combustion such as carbon monoxide throughout the building | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Unit.png | file://x:/photopub/docs/0000000644/98aa5667-d7e4-44a0-8953-20ec8bf8b43e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2e8be72_4a72_4a47_b049_b8c54c679daa
ELIN-873356-2017 | EL-562390-2017 | 8/8/2017 9:40:43 AM | ASSESS: EL: Service Connection | png | #asFound Weatherproof connecter not tight, loose to finger | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Weatherproof_connecter.png Weatherproof connecter not tight, 1) likelihood of water or rain can permeate into electrical equipment, 2) Should a short circuit occur in the service conduit any fault current would not make its way back to the electrical distribution equipment and facilitate the overcurrent device. Should anyone touch the conduit under a short-circuit condition they may receive a shock because the bonding path through the EMT connecter is not complete. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Weatherproof_connecter.png | file://x:/photopub/docs/0000000642/7706ae71-80dd-4b82-83a3-30baa862d638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05003245_31fd_4d69_8588_7d95a01fd7bc
ELHE-883053-2017 | HE-572511-2017 | 8/17/2017 4:35:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_service_equipment_reinstalled_on_new_siding1.png,Existing_service_equipment_reinstalled_on_new_siding2.png,Existing_service_equipment_reinstalled_on_new_siding3.png The existing 200 amp 120/240 volt residential service equipment (consumer service conduits/conductors, meterbase and utility overhead point of attachment) on the exterior of residence were loosened from wall to remove old siding and re-mounted on new siding all while energized without utility disconnect/reconnect requirements. This is both a shock and thermal hazard. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Existing_service_equipment_reinstalled_on_new_siding3.png | file://x:/photopub/docs/0000000648/4d2f5c22-4d01-4efd-a818-13127d2c52d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91ee4c3a_699c_442a_a60f_e748980fd81f
ELHE-883053-2017 | HE-572511-2017 | 8/17/2017 4:35:55 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_service_equipment_reinstalled_on_new_siding1.png,Existing_service_equipment_reinstalled_on_new_siding2.png,Existing_service_equipment_reinstalled_on_new_siding3.png The existing 200 amp 120/240 volt residential service equipment (consumer service conduits/conductors, meterbase and utility overhead point of attachment) on the exterior of residence were loosened from wall to remove old siding and re-mounted on new siding all while energized without utility disconnect/reconnect requirements. This is both a shock and thermal hazard. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Existing_service_equipment_reinstalled_on_new_siding2.png | file://x:/photopub/docs/0000000648/d0173102-1f84-4f11-b711-263c3d17a9d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91ee4c3a_699c_442a_a60f_e748980fd81f
GAIN-849373-2017 | GA-513596-2017 | 8/23/2017 3:59:12 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | #Airsupply.png Combustion air supply missing for a gas furnace and hot water heater. Properly sized combustion air is required for the Natural Gas appliances to function properly. This may lead to incomplete combustion creating an unsafe condition and pre-mature failure of appliances. | 4 | Combustion air supply missing | Airsupply.png | file://x:/photopub/docs/0000000651/287a95f9-cc02-46d3-b273-b5b9a4219bb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8d87d16_b91d_475d_ae67_a5258f2e6c55
ELIN-890995-2017 | EL-576923-2017 | 8/29/2017 2:38:26 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Weathertight_box_compromised.png | 0 | No Created Hazard Identified | Weathertight_box_compromised.png | file://x:/photopub/docs/0000000654/882f9a14-3abc-4003-aef1-f278d2975699.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4217bff6_2db6_4798_ae97_c7234ff9f139
ELIN-881998-2017 | EL-474758-2016 | 8/30/2017 11:06:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #AC90_outdoors.png The 30 amp 250 volt AC90 cable feeding the Hot Tub located outdoors is in a Wet location, the AC90 cable is not rated for the wet location and will corrode and become damaged over time, this can lead to all of Thermal, Equipment damage and a shock issue | 3 | Conductors Equipment is not approved for the specific use. | AC90_outdoors.png | file://x:/photopub/docs/0000000655/7cba3b6d-4ba2-4906-a942-c5f653e98dcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd2761c3_3a8e_495f_95f7_bc83ae5e340d
BPVIN-902867-2017 | UW-582513-2017 | 9/7/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_devices1.png,Safety_relief_devices2.png All pressure relief devices require periodic servicing and maintenance. There was no evidence to support when the pressure relief devices were last tested, serviced or replaced. Potential exists for an incident if the pressure relief devices fail. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_devices2.png | file://x:/photopub/docs/0000000660/c8abbfba-fe0a-4639-838f-bdd23ddb8479.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__936414f7_4c5e_4b59_ac92_138bc6f91dd7
BPVIN-902867-2017 | UW-582513-2017 | 9/7/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_devices1.png,Safety_relief_devices2.png All pressure relief devices require periodic servicing and maintenance. There was no evidence to support when the pressure relief devices were last tested, serviced or replaced. Potential exists for an incident if the pressure relief devices fail. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_devices1.png | file://x:/photopub/docs/0000000660/d290d871-8ee3-413b-8168-977da05d18a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__936414f7_4c5e_4b59_ac92_138bc6f91dd7
ELIN-896640-2017 | EL-577117-2017 | 9/8/2017 11:01:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Service_.png Single family dwelling overhead 200A, 240V, 1PH service displays evidence of a short circuit/electrical continuity between the grounded service conductors and the ungrounded service conductors in the section between the meter mounting enclosure and the main panelboard. All other aspects of the installation are safe and compliant. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_.png | file://x:/photopub/docs/0000000660/ab049584-903b-4177-a5ed-c1fc983dc691.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c661ffd0_3c3f_4fc4_8829_6023d8a846db
ELIN-900162-2017 | EL-580248-2017 | 9/8/2017 1:00:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service1.png,Service2.png Single family dwelling electrically supplied by a 200A 240V 1PH underground service is under construction; currently without a roof or floor system. Licensed electrical contractor has requested a service connection, however the main panelboard (dry location type 1 enclosure) is installed to a perimeter wall, exposed to the elements and weather, without any adequate protection to protect the panelboard from the elements. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service1.png | file://x:/photopub/docs/0000000660/f1f6e4aa-fa29-489b-b891-51caa8d337e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15eb4cf5_e719_4c80_98a0_cb1ac0542556
ELIN-900162-2017 | EL-580248-2017 | 9/8/2017 1:00:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service1.png,Service2.png Single family dwelling electrically supplied by a 200A 240V 1PH underground service is under construction; currently without a roof or floor system. Licensed electrical contractor has requested a service connection, however the main panelboard (dry location type 1 enclosure) is installed to a perimeter wall, exposed to the elements and weather, without any adequate protection to protect the panelboard from the elements. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service2.png | file://x:/photopub/docs/0000000660/8c344f79-ea87-49f0-9c75-9943f777c6b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15eb4cf5_e719_4c80_98a0_cb1ac0542556
ELIN-897919-2017 | EL-533609-2017 | 9/5/2017 7:51:34 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Swamp_cooler_branch_circuit1.png,Swamp_cooler_branch_circuit2.png The 15 amp 120 volt teck branch circuit cable does is not suitably strapped and is exposed to mechanical damage, this can lead to an equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Swamp_cooler_branch_circuit1.png | file://x:/photopub/docs/0000000657/716c1cef-8efc-439a-ae57-1cffecdf60bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0993bd91_e55f_4e2f_9259_92ae4f0196ba
ELIN-897919-2017 | EL-533609-2017 | 9/5/2017 7:51:34 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Swamp_cooler_branch_circuit1.png,Swamp_cooler_branch_circuit2.png The 15 amp 120 volt teck branch circuit cable does is not suitably strapped and is exposed to mechanical damage, this can lead to an equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Swamp_cooler_branch_circuit2.png | file://x:/photopub/docs/0000000657/ebf23c7e-490e-4351-a1fc-308b2bbd35c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0993bd91_e55f_4e2f_9259_92ae4f0196ba
ELIN-887482-2017 | EL-572017-2017 | 8/25/2017 12:50:21 PM | ASSESS: EL: Service Connection | png | #asFound Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker unknowingly could come in contact with energized conductors in the distribution compartment and could be an electrical fire or shock hazard to people and property. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Backfed_distribution_from_service_conductor_from_meterbase1.png,Backfed_distribution_from_service_conductor_from_meterbase2.png,Backfed_distribution_from_service_conductor_from_meterbase3.png,Backfed_distribution_from_service_conductor_from_meterbase4.png,Backfed_distribution_from_service_conductor_from_meterbase5.png,Backfed_distribution_from_service_conductor_from_meterbase6.png Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in type ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other branch circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker thinking main breaker is off could unknowingly come in contact with energized conductors i | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Backfed_distribution_from_service_conductor_from_meterbase5.png | file://x:/photopub/docs/0000000652/88177ecf-116a-416d-8b8d-a3c9af53a990.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3acff245_2886_4afe_be93_bae75c7b9085
ELIN-887482-2017 | EL-572017-2017 | 8/25/2017 12:50:21 PM | ASSESS: EL: Service Connection | png | #asFound Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker unknowingly could come in contact with energized conductors in the distribution compartment and could be an electrical fire or shock hazard to people and property. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Backfed_distribution_from_service_conductor_from_meterbase1.png,Backfed_distribution_from_service_conductor_from_meterbase2.png,Backfed_distribution_from_service_conductor_from_meterbase3.png,Backfed_distribution_from_service_conductor_from_meterbase4.png,Backfed_distribution_from_service_conductor_from_meterbase5.png,Backfed_distribution_from_service_conductor_from_meterbase6.png Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in type ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other branch circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker thinking main breaker is off could unknowingly come in contact with energized conductors i | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Backfed_distribution_from_service_conductor_from_meterbase2.png | file://x:/photopub/docs/0000000652/7d060ebb-efe1-482b-9d8d-da1d4fbd9fb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3acff245_2886_4afe_be93_bae75c7b9085
ELIN-898972-2017 | EL-577809-2017 | 9/6/2017 12:56:58 PM | ASSESS: EL: Service Connection | png | #asFound Grounding electrode not not buried. | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_electrode.png Grounding electrode not buried. Should a short circuit occur when someone is walking past the electrical equipment, that person will not be at equal potential and will receive a shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_electrode.png | file://x:/photopub/docs/0000000658/5c8ef411-9faf-48e7-bad7-60e47ac8882f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd42e46_49ff_474e_84ef_1814da10a202
ELIN-898972-2017 | EL-577809-2017 | 9/6/2017 12:56:58 PM | ASSESS: EL: Service Connection | png | #asFound Grounding electrode not buried | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Grounding_electrode.png Grounding electrode not buried. Should a short circuit occur when someone is walking past the electrical equipment, that person will not be at equal potential and will receive a shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | grounding_electrode.png | file://x:/photopub/docs/0000000658/14edd66e-cfbb-44d4-ac21-531e7a086ad5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd42e46_49ff_474e_84ef_1814da10a202
ELIN-881130-2017 | UW-571611-2017 | 8/15/2017 3:28:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Installation of equipment without permit. | EL234 | Class II, all locations Area classification required | 2 | 2 | #equipment1.png,equipment2.png,equipment3.png,equipment4.png,equipment5.png,equipment6.png Agriculture grow facility added to existing residential dwelling unit and without permit. Added load to service unknown, equipment certification unknown, wiring not approved for Cat 2 location. | 2 | Class II, all locations Area classification required | equipment6.png | file://x:/photopub/docs/0000000646/c5c6f1dc-fec3-41cd-96f1-4179b279df02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6576274b_6300_4043_916a_cbe4485131bb
ELIN-881130-2017 | UW-571611-2017 | 8/15/2017 3:28:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL234 | Class II, all locations Area classification required | 2 | 2 | #equipment1.png,equipment2.png,equipment3.png,equipment4.png,equipment5.png,equipment6.png Agriculture grow facility added to existing residential dwelling unit and without permit. Added load to service unknown, equipment certification unknown, wiring not approved for Cat 2 location. | 2 | Class II, all locations Area classification required | equipment1.png | file://x:/photopub/docs/0000000646/a3c178fa-3d54-4f3b-bfef-49cd703bf126.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6576274b_6300_4043_916a_cbe4485131bb
ELIN-881130-2017 | UW-571611-2017 | 8/15/2017 3:28:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL234 | Class II, all locations Area classification required | 2 | 2 | #equipment1.png,equipment2.png,equipment3.png,equipment4.png,equipment5.png,equipment6.png Agriculture grow facility added to existing residential dwelling unit and without permit. Added load to service unknown, equipment certification unknown, wiring not approved for Cat 2 location. | 2 | Class II, all locations Area classification required | equipment2.png | file://x:/photopub/docs/0000000646/356d0f9e-eaa4-4bf9-8e08-260ca843d883.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6576274b_6300_4043_916a_cbe4485131bb
ELIN-881130-2017 | UW-571611-2017 | 8/15/2017 3:28:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL234 | Class II, all locations Area classification required | 2 | 2 | #equipment1.png,equipment2.png,equipment3.png,equipment4.png,equipment5.png,equipment6.png Agriculture grow facility added to existing residential dwelling unit and without permit. Added load to service unknown, equipment certification unknown, wiring not approved for Cat 2 location. | 2 | Class II, all locations Area classification required | equipment3.png | file://x:/photopub/docs/0000000646/c51727e9-7f79-4272-8ac2-58faa9b8d72f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6576274b_6300_4043_916a_cbe4485131bb
ELIN-881130-2017 | UW-571611-2017 | 8/15/2017 3:28:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL234 | Class II, all locations Area classification required | 2 | 2 | #equipment1.png,equipment2.png,equipment3.png,equipment4.png,equipment5.png,equipment6.png Agriculture grow facility added to existing residential dwelling unit and without permit. Added load to service unknown, equipment certification unknown, wiring not approved for Cat 2 location. | 2 | Class II, all locations Area classification required | equipment4.png | file://x:/photopub/docs/0000000646/99887ca6-b5f9-4bf4-bb59-16b64c9bb557.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6576274b_6300_4043_916a_cbe4485131bb
ELIN-881130-2017 | UW-571611-2017 | 8/15/2017 3:28:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL234 | Class II, all locations Area classification required | 2 | 2 | #equipment1.png,equipment2.png,equipment3.png,equipment4.png,equipment5.png,equipment6.png Agriculture grow facility added to existing residential dwelling unit and without permit. Added load to service unknown, equipment certification unknown, wiring not approved for Cat 2 location. | 2 | Class II, all locations Area classification required | equipment5.png | file://x:/photopub/docs/0000000646/2790221b-d345-47ca-91b8-4e52da0243e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6576274b_6300_4043_916a_cbe4485131bb
BPVIN-904828-2017 | UW-583339-2017 | 8/17/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Overall_picture.png During site assessment, I found the 34 years old in-service air receiver mounted with machine. It is non-compliant to Safety Order requirements. Due to long period of cyclic loading service and internal corrosion, there is a greater possibility that the shell thickness may have been reduced below design metal thickness due to corrosion over time. There is also possibility of pitting and cracking on all welded joints. Both these conditions may cause catastrophic failure of the air receiver, resulting in release of energy which will cause damage to nearby personnel and property. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Overall_picture.png | file://x:/photopub/docs/0000000660/6afd70a1-c937-4b60-a80a-e394b803f3c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea740ab9_0462_4098_98c1_691faeaca807
ELIN-902298-2017 | EL-572455-2017 | 9/11/2017 10:21:50 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Non_metallic_sheathed_cable_exposed_below_1_5_meters_at_final.png Non metallic sheathed cable is installed exposed. This type of cable requires mechanical protection from 1.5 m to grade. Soft exterior sheathing of this type of cable is susceptible to damage and there is a potential for energized conductor to become exposed, causing a risk of shock or fire. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Non_metallic_sheathed_cable_exposed_below_1_5_meters_at_final.png | file://x:/photopub/docs/0000000660/fc665cb8-06ce-4000-b050-0e7473147025.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3dc8ab_602a_4fb2_88e4_30580037e995
ELIN-887482-2017 | EL-572017-2017 | 8/25/2017 12:50:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Backfed_distribution_from_service_conductor_from_meterbase1.png,Backfed_distribution_from_service_conductor_from_meterbase2.png,Backfed_distribution_from_service_conductor_from_meterbase3.png,Backfed_distribution_from_service_conductor_from_meterbase4.png,Backfed_distribution_from_service_conductor_from_meterbase5.png,Backfed_distribution_from_service_conductor_from_meterbase6.png Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in type ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other branch circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker thinking main breaker is off could unknowingly come in contact with energized conductors i | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Backfed_distribution_from_service_conductor_from_meterbase6.png | file://x:/photopub/docs/0000000652/1124f211-5740-47a4-9ee3-1fa321ee60de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3acff245_2886_4afe_be93_bae75c7b9085
ELIN-884168-2017 | EL-572974-2017 | 8/22/2017 8:21:22 AM | ASSESS: EL: Service Connection | png | #asFound Lying side of metre base jaw | EL020 | Damage to equipment may result in overheating. | 4 | 4 | #__metre_base_jaws.png Line side of metre base jawsare damaged, utility metre will not properly seat within the jaw. overheating and fire will likely occur as a result of the utility metre not seating properly within the jaws of the metre base. | 4 | Damage to equipment may result in overheating. | __metre_base_jaws.png | file://x:/photopub/docs/0000000649/3c4ff13d-7de0-4e3d-96e0-4a76999ff10d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46b7347e_0dd2_491f_9c84_3f6de1249e4f
GAHE-890734-2017 | HE-576763-2017 | 8/31/2017 2:16:32 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Heater.png Space Heaters installed within 10" to combustible materials, manufactures installation manual requires a minimum of 36" clearance. Signs of vinyl soffit warping due to heat. Fir hazard present due to excessive heat | 3 | Clearance to combustible not met | Heater.png | file://x:/photopub/docs/0000000655/b28af930-d2a5-4d55-8648-6409ab97b9f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd0534b_cef8_4cd5_a96e_75bee2e6c4c9
ELIN-887482-2017 | EL-572017-2017 | 8/25/2017 12:50:21 PM | ASSESS: EL: Service Connection | png | #asFound Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker unknowingly could come in contact with energized conductors in the distribution compartment and could be an electrical fire or shock hazard to people and property. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Backfed_distribution_from_service_conductor_from_meterbase1.png,Backfed_distribution_from_service_conductor_from_meterbase2.png,Backfed_distribution_from_service_conductor_from_meterbase3.png,Backfed_distribution_from_service_conductor_from_meterbase4.png,Backfed_distribution_from_service_conductor_from_meterbase5.png,Backfed_distribution_from_service_conductor_from_meterbase6.png Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in type ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other branch circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker thinking main breaker is off could unknowingly come in contact with energized conductors i | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Backfed_distribution_from_service_conductor_from_meterbase3.png | file://x:/photopub/docs/0000000652/5a60f11b-53a6-4763-88f2-6ed2e615e631.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3acff245_2886_4afe_be93_bae75c7b9085
ELIN-887482-2017 | EL-572017-2017 | 8/25/2017 12:50:21 PM | ASSESS: EL: Service Connection | png | #asFound Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker unknowingly could come in contact with energized conductors in the distribution compartment and could be an electrical fire or shock hazard to people and property. | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Backfed_distribution_from_service_conductor_from_meterbase1.png,Backfed_distribution_from_service_conductor_from_meterbase2.png,Backfed_distribution_from_service_conductor_from_meterbase3.png,Backfed_distribution_from_service_conductor_from_meterbase4.png,Backfed_distribution_from_service_conductor_from_meterbase5.png,Backfed_distribution_from_service_conductor_from_meterbase6.png Found 120/240 volt existing 100amp service in progress of being upgraded to a 120/240 volt 200amp service using #6AWG aluminum conductors in type ACWU cable. This cable was fed through 200amp service compartment bypassing 200amp service breaker and was used to back feed 70amp 2 pole breaker in distribution panelboard bus bars for feeding power to other branch circuits. When a #6 AWG conductor back feeds a 70 amp breaker in distribution compartment of 200amp panel and main 200amp service breaker is switched off, an individual electrical worker thinking main breaker is off could unknowingly come in contact with energized conductors i | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Backfed_distribution_from_service_conductor_from_meterbase1.png | file://x:/photopub/docs/0000000652/4b5ff62a-eb6b-4e09-b74e-5a21c9a02a1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3acff245_2886_4afe_be93_bae75c7b9085
ELIN-901480-2017 | EL-579649-2017 | 9/7/2017 10:32:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Outlet box inset into wall. | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 2 | #Outlet_box_.png Kitchen renovation for 1/2 of duplex dwelling. Outlet box for future cabinet lighting is inset too far in the wall behind cabinet. If the wrong device or cover plate is used any fault in the device or cable could ignite surrounding combustibles. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Outlet_box_.png | file://x:/photopub/docs/0000000659/e2944a36-683d-4287-a4e0-13752ae241f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0aa10747_373f_4bd8_b68b_f8d95b49222b
ELIN-888485-2017 | EL-508567-2017 | 8/28/2017 2:45:20 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Improper_staple_1.png,Improper_staple_2.png,Improper_staple_3.png Multiple cables were installed under an improper (too small) staple support. Use of staple too small for cables could damage the insulation and and cause arcing leading to fire risk. | 3 | Conductors Equipment is not approved for the specific use. | Improper_staple_1.png | file://x:/photopub/docs/0000000653/e7807c94-3995-4dcc-9701-16fa2b947db5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e326740_5c55_4dcc_bdc3_6342c86e35e7
ELIN-899204-2017 | EL-552541-2017 | 9/7/2017 3:17:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | #No_expansion_joint1.png,No_expansion_joint2.png No expansion joint installed for sub fed from service to house panel board | 3 | Conductors, No expansion joint or not installed correctly. | No_expansion_joint1.png | file://x:/photopub/docs/0000000659/841f969f-691f-4fe2-befa-e40e495620d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de86061f_788f_461d_a740_118b2c71f85c
ELIN-899204-2017 | EL-552541-2017 | 9/7/2017 3:17:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound No expansion joint as required is installed on feeder conduit for house panelboard | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | #No_expansion_joint1.png,No_expansion_joint2.png No expansion joint installed for sub fed from service to house panel board | 3 | Conductors, No expansion joint or not installed correctly. | No_expansion_joint2.png | file://x:/photopub/docs/0000000659/5270fe62-efe1-4e02-903e-071738ad62f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de86061f_788f_461d_a740_118b2c71f85c
GAIN-871602-2017 | GA-553638-2017 | 8/3/2017 3:57:18 PM | ASSESS: GA: Rough-In | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | #CSST.png Corrugated stainless steel tubing installed without proper electrical bonding. This may allow the gas line to either become energized with potential for electrical shock or allow a lightning strike to energize the line and arc causing a hole in the gas line and a gas leak. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | CSST.png | file://x:/photopub/docs/0000000641/0ed79dce-0a64-4462-90b2-e551ec735735.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3206c5dd_86ec_41e0_aac5_34d4c57bb1f8
BPVIN-849954-2017 | BPV-552533-2017 | 8/4/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect_.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no remote shutdown switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnect_.png | file://x:/photopub/docs/0000000642/35da7cb8-bc80-4319-9366-3fb30086f7e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d1388a4_e0ab_4fc7_86ba_17ca50dad6f0
ELHE-901199-2017 | HE-580883-2017 | 9/6/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #hazard1.png,hazard2.png Panel covers removed on energized panels leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | hazard1.png | file://x:/photopub/docs/0000000660/3b1543a9-c61e-4357-9a3f-ef180196e2e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3bafe2b_87f6_4523_be63_32330c7bf82c
ELIN-889023-2017 | EL-560485-2017 | 8/28/2017 3:52:26 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #No_8_Panel_Feeder1.png,No_8_Panel_Feeder2.png,No_8_Panel_Feeder3.png,No_8_Panel_Feeder4.png,No_8_Panel_Feeder5.png Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for a tenant improvement, a #8 copper teck cable rated for 50A was used for an existing 120/208V sub-panel. The teck cable was connected to a 60A, two pole breaker in the main electrical panel used to feed the sub-panel. The potential overloading of the conductors could break down the insulation which would lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 0 | No Created Hazard Identified | No_8_Panel_Feeder5.png | file://x:/photopub/docs/0000000653/278cbf4a-aa93-4ca5-947d-6d45a455e389.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce401921_2611_445a_8b8d_637fd4668fb7
ELIN-889023-2017 | EL-560485-2017 | 8/28/2017 3:52:26 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #No_8_Panel_Feeder1.png,No_8_Panel_Feeder2.png,No_8_Panel_Feeder3.png,No_8_Panel_Feeder4.png,No_8_Panel_Feeder5.png Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for a tenant improvement, a #8 copper teck cable rated for 50A was used for an existing 120/208V sub-panel. The teck cable was connected to a 60A, two pole breaker in the main electrical panel used to feed the sub-panel. The potential overloading of the conductors could break down the insulation which would lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 0 | No Created Hazard Identified | No_8_Panel_Feeder2.png | file://x:/photopub/docs/0000000653/b6e5dd86-357b-4553-a5eb-dd3d84752ce2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce401921_2611_445a_8b8d_637fd4668fb7
ELIN-889023-2017 | EL-560485-2017 | 8/28/2017 3:52:26 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #No_8_Panel_Feeder1.png,No_8_Panel_Feeder2.png,No_8_Panel_Feeder3.png,No_8_Panel_Feeder4.png,No_8_Panel_Feeder5.png Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for a tenant improvement, a #8 copper teck cable rated for 50A was used for an existing 120/208V sub-panel. The teck cable was connected to a 60A, two pole breaker in the main electrical panel used to feed the sub-panel. The potential overloading of the conductors could break down the insulation which would lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 0 | No Created Hazard Identified | No_8_Panel_Feeder3.png | file://x:/photopub/docs/0000000653/cfff5a79-7c8e-4e67-b5b0-dc343fb4e1c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce401921_2611_445a_8b8d_637fd4668fb7
ELIN-889023-2017 | EL-560485-2017 | 8/28/2017 3:52:26 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #No_8_Panel_Feeder1.png,No_8_Panel_Feeder2.png,No_8_Panel_Feeder3.png,No_8_Panel_Feeder4.png,No_8_Panel_Feeder5.png Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for a tenant improvement, a #8 copper teck cable rated for 50A was used for an existing 120/208V sub-panel. The teck cable was connected to a 60A, two pole breaker in the main electrical panel used to feed the sub-panel. The potential overloading of the conductors could break down the insulation which would lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 0 | No Created Hazard Identified | No_8_Panel_Feeder1.png | file://x:/photopub/docs/0000000653/789843ce-073b-4c4d-ab75-50713de05b26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce401921_2611_445a_8b8d_637fd4668fb7
ELIN-889023-2017 | EL-560485-2017 | 8/28/2017 3:52:26 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #No_8_Panel_Feeder1.png,No_8_Panel_Feeder2.png,No_8_Panel_Feeder3.png,No_8_Panel_Feeder4.png,No_8_Panel_Feeder5.png Ungrounded conductors are required to be protected by correctly sized devices (usually fuses or circuit breakers) that de-energize the circuit if an overload or short-circuit occurs. Correctly sized devices prevent the overloading of conductors which can cause overheating and the breakdown of the conductor insulation. During an assessment for a tenant improvement, a #8 copper teck cable rated for 50A was used for an existing 120/208V sub-panel. The teck cable was connected to a 60A, two pole breaker in the main electrical panel used to feed the sub-panel. The potential overloading of the conductors could break down the insulation which would lead to equipment damage. The breakdown of the insulation can also lead to a short circuit on the conductor which could create a shock or fire hazard within the building. | 0 | No Created Hazard Identified | No_8_Panel_Feeder4.png | file://x:/photopub/docs/0000000653/b01efedf-2fbc-48f0-b73d-910a81adc422.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce401921_2611_445a_8b8d_637fd4668fb7
ELOP-901262-2017 | 4997978 | 9/6/2017 2:38:05 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #As_found1.png,As_found2.png Covers removed on energized boxes leaving exposed electrical parts and a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | As_found2.png | file://x:/photopub/docs/0000000661/dc4c4a3c-8783-486a-baea-4592c164efab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__130065db_a9db_4679_8f27_ab2d5d82ad42
ELIN-821923-2017 | EL-534521-2017 | 8/30/2017 10:44:41 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Mech_protection_not_in_place.png In an existing single family dwelling, the 15amp 120/240volt branch circuits entering the panel location are not mechanically protected below the panel location. This could lead to a "shock hazard" scenario. Pic attached. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Mech_protection_not_in_place.png | file://x:/photopub/docs/0000000654/cda1915a-eb8e-4ee7-8715-27ae39d1e1ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95fce034_530c_40f0_8cda_b731f284827a
ELOP-867007-2017 | 5300152 | 7/31/2017 2:12:41 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Private_breaker.png The incoming service is 25Kv overhead to Sawmill, Planer & kilns. There is a utility Recloser that can reclose the main circuit breaker after a fault. This is coordinated with BC Hydro substation over current that does reclose. The private line having a breaker that recloses after a fault without someone confirming it is safe to do so creates a shock risk to Employees. | 3 | General Equipment is not approved for the specific use | Private_breaker.png | file://x:/photopub/docs/0000000638/65f7afb0-def0-46cc-9839-8ab7060d7747.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c5d8c86_4cb3_436c_b038_f11744bc5a4d
ELIN-870710-2017 | EL-565834-2017 | 8/2/2017 10:41:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Bonding_screw_removed_at_service_switch.png This assessment found that the grounding was terminated after the service switch, this could energize grounded equipment in a fault condition. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bonding_screw_removed_at_service_switch.png | file://x:/photopub/docs/0000000640/3950c89c-0454-4d82-812d-1c8690add05f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72f38e32_2918_466d_8fb2_ac4b6dda0884
GAIN-855486-2017 | GA-531897-2017 | 8/16/2017 1:14:19 PM | ASSESS: GA: Final | png | #asFound | GA028 | Meter set /regulatory assembly undersized for connected load | 3 | 3 | #Meter.png Natural gas meter is undersized for the total connected load. Possible equipment damage could occur. | 3 | Meter set /regulatory assembly undersized for connected load | Meter.png | file://x:/photopub/docs/0000000647/e2c5f1f0-e4f1-4740-9188-39c77dc66869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfa23f16_99cb_4de2_8312_5bdf9502b5aa
ELIN-885314-2017 | EL-573647-2017 | 8/25/2017 2:24:45 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 2 | #Peninsula_plug_missing.png This assessment found that the peninsula receptacle wire was missed. As a result, a cord may be stretched over the sink, potentially causing a shock hazard | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Peninsula_plug_missing.png | file://x:/photopub/docs/0000000652/36455791-118f-4412-ba7c-4e8ad7d745c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f8bcd17_4da3_4b49_9766_c591919a9a21
EDIN-894408-2017 | ED-483096-2016 | 8/29/2017 6:11:48 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Roof_access_without_protective_barrier.png A protective barrier (guardrails) is installed to protect personnel from possibly falling from the roof while accessing the Elevator Control Room. During an inspection assessment it was found that the protective barrier (guardrails) is missing for the roof access to the Elevator Control Room. It was found that the general contractor failed to have them installed. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Roof_access_without_protective_barrier.png | file://x:/photopub/docs/0000000654/46aa1499-1d93-4fe1-9758-2d3b3c1ac3c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26dd0508_d503_4b12_88a7_7eaf9bd03237
ELOP-901262-2017 | 4997978 | 9/6/2017 2:38:05 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #As_found1.png,As_found2.png Covers removed on energized boxes leaving exposed electrical parts and a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | As_found1.png | file://x:/photopub/docs/0000000661/e836f13e-74b0-48a6-b3c7-02945e69f1a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__130065db_a9db_4679_8f27_ab2d5d82ad42
ELIN-869033-2017 | EL-505794-2017 | 8/1/2017 12:10:40 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #INcorrect_grounding_of_communication_equipment.png This assessment found that grounding the communications system has not been installed properly, this can create a shock hazard on a fault situation. | 3 | Continuity Bonding; method for equipment is not adequate. | INcorrect_grounding_of_communication_equipment.png | file://x:/photopub/docs/0000000639/a4152570-e768-4586-9e6c-ccd7228f8807.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6510819_3714_40e2_abb3_fbde15d4a550
BPVOP-894654-2017 | 2270391 | 8/29/2017 2:32:28 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | #SAFETY_RELIEF_VALVE.png Upon assessment of hot water heating boiler with 25square meters heating surface, it is determined that capacity of safety valve is less than theoretical minimum capacity required. In the event of over-pressure built up in the boiler (due to failure of control and other safety devices) there is possibility of permanent damage or even rupture of pressure boundary of boiler which can lead to incident. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000654/b8fed200-55b7-466b-b467-4d63c7d2b7c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f971c74_0166_46af_9585_5af676e0d48c
GAIN-883917-2017 | GA-541903-2017 | 9/12/2017 9:28:48 AM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Gas_line.png A gas line was installed from a new gas meter to a new furnace not yet in operation. The meter has a delivery pressure of 2psi and a line pressure regulator was not installed. This would allow gas to enter the appliance inlet at a much higher pressure than allowed by the design of the appliance manufacturer. This could lead to a damaged gas valve or over firing of the appliance. Over firing of the appliance could cause incomplete combustion and the production of carbon monoxide or damage to the appliance heat exchanger allowing for the products of combustion to enter the living space. | 4 | Appliance regulator not installed, incorrect delivery pressure | Gas_line.png | file://x:/photopub/docs/0000000661/34d5a545-2825-4298-b3dd-9bf3b8473bae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d6ce0a3_876e_41d2_b7c2_07799f2c44ca
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Unapproved_gate_operator4.png | file://x:/photopub/docs/0000000646/991fde5e-0285-4443-84b3-6a171e8e9575.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval7.png | file://x:/photopub/docs/0000000646/13ee0875-f4d8-49ba-a045-bf113399b121.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
GAIN-883917-2017 | GA-541903-2017 | 9/12/2017 9:28:48 AM | ASSESS: GA: Final | png | #asFound Black iron gas line running from a 2psi meter to the appliance without the installation of a line pressure regulator. | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Gas_line.png A gas line was installed from a new gas meter to a new furnace not yet in operation. The meter has a delivery pressure of 2psi and a line pressure regulator was not installed. This would allow gas to enter the appliance inlet at a much higher pressure than allowed by the design of the appliance manufacturer. This could lead to a damaged gas valve or over firing of the appliance. Over firing of the appliance could cause incomplete combustion and the production of carbon monoxide or damage to the appliance heat exchanger allowing for the products of combustion to enter the living space. | 4 | Appliance regulator not installed, incorrect delivery pressure | Gas_line.png | file://x:/photopub/docs/0000000661/8524da9e-cc38-4bb4-905f-9913de25ca1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d6ce0a3_876e_41d2_b7c2_07799f2c44ca
EDIN-896147-2017 | ED-451897-2016 | 8/30/2017 5:21:22 PM | ASSESS: ED IN: Acceptance | png | #asFound Conveyor system at top of landing | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | #Conveyor_.png Conveyor system in front of top floor opening. Unit shall be removed within 7 days | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Conveyor_.png | file://x:/photopub/docs/0000000654/ab712ebf-53d1-4d50-bbab-28e204624cd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93f4aae7_6b75_4cd0_8aaa_a1fe6d6d4a6f
ELIN-871299-2017 | UW-566784-2017 | 8/2/2017 5:20:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Receptacle installed without covers, afci protection, pigtails and is not properly bonded. This is a shock and fire hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | A2.png | file://x:/photopub/docs/0000000640/c04c2534-9dbd-4e2d-9197-4d831974ffd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4bf7766_f169_4c5c_9780_607da773cb50
ELIN-871299-2017 | UW-566784-2017 | 8/2/2017 5:20:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Receptacle installed without covers, afci protection, pigtails and is not properly bonded. This is a shock and fire hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | A4.png | file://x:/photopub/docs/0000000640/36bbd1c1-b256-46b7-b077-5f20fde8cd73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4bf7766_f169_4c5c_9780_607da773cb50
ELIN-871299-2017 | UW-566784-2017 | 8/2/2017 5:20:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Receptacle installed without covers, afci protection, pigtails and is not properly bonded. This is a shock and fire hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | A1.png | file://x:/photopub/docs/0000000640/85a9ce33-b172-42ef-8a6a-3c1b98c702e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4bf7766_f169_4c5c_9780_607da773cb50
ELIN-871299-2017 | UW-566784-2017 | 8/2/2017 5:20:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 4 | #A1.png,A2.png,A3.png,A4.png Receptacle installed without covers, afci protection, pigtails and is not properly bonded. This is a shock and fire hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | A3.png | file://x:/photopub/docs/0000000640/e49455cf-80af-4af9-97fa-d37f74984956.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4bf7766_f169_4c5c_9780_607da773cb50
ELIN-883318-2017 | EL-538325-2017 | 8/22/2017 11:04:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #Joint_compound_needed.png This assessment found that a joint compound with aluminum cables was not used, this can create oxidization at the connections creating a fire hazard. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Joint_compound_needed.png | file://x:/photopub/docs/0000000650/cf66f06c-98f9-4572-ae83-ce9596041265.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20e5f32f_421c_4cc2_abfb_8e7af7d7ebe2
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png | file://x:/photopub/docs/0000000646/0c4cb65f-7ad9-46ef-92f8-dc64daaf9df8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png | file://x:/photopub/docs/0000000646/38504a0e-d8d9-47cc-b017-60dd8a97c237.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval2.png | file://x:/photopub/docs/0000000646/1eecf7a6-e723-481c-8e1f-707d08adfddf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Unapproved_gate_operator2.png | file://x:/photopub/docs/0000000646/0a980684-d637-48c3-8870-1f806fc2a3d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval4.png | file://x:/photopub/docs/0000000646/d3dbd8d6-1d64-4961-ac0d-340bba41eca0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
GAIN-857905-2017 | GA-483031-2016 | 8/4/2017 2:36:04 PM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Bushing.png The as-found condition is that a prohibited bushing has been installed on a piping system. The potential hazard is that the thin-walled material of the bushing will be subject to stress and crack, causing a gas leak in an occupied space, which could result in fire or explosion | 3 | Non-compliant material/fittings installed | Bushing.png | file://x:/photopub/docs/0000000642/53231875-bcfd-4580-956e-c0943510fadc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94776b86_46a7_4588_a629_9351170bbcf8
ELIN-877874-2017 | EL-569881-2017 | 8/11/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound No metal raceway or no bonding and no protection of existing 100amp service conductors between existing 100amp 120/240volt meterbase and newly installed 200amp main combination service panelboard. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_equipment_without_a_raceway_for_service_conductors1.png,Service_equipment_without_a_raceway_for_service_conductors2.png,Service_equipment_without_a_raceway_for_service_conductors3.png,Service_equipment_without_a_raceway_for_service_conductors4.png,Service_equipment_without_a_raceway_for_service_conductors5.png Found an existing 120/240volt single phase main service with 100amp meterbase and a new 200Amp main service panelboard has 3 single 100amp conductors run on the surface exposed and energized and without a raceway for bonding between meterbase and panelboard. This service equipment has no raceway to protect conductors and no electrical bonding for bonding all the electrical service equipment together. When single conductors are installed without a raceway for bonding electrical service equipment together the electrical equipment is a possible electrical fire and shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_equipment_without_a_raceway_for_service_conductors4.png | file://x:/photopub/docs/0000000646/27e3fe6c-ead0-4958-bcc9-cf7b70baea1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed427825_f35a_4e28_b549_2a5635472629
ELIN-877874-2017 | EL-569881-2017 | 8/11/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound No metal raceway or no bonding and no protection of existing 100amp service conductors between existing 100amp 120/240volt meterbase and newly installed 200amp main combination service panelboard. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_equipment_without_a_raceway_for_service_conductors1.png,Service_equipment_without_a_raceway_for_service_conductors2.png,Service_equipment_without_a_raceway_for_service_conductors3.png,Service_equipment_without_a_raceway_for_service_conductors4.png,Service_equipment_without_a_raceway_for_service_conductors5.png Found an existing 120/240volt single phase main service with 100amp meterbase and a new 200Amp main service panelboard has 3 single 100amp conductors run on the surface exposed and energized and without a raceway for bonding between meterbase and panelboard. This service equipment has no raceway to protect conductors and no electrical bonding for bonding all the electrical service equipment together. When single conductors are installed without a raceway for bonding electrical service equipment together the electrical equipment is a possible electrical fire and shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_equipment_without_a_raceway_for_service_conductors5.png | file://x:/photopub/docs/0000000646/4af15390-3b6a-4c48-ad1c-5e8a21028706.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed427825_f35a_4e28_b549_2a5635472629
ELIN-877874-2017 | EL-569881-2017 | 8/11/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_equipment_without_a_raceway_for_service_conductors1.png,Service_equipment_without_a_raceway_for_service_conductors2.png,Service_equipment_without_a_raceway_for_service_conductors3.png,Service_equipment_without_a_raceway_for_service_conductors4.png,Service_equipment_without_a_raceway_for_service_conductors5.png Found an existing 120/240volt single phase main service with 100amp meterbase and a new 200Amp main service panelboard has 3 single 100amp conductors run on the surface exposed and energized and without a raceway for bonding between meterbase and panelboard. This service equipment has no raceway to protect conductors and no electrical bonding for bonding all the electrical service equipment together. When single conductors are installed without a raceway for bonding electrical service equipment together the electrical equipment is a possible electrical fire and shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_equipment_without_a_raceway_for_service_conductors3.png | file://x:/photopub/docs/0000000646/5e66b4a7-b3fe-447f-b2c1-53217e760ad5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed427825_f35a_4e28_b549_2a5635472629
ELIN-877874-2017 | EL-569881-2017 | 8/11/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound No metal raceway or no bonding and no protection of existing 100amp service conductors between existing 100amp 120/240volt meterbase and newly installed 200amp main combination service panelboard. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_equipment_without_a_raceway_for_service_conductors1.png,Service_equipment_without_a_raceway_for_service_conductors2.png,Service_equipment_without_a_raceway_for_service_conductors3.png,Service_equipment_without_a_raceway_for_service_conductors4.png,Service_equipment_without_a_raceway_for_service_conductors5.png Found an existing 120/240volt single phase main service with 100amp meterbase and a new 200Amp main service panelboard has 3 single 100amp conductors run on the surface exposed and energized and without a raceway for bonding between meterbase and panelboard. This service equipment has no raceway to protect conductors and no electrical bonding for bonding all the electrical service equipment together. When single conductors are installed without a raceway for bonding electrical service equipment together the electrical equipment is a possible electrical fire and shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_equipment_without_a_raceway_for_service_conductors1.png | file://x:/photopub/docs/0000000646/d2a8a19f-6ca2-47ed-b47a-5a20262fb650.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed427825_f35a_4e28_b549_2a5635472629
ELIN-877874-2017 | EL-569881-2017 | 8/11/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound No metal raceway or no bonding and no protection of existing 100amp service conductors between existing 100amp 120/240volt meterbase and newly installed 200amp main combination service panelboard. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_equipment_without_a_raceway_for_service_conductors1.png,Service_equipment_without_a_raceway_for_service_conductors2.png,Service_equipment_without_a_raceway_for_service_conductors3.png,Service_equipment_without_a_raceway_for_service_conductors4.png,Service_equipment_without_a_raceway_for_service_conductors5.png Found an existing 120/240volt single phase main service with 100amp meterbase and a new 200Amp main service panelboard has 3 single 100amp conductors run on the surface exposed and energized and without a raceway for bonding between meterbase and panelboard. This service equipment has no raceway to protect conductors and no electrical bonding for bonding all the electrical service equipment together. When single conductors are installed without a raceway for bonding electrical service equipment together the electrical equipment is a possible electrical fire and shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_equipment_without_a_raceway_for_service_conductors2.png | file://x:/photopub/docs/0000000646/da100b1e-0e7b-4adb-86eb-9eeec4858f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed427825_f35a_4e28_b549_2a5635472629
ELIN-860345-2017 | EL-560298-2017 | 8/1/2017 12:36:00 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Breaker_installed_in_main_distribution_.png 15 amp, 120 volt rated breaker installed in the main distribution not rated or approved for installation. This could cause equipment damage. | 3 | General Equipment is not approved for the specific use | Breaker_installed_in_main_distribution_.png | file://x:/photopub/docs/0000000639/b2818513-c5fb-47cd-a770-2adc2fbc214e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__937eec8b_55df_474e_90d3_8634e350930e
ELIN-860301-2017 | EL-537091-2017 | 8/1/2017 10:59:44 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Breaker_installed_in_main_distribution.png 15 amp, 120/208 volt breaker installed in main distribution panel that is not of the type or rating approved for installation. This could cause equipment damage. | 3 | General Equipment is not approved for the specific use | Breaker_installed_in_main_distribution.png | file://x:/photopub/docs/0000000639/5f2b13b9-1741-4e27-ae27-c1e095466777.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f0fc866_83a9_4c9c_8733_0b8e74658652
ELIN-860340-2017 | EL-560295-2017 | 8/1/2017 11:41:21 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Type_BR_breaker_installed_within_main_distribution.png 15 amp, 120 volt type BR overcurrent device installed within main distribution not approved for installation. This could cause equipment damage. | 3 | General Equipment is not approved for the specific use | Type_BR_breaker_installed_within_main_distribution.png | file://x:/photopub/docs/0000000639/db516844-db52-49ba-9cea-634197a5fb33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a6f9070_0094_4c04_ad67_d8ab77a893b1
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval5.png | file://x:/photopub/docs/0000000646/aa6aba7c-e594-48da-9e5c-ee9a288957cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval6.png | file://x:/photopub/docs/0000000646/27ebb78b-d35e-4646-8d51-58ca4c49096b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Unapproved_gate_operator3.png | file://x:/photopub/docs/0000000646/60e0a64f-16b5-443f-9022-eeb3c270d159.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png | file://x:/photopub/docs/0000000647/d1e50190-8b94-4b0a-8e5a-28a7944e968c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png | file://x:/photopub/docs/0000000647/87bea067-d24d-4c36-8bbd-cad5f2689a98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png | file://x:/photopub/docs/0000000647/ce5b8986-f3fb-4e3f-8bd5-8e0677bdeeb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png | file://x:/photopub/docs/0000000647/17b47353-7c63-4b5d-b342-c6aef7d351d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
ELIN-874247-2017 | EL-565020-2017 | 8/10/2017 11:40:36 AM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Plastic_inverter_housing_and_metal_jacket_cables.png I bonded metallic parts may pose a shock hazard | 3 | Continuity Bonding; method for equipment is not adequate. | Plastic_inverter_housing_and_metal_jacket_cables.png | file://x:/photopub/docs/0000000644/b41dec62-ba51-4a14-a2fb-7389034b80e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51bee9f4_b4f1_4696_b88d_b7c68d158086
ELIN-890564-2017 | EL-570826-2017 | 8/30/2017 8:47:05 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Fluorescent_temp_lights.png Temporary fluorescent light fixtures at floor level with unprotected fluorescent tubes and unapproved splicing methods on cord cables presenting potential shock and fire hazards. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fluorescent_temp_lights.png | file://x:/photopub/docs/0000000654/12b89d62-0127-4e57-a5ae-db049c653e44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11901403_774c_4217_8d72_ddd1f9c207c0
ELIN-884668-2017 | EL-571182-2017 | 8/22/2017 12:48:07 PM | ASSESS: EL: Service Connection | png | #asFound Found existing extension cords for luminaires used as permanent wiring and these cords are stapled with unapproved staples supporting the cord. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Luminaires_extension_cords_suppiorted_with_unapproved_staples1.png,Luminaires_extension_cords_suppiorted_with_unapproved_staples2.png Found existing extension cords for luminaires used as permanent wiring and these cords are stapled with unapproved staples supporting the cords. When extension cords for luminaires are used as permanent wiring supported with unapproved staples, the electrical equipment is subject to possible mechanical damage and possible short circuit and could become an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | Luminaires_extension_cords_suppiorted_with_unapproved_staples1.png | file://x:/photopub/docs/0000000650/b654b576-fef5-4469-a5ae-c0fed0b084b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb39ab1_d563_47e4_be30_a4bc78a75d40
ELIN-884668-2017 | EL-571182-2017 | 8/22/2017 12:48:07 PM | ASSESS: EL: Service Connection | png | #asFound Found existing extension cords for luminaires used as permanent wiring and these cords are stapled with unapproved staples supporting the cord. | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Luminaires_extension_cords_suppiorted_with_unapproved_staples1.png,Luminaires_extension_cords_suppiorted_with_unapproved_staples2.png Found existing extension cords for luminaires used as permanent wiring and these cords are stapled with unapproved staples supporting the cords. When extension cords for luminaires are used as permanent wiring supported with unapproved staples, the electrical equipment is subject to possible mechanical damage and possible short circuit and could become an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | Luminaires_extension_cords_suppiorted_with_unapproved_staples2.png | file://x:/photopub/docs/0000000650/dd55e674-abec-46a9-85b5-dbbee56bfdd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb39ab1_d563_47e4_be30_a4bc78a75d40
GAIN-882328-2017 | GA-518870-2017 | 8/18/2017 8:37:52 AM | ASSESS: GA: Final | png | #asFound | GA038 | Pipe supports not compliant but in place | 1 | 1 | #Non_compliant_tubing_support.png Tubing support for copper tubing non compliant. Galvanic corrosion can cause damage to copper tubing. | 1 | Pipe supports not compliant but in place | Non_compliant_tubing_support.png | file://x:/photopub/docs/0000000648/b2d82a1b-ad3a-4f4c-a9b7-f1fa9f81e48e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c6b610e_ad51_4c96_990c_547a0c126d40
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png | file://x:/photopub/docs/0000000647/0ebd1f05-022e-4283-8d84-46fbe5a0c83c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Front_of_mobile_home_.png | file://x:/photopub/docs/0000000647/4ea4d6ee-e01b-4875-9c1c-eb88a83c3201.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
ELIN-869825-2017 | EL-565970-2017 | 8/17/2017 10:54:11 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home1.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home2.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home3.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home4.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png,Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home6.png,Front_of_mobile_home_.png The grounded circuit conductor (neutral) is required to be isolated from the non-current carrying metal parts of the electrical system (the panel enclosure) on the load side of the service box or equivalent device. This is required to prevent circuit current from flowing through parallel paths of metal parts and enclosures of electrical systems and to prevent all the circuit current intended to be c | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_bonding_jumper_installed_in_branch_circuit_section_of_ungrounded_panel_in_mobile_home5.png | file://x:/photopub/docs/0000000647/b89033eb-ffd2-41bd-aa7c-a8486010f4b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e87a171_ad3b_4a3f_90ee_3aa2712f7717
BPVIN-874250-2017 | UW-568329-2017 | 8/14/2017 7:24:21 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound Hi and low pressure gauges and limits not calibrated. | BP133 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | 3 | 3 | #Pressuregauges.png There is no evidence available that the safety devices, controls and pressure relief valves on this system have been maintained and confirmed to operate properly. There is a possibility that the system could exceed it's design limits for pressure or temperature with these devices in an unknown state of operation. | 3 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | Pressuregauges.png | file://x:/photopub/docs/0000000647/f3622caf-f2c0-4c09-809e-95d74fb13769.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b50784e_da5d_4fac_8702_5e83c5074f65
BPVOP-888339-2017 | BPV-163639-2014 | 8/24/2017 12:26:28 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_valve.png Upon assessment it is determined that horizontal machine mounted air receiver (1.0m long and 0.40m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has pressure relief valve that exceeded the required 3 year interval for servicing or replacement. Failure to have pressure relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve.png | file://x:/photopub/docs/0000000651/8890f41a-5194-4869-8e92-6db7716723a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__679bf412_4637_44a7_8da8_db2b84933fcd
ELIN-871942-2017 | EL-542915-2017 | 8/8/2017 7:39:20 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Missing_outlets1.png,Missing_outlets2.png In a new home under construction 15 amp 120 volt outlets have not been provided in all the required wall locations. This could result in use of extension cords or other means to provide power along the walls where outlets have not been provided. This poses a safety risk to the electrical equipment. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Missing_outlets1.png | file://x:/photopub/docs/0000000642/06b2b0fe-0332-4ec8-81e6-65089c07f09c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a179afd7_ea28_43ab_bb79_efb0420e43f8
ELIN-871942-2017 | EL-542915-2017 | 8/8/2017 7:39:20 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Missing_outlets1.png,Missing_outlets2.png In a new home under construction 15 amp 120 volt outlets have not been provided in all the required wall locations. This could result in use of extension cords or other means to provide power along the walls where outlets have not been provided. This poses a safety risk to the electrical equipment. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Missing_outlets2.png | file://x:/photopub/docs/0000000642/82d8ebf6-71a8-4121-b6ca-80a8971c0ad0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a179afd7_ea28_43ab_bb79_efb0420e43f8
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png | file://x:/photopub/docs/0000000646/2a8c167b-5252-45bc-bbdd-7cb1ce0870bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Unapproved_gate_operator1.png | file://x:/photopub/docs/0000000646/40749be7-6e96-4c79-8f06-90ece6e4f8fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval1.png | file://x:/photopub/docs/0000000646/85cf98d9-3202-40b9-9c0e-f8a1ab7b73f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Unapproved_gate_operator5.png | file://x:/photopub/docs/0000000646/e24e0975-bad5-4b75-af62-35fc7832f179.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 1000W_HID_growing_lights_with_no_evidence_of_approval3.png | file://x:/photopub/docs/0000000646/84a928ab-7712-468a-8146-bdbc641a53f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-878144-2017 | UW-570213-2017 | 8/11/2017 3:17:51 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #flexible_cord_installed_and_left_on_the_ground.png Flexible cord has been installed on the ground and is exiting a garage, it has been run to a security camera system for a neighbouring site. Flexible cord if installed in this manner is susceptible to mechanical damage. Mechanical damage may result in exposed energized conductors and may lead to shock and fire to persons and property. | 3 | Conductors Equipment is not approved for the specific use. | flexible_cord_installed_and_left_on_the_ground.png | file://x:/photopub/docs/0000000645/87e227ea-8fea-4ada-b02e-50ce5ae00ace.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__379059d2_17d1_40b2_9208_315dbb541bcc
GAHE-882109-2017 | HE-471414-2016 | 8/16/2017 3:46:11 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Corroded_1.png,Corroded_2.png,Corroded_3.png Hot water boiler was found in operation with a badly corroded flue collector which connects to the venting system. This will lead to flue gases from the boiler spilling into the boiler room. An appliance operating in this condition can begin to produce higher than normal levels of carbon monoxide that anyone in the area would be exposed to. | 0 | No Created Hazard Identified | Corroded_3.png | file://x:/photopub/docs/0000000647/13d3be23-b199-4f01-ab53-03b7718211ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7eeb7bc9_9098_486c_8f59_35117281fca8
GAHE-882109-2017 | HE-471414-2016 | 8/16/2017 3:46:11 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Corroded_1.png,Corroded_2.png,Corroded_3.png Hot water boiler was found in operation with a badly corroded flue collector which connects to the venting system. This will lead to flue gases from the boiler spilling into the boiler room. An appliance operating in this condition can begin to produce higher than normal levels of carbon monoxide that anyone in the area would be exposed to. | 0 | No Created Hazard Identified | Corroded_1.png | file://x:/photopub/docs/0000000647/351dac06-ba2f-456c-9fdb-053d87ccfbb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7eeb7bc9_9098_486c_8f59_35117281fca8
GAHE-882109-2017 | HE-471414-2016 | 8/16/2017 3:46:11 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | #Corroded_1.png,Corroded_2.png,Corroded_3.png Hot water boiler was found in operation with a badly corroded flue collector which connects to the venting system. This will lead to flue gases from the boiler spilling into the boiler room. An appliance operating in this condition can begin to produce higher than normal levels of carbon monoxide that anyone in the area would be exposed to. | 0 | No Created Hazard Identified | Corroded_2.png | file://x:/photopub/docs/0000000647/483f3111-0745-48d2-bc3d-d4a26196a4d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7eeb7bc9_9098_486c_8f59_35117281fca8
ELIN-890752-2017 | UW-524478-2017 | 8/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Outlets1.png,Outlets2.png 120 Volt receptacle cover plates are missing leaving open access to energized parts and a potential shock fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets1.png | file://x:/photopub/docs/0000000653/249d47ed-945d-4767-a390-7be37eae42bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e58096d_75ad_469a_98bb_8e2c27b32b2c
ELIN-890752-2017 | UW-524478-2017 | 8/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | #Outlets1.png,Outlets2.png 120 Volt receptacle cover plates are missing leaving open access to energized parts and a potential shock fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlets2.png | file://x:/photopub/docs/0000000653/29529dc0-fb69-4f74-ae12-bbc764cdf78e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e58096d_75ad_469a_98bb_8e2c27b32b2c
ELIN-890750-2017 | EL-520352-2017 | 8/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png Indoor style panel board installed outdoor, unsecured and in close proximity to fuel containers. Potential shock and fire hazard. | 3 | General Equipment is not approved for the specific use | As_found1.png | file://x:/photopub/docs/0000000653/f1fbba12-457b-4305-ba3b-694ad5206f7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12ee09c5_a712_4423_97cb_f73a122ab238
ELIN-890750-2017 | EL-520352-2017 | 8/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #As_found1.png,As_found2.png Indoor style panel board installed outdoor, unsecured and in close proximity to fuel containers. Potential shock and fire hazard. | 3 | General Equipment is not approved for the specific use | As_found2.png | file://x:/photopub/docs/0000000653/2441b228-cde3-4732-bfaa-d79c5b094cfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12ee09c5_a712_4423_97cb_f73a122ab238
ELIN-876040-2017 | EL-544335-2017 | 8/15/2017 2:08:27 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Unapproved_gate_operator1.png,Unapproved_gate_operator2.png,Unapproved_gate_operator3.png,Unapproved_gate_operator4.png,Unapproved_gate_operator5.png,1000W_HID_growing_lights_with_no_evidence_of_approval1.png,1000W_HID_growing_lights_with_no_evidence_of_approval2.png,1000W_HID_growing_lights_with_no_evidence_of_approval3.png,1000W_HID_growing_lights_with_no_evidence_of_approval4.png,1000W_HID_growing_lights_with_no_evidence_of_approval5.png,1000W_HID_growing_lights_with_no_evidence_of_approval6.png,1000W_HID_growing_lights_with_no_evidence_of_approval7.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand1.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand2.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand3.png,No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png Electrical equipment used in BC is required to be tested, approved, and labeled by a certification agency. This is required to ensure that electrical products used | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | No_evidnce_of_approval_on_climate_control_equipmnet_-_Sentinel_brand4.png | file://x:/photopub/docs/0000000646/697c61a4-268c-4657-a78a-be7eb22fd675.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b66d3206_dfe3_4b47_9a2d_30e6ca4f27dc
ELIN-889287-2017 | EL-576038-2017 | 8/30/2017 11:43:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound The cable should have been terminated with WP cable connectors which would provide the necessary bonding of the cables armour. Rigid PVC conduit would then have been slid up over the cable to provide mechanical protection and improve the aesthetics | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | #Ungrounded_armoured_cable.png Ungrounded cable armour may pose a shock hazard if equipment failure occurs | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Ungrounded_armoured_cable.png | file://x:/photopub/docs/0000000655/b18ed98d-16bb-4cb1-9331-6b4263aec2d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a36e2e3_b6e5_4b64_8cc9_96ef1e5117b9
ELIN-882936-2017 | EL-547384-2017 | 8/22/2017 8:40:39 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Main_service.png At an existing single family residence , a new 200amp 120/240volt 1phase service upgrade was found with the system ground connection not terminated to the identified conductor. This can lead to a "Shock" hazard condition. Pic attached | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Main_service.png | file://x:/photopub/docs/0000000650/69a1d276-7b7c-4881-ae02-43589633ba9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f452fe9b_d8c2_47be_bb98_1d5f591b8323
GAIN-904848-2017 | GA-495305-2017 | 9/11/2017 10:51:54 AM | ASSESS: GA: Rough-In | png | #asFound | GA058 | Cathodic protection missing causing a hazard | 3 | 3 | #Piping_underground.png The as found condition is black iron piping intended for gas transmission (but not energized at time of inspection) is installed partially underground with a protective wrapping. The as found hazard is black iron piping systems require engineered (cathodic) corrosion protection to prevent undue deterioration that can lead to a hazardous gas leak. | 3 | Cathodic protection missing causing a hazard | Piping_underground.png | file://x:/photopub/docs/0000000660/0a94daaa-afd5-4749-8540-a136e66c8706.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64d2becd_2782_44f3_954f_0793e6cf681a
GAIN-903182-2017 | GA-564930-2017 | 9/11/2017 12:24:02 PM | ASSESS: GA: Final | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | #Undersized_gas_connector.png Gas Connector is used to connect appliance to main gas line. Gas connector is undersized for BTU demand of appliance. Appliance will not burn efficiently at full capacity, gas flow to appliance will be hindered causing misfiring or flames could repeatedly go out. | 3 | Undersized hose or appliance connector | Undersized_gas_connector.png | file://x:/photopub/docs/0000000660/c4515ccb-c1e2-4dd5-a4fc-bac94718ae57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eea587c_44a0_44b9_b38a_05b26f64e459
GAHE-896998-2017 | HE-578785-2017 | 8/31/2017 10:43:49 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound Fusible link is hanging off the wire connector and not connected in series to ISC valve (top left of photo) | GA144 | Missing mandatory safety controls | 4 | 4 | #Fusible_link.png An ISC (internal Safety Control) valve is installed to a propane tank. This is connected to a spring and a handle with a fusible link. The fusible link will melt if a fire is present and the spring will help close the ICS valve. Fusible link is not installed if a fire was to occur near the propane tank the propane tank could fuel the fire with more propane causing an explosion | 4 | Missing mandatory safety controls | Fusible_link.png | file://x:/photopub/docs/0000000655/07b37794-9ea5-4f2f-928e-77511f2622c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65094e86_7822_4ddb_b0ed_f7545b637c21
GAIN-890665-2017 | GA-540873-2017 | 8/31/2017 2:11:16 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #Concentric_vent_within_minimum_clearances_of_gas_regulator.png Exhaust vent of Navien heater is installed within the minimum distances of a gas regulator. Condensate and or water vapour can land on gas Regulator vent and freeze in certain weather conditions causing a malfunction to regulator and possibly causing regulator to stop flow of gas to appliances inside the residence. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Concentric_vent_within_minimum_clearances_of_gas_regulator.png | file://x:/photopub/docs/0000000655/895d03cc-6d62-44cd-8231-ef6ea3539c2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__115b3384_9cea_434e_85c7_662d9ee1278e
ELIN-889704-2017 | EL-576350-2017 | 9/11/2017 11:13:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Low_service.png A new temporary 100 amp 120/240 volt service point of attachment is 3.8 meters above grade at service post (pedestrian traffic only), the utility conductors are to cross a roadway which requires 5.5 meters and clearances may very likely not be met and this could become an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Low_service.png | file://x:/photopub/docs/0000000661/b2b72901-1f1e-4197-bcae-1ba38d957f72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce9a05f_dea8_4f23_b87d_3159aa4ea8ee
ELIN-798895-2017 | UW-524478-2017 | 8/25/2017 3:15:34 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Panel.png Indoor style panel board not approved for outdoor use, unsecured and in close proximity to fuel containers. | 3 | General Equipment is not approved for the specific use | Panel.png | file://x:/photopub/docs/0000000652/07eda74e-5d3f-41da-8cad-fa2bcb91bbd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__631ec418_a0f7_458e_ae9f_063fb28aa942
ELIN-894398-2017 | EL-434596-2016 | 9/5/2017 4:04:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Usable_Wall_Space.png In the new home, 15 amp 120 volt receptacle locations have not been provided in all locations and have been spaced to far apart. This poses a future shock hazard and potential damage to the electrical outlets, as extension cords may be used to provide power in locations without the proper receptacle locations provided. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Usable_Wall_Space.png | file://x:/photopub/docs/0000000657/a5fee66a-64ca-4bd7-a66c-1057041d06f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a6fb343_7b4f_4c92_8e6b_a8d19132b627
ELIN-900770-2017 | EL-580542-2017 | 9/7/2017 3:01:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | #Gas_range_plug_overloaded.png This assessment found that the gas range receptacle has more than allowed by code, creating a overloading circuit with a potential fire hazard. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Gas_range_plug_overloaded.png | file://x:/photopub/docs/0000000659/82ceca17-f24e-4c07-aaee-95d92e719ba5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f4fd9a5_8f1f_4185_8aa7_f8b6220d6992
BPVOP-866293-2017 | 2289058 | 9/5/2017 11:29:19 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Decal_and_the_NDT_from_2010.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and no NDT was done in the last 5 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Decal_and_the_NDT_from_2010.png | file://x:/photopub/docs/0000000660/ca72b2b1-30e1-4006-9940-a488987039c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c360afb_25b6_4bf8_bdb1_cdd681d7ba9a
GAWP-876234-2017 | GA-326218-2015 | 8/11/2017 9:53:14 AM | ASSESS: GA Work In Progress | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Furnace_vent_termination.png Furnace vent termination is installed too close to a mechanical air intake to the building. This may allow the products of combustion to recirculate into the living space. This could lead to carbon monoxide poisoning. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Furnace_vent_termination.png | file://x:/photopub/docs/0000000645/1b0072b1-ac07-461d-af9f-cddb0b25ce50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a082cd7_1b19_49e3_81f9_3772a08d78df
BPVIN-888638-2017 | BPV-519666-2017 | 9/5/2017 11:39:36 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound Vessel MAWP is 125 PSIG | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #PSV_rating1.png,PSV_rating2.png The pressure relief valve connected to the expansion tank is set above the maximum allowable pressure rating of the tank. If an overpressure situation was to occur, the vessel would be subjected to pressures above what it was designed to hold. Damage or failure of the vessel could possibly occur. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | PSV_rating1.png | file://x:/photopub/docs/0000000658/251deadf-5666-4520-bf2d-64de603262e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc9eab89_e21e_465a_8941_183ff5bd6804
BPVIN-888638-2017 | BPV-519666-2017 | 9/5/2017 11:39:36 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound PSV set at 150 PSIG | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | #PSV_rating1.png,PSV_rating2.png The pressure relief valve connected to the expansion tank is set above the maximum allowable pressure rating of the tank. If an overpressure situation was to occur, the vessel would be subjected to pressures above what it was designed to hold. Damage or failure of the vessel could possibly occur. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | PSV_rating2.png | file://x:/photopub/docs/0000000658/7f36d2d6-0ff8-451c-9f7d-88a7c9d80711.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc9eab89_e21e_465a_8941_183ff5bd6804
GAIN-871282-2017 | GA-555281-2017 | 8/23/2017 1:27:24 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Clearances.png The as-found condition is a barbecue has been installed within the minimum allowable clearance to combustible material. The as-found hazard is heat emanating from the appliance can cause pyrolysis of the combustible material within the clearance zone leading to a fire. | 3 | Clearance to combustible not met | Clearances.png | file://x:/photopub/docs/0000000650/fb281cc3-0b6a-411e-bcc2-ea277d952207.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99c12efa_a34d_49f7_a57e_61f545b61494
GAIN-861345-2017 | GA-522127-2017 | 8/10/2017 9:21:02 AM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #No_reg.png 2 PSI gas supplied to unit heater installed in garage and no 2 psi to inches regulator installed on the system. Gas valve designed for inches water column, high pressure gas could cause gas valve to malfunction and cause failure of gas valve or heater to over fire and causing heater to overheat and damage the heat exchanger. | 4 | Appliance regulator not installed, incorrect delivery pressure | No_reg.png | file://x:/photopub/docs/0000000644/4678e921-3780-480f-9979-d4ef8bd3959b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a482eb40_4b7e_42dd_963d_10c087767af5
ELIN-876628-2017 | EL-569113-2017 | 8/11/2017 12:17:52 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #J.png Armoured cables have been entered into plastic device boxes without the use of proper connectors. This is a shock hazard as the continuity of the armour of the cable is not continuous. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | J.png | file://x:/photopub/docs/0000000644/9438425f-33f9-4188-998f-f19098fab4cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edb92555_5089_47aa_befc_d9109e4b2140
ELHE-912589-2017 | HE-587712-2017 | 9/20/2017 11:24:17 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Panel_installed_as_found.png A panel board has been installed and energized such that the panel cover cannot be installed without pinching the supply conductors. Therefore the energized parts within are accessible and pose a potential shock hazard | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_installed_as_found.png | file://x:/photopub/docs/0000000666/6af22d7f-0fa4-4537-a88b-e55fc220bcf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__731efb51_11b1_40ba_9f3c_73e51bebcbfb
ELIN-911794-2017 | EL-585434-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #As-found1.png,As-found2.png,As-found3.png,As-found4.png Service cable weather head sealing is configured such that water ingress is occurring creating potential shock and electrical explosion hazards. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | As-found3.png | file://x:/photopub/docs/0000000665/9794e892-d0c8-453b-b531-1d559060af00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99bb6929_8aa8_467c_a437_2612194d8a03
PRIN-906144-2017 | PR-575766-2017 | 9/13/2017 | ASSESS: PR IN: Acceptance | png | #asFound | PR019 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | 2 | 2 | #Leaking_brake_line.png Brake line leaking hydraulic fluid. | 2 | Defect that impairs performance: Performance remains within limits Non-degenerative or very slow Reasonably detectable by the maintenance or operation program | Leaking_brake_line.png | file://x:/photopub/docs/0000000664/a1318e47-070d-4eca-8628-159370acef91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__714a839f_f0a9_4f98_90b0_3defe76c2ec2
ELIN-904124-2017 | EL-583026-2017 | 9/14/2017 9:37:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png,No_cover_plates5.png 120 volt 15 amp junction box, receptacles and switches have not been provided with cover plates in areas where the wiring and devices are could be accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring and devices. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates5.png | file://x:/photopub/docs/0000000663/d036552d-8d72-46c1-8e31-5f378301a562.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21b1ed92_f9a2_44ab_80fc_8eaa8d6dc93c
ELIN-904124-2017 | EL-583026-2017 | 9/14/2017 9:37:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png,No_cover_plates5.png 120 volt 15 amp junction box, receptacles and switches have not been provided with cover plates in areas where the wiring and devices are could be accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring and devices. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates3.png | file://x:/photopub/docs/0000000663/e45f7076-9267-4e75-ad27-3429b9fa61e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21b1ed92_f9a2_44ab_80fc_8eaa8d6dc93c
ELIN-904124-2017 | EL-583026-2017 | 9/14/2017 9:37:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png,No_cover_plates5.png 120 volt 15 amp junction box, receptacles and switches have not been provided with cover plates in areas where the wiring and devices are could be accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring and devices. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates2.png | file://x:/photopub/docs/0000000663/86de67b4-f3e9-45e4-8cc0-23dde598dab9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21b1ed92_f9a2_44ab_80fc_8eaa8d6dc93c
ELIN-904124-2017 | EL-583026-2017 | 9/14/2017 9:37:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png,No_cover_plates5.png 120 volt 15 amp junction box, receptacles and switches have not been provided with cover plates in areas where the wiring and devices are could be accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring and devices. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates4.png | file://x:/photopub/docs/0000000663/f8748396-2360-4806-8e40-ade2dfbaee0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21b1ed92_f9a2_44ab_80fc_8eaa8d6dc93c
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png | file://x:/photopub/docs/0000000666/155555e1-fdec-487b-8c44-3a1b73e1a570.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
ELIN-904981-2017 | EL-580267-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base1.png,PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base2.png,PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base3.png When terminating PVC conduits and fittings into electrical equipment threaded male PVC terminal adapters are not permitted to be installed into threaded metal conduit entries in metal enclosures. This is not permitted because PVC conduit and fittings can expand and contract at different rates than metal fittings on enclosures. This can cause PVC fittings to break if they expand to much or cause loose connections between fittings and enclosures if the PVC contracts which can cause issues with water entering enclosures and equipment located outdoors. This installation for a service upgrade for an existing house has a new 2" PVC service conduit installed into the top of a new meter base installed on a pole outdoors. The PVC conduit has a PVC male terminal adapter that is threaded into a female metal hu | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base1.png | file://x:/photopub/docs/0000000666/15db40ba-47d8-45d4-affa-878864c44075.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fb2de0a_311b_4508_8f64_762ed07af0ae
ELIN-910520-2017 | EL-581338-2017 | 9/19/2017 2:32:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Z1.png,Z2.png Grounding electrode is not properly installed. This is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Z1.png | file://x:/photopub/docs/0000000665/6ed14f8c-ef57-4780-8096-00682fa61693.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ead8769_dcc1_445c_a529_bdcbe0a4ef3b
ELIN-910520-2017 | EL-581338-2017 | 9/19/2017 2:32:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Z1.png,Z2.png Grounding electrode is not properly installed. This is a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Z2.png | file://x:/photopub/docs/0000000665/84acc228-1238-49d0-bad6-0bd9162279b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ead8769_dcc1_445c_a529_bdcbe0a4ef3b
GAIN-908711-2017 | GA-535343-2017 | 9/21/2017 8:09:36 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Pool_heater2.png A pool heater installed in a outbuilding was found to be installed without combustion air provided. Lack of combustion air can lead to poor combustion and possible premature failure of the equipment | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Pool_heater2.png | file://x:/photopub/docs/0000000666/29e54882-730f-4245-9eca-df7d0ec29657.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f618a9f0_c266_4703_ab73_1aaaaa43c383
ELIN-903716-2017 | EL-579074-2017 | 9/12/2017 | ASSESS: EL: Service Connection | png | #asFound Coverplate not installed on receptacle. Possibility of contact with live terminals in side of receptacle with out cover. | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Missing_cover.png | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Missing_cover.png | file://x:/photopub/docs/0000000662/5424c0e6-f002-4824-9051-1d74ce2dafc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e66037cf_5009_4a50_9df0_2770c31a07ff
ELIN-907644-2017 | EL-540339-2017 | 9/14/2017 12:35:36 PM | ASSESS: EL: Final | png | #asFound Photo showing outlet box in the wall too far. Excessive gap's in front of the outlet box inside the wall. | EL135 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | 3 | 3 | #Outlet_box.png Reinspection of noncompliances on final assessment of new dental clinic. The outlet boxes for two receptacles on a counter in the mechanical room have been an inset into the wall too far. No provision has been made to close the gap between the box and the finished wall. An extension ring on the outlet boxes are required. This has the potential of being a fire hazard if the device fails within the box and the fault cannot be contained within the box. | 3 | Installation of electrical equipment General: excessive gaps between edges of boxes and finished surfaces. | Outlet_box.png | file://x:/photopub/docs/0000000663/a3d71106-860a-4c88-a746-4c8c5a459629.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11fefa07_f4ab_434b_8a78_fc066c15501c
GAIN-887276-2017 | GA-471895-2016 | 9/18/2017 12:10:19 PM | ASSESS: GA: Final | png | #asFound Range | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Range.png At time of inspection anti trip bracket not installed , this could cause an injury to homeowner if range tips forward | 3 | Appliance not installed according to installation instructions | Range.png | file://x:/photopub/docs/0000000665/0adf5943-3b4f-412b-bea0-53fef6f6c3da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cca4b2e_409d_4983_9b16_83b1d5d14573
ELIN-904124-2017 | EL-583026-2017 | 9/14/2017 9:37:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #No_cover_plates1.png,No_cover_plates2.png,No_cover_plates3.png,No_cover_plates4.png,No_cover_plates5.png 120 volt 15 amp junction box, receptacles and switches have not been provided with cover plates in areas where the wiring and devices are could be accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring and devices. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_cover_plates1.png | file://x:/photopub/docs/0000000663/413a89c5-db98-4def-ae45-448b209507d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21b1ed92_f9a2_44ab_80fc_8eaa8d6dc93c
ELIN-905106-2017 | EL-576337-2017 | 9/14/2017 1:50:24 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Bathroom_receptacle.png A 15 amp 120 volt receptacle has been installed next to the bathroom sink and within 1.5m without GFCI protection. This poses a shock hazard to persons using the receptacle, and possible equipment damage to appliances or items plugged into this receptacle and used in the vicinity of the sink. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Bathroom_receptacle.png | file://x:/photopub/docs/0000000663/a67dc624-22ce-4767-9c95-c4a1e52d0661.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b89c8dc_7b9b_4ced_9616_4c8bb4965730
ELIN-908103-2017 | EL-558939-2017 | 9/18/2017 9:38:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png In the energized 200 amp 120/240 volt electrical panel, unused opening in the panel cover have not been filled or effectively covered/guarded to prevent persons from contacting the energized components inside the panel. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Main_Panel2.png | file://x:/photopub/docs/0000000664/cfcf2153-c813-4534-a509-ec5e854b59a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca4e19ed_0ef8_4b39_b9be_4193b17465de
ELIN-908103-2017 | EL-558939-2017 | 9/18/2017 9:38:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Main_Panel1.png,Main_Panel2.png In the energized 200 amp 120/240 volt electrical panel, unused opening in the panel cover have not been filled or effectively covered/guarded to prevent persons from contacting the energized components inside the panel. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Main_Panel1.png | file://x:/photopub/docs/0000000664/d69e0573-7d61-43af-a466-9d3084f883bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca4e19ed_0ef8_4b39_b9be_4193b17465de
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png | file://x:/photopub/docs/0000000666/132294ea-d6a8-43e3-920e-00c537c7611b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png | file://x:/photopub/docs/0000000666/382122d7-6161-4062-b0c2-276b8c8eb0d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
ELIN-904981-2017 | EL-580267-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base1.png,PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base2.png,PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base3.png When terminating PVC conduits and fittings into electrical equipment threaded male PVC terminal adapters are not permitted to be installed into threaded metal conduit entries in metal enclosures. This is not permitted because PVC conduit and fittings can expand and contract at different rates than metal fittings on enclosures. This can cause PVC fittings to break if they expand to much or cause loose connections between fittings and enclosures if the PVC contracts which can cause issues with water entering enclosures and equipment located outdoors. This installation for a service upgrade for an existing house has a new 2" PVC service conduit installed into the top of a new meter base installed on a pole outdoors. The PVC conduit has a PVC male terminal adapter that is threaded into a female metal hu | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base2.png | file://x:/photopub/docs/0000000666/52e001ab-8449-4574-b7c8-73c0ecc9a34a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fb2de0a_311b_4508_8f64_762ed07af0ae
ELIN-906080-2017 | EL-569452-2017 | 9/13/2017 1:48:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_circuits1.png,Energized_circuits2.png,Energized_circuits3.png,Energized_circuits4.png,Energized_circuits5.png Existing circuits have been removed from device boxes and left exposed and energized after a request for a rough wiring cover up. Hi potential for electric shock and fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_circuits3.png | file://x:/photopub/docs/0000000662/bc127041-40d0-47e8-925b-23847510317e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2bc6c89_8600_4a51_b0ca_1a30cfd3cce2
ELIN-906080-2017 | EL-569452-2017 | 9/13/2017 1:48:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_circuits1.png,Energized_circuits2.png,Energized_circuits3.png,Energized_circuits4.png,Energized_circuits5.png Existing circuits have been removed from device boxes and left exposed and energized after a request for a rough wiring cover up. Hi potential for electric shock and fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_circuits4.png | file://x:/photopub/docs/0000000662/929bcf3f-e160-4807-9516-58a043dade1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2bc6c89_8600_4a51_b0ca_1a30cfd3cce2
ELIN-906080-2017 | EL-569452-2017 | 9/13/2017 1:48:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_circuits1.png,Energized_circuits2.png,Energized_circuits3.png,Energized_circuits4.png,Energized_circuits5.png Existing circuits have been removed from device boxes and left exposed and energized after a request for a rough wiring cover up. Hi potential for electric shock and fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_circuits1.png | file://x:/photopub/docs/0000000662/5947b8be-9ae1-4bd5-955f-a1166aa72a17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2bc6c89_8600_4a51_b0ca_1a30cfd3cce2
ELIN-906080-2017 | EL-569452-2017 | 9/13/2017 1:48:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_circuits1.png,Energized_circuits2.png,Energized_circuits3.png,Energized_circuits4.png,Energized_circuits5.png Existing circuits have been removed from device boxes and left exposed and energized after a request for a rough wiring cover up. Hi potential for electric shock and fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_circuits5.png | file://x:/photopub/docs/0000000662/1aaaf3dc-7a61-4ae3-9bd2-32ba459e9c15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2bc6c89_8600_4a51_b0ca_1a30cfd3cce2
ELIN-906080-2017 | EL-569452-2017 | 9/13/2017 1:48:21 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_circuits1.png,Energized_circuits2.png,Energized_circuits3.png,Energized_circuits4.png,Energized_circuits5.png Existing circuits have been removed from device boxes and left exposed and energized after a request for a rough wiring cover up. Hi potential for electric shock and fire. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_circuits2.png | file://x:/photopub/docs/0000000662/ac26b42d-87a2-46ad-95f8-f84e5320f6d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2bc6c89_8600_4a51_b0ca_1a30cfd3cce2
GAIN-881033-2017 | GA-553044-2017 | 9/19/2017 8:59:13 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Regulator_clearance1.png,Regulator_clearance2.png 10 psi to 2 psi propane regulator installed too close to 2 pipe direct vent fireplace. If regulator vent reliefs, propane vapour could be drawn into air intake of fire place causing an explosion or fire | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulator_clearance2.png | file://x:/photopub/docs/0000000665/d946b80e-2ecd-4b80-b142-e40f9fe55604.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87766331_01f8_4b2d_80c3_d586cad37c0a
GAIN-881033-2017 | GA-553044-2017 | 9/19/2017 8:59:13 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Regulator_clearance1.png,Regulator_clearance2.png 10 psi to 2 psi propane regulator installed too close to 2 pipe direct vent fireplace. If regulator vent reliefs, propane vapour could be drawn into air intake of fire place causing an explosion or fire | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulator_clearance1.png | file://x:/photopub/docs/0000000665/0884c739-e30e-41eb-b54f-d2d3b6487bf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87766331_01f8_4b2d_80c3_d586cad37c0a
ELHE-907899-2017 | HE-585120-2017 | 9/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found electrical equipment cable 120 volt 15 amp is damaged and altered while branch circuit conductor is still connected to power supply system and cable has exposed bare copper ends on the end of cable. When electrical equipment is connected to power supply system and has bare copper conductor metal exposed on ends of cable without a junction box and cover enclosing the ends of insulated and protected bare conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal1.png,Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal2.png,Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal3.png Found electrical equipment cable 120 volt 15 amp is damaged and altered while branch circuit conductor is still connected to power supply system and cable has exposed bare copper ends on the end of cable. When electrical equipment is connected to power supply system and has bare copper conductor metal exposed on ends of cable without a junction box and cover enclosing the ends of insulated and protected bare conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal1.png | file://x:/photopub/docs/0000000663/b74b973a-9268-49b8-84ab-3f1a2e78e5f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4f3c4c_88e7_4b13_b36e_b5dd9f872938
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png | file://x:/photopub/docs/0000000666/2a924f71-b95e-4729-ac56-ad8d32a75628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png | file://x:/photopub/docs/0000000666/30b60028-b530-447d-bd85-db491f68a62f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png | file://x:/photopub/docs/0000000666/307e3641-4773-4176-9ed5-893c9f19610a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
BPVIN-838127-2017 | BPV-547591-2017 | 8/31/2017 5:04:10 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Scrubber_vessel1.png,Scrubber_vessel2.png,No_PSV_on_main_vesssel.png Please see administrative findings. | 0 | No Created Hazard Identified | No_PSV_on_main_vesssel.png | file://x:/photopub/docs/0000000665/45506fb8-78dc-4b18-88c4-af5714e707e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07f24440_1d3a_4001_8e6b_40340c7e7b71
BPVIN-838127-2017 | BPV-547591-2017 | 8/31/2017 5:04:10 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Scrubber_vessel1.png,Scrubber_vessel2.png,No_PSV_on_main_vesssel.png Please see administrative findings. | 0 | No Created Hazard Identified | Scrubber_vessel1.png | file://x:/photopub/docs/0000000665/b5c0f592-df75-4e71-b43b-a242a3f77357.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07f24440_1d3a_4001_8e6b_40340c7e7b71
BPVIN-838127-2017 | BPV-547591-2017 | 8/31/2017 5:04:10 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | #Scrubber_vessel1.png,Scrubber_vessel2.png,No_PSV_on_main_vesssel.png Please see administrative findings. | 0 | No Created Hazard Identified | Scrubber_vessel2.png | file://x:/photopub/docs/0000000665/170e2bc4-2f47-4ace-becc-61f34ded4f47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07f24440_1d3a_4001_8e6b_40340c7e7b71
ELHE-907899-2017 | HE-585120-2017 | 9/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found electrical equipment cable 120 volt 15 amp is damaged and altered while branch circuit conductor is still connected to power supply system and cable has exposed bare copper ends on the end of cable. When electrical equipment is connected to power supply system and has bare copper conductor metal exposed on ends of cable without a junction box and cover enclosing the ends of insulated and protected bare conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal1.png,Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal2.png,Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal3.png Found electrical equipment cable 120 volt 15 amp is damaged and altered while branch circuit conductor is still connected to power supply system and cable has exposed bare copper ends on the end of cable. When electrical equipment is connected to power supply system and has bare copper conductor metal exposed on ends of cable without a junction box and cover enclosing the ends of insulated and protected bare conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal3.png | file://x:/photopub/docs/0000000663/1c634fd9-70bb-423e-ad1f-cb4650f8d423.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4f3c4c_88e7_4b13_b36e_b5dd9f872938
ELHE-907899-2017 | HE-585120-2017 | 9/13/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found electrical equipment cable 120 volt 15 amp is damaged and altered while branch circuit conductor is still connected to power supply system and cable has exposed bare copper ends on the end of cable. When electrical equipment is connected to power supply system and has bare copper conductor metal exposed on ends of cable without a junction box and cover enclosing the ends of insulated and protected bare conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal1.png,Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal2.png,Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal3.png Found electrical equipment cable 120 volt 15 amp is damaged and altered while branch circuit conductor is still connected to power supply system and cable has exposed bare copper ends on the end of cable. When electrical equipment is connected to power supply system and has bare copper conductor metal exposed on ends of cable without a junction box and cover enclosing the ends of insulated and protected bare conductors, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Damaged_non-metallic_sheathed_cable_with_exposed_copper_conductor_metal2.png | file://x:/photopub/docs/0000000663/303d8106-6428-4030-99a9-9c00ac98346c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4f3c4c_88e7_4b13_b36e_b5dd9f872938
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G7.png | file://x:/photopub/docs/0000000666/765d60e5-4ff5-4ee2-9d54-2240c990ca50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G1.png | file://x:/photopub/docs/0000000666/493b6700-a32a-4a20-8a46-9f1393e37032.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G6.png | file://x:/photopub/docs/0000000666/7fcff52e-35fd-4b1c-878b-f78b08398bde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G3.png | file://x:/photopub/docs/0000000666/60d3cc08-a885-4205-8d78-7004a9403471.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
BPVOP-906843-2017 | 2939790 | 9/13/2017 9:09:48 AM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve.png On assessment of a high pressure steam boiler with a maximum working pressure of 125 psig and a maximum working temperature of 350 Fahrenheit, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000662/3b3c9329-2cbb-46bb-8ff8-e602f0972222.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e350eae5_2f29_4485_ad9f_ee93cc3d6e90
BPVOP-906858-2017 | 4451154 | 9/13/2017 9:12:29 AM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD.png On assessment of a hot water boiler with a maximum working pressure of 30 psig and a maximum working temperature of 250 Fahrenheit, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD.png | file://x:/photopub/docs/0000000662/b43a3c31-ea96-46f1-a67a-6138ec03c0bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f0166a8_b4af_48c0_900d_67de48741234
GAUP-907090-2017 | UW-584737-2017 | 9/13/2017 3:34:32 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Chimney_liner_connected_straight_to_appliance.png Original venting is oversized for new install. Chimney liner install at right size however chimney liner is connected to vent of appliance. Chimney liner is not approved as a horizontal vent connector due to possibility of corrosion inside causing holes and putting flue gases into space. | 3 | Unapproved venting material | Chimney_liner_connected_straight_to_appliance.png | file://x:/photopub/docs/0000000662/e4c15976-a52d-420e-bd59-b995dfddf812.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ca1b36d_d33f_4667_9ed3_e5d395203610
ELOP-909368-2017 | 1660 | 9/15/2017 2:51:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found1.png,As_found2.png,As_found3.png Open breaker space on an unlocked energized panel leaving exposed electrical parts and a potential shock hazard in an area accessible to secondary students. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found2.png | file://x:/photopub/docs/0000000663/167f18d5-0df0-4594-a582-7c4fe86de466.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd7c24ed_3c5b_4e81_a53c_50ed57e3e927
ELOP-909368-2017 | 1660 | 9/15/2017 2:51:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found1.png,As_found2.png,As_found3.png Open breaker space on an unlocked energized panel leaving exposed electrical parts and a potential shock hazard in an area accessible to secondary students. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found3.png | file://x:/photopub/docs/0000000663/38e18bed-1dfc-4f31-9b87-c2c914794d2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd7c24ed_3c5b_4e81_a53c_50ed57e3e927
ELOP-909368-2017 | 1660 | 9/15/2017 2:51:50 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #As_found1.png,As_found2.png,As_found3.png Open breaker space on an unlocked energized panel leaving exposed electrical parts and a potential shock hazard in an area accessible to secondary students. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found1.png | file://x:/photopub/docs/0000000663/729346df-b0fb-4c07-bf3e-a99769a476ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd7c24ed_3c5b_4e81_a53c_50ed57e3e927
BPVIN-906939-2017 | BPV-584609-2017 | 9/13/2017 10:01:04 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | #Compressor_stage_PRVs1.png,Compressor_stage_PRVs2.png,Compressor_stage_PRVs3.png At least one pressure relief valve shall be provided for protection of a pressure vessel with the set pressure marked on the device not to exceed the maximum allowable working pressure of the vessel its protecting. I found 150psi pressure relief valves installed on the first and second stage motor but not one directly on the pressure vessel. Potential exists for an incident due to over pressure conditions. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Compressor_stage_PRVs3.png | file://x:/photopub/docs/0000000662/a7cf3502-087f-430f-b328-d2e08b74b5d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92b5a947_9250_4d55_a256_f84afbc46147
BPVIN-906939-2017 | BPV-584609-2017 | 9/13/2017 10:01:04 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | #Compressor_stage_PRVs1.png,Compressor_stage_PRVs2.png,Compressor_stage_PRVs3.png At least one pressure relief valve shall be provided for protection of a pressure vessel with the set pressure marked on the device not to exceed the maximum allowable working pressure of the vessel its protecting. I found 150psi pressure relief valves installed on the first and second stage motor but not one directly on the pressure vessel. Potential exists for an incident due to over pressure conditions. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Compressor_stage_PRVs1.png | file://x:/photopub/docs/0000000662/611ae1ad-f017-4426-8815-771e91dd9228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92b5a947_9250_4d55_a256_f84afbc46147
BPVIN-906939-2017 | BPV-584609-2017 | 9/13/2017 10:01:04 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | #Compressor_stage_PRVs1.png,Compressor_stage_PRVs2.png,Compressor_stage_PRVs3.png At least one pressure relief valve shall be provided for protection of a pressure vessel with the set pressure marked on the device not to exceed the maximum allowable working pressure of the vessel its protecting. I found 150psi pressure relief valves installed on the first and second stage motor but not one directly on the pressure vessel. Potential exists for an incident due to over pressure conditions. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Compressor_stage_PRVs2.png | file://x:/photopub/docs/0000000662/f9e17855-561a-47a5-b839-57935b20ebb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92b5a947_9250_4d55_a256_f84afbc46147
GAIN-901034-2017 | GA-454671-2016 | 9/14/2017 10:55:26 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #Clearances.png The as found condition is a built in barbecue installed within the minimum 3 foot clearance to combustible material (wood framing behind a stone wall) designated in the installation guide. The as found hazard is failure to maintain these minimum clearances could lead to pyrolysis and ignition of the combustible material due to excessive heat from the appliance when it is in operation. | 3 | Clearance to combustible not met | Clearances.png | file://x:/photopub/docs/0000000663/7815a10d-6943-4d04-963a-5e59c4763705.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d116c983_d8c9_40f9_a660_e4a31bd1f72a
ELIN-910359-2017 | EL-526549-2017 | 9/19/2017 4:23:47 PM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Walk_in_coolers.png Equipment that has no been approved or certified for use in Canada has not gone through recognized testing for failures that could occur causing the unapproved equipment to be a fire and shock hazard | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Walk_in_coolers.png | file://x:/photopub/docs/0000000665/1e14eee9-5164-4838-bbb6-0ea595b9aeec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__470fdc45_417c_4990_ad45_45535ad52888
BPVOP-909797-2017 | 2992667 | 9/15/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #As_found_safety_valve1.png,As_found_safety_valve2.png Valve found leaking at 30 psi Boiler will have constant raw water make-up, adding to boiler scale problem. Boiler controls will fire boiler continuously as pressure control set point will not be reached. Boiler could over heat. Failure is possible. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | As_found_safety_valve2.png | file://x:/photopub/docs/0000000664/a49fe00e-19b0-4c45-a514-9ba77c3a5cba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90a790d2_5035_45c8_a257_00251961c71e
BPVOP-909797-2017 | 2992667 | 9/15/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #As_found_safety_valve1.png,As_found_safety_valve2.png Valve found leaking at 30 psi Boiler will have constant raw water make-up, adding to boiler scale problem. Boiler controls will fire boiler continuously as pressure control set point will not be reached. Boiler could over heat. Failure is possible. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | As_found_safety_valve1.png | file://x:/photopub/docs/0000000664/16250745-bd28-4f1e-81af-d96bbbb29956.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90a790d2_5035_45c8_a257_00251961c71e
GAIN-898561-2017 | GA-579688-2017 | 9/19/2017 11:58:03 AM | ASSESS: GA: Final | png | #asFound Exhaust is located on the right side of the water heater. | GA105 | Unapproved venting material | 3 | 3 | #Dunsterville6.png Non S 636 venting material used for exhaust venting on a on demand water heater. Possible failure of the venting material could be caused by exposure to flue temperatures in excess of its design temperature. Possible failure of venting could result in the release of flue products containing carbon monoxide. | 3 | Unapproved venting material | Dunsterville6.png | file://x:/photopub/docs/0000000665/aea92f2b-b9ee-48d9-b2b3-82ed8d6a55df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ae132e5_e47a_4cb3_aeea_f28b99332864
ELIN-908651-2017 | EL-579544-2017 | 9/15/2017 1:10:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #1_5m_exceeded1.png,1_5m_exceeded2.png This assessment found that the 1.5m of exposed service conductors was exceeded, this creates an increased potential for damage causing a fire and shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 1_5m_exceeded1.png | file://x:/photopub/docs/0000000663/2ae98735-fa91-440d-adcc-c36d040bb147.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960df949_4034_4d5b_a574_a032ea0dbcdd
ELIN-908651-2017 | EL-579544-2017 | 9/15/2017 1:10:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #1_5m_exceeded1.png,1_5m_exceeded2.png This assessment found that the 1.5m of exposed service conductors was exceeded, this creates an increased potential for damage causing a fire and shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 1_5m_exceeded2.png | file://x:/photopub/docs/0000000663/ad1fd8e4-cfc5-40e6-a564-ad8a7090b09c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960df949_4034_4d5b_a574_a032ea0dbcdd
ELIN-907219-2017 | EL-471432-2016 | 9/14/2017 10:10:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_unprotected1.png,NMSC_unprotected2.png,NMSC_unprotected3.png,NMSC_unprotected4.png,NMSC_unprotected5.png,NMSC_unprotected6.png In a new residential Rough Wiring it was found the homeowner installed the NMSC at surface level of the ICI (insulation/concrete/ insulation) construction and at ceilings at same height as strapping material which exposes the cables to mechanical damage and can lead to a shock, thermal and equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_unprotected2.png | file://x:/photopub/docs/0000000663/9ac5d4a4-192f-439e-b46a-3b99d40e0e7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c7a1d8_01c4_477d_ad34_55df3a6f4ad3
ELIN-907219-2017 | EL-471432-2016 | 9/14/2017 10:10:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_unprotected1.png,NMSC_unprotected2.png,NMSC_unprotected3.png,NMSC_unprotected4.png,NMSC_unprotected5.png,NMSC_unprotected6.png In a new residential Rough Wiring it was found the homeowner installed the NMSC at surface level of the ICI (insulation/concrete/ insulation) construction and at ceilings at same height as strapping material which exposes the cables to mechanical damage and can lead to a shock, thermal and equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_unprotected6.png | file://x:/photopub/docs/0000000663/c8d61776-a5fc-4e42-a519-408a3437d551.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c7a1d8_01c4_477d_ad34_55df3a6f4ad3
ELIN-907219-2017 | EL-471432-2016 | 9/14/2017 10:10:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_unprotected1.png,NMSC_unprotected2.png,NMSC_unprotected3.png,NMSC_unprotected4.png,NMSC_unprotected5.png,NMSC_unprotected6.png In a new residential Rough Wiring it was found the homeowner installed the NMSC at surface level of the ICI (insulation/concrete/ insulation) construction and at ceilings at same height as strapping material which exposes the cables to mechanical damage and can lead to a shock, thermal and equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_unprotected4.png | file://x:/photopub/docs/0000000663/9e9d5b15-0a80-4255-af83-a6e4729c3555.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c7a1d8_01c4_477d_ad34_55df3a6f4ad3
ELIN-907219-2017 | EL-471432-2016 | 9/14/2017 10:10:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_unprotected1.png,NMSC_unprotected2.png,NMSC_unprotected3.png,NMSC_unprotected4.png,NMSC_unprotected5.png,NMSC_unprotected6.png In a new residential Rough Wiring it was found the homeowner installed the NMSC at surface level of the ICI (insulation/concrete/ insulation) construction and at ceilings at same height as strapping material which exposes the cables to mechanical damage and can lead to a shock, thermal and equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_unprotected5.png | file://x:/photopub/docs/0000000663/89bac13b-86fe-4b52-be99-d2372386cd18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c7a1d8_01c4_477d_ad34_55df3a6f4ad3
ELIN-907219-2017 | EL-471432-2016 | 9/14/2017 10:10:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_unprotected1.png,NMSC_unprotected2.png,NMSC_unprotected3.png,NMSC_unprotected4.png,NMSC_unprotected5.png,NMSC_unprotected6.png In a new residential Rough Wiring it was found the homeowner installed the NMSC at surface level of the ICI (insulation/concrete/ insulation) construction and at ceilings at same height as strapping material which exposes the cables to mechanical damage and can lead to a shock, thermal and equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_unprotected3.png | file://x:/photopub/docs/0000000663/1b123e9f-db8f-4828-a2c7-ee0517069b37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c7a1d8_01c4_477d_ad34_55df3a6f4ad3
ELIN-907219-2017 | EL-471432-2016 | 9/14/2017 10:10:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_unprotected1.png,NMSC_unprotected2.png,NMSC_unprotected3.png,NMSC_unprotected4.png,NMSC_unprotected5.png,NMSC_unprotected6.png In a new residential Rough Wiring it was found the homeowner installed the NMSC at surface level of the ICI (insulation/concrete/ insulation) construction and at ceilings at same height as strapping material which exposes the cables to mechanical damage and can lead to a shock, thermal and equipment damage issue | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_unprotected1.png | file://x:/photopub/docs/0000000663/859db6fa-341e-4de3-bbd9-4d2d085fc291.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7c7a1d8_01c4_477d_ad34_55df3a6f4ad3
ELIN-904540-2017 | EL-548362-2017 | 9/13/2017 1:07:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Main_Panel.png A 200 amp 120/240 volt new Main Electrical Panel has been installed in a new home addition and temporarily energized from a 100 amp 120/240 volt electrical temporary construction service. The panel cover is not in place on the energized Main Panel and the energized components are accessible to accidental contact by workers in the addition. This could result is a shock and possible electrocution hazard to persons and potential mechanical damage to the Electrical Panel and components. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Main_Panel.png | file://x:/photopub/docs/0000000662/a38be2fb-99ee-4b71-a41b-7b564d5dee65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__684fa61d_df84_4ec0_8836_045c1064ba7c
ELIN-904541-2017 | EL-548362-2017 | 9/13/2017 2:25:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #New_Main_Panel.png A new 200 amp 120/240 volt electrical panel has been installed and supplied by an existing 100 amp 120/240 volt Temporary Electrical Service. In both panels the bonding jumpers are in place to the neutral bar, this allows for circulating currents and fault currents to exist in the new panel, as a clear path to ground at the Temporary Service has not been established. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | New_Main_Panel.png | file://x:/photopub/docs/0000000662/88f7eb7c-2000-40d4-9044-82d8095a525b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0986545_01da_4b27_8135_aed940c9f16f
GAIN-906114-2017 | GA-569789-2017 | 9/15/2017 1:47:04 PM | ASSESS: GA: Final | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Unapproved_product.png Appliance is not approved for use in Canada. No evidence of testing the appliance by a recognized testing/approval agency. Because of this we have no idea if the appliance is safe, ie gas flame rectification, pressure vessel for water, venting of flue gases. | 3 | Uncertified appliance connected to gas supply but not in service | Unapproved_product.png | file://x:/photopub/docs/0000000663/b84e6f77-2abc-4fd8-84bd-b94567beb014.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebe9b5fb_9bd9_4a6c_a49b_06d12bd48e41
EDIN-907523-2017 | ED-452042-2016 | 9/14/2017 2:36:53 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Communication.png The 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found that the 2-way emergency communication was not functioning properly because the monitoring station had incorrect address of the elevator. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevator. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This is a 3 stop MRL traction elevator located in a commercial building. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Communication.png | file://x:/photopub/docs/0000000663/94425974-2bb9-49c3-bef1-9ac2ce89a460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a864691_0724_4a4c_adba_7d9b25ed5aec
EDIN-907522-2017 | ED-452046-2016 | 9/14/2017 2:27:25 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #2-way_comm.png The 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found that the 2-way emergency communication was not functioning properly because the monitoring station had incorrect address of the elevator. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevator. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This is a 3 stop MRL traction elevator located in a commercial building. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 2-way_comm.png | file://x:/photopub/docs/0000000663/08786855-e44d-4b56-93c6-102c1a7ddf5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8d92abd_2318_4069_a122_5f1f1a558d51
EDIN-907526-2017 | ED-509367-2017 | 9/13/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Phone.png The 2-way emergency communication in the elevator is a means of communication to a 24 hours/day monitored station. During an acceptance inspection it was found that the 2-way emergency communication was not functioning properly because an account with the monitoring company was not set up. Without a properly functioning 2-way emergency communication in the elevator it may be difficult to get help in case of an entrapment in the elevator. This may result in a serious situation if panic sets in or if a person had a medical emergency and was trapped in the elevator. This is a 3 stop MRL traction elevator located in a commercial building. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Phone.png | file://x:/photopub/docs/0000000663/66366c53-f2e0-4ac3-8950-69927bbc103a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7613876_b273_4e84_874a_0c8016c17da0
GAWP-906177-2017 | GA-530702-2017 | 9/12/2017 2:50:42 PM | ASSESS: GA Work In Progress | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | #Connector.png Residential corrugated appliance connectors installed on all commercial gas fired equipment. Smooth coating appliance connector required or hard piped to prevent grease build up and easy cleaning | 3 | Non-certified appliance connector | Connector.png | file://x:/photopub/docs/0000000662/8d9b8ebf-ce23-43b9-a40d-8f6492d52d7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__722f3684_48a1_4d4e_9a44_673f52c8755b
EDIN-908718-2017 | ED-484382-2016 | 9/14/2017 8:24:54 PM | ASSESS: ED IN: Construction Use | png | #asFound | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | #Sprinkler_Pipe_for_Mechanical_room1.png,Sprinkler_Pipe_for_Mechanical_room2.png A branch sprinkler line placed in the elevator machine room for use in the mechanical room below the elevator machine room. This installation is not allowed in the elevator machine room as per code requirement. Unauthorized personnel who are not trained in the dangers of elevator equipment may enter the room to perform work on the sprinkler line which could result serious injuries by the rotating elevator equipment | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Sprinkler_Pipe_for_Mechanical_room1.png | file://x:/photopub/docs/0000000663/d385611e-3ecb-461a-97d2-5429c6e1b5dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62e839b3_65fe_4b1f_baf2_cc327c5c91be
EDIN-908718-2017 | ED-484382-2016 | 9/14/2017 8:24:54 PM | ASSESS: ED IN: Construction Use | png | #asFound Branch sprinkler line for mechanical room installed in elevator machine room | ED016 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | 4 | 4 | #Sprinkler_Pipe_for_Mechanical_room1.png,Sprinkler_Pipe_for_Mechanical_room2.png A branch sprinkler line placed in the elevator machine room for use in the mechanical room below the elevator machine room. This installation is not allowed in the elevator machine room as per code requirement. Unauthorized personnel who are not trained in the dangers of elevator equipment may enter the room to perform work on the sprinkler line which could result serious injuries by the rotating elevator equipment | 4 | Oil/Water/Other Debris is found that: Is likely to affect components or operation | Sprinkler_Pipe_for_Mechanical_room2.png | file://x:/photopub/docs/0000000663/aa4ad28b-d793-495c-9b9a-a41e43e05050.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62e839b3_65fe_4b1f_baf2_cc327c5c91be
ELIN-910747-2017 | EL-585467-2017 | 9/19/2017 4:01:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Dry_equipment1.png,Dry_equipment2.png Dry location equipment installed outdoors | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Dry_equipment2.png | file://x:/photopub/docs/0000000665/9de3f469-71ca-4323-b135-8ebca4de96a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0609281a_c5ff_4153_bf0e_294211452e05
ELIN-910747-2017 | EL-585467-2017 | 9/19/2017 4:01:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Dry_equipment1.png,Dry_equipment2.png Dry location equipment installed outdoors | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Dry_equipment1.png | file://x:/photopub/docs/0000000665/c2d8bea8-3d43-4e4a-8cab-473163ebe44a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0609281a_c5ff_4153_bf0e_294211452e05
BPVOP-907467-2017 | 5034660 | 9/12/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD8.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD8.png | file://x:/photopub/docs/0000000662/123cb8ea-f149-4331-af1e-62527c7d5e3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f756720d_4b26_4835_846d_723821bd5c02
BPVOP-907458-2017 | 4758594 | 9/12/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD4.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. No seismic mounting supports installed. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD4.png | file://x:/photopub/docs/0000000662/bc2149b6-c0d6-4f34-8a1c-e38e984a8701.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__112a03e8_7251_44ed_9f2c_31afeabd7ed1
BPVOP-907441-2017 | 4758391 | 9/12/2017 | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD_.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_.png | file://x:/photopub/docs/0000000662/2a28a4c6-f1ed-443c-a356-daf9c0e24c2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8eb3f64c_6739_405e_90c0_9783fe545e81
BPVOP-907464-2017 | 5034639 | 9/12/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV3.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV3.png | file://x:/photopub/docs/0000000662/dd1ed0c4-c3db-4d5a-8167-dcc95bef7a33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ac4ea05_bc0f_4d6a_a9c1_846f546138b4
BPVOP-907462-2017 | 4758606 | 9/12/2017 | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV.png | file://x:/photopub/docs/0000000662/b01ff302-9317-4666-a632-bfff936a43a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5b95026_0635_41bb_97b2_798f7483317c
BPVOP-907454-2017 | 4758592 | 9/12/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD3.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD3.png | file://x:/photopub/docs/0000000662/14cc82cd-6a24-4518-a4f4-2a0eab80ce78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8e59c7_6dd5_4761_ae00_77b6001a35bd
BPVOP-907451-2017 | 4758403 | 9/12/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD2.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD2.png | file://x:/photopub/docs/0000000662/e240f21a-01f7-494e-a4f4-909dd57c6515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__376cff17_ff38_4614_9ff6_c458bb628c1c
BPVOP-907446-2017 | 4758397 | 9/12/2017 | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #PRD1.png On assessment of a pressure vessel with a maximum working pressure of 87 psig, it was determined there was no evidence to support the last service or replacement of the pressure relief device. This creates risk to personnel and equipment. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD1.png | file://x:/photopub/docs/0000000662/cf25298c-af8e-49ed-83be-b8a9387af15f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f21669a_cbf1_4278_a742_0e78d7db37f3
ELIN-909320-2017 | EL-495628-2017 | 9/19/2017 2:00:51 PM | ASSESS: EL: Final | png | #asFound No slip joint | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | #Y.png No slip joint has been installed in 3" PVC service conduit. If settling occurs in the service conduit excessive strain could be placed on the conductors and the termination lugs in the meter base. This could cause the conductors to be pulled out of the lugs resulting in a shock and fire hazard. | 3 | Conductors, No expansion joint or not installed correctly. | Y.png | file://x:/photopub/docs/0000000665/f8545452-2867-4d6d-81c0-61878747a338.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f953216_0959_4ded_b4e7_692fd68609cb
GAIN-907209-2017 | GA-584594-2017 | 9/15/2017 11:29:55 AM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Straps-.png The as found condition is the gas piping system is supported with plastic "zap straps" instead of the required metallic supports. The as found hazard is in the event of a fire, unlike metal supports, plastic supports will deteriorate, allowing the piping system to dislodge and potentially be compromised, potentially leaking combustible gas into the structure. | 3 | Code prohibited practices or materials | Straps-.png | file://x:/photopub/docs/0000000663/6a0a39fe-abcf-4abd-b24f-b92609a92a51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9e56678_f1a8_4795_9075_a97d07bb80a3
ELOP-896815-2017 | 6591 | 9/8/2017 2:09:35 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png Ground wire from transformer is split bolt to the system grounding conductor. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | G4.png | file://x:/photopub/docs/0000000662/5b6d3d05-59a9-48f3-b762-e7af9837ab84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A250EB4_281D_4011_B7EE_5D61B4149427
ELOP-896815-2017 | 6591 | 9/8/2017 2:09:35 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png Ground wire from transformer is split bolt to the system grounding conductor. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | G3.png | file://x:/photopub/docs/0000000662/2133d202-7eb6-4fe5-bf8e-a437a2f3666b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A250EB4_281D_4011_B7EE_5D61B4149427
ELOP-896815-2017 | 6591 | 9/8/2017 2:09:35 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png Ground wire from transformer is split bolt to the system grounding conductor. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | G2.png | file://x:/photopub/docs/0000000662/96424120-aa1c-4890-9e09-f19492a25fa4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A250EB4_281D_4011_B7EE_5D61B4149427
ELOP-896815-2017 | 6591 | 9/8/2017 2:09:35 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #G1.png,G2.png,G3.png,G4.png Ground wire from transformer is split bolt to the system grounding conductor. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | G1.png | file://x:/photopub/docs/0000000662/a10408f5-2a1f-4b5f-a074-860cb1ec0139.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A250EB4_281D_4011_B7EE_5D61B4149427
ELIN-906333-2017 | EL-370229-2016 | 9/12/2017 | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Branch_circuits_not_protected_by_AFCI.png 15 amp, 120 volt branch circuit supplying general use receptacles not protected by an arc fault circuit interrupter. This is a thermal issue. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Branch_circuits_not_protected_by_AFCI.png | file://x:/photopub/docs/0000000663/e5ecd6bc-f882-487e-bb6f-069a0da73513.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cc8feca_0f89_4735_94db_10bc375e1244
AMOP-906311-2017 | AM-304424-2015 | 9/13/2017 10:41:29 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #Greenhouse_crossarm1.png,Greenhouse_crossarm2.png Greenhouse cross arms are being held clear of the inflatable' slide entrance by a single zap strap. If the zap strap were to fail, chance of crossarm swinging down and striking user. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Greenhouse_crossarm2.png | file://x:/photopub/docs/0000000662/e01a0052-4d74-4862-88bd-14a89acd3f95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ddbe709_681b_45ad_80be_6e1e970677fb
AMOP-906311-2017 | AM-304424-2015 | 9/13/2017 10:41:29 AM | ASSESS: AM OP: Periodic | png | #asFound | AM002 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | 3 | 3 | #Greenhouse_crossarm1.png,Greenhouse_crossarm2.png Greenhouse cross arms are being held clear of the inflatable' slide entrance by a single zap strap. If the zap strap were to fail, chance of crossarm swinging down and striking user. | 3 | Suspected Defects that: May not be reasonably detectable by maintenance/setup program Are likely to propagate | Greenhouse_crossarm1.png | file://x:/photopub/docs/0000000662/332e628a-9194-40c9-986c-5329a3384eb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ddbe709_681b_45ad_80be_6e1e970677fb
EDOP-596824-2016 | 2048783 | 9/13/2017 8:53:33 AM | ASSESS: ED OP: RAP | png | #asFound Electrical wiring exposed in machine room directly above hoisting machine. Also potential to fall on machine and into brakes | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Exposed_electrical_wires_above_machine.png Electrical wiring exposed in machine room directly above hoisting machine. Also potential to fall on machine and into brakes | 3 | Defects that are: Not detected by maintenance program Likely to progress | Exposed_electrical_wires_above_machine.png | file://x:/photopub/docs/0000000662/f4863656-ccaa-4264-a381-a69bec6e44cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__168C1844_55FF_4417_970F_36AEB919F7B4
ELHE-907477-2017 | HE-584933-2017 | 9/15/2017 9:04:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | #Park_service1.png,Park_service2.png The existing 400 amp 120/240 volt distribution system for a mobile home park has original poles completely rotted off at bases with stub post installed beside each with through bolts attaching them together. The poles are leaning and this can lead to an Equipment damage issue as well as shock and thermal hazards. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Park_service1.png | file://x:/photopub/docs/0000000663/e06aca32-9c0c-4365-b225-49f1c355bca3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b3579de_78f0_4f63_981f_52d0265d3c64
ELHE-907477-2017 | HE-584933-2017 | 9/15/2017 9:04:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | #Park_service1.png,Park_service2.png The existing 400 amp 120/240 volt distribution system for a mobile home park has original poles completely rotted off at bases with stub post installed beside each with through bolts attaching them together. The poles are leaning and this can lead to an Equipment damage issue as well as shock and thermal hazards. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Park_service2.png | file://x:/photopub/docs/0000000663/73029205-8fb9-46b1-b407-6226fd262950.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b3579de_78f0_4f63_981f_52d0265d3c64
PROP-909512-2017 | 2224163 | 9/14/2017 | ASSESS: PR OP: Incident | png | #asFound | PR017 | Defects found where the required strength may no longer exist. | 4 | 4 | #Corrosion_Mast_Base1.png,Corrosion_Mast_Base2.png,Corrosion_Mast_Base3.png Top drive station support mast. Corrosion to steel at base level deemed significant enough that structural integrity is questionable. | 4 | Defects found where the required strength may no longer exist. | Corrosion_Mast_Base3.png | file://x:/photopub/docs/0000000664/9fdd40f2-ae55-4ab6-b7ef-49dcc876e366.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e797f69_8cf4_4511_b557_b5f328f0aaa0
PROP-909512-2017 | 2224163 | 9/14/2017 | ASSESS: PR OP: Incident | png | #asFound | PR017 | Defects found where the required strength may no longer exist. | 4 | 4 | #Corrosion_Mast_Base1.png,Corrosion_Mast_Base2.png,Corrosion_Mast_Base3.png Top drive station support mast. Corrosion to steel at base level deemed significant enough that structural integrity is questionable. | 4 | Defects found where the required strength may no longer exist. | Corrosion_Mast_Base1.png | file://x:/photopub/docs/0000000664/5be3dd6e-8003-42e0-b1fa-23b8517a32c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e797f69_8cf4_4511_b557_b5f328f0aaa0
PROP-909512-2017 | 2224163 | 9/14/2017 | ASSESS: PR OP: Incident | png | #asFound Significant corrosion to mast base | PR017 | Defects found where the required strength may no longer exist. | 4 | 4 | #Corrosion_Mast_Base1.png,Corrosion_Mast_Base2.png,Corrosion_Mast_Base3.png Top drive station support mast. Corrosion to steel at base level deemed significant enough that structural integrity is questionable. | 4 | Defects found where the required strength may no longer exist. | Corrosion_Mast_Base2.png | file://x:/photopub/docs/0000000664/d5d3c2ec-54b2-45d5-9e0a-ffe4fd0e5cac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e797f69_8cf4_4511_b557_b5f328f0aaa0
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G2.png | file://x:/photopub/docs/0000000666/429aba4e-1664-4e91-b778-818df45faf8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G5.png | file://x:/photopub/docs/0000000666/34b51350-fe54-443a-8032-85224a43e532.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
ELIN-904605-2017 | EL-577894-2017 | 9/20/2017 3:24:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #G1.png,G2.png,G3.png,G4.png,G5.png,G6.png,G7.png Consumer service not grounded. This is a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | G4.png | file://x:/photopub/docs/0000000666/76e2356b-12a6-4682-9bbe-385198f6c23b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc13a22e_cc15_49f1_9755_071be5ba1ab6
GAIN-909051-2017 | GA-537261-2017 | 9/19/2017 10:01:27 AM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Gas_lines_entering_building_underground1.png,Gas_lines_entering_building_underground2.png,Gas_lines_entering_building_underground3.png Three underground polypropylene gas lines enter the parking structure of as new apartment complex underground. If the gas lines were to become damaged they would allow gas to enter the building underground possibly leading to a fire or explosion. | 3 | Underground piping entering a building below grade (unapproved) | Gas_lines_entering_building_underground1.png | file://x:/photopub/docs/0000000665/b5b7c153-2b94-4f75-b3ba-10d1d593e983.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d824402_56b1_46ae_840c_014285f99d15
GAIN-909051-2017 | GA-537261-2017 | 9/19/2017 10:01:27 AM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Gas_lines_entering_building_underground1.png,Gas_lines_entering_building_underground2.png,Gas_lines_entering_building_underground3.png Three underground polypropylene gas lines enter the parking structure of as new apartment complex underground. If the gas lines were to become damaged they would allow gas to enter the building underground possibly leading to a fire or explosion. | 3 | Underground piping entering a building below grade (unapproved) | Gas_lines_entering_building_underground3.png | file://x:/photopub/docs/0000000665/c635b85b-16ee-4299-bf3b-0273af61da3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d824402_56b1_46ae_840c_014285f99d15
GAIN-909051-2017 | GA-537261-2017 | 9/19/2017 10:01:27 AM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | #Gas_lines_entering_building_underground1.png,Gas_lines_entering_building_underground2.png,Gas_lines_entering_building_underground3.png Three underground polypropylene gas lines enter the parking structure of as new apartment complex underground. If the gas lines were to become damaged they would allow gas to enter the building underground possibly leading to a fire or explosion. | 3 | Underground piping entering a building below grade (unapproved) | Gas_lines_entering_building_underground2.png | file://x:/photopub/docs/0000000665/214fa5e8-b7ab-4c5d-83ef-bb62e58c6e8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d824402_56b1_46ae_840c_014285f99d15
ELIN-905375-2017 | EL-532852-2017 | 9/19/2017 1:34:31 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection1.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection2.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection3.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection4.png Termination of electrical conductors must be made up tight according to the manufactures torque specifications related to the equipment involved. Also termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a new house had a 100A 120/240V sub-panel feeder cable neutral conductor termination that was not installed properly and not tightened properly. The terminatio | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection2.png | file://x:/photopub/docs/0000000665/d52b3631-48cd-43b9-a893-29eac8b26558.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6342917_2201_4cdb_92a4_b321cdc71930
ELIN-905375-2017 | EL-532852-2017 | 9/19/2017 1:34:31 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection1.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection2.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection3.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection4.png Termination of electrical conductors must be made up tight according to the manufactures torque specifications related to the equipment involved. Also termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a new house had a 100A 120/240V sub-panel feeder cable neutral conductor termination that was not installed properly and not tightened properly. The terminatio | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection1.png | file://x:/photopub/docs/0000000665/1f2b0ece-1797-46ee-a2cc-deccabc903fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6342917_2201_4cdb_92a4_b321cdc71930
ELIN-907996-2017 | EL-582820-2017 | 9/15/2017 9:50:10 AM | ASSESS: EL: Service Connection | png | #asFound Grounding conductor terminated in the wrong location | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #grounding_conductor.png Grounding conductor has not been properly terminated at the neutral XO point, should a ground fault occur the electrical equipment and anyone standing nearby will not be at equal potential and will likely receive a shock | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | grounding_conductor.png | file://x:/photopub/docs/0000000663/871cff15-2357-4a86-b332-d9e056afa7bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdbbf61f_3486_4dbf_9c4d_061afd493094
GAIN-911066-2017 | GA-578455-2017 | 9/19/2017 2:08:10 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Regulator_inlet_fittings.png The pipe fittings used at the inlet to the propane pressure regulator are not approved for the potential pressures that could be achieved inside of the piping. This could lead to the failure of a fitting and the release of gas. | 3 | Non-compliant material/fittings installed | Regulator_inlet_fittings.png | file://x:/photopub/docs/0000000665/8f8cda8f-f666-4c7d-8056-1dadb98eaf48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a0fed8d_7d18_4b3f_96bb_fe9b3ca56235
ELIN-906045-2017 | EL-574194-2017 | 9/19/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Open_Panel.png Panel cover was left off of main panel. Live bus exposed to persons causing an exposure to possible shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_Panel.png | file://x:/photopub/docs/0000000666/940fb933-c205-4206-8304-50a4469b7e3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5ccf058_a0a9_4e44_97b8_e080c1d6d336
ELIN-905375-2017 | EL-532852-2017 | 9/19/2017 1:34:31 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection1.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection2.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection3.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection4.png Termination of electrical conductors must be made up tight according to the manufactures torque specifications related to the equipment involved. Also termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a new house had a 100A 120/240V sub-panel feeder cable neutral conductor termination that was not installed properly and not tightened properly. The terminatio | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection4.png | file://x:/photopub/docs/0000000665/fe817aa7-6bb2-4d94-abf7-fc6a5cc9b990.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6342917_2201_4cdb_92a4_b321cdc71930
ELIN-905375-2017 | EL-532852-2017 | 9/19/2017 1:34:31 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection1.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection2.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection3.png,Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection4.png Termination of electrical conductors must be made up tight according to the manufactures torque specifications related to the equipment involved. Also termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a new house had a 100A 120/240V sub-panel feeder cable neutral conductor termination that was not installed properly and not tightened properly. The terminatio | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Improper_neutral_lug_termination_for_sub-feeder_neutral_conductor_-_also_loose_connection3.png | file://x:/photopub/docs/0000000665/e1c48eee-fc98-48b4-a528-b6a9a75cc242.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6342917_2201_4cdb_92a4_b321cdc71930
EDMA-912713-2017 | ED-267695-2015 | 9/20/2017 11:12:27 AM | ASSESS: ED MA: Acceptance | png | #asFound | ED029 | Defect that is: • undetectable by maintenance program • Likely to progress | 3 | 3 | #Fire_panel.png The elevator system has not been tested or verified after the major modernization. There has been no confirmation how the elevator would respond in a fire situation. This may place occupants of the building in harms way and also the first responders. | 3 | Defect that is: • undetectable by maintenance program • Likely to progress | Fire_panel.png | file://x:/photopub/docs/0000000666/08e99291-cbd3-491d-a897-aba37ce70d25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bb38772_fb93_4523_b1b4_78979e006ca9
EDMA-912716-2017 | ED-267680-2015 | 9/20/2017 11:25:43 AM | ASSESS: ED MA: Acceptance | png | #asFound | ED029 | Defect that is: • undetectable by maintenance program • Likely to progress | 3 | 3 | #Fire_panel_.png The elevator system has not been tested or verified after the major modernization. There has been no confirmation how the elevator would respond in a fire situation. This may place occupants of the building in harms way and also the first responders. | 3 | Defect that is: • undetectable by maintenance program • Likely to progress | Fire_panel_.png | file://x:/photopub/docs/0000000666/12e47eb9-9f57-446d-b397-be874bd72b09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91560f16_e298_4694_9c02_a862a0123cb6
EDMA-912996-2017 | 5432228 | 9/20/2017 12:09:58 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED029 | Defect that is: • undetectable by maintenance program • Likely to progress | 3 | 3 | #Fire_panel.png Firefighters emergency operation and emergency power has not been tested since the major modernization upgrades. The elevator may not respond in an emergency situation. This may place building occupants and also first responders in harms way. | 3 | Defect that is: • undetectable by maintenance program • Likely to progress | Fire_panel.png | file://x:/photopub/docs/0000000666/6eeb81c2-3093-4b8c-801a-aa96ba108ea3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6deac3a5_a5fa_4562_8e1d_1f5f35cc5149
ELIN-911170-2017 | EL-583776-2017 | 9/20/2017 8:35:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Main_Panel.png In the 200 amp 120/240 volt electrical panel, unused opening in the panel cover have not been filled or effectively covered/guarded to prevent persons from contacting the components inside the panel that will be energized. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_Panel.png | file://x:/photopub/docs/0000000666/d9e6bcf4-28c2-4fec-9a3c-fe35dafffe66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__035119c5_4e59_44e2_960f_6c5c0aef9c37
ELOP-904894-2017 | 2168170 | 9/14/2017 4:31:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Aquila_cedar1.png,Aquila_cedar2.png,Aquila_cedar3.png,Aquila_cedar4.png | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Aquila_cedar1.png | file://x:/photopub/docs/0000000663/1cc5d45f-a3bc-4eeb-a24d-f9c056d8e0df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3c2a86c_a9ea_404d_ba20_b65060fe6ca1
ELOP-904894-2017 | 2168170 | 9/14/2017 4:31:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Aquila_cedar1.png,Aquila_cedar2.png,Aquila_cedar3.png,Aquila_cedar4.png | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Aquila_cedar2.png | file://x:/photopub/docs/0000000663/5d8fe164-fd96-4f48-91c0-7801f1782dac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3c2a86c_a9ea_404d_ba20_b65060fe6ca1
ELOP-904894-2017 | 2168170 | 9/14/2017 4:31:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Aquila_cedar1.png,Aquila_cedar2.png,Aquila_cedar3.png,Aquila_cedar4.png | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Aquila_cedar3.png | file://x:/photopub/docs/0000000663/279924bb-6ea9-4dad-a608-96bd53175d42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3c2a86c_a9ea_404d_ba20_b65060fe6ca1
ELOP-904894-2017 | 2168170 | 9/14/2017 4:31:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Aquila_cedar1.png,Aquila_cedar2.png,Aquila_cedar3.png,Aquila_cedar4.png | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Aquila_cedar4.png | file://x:/photopub/docs/0000000663/e106a52c-9b41-4140-bff4-49864ddc00cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3c2a86c_a9ea_404d_ba20_b65060fe6ca1
EDMA-912956-2017 | 5432230 | 9/20/2017 12:25:46 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Fire_panel_.png Firefighters emergency operation and emergency power has not been tested since the major modernization upgrades. The elevator may not respond in an emergency situation. This may place building occupants and also first responders in harms way. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Fire_panel_.png | file://x:/photopub/docs/0000000666/fbeee501-f585-475e-a89d-f1fe2068a8bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82326497_9cbf_4c54_9c9f_5e4159b9bac9
BPVOP-909788-2017 | 2284136 | 9/15/2017 2:00:00 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Air_Receiver_BCSA_decal.png Owners have not yet complied with safety order SO-B6 0505303 that requires all machine mounted air receivers undergo NDE thickness testing to ensure that internal metal thickness are still greater than minimum allowed to retain the pressure. Worst possible consequences, catastrophic vessel failure. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Air_Receiver_BCSA_decal.png | file://x:/photopub/docs/0000000664/90f41bb5-e83d-448b-9035-6757cbee40f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0908dc25_2600_4638_8b93_b4d94bce3f5b
GAIN-896867-2017 | GA-529408-2017 | 9/19/2017 8:28:19 PM | ASSESS: GA: Final | png | #asFound Direct fired make-up air unit on sloped roof. There is no access to roof. No platform for service or filter change,and no guard rail for service people to safely work. | GA146 | Appliance installed in a hazardous location, where a hazardous material is present | 4 | 4 | #Nelson_Rod_and_Gun_Bldg1.png,Nelson_Rod_and_Gun_Bldg2.png Direct Fired Make-Up Air installed on building with sloping roof. There is no service platform on service side of unit ,no guard rail installed for protection of service people. There is also no access or ladder to get up to the roof. Should this unit shut down a service person could risk injury or death from falling off roof | 4 | Appliance installed in a hazardous location, where a hazardous material is present | Nelson_Rod_and_Gun_Bldg1.png | file://x:/photopub/docs/0000000665/2370d37d-cb8b-4fb2-afc8-2d2ad650e4b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__addb54ce_287b_4437_b338_5bacf898c435
GAIN-896867-2017 | GA-529408-2017 | 9/19/2017 8:28:19 PM | ASSESS: GA: Final | png | #asFound Unit over 13 feet above grade. No Ladder to access roof. No service platform in place and no guard rail for safety of service person. | GA146 | Appliance installed in a hazardous location, where a hazardous material is present | 4 | 4 | #Nelson_Rod_and_Gun_Bldg1.png,Nelson_Rod_and_Gun_Bldg2.png Direct Fired Make-Up Air installed on building with sloping roof. There is no service platform on service side of unit ,no guard rail installed for protection of service people. There is also no access or ladder to get up to the roof. Should this unit shut down a service person could risk injury or death from falling off roof | 4 | Appliance installed in a hazardous location, where a hazardous material is present | Nelson_Rod_and_Gun_Bldg2.png | file://x:/photopub/docs/0000000665/30dd35ae-4bb9-41fc-bd77-bae81b84ed4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__addb54ce_287b_4437_b338_5bacf898c435
EDRI-912160-2017 | ED-542231-2017 | 9/19/2017 8:26:48 PM | ASSESS: ED RI: Extension | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Ramp_construction.png Access ramp incomplete and under construction when arriving at landing. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Ramp_construction.png | file://x:/photopub/docs/0000000666/785bd95a-ad02-4bfb-85f7-a4df506611f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa56ae69_e9af_44c6_b065_47cdd54ac708
EDIN-913543-2017 | ED-509364-2017 | 9/20/2017 9:55:43 PM | ASSESS: ED IN: Acceptance | png | #asFound Lighting in machine space | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #Switch.png The lighting control switch is located at the top of the hoistway instead near a access point to the working platform. This poses a high rick of falling since the operator has to operate the car without any lighting until they reach the top of the hoistway to turn on the light located at the top of the hoistway. The lighting at the top of the hoistway is also inadequate which may cause the operator to trip and fall from the top of the elevator car. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Switch.png | file://x:/photopub/docs/0000000666/d6345105-cbef-4594-a828-129d6bb6b703.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a1f29e6_85de_495c_b3f6_a39f5d1d0c16
ELIN-912408-2017 | EL-448758-2016 | 9/20/2017 11:15:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #No_box_for_termination_of_light.png In a new single family dwelling a 15 amp 120 volt exterior light was found to be terminated without the use of a box. This could result in a thermal effect condition. Picture attached. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | No_box_for_termination_of_light.png | file://x:/photopub/docs/0000000666/9ae4f542-6b4e-4fe1-83ff-a18973845a6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05500b56_ff8f_451b_9aac_93c62528bc8c
ELIN-905920-2017 | EL-572930-2017 | 9/18/2017 12:22:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Rafter_wiring.png In an existing single family dwelling, a new garage and shop addition has 15 and 20amp 120volt branch circuit feeders running across the attic without mechanical protection in place. This could lead to a "Shock" hazard. Pic attached | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Rafter_wiring.png | file://x:/photopub/docs/0000000664/3c2668a4-d62a-4bcb-902c-7eeedc1fa91e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a71c5922_8d3e_4ea4_b073_6df891198327
ELIN-911794-2017 | EL-585434-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #As-found1.png,As-found2.png,As-found3.png,As-found4.png Service cable weather head sealing is configured such that water ingress is occurring creating potential shock and electrical explosion hazards. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | As-found4.png | file://x:/photopub/docs/0000000665/415734b5-3d88-4316-848b-f93e9fe765be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99bb6929_8aa8_467c_a437_2612194d8a03
ELIN-911794-2017 | EL-585434-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #As-found1.png,As-found2.png,As-found3.png,As-found4.png Service cable weather head sealing is configured such that water ingress is occurring creating potential shock and electrical explosion hazards. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | As-found2.png | file://x:/photopub/docs/0000000665/049cab34-5d48-41fc-8726-4885b24e1db5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99bb6929_8aa8_467c_a437_2612194d8a03
ELIN-911794-2017 | EL-585434-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #As-found1.png,As-found2.png,As-found3.png,As-found4.png Service cable weather head sealing is configured such that water ingress is occurring creating potential shock and electrical explosion hazards. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | As-found1.png | file://x:/photopub/docs/0000000665/b1991bc4-45fb-4221-bb56-6457c0318126.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99bb6929_8aa8_467c_a437_2612194d8a03
ELIN-906703-2017 | EL-509993-2017 | 9/15/2017 12:45:39 PM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | #Spliced_service_conductors.png Spliced service conductors can fail and create dangerous under and over voltage conditions leading to equipment failure and potential fire hazards | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Spliced_service_conductors.png | file://x:/photopub/docs/0000000665/dced829e-5a67-4ef9-b357-2c16e9bd87a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28f7f6a1_7587_47a8_ace6_15a7cd5ee1e5
ELIN-910104-2017 | EL-553581-2017 | 9/19/2017 12:38:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Line_side_safety_switch_wiring_results_in_overcrowding.png Overcrowding of a cabinets internal space may result in strain on terminations and overheating of conductors and terminal parts | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Line_side_safety_switch_wiring_results_in_overcrowding.png | file://x:/photopub/docs/0000000665/b7da79ac-0eae-4e89-9024-0ccae2a65c63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9026dd46_c67d_420a_badc_b1e020ac7d4b
ELIN-910921-2017 | EL-578401-2017 | 9/20/2017 5:41:23 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #T1.png,T2.png,T3.png PLTC cables have been installed in a concealed location inside a dwelling. This is a fire hazard as this type of conductors are not suitable for the conditions in which they were installed. | 3 | Conductors Equipment is not approved for the specific use. | T2.png | file://x:/photopub/docs/0000000666/c8992e5d-ab72-418c-b4f6-fdd8951dcfe6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04f695e3_24cd_4537_9611_ec49e0e7f568
ELIN-909344-2017 | EL-578122-2017 | 9/19/2017 7:33:00 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #D1.png,D2.png,D3.png Conductors are concealed inside a dwelling. These types of conductors are not suitable for this particular location and condition of use. This is a fire hazard to individuals inside the dwelling. | 3 | Conductors Equipment is not approved for the specific use. | D1.png | file://x:/photopub/docs/0000000666/0597edde-942e-472f-8b74-773f8f483cf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeee0e48_46fc_4729_bbb8_6a4465e7638e
ELIN-909344-2017 | EL-578122-2017 | 9/19/2017 7:33:00 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #D1.png,D2.png,D3.png Conductors are concealed inside a dwelling. These types of conductors are not suitable for this particular location and condition of use. This is a fire hazard to individuals inside the dwelling. | 3 | Conductors Equipment is not approved for the specific use. | D2.png | file://x:/photopub/docs/0000000666/144ec4b6-57c6-4a9f-9c39-c9f4f4f25004.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeee0e48_46fc_4729_bbb8_6a4465e7638e
ELIN-910921-2017 | EL-578401-2017 | 9/20/2017 5:41:23 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #T1.png,T2.png,T3.png PLTC cables have been installed in a concealed location inside a dwelling. This is a fire hazard as this type of conductors are not suitable for the conditions in which they were installed. | 3 | Conductors Equipment is not approved for the specific use. | T1.png | file://x:/photopub/docs/0000000666/48ddf0bb-d513-492a-8b4e-764f8ce16e21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04f695e3_24cd_4537_9611_ec49e0e7f568
ELIN-910921-2017 | EL-578401-2017 | 9/20/2017 5:41:23 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #T1.png,T2.png,T3.png PLTC cables have been installed in a concealed location inside a dwelling. This is a fire hazard as this type of conductors are not suitable for the conditions in which they were installed. | 3 | Conductors Equipment is not approved for the specific use. | T3.png | file://x:/photopub/docs/0000000666/f05b124b-63a3-4a53-a0b9-590d62a32141.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04f695e3_24cd_4537_9611_ec49e0e7f568
ELIN-909344-2017 | EL-578122-2017 | 9/19/2017 7:33:00 AM | ASSESS: EL: Final | png | #asFound Conductors used inside dwelling | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #D1.png,D2.png,D3.png Conductors are concealed inside a dwelling. These types of conductors are not suitable for this particular location and condition of use. This is a fire hazard to individuals inside the dwelling. | 3 | Conductors Equipment is not approved for the specific use. | D3.png | file://x:/photopub/docs/0000000666/7e856683-6659-4f10-aab6-f4c21b6dc951.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeee0e48_46fc_4729_bbb8_6a4465e7638e
ELIN-904981-2017 | EL-580267-2017 | 9/19/2017 | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base1.png,PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base2.png,PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base3.png When terminating PVC conduits and fittings into electrical equipment threaded male PVC terminal adapters are not permitted to be installed into threaded metal conduit entries in metal enclosures. This is not permitted because PVC conduit and fittings can expand and contract at different rates than metal fittings on enclosures. This can cause PVC fittings to break if they expand to much or cause loose connections between fittings and enclosures if the PVC contracts which can cause issues with water entering enclosures and equipment located outdoors. This installation for a service upgrade for an existing house has a new 2" PVC service conduit installed into the top of a new meter base installed on a pole outdoors. The PVC conduit has a PVC male terminal adapter that is threaded into a female metal hu | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_terminal_adapter_threaded_into_metal_hub_on_top_of_meter_base3.png | file://x:/photopub/docs/0000000666/70f378ca-6a88-4e2e-a932-022e7df8bbe2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fb2de0a_311b_4508_8f64_762ed07af0ae
ELIN-911944-2017 | EL-531722-2017 | 9/18/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent2.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent3.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent4.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent5.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent6.png,Exterior_100A_switch_installed_to_close_to_gas_relief_vent7.png Arc producing electrical equipment is required to be installed with a minimum clearance of 1M from a natural gas relief vent or device. This is required to prevent combustible gas from being ignited by electrical arcs in the event that there is a gas discharge and a simultaneous electrical arc from electrical equipment installed in close proximity. This installation at a new house has an exterior 100A 120/240V switch installed within 1M of the gas relief vent. This is a fire hazard if the refrig vent discharges gas and it is ignited by an electrical arc from the switch | 3 | General Equipment is not approved for the specific use | Exterior_100A_switch_installed_to_close_to_gas_relief_vent1.png | file://x:/photopub/docs/0000000666/393861ad-98e9-42eb-94b4-c20feb7727f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab4dfe1f_557a_4803_98e0_bcdfa201cada
GAIN-908334-2017 | GA-585169-2017 | 9/26/2017 8:45:39 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Rooftop_piping-.png Rooftop piping runs exceeding 100 feet are installed without expansion loops. This may lead to overstressed joints due to linear expansion and contraction and possible damage to the gas line. | 2 | Physical protection of piping and tubing absent. | Rooftop_piping-.png | file://x:/photopub/docs/0000000669/c23d80e0-e1db-45e0-ba8e-6ad1b021f74d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52ff3e6d_0078_4d98_8204_f0c53f399625
GAIN-909703-2017 | GA-533252-2017 | 9/26/2017 2:25:13 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_termination_4.png Appliance air intake and vent termination are too close to each other. This may allow the flue products to enter the air intake and lead to incomplete combustion and the production of carbon monoxide. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination_4.png | file://x:/photopub/docs/0000000669/d5f21f0c-14c0-4703-b5c2-a5c58be640bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f36daba1_8ae6_4547_938d_9fc5093be764
EDMA-914516-2017 | ED-492251-2017 | 9/21/2017 4:41:31 PM | ASSESS: ED MA: Acceptance | png | #asFound Security keypad | ED031 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | 4 | 4 | #Security_Keypad.png Phase 2 firefighters emergency operation does not override in car security which is preventing the elevator to travel to all floors that the elevator services | 4 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | Security_Keypad.png | file://x:/photopub/docs/0000000667/17b04bac-00ae-4afa-a7ce-a9bcf331be24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a64e43e9_d113_4584_bdc5_c84e8ee6e8be
EDMA-914515-2017 | ED-492243-2017 | 9/21/2017 4:22:57 PM | ASSESS: ED MA: Acceptance | png | #asFound In-car security device | ED031 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | 4 | 4 | #Security.png Phase 2 firefighters emergency operation does not override in car security which is preventing the elevator to travel to all floors that the elevator services | 4 | Emergency controls/circuits installed incorrectly bypassed or failed . Other system in place that will take over. Risk Reg ED-02 | Security.png | file://x:/photopub/docs/0000000667/c830023f-3bda-4ce1-b72f-ea7a80fceb09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fff038e3_2f87_4aee_bf58_8b76567d03f2
GAIN-913450-2017 | GA-449410-2016 | 9/21/2017 11:21:43 AM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | #Boiler.png Liquid fertilizer mixing tanks are installed next the a boiler burner air intake. The fumes from the fertilizer could cause corrosion of the burner and flue passages in the boiler. This could lead to improper combustion and the production of carbon monoxide. | 2 | Appliance installed in a proposed hazardous location | Boiler.png | file://x:/photopub/docs/0000000666/228fb4a9-14f4-487a-b5a4-15c60eb59554.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c97c6ab5_d91d_4c31_b3d0_e110b47c71ba
GAIN-910307-2017 | GA-534415-2017 | 9/21/2017 11:02:29 AM | ASSESS: GA: Final | png | #asFound Relief regulators too close to rooftop mechanical air intake. | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Relief_regulators.png Gas regulators with internal relief devices installed too close to a mechanical air intake to a building. If the regulators were to relieve gas, the gas may be drawn into the building by the mechanical air intake fan. This could lead to a possible fire or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Relief_regulators.png | file://x:/photopub/docs/0000000666/208f36e8-295b-4818-a1aa-5cc0458dcd95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df7aca3b_6e86_43d5_95c2_ff458fa20edf
ELIN-912421-2017 | EL-499789-2017 | 9/27/2017 8:13:22 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Not_GFCI_protected.png Receptacles located within 1.5 meters of sink are not GFCI protected. GFCI are installed to protect people from electrical shock due to monitoring the current that is coming back on the neutral. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Not_GFCI_protected.png | file://x:/photopub/docs/0000000669/07edd559-c144-495c-9013-93fec27b1183.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__564dc4e6_e987_4874_a8b7_704fdd76b75a
GAHE-918724-2017 | HE-591183-2017 | 9/27/2017 2:12:38 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Range | GA137 | Clearance to combustible not met | 3 | 3 | #Kenmore_range.png At time of inspection range was too close to combustible material , this condition could cause a kitchen fire. | 3 | Clearance to combustible not met | Kenmore_range.png | file://x:/photopub/docs/0000000670/eec846a0-eb1c-4e63-9f36-ee8d39d6cc8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22058be7_8f6b_42ba_a6d2_4be9086bd40e
BPVOP-918130-2017 | 4885643 | 9/20/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Nameplate_verification_of_vessels_age.png All machine mounted air receivers that exceed 20 years of age must undergo nondestructive examination | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Nameplate_verification_of_vessels_age.png | file://x:/photopub/docs/0000000670/8e3c213b-ac29-4737-8d52-eef58fa7b349.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eae71a9_db5d_4c9d_8141_da0b3967074a
BPVOP-917464-2017 | 4885642 | 9/18/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Nameplate_verification_of_vessel_age.png Safety order requires that non-destructive examination be done and include Magnetic Particle and Ultrasonic thicknesses. This air receiver could have local thin spots, that could fail. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Nameplate_verification_of_vessel_age.png | file://x:/photopub/docs/0000000670/e3d44032-534f-486d-8e07-2938a7034e05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c061810_638a_419b_8bea_76497683efe9
BPVOP-917451-2017 | 4885638 | 9/20/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Air_Compressor_and_Receiver.png Air receivers may suffer internal corrosion that may corrode metal thicknesses to the point of failure, possibility of catastrophic failure could happen. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Air_Compressor_and_Receiver.png | file://x:/photopub/docs/0000000670/a58207e2-a806-4788-8bee-7cfe68398707.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b99f48d_1454_4c13_a106_9763edc25091
ELIN-914260-2017 | EL-535686-2017 | 9/26/2017 9:52:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #T_an_B_crimper__ideal_crimps_do_not_go_together.png A residence with a 125 amp 240 volt service is undergoing rewiring. The bonding conductors which ensure safe operation of the system were connected in all locations using an assortment of unapproved compression lugs and tool combinations. This can lead to loose connections that can prevent overcurrent protection from operating. Property damage or injury to persons can occur | 3 | Continuity Bonding; method for equipment is not adequate. | T_an_B_crimper__ideal_crimps_do_not_go_together.png | file://x:/photopub/docs/0000000669/281a897f-170c-414f-bf0a-dca941aa84e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8582c99_9a20_40cd_9f05_1cd0b2f73787
GAIN-907507-2017 | GA-577912-2017 | 9/26/2017 7:46:13 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Vent_connector.png The as-found condition is that a vent system serving a boiler is constructed of galvanized steel that is of a thinner gauge than permitted by code. The potential hazard is that the thin-walled material of the vent will warp and corrode over time, causing flue gas spillage into an occupied space where people could be exposed to harmful emissions such as carbon monoxide. | 3 | Unapproved venting material | Vent_connector.png | file://x:/photopub/docs/0000000669/e70a06b4-4050-478b-8183-da464c5f49d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94e86756_94b4_4331_a8ad_5c6be110e2ae
BPVIN-910637-2017 | BPV-504676-2017 | 9/18/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_emergency_shutdown_switch_at_boiler_room_door.png Upon assessment of Hot Water Boilers with combined Heating Surface (HS) of 5.4 square meters, Maximum Allowable Working Pressure (MAWP) of 125psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_emergency_shutdown_switch_at_boiler_room_door.png | file://x:/photopub/docs/0000000667/76e68ce6-a4e7-43d3-9b7a-a78700a0fbaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9106ceda_47ed_41bf_8d7b_b66cee4f9042
ELIN-907588-2017 | EL-584995-2017 | 9/27/2017 11:00:07 AM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | #Breaker_size.png At an existing single family dwelling modular home, a 100amp 120/240volt service was found with the over-current protection set at 125amps. This can lead to a "Thermal Effect" condition. Pic attached. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Breaker_size.png | file://x:/photopub/docs/0000000670/dd29b690-fd90-4bf8-b3e7-bda318966711.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8e8e38e_415b_4aa3_b0aa_766d39b8a9d3
BPVOP-915023-2017 | BPV-0000504970-2017 | 9/22/2017 | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 3 | #Crack_in_weld.png Upon assessment of hot water heating boiler with Maximum Allowable Working Pressure (MAWP) of 100psig and Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit, it is determined that water weeps through minor crack in weld in tubesheet. Crack in weld may propagate and lead to major leakage of boiler water resulting in complete shutdown of boiler, costly repair if crack is not repaired as per code before any further operation. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Crack_in_weld.png | file://x:/photopub/docs/0000000667/3a01e827-ea08-46c2-91d2-5bb3ef925797.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04e82e2b_0154_4399_b61a_9ff72b1002ce
ELIN-889597-2017 | EL-570008-2017 | 9/26/2017 11:00:09 AM | ASSESS: EL: Service Connection | png | #asFound Service grounding plate electrode in earth has #6 AWG copper conductor installed but where copper #6 enters earth to connect to plate electrode the #6 copper is cut off below grade. The service grounding plate electrode is not connected to service by a continuous run of #6 copper grounding conductor to ground service properly. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded1.png,Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded2.png,Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded3.png Found 120/240 volt 90 amp temporary construction service grounding plate electrode in earth has #6 AWG copper conductor installed to connect to plate electrode but the #6 copper is damaged and is cut off below grade. The service grounding plate electrode is not connected to service by a continuous run of #6 copper grounding conductor to ground service properly to plate electrode. When service is not grounded properly the system is a possible electrical shock hazard to people | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded2.png | file://x:/photopub/docs/0000000669/1e1cbd18-3922-4f9d-bb61-e322f0b9897e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7194961_b620_4830_8132_32b1e3eeb374
ELIN-914043-2017 | UW-588446-2017 | 9/21/2017 12:50:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Load_centres1.png,Load_centres2.png,Load_centres3.png While performing a Final Assessment on a contractor permit, I noted that work had been performed beyond the scope of the permit. When asked, the homeowner admitted to doing the work and said he was not sure that had required a permit and failed to inquire. The homeowner had installed two used distribution panels which were both rated for dry locations. Both were installed outdoors on wooden pedestals with garbage bags over top for weatherproofing. Both panels had several unfilled openings. Both these panels were at risk of having rain/snow, rodents or small items enter into their energized interiors creating a potential shock hazard. | 3 | General Equipment is not approved for the specific use | Load_centres3.png | file://x:/photopub/docs/0000000666/70a806dc-a9df-47aa-a5b5-39d4864c4707.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9a7108_efb5_4ce3_80b6_367054a794ae
ELIN-914043-2017 | UW-588446-2017 | 9/21/2017 12:50:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Load_centres1.png,Load_centres2.png,Load_centres3.png While performing a Final Assessment on a contractor permit, I noted that work had been performed beyond the scope of the permit. When asked, the homeowner admitted to doing the work and said he was not sure that had required a permit and failed to inquire. The homeowner had installed two used distribution panels which were both rated for dry locations. Both were installed outdoors on wooden pedestals with garbage bags over top for weatherproofing. Both panels had several unfilled openings. Both these panels were at risk of having rain/snow, rodents or small items enter into their energized interiors creating a potential shock hazard. | 3 | General Equipment is not approved for the specific use | Load_centres1.png | file://x:/photopub/docs/0000000666/6e89157f-a3ae-4e2a-b5c1-99f02d921715.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9a7108_efb5_4ce3_80b6_367054a794ae
ELIN-914043-2017 | UW-588446-2017 | 9/21/2017 12:50:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #Load_centres1.png,Load_centres2.png,Load_centres3.png While performing a Final Assessment on a contractor permit, I noted that work had been performed beyond the scope of the permit. When asked, the homeowner admitted to doing the work and said he was not sure that had required a permit and failed to inquire. The homeowner had installed two used distribution panels which were both rated for dry locations. Both were installed outdoors on wooden pedestals with garbage bags over top for weatherproofing. Both panels had several unfilled openings. Both these panels were at risk of having rain/snow, rodents or small items enter into their energized interiors creating a potential shock hazard. | 3 | General Equipment is not approved for the specific use | Load_centres2.png | file://x:/photopub/docs/0000000666/8ef16bcc-4404-4615-b0f1-7ad6996d51ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9a7108_efb5_4ce3_80b6_367054a794ae
GAIN-910600-2017 | GA-511919-2017 | 9/22/2017 1:09:19 PM | ASSESS: GA: Rough-In | png | #asFound No cap on line | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open_gas_line.png Found open gas line without certified individual on site, line was being supervised by other individuals. If someone was to hit the gas line, there would be a gas leak which could lead to damage, injury or explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000667/a153ab50-73b2-4426-96fd-0b24a707e265.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e1d951b_605d_4073_ad45_a4db51be7dff
GAIN-889244-2017 | GA-525820-2017 | 9/21/2017 11:53:14 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Relief_too_close_to_air_intake.png Relief vent from a regulator is installed too close to a Mechanical air inlet of an appliance. In an over pressure scenario the relief will relief the pressure and the Mechanical air will suck gas into the building through the appliance, possibly causing an explosion inside the building | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Relief_too_close_to_air_intake.png | file://x:/photopub/docs/0000000666/ad1b80a3-4cbf-485a-bf59-bd8a9eef9b31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cba562b1_ff68_4b2a_adb9_11f01e33fbfc
EDIN-918207-2017 | ED-406439-2016 | 9/26/2017 9:06:13 PM | ASSESS: ED IN: Acceptance | png | #asFound The lighting levels are not adequate and therefore the public will not the able to see tripping and falling hazards | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | #Lighting_1.png Lack a adequate lighting levels will cause the public to become injured due to trips and fall hazards | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Lighting_1.png | file://x:/photopub/docs/0000000669/0bc695cc-fd00-43cd-8fe7-f8e516879d11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dba6aed2_76ee_4a2b_ac7a_f39d118374db
EDIN-918208-2017 | ED-406437-2016 | 9/26/2017 9:23:59 PM | ASSESS: ED IN: Acceptance | png | #asFound Lighting level at landing sills | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | #Landing_lights.png Inadequate lighting levels will cause the public to trip and fall. The public will be unable to see tripping and fall hazards | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Landing_lights.png | file://x:/photopub/docs/0000000669/473c6110-c65d-438a-839d-3ab08db19367.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2258332a_3716_4437_97c9_6129c643315b
EDIN-916278-2017 | ED-511058-2017 | 9/22/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Unsafe_access_for_wheelchair1.png,Unsafe_access_for_wheelchair2.png,Unsafe_access_for_wheelchair3.png With hall door closed and elevator door open, a wheelchair would be stuck and only able to get back in elevator. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Unsafe_access_for_wheelchair3.png | file://x:/photopub/docs/0000000668/d256151d-52df-4303-928e-0de5c53d7460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a4a10f_c0d2_4317_9e32_9d2fce05de37
EDIN-916278-2017 | ED-511058-2017 | 9/22/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Unsafe_access_for_wheelchair1.png,Unsafe_access_for_wheelchair2.png,Unsafe_access_for_wheelchair3.png With hall door closed and elevator door open, a wheelchair would be stuck and only able to get back in elevator. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Unsafe_access_for_wheelchair2.png | file://x:/photopub/docs/0000000668/64f97cb4-c62d-48a2-9b82-07ce809a9728.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a4a10f_c0d2_4317_9e32_9d2fce05de37
EDIN-916278-2017 | ED-511058-2017 | 9/22/2017 | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Unsafe_access_for_wheelchair1.png,Unsafe_access_for_wheelchair2.png,Unsafe_access_for_wheelchair3.png With hall door closed and elevator door open, a wheelchair would be stuck and only able to get back in elevator. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Unsafe_access_for_wheelchair1.png | file://x:/photopub/docs/0000000668/d2c10fd9-6e94-4d47-add6-46603c9c63da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a4a10f_c0d2_4317_9e32_9d2fce05de37
GAIN-865087-2017 | GA-547576-2017 | 9/25/2017 10:41:11 AM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Open_gas_line.png Gas Valve connected to live gas system does not have a plug or cap on other side of valve. Valve is in shut off position however could easily get bumped or turned on causing a steady flow of propane into residence. This could possibly cause a fire or an explosion | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000668/790e791f-72e7-455f-a487-f3304025b6a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c17d8c66_907a_4969_9bf4_f6802a33a6ea
GAIN-894466-2017 | GA-564897-2017 | 9/25/2017 11:14:26 AM | ASSESS: GA: Final | png | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #Cylinder_inside_storage_shed.png,Relief_inside_storage_shed.png Dual stage propane regulator installed inside tool storage shed. The relief from the regulator should be piped outside. If the relief from Pressure regulator was to relief pressure the storage shed would become filled with propane gas possible causing an explosion or fire | 5 | Relief style regulator/device allowed to vent within building/confined space | Relief_inside_storage_shed.png | file://x:/photopub/docs/0000000668/a72f1a89-c37f-4354-98b8-6a420668054d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57650a2f_dd9c_4916_983a_0091b4b23e5d
BPVIN-916240-2017 | BPV-565165-2017 | 9/25/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler_Nameplate.png Boiler can be shutdown by local panel switch, operators need to get in close proximity to be able to shutdown the unit. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_Nameplate.png | file://x:/photopub/docs/0000000669/8d3fbea3-3359-4698-912c-4df4a89f0bdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d35164e3_5d95_4552_b363_6bbfb8162001
ELIN-889597-2017 | EL-570008-2017 | 9/26/2017 11:00:09 AM | ASSESS: EL: Service Connection | png | #asFound Service grounding plate electrode in earth has #6 AWG copper conductor installed but where copper #6 enters earth to connect to plate electrode the #6 copper is cut off below grade. The service grounding plate electrode is not connected to service by a continuous run of #6 copper grounding conductor to ground service properly. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded1.png,Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded2.png,Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded3.png Found 120/240 volt 90 amp temporary construction service grounding plate electrode in earth has #6 AWG copper conductor installed to connect to plate electrode but the #6 copper is damaged and is cut off below grade. The service grounding plate electrode is not connected to service by a continuous run of #6 copper grounding conductor to ground service properly to plate electrode. When service is not grounded properly the system is a possible electrical shock hazard to people | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded3.png | file://x:/photopub/docs/0000000669/72640e35-eafd-432f-86e4-45cd7705c554.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7194961_b620_4830_8132_32b1e3eeb374
ELHE-914860-2017 | HE-550928-2017 | 9/22/2017 10:34:24 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound Photo of meter base and the revenue meter. The meter seal has been the cut and removed. This is a three phase meter in a single phase meter base. | EL198 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | #Meter.png Hazard elimination to existing single family dwelling. The BC Hydro revenue meter to this dwelling has been removed and a three phase metre, that BC Hydro security reports as stolen, has replaced it. This is not the correct meter for this system. Shock and fire could result from attempts to instal or remove this meter under load. BC Hydro will disconnect the premises at the street. | 3 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Meter.png | file://x:/photopub/docs/0000000667/2633b7fb-a23e-42f2-b192-e19b4e854ec4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d201b7eb_fa08_41d3_9afc_673947a4b099
ELIN-914998-2017 | EL-588432-2017 | 9/25/2017 2:28:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #Enclosed_mast.png This assessment found that without over current protection on the consumer's service conductors, there is a risk of over heating. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Enclosed_mast.png | file://x:/photopub/docs/0000000668/9317db03-f632-4648-9049-9849fb7ae6bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4acff8e0_19f1_416a_9d46_3dbaa420f5ce
ELIN-907406-2017 | EL-562885-2017 | 9/22/2017 1:24:41 PM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Pic_6.png Solar photovoltaic systems combiner box is not certified for use in Canada. The disconnecting means is not accessible when the assembly is closed and if open exposes live insulated conductors that may cause a shock hazard. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Pic_6.png | file://x:/photopub/docs/0000000668/00cf63fa-80a9-4e94-99ab-8c2235c77a22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff12a3e2_af45_4eac_ac09_02f44dd3eaf6
ELIN-912605-2017 | EL-579658-2017 | 9/21/2017 3:17:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Hazard_Picture.png,Pic_6.png Damage to non-metallic sheaths, conductor insulation and conductors pose a variety of risk including arcing and fire hazards. Damaging the conductor insulation and conductors may cause a week spot in the length of the cable where hazards like shock and fire become much greater due to the damage. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Hazard_Picture.png | file://x:/photopub/docs/0000000667/976b5d91-a680-4249-8980-bfad07af0c01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69cc1ee6_ff08_45fd_bd6f_012f85a3754b
ELIN-913917-2017 | UW-588357-2017 | 9/22/2017 8:47:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F1.png,F2.png,F3.png 240V outlet, no cover and recessed to far in the wall. This is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F1.png | file://x:/photopub/docs/0000000667/92c53afb-9e11-4913-b378-05fdadc6bdaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47d9d401_777d_4dfa_990b_2827c7896087
ELIN-913917-2017 | UW-588357-2017 | 9/22/2017 8:47:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F1.png,F2.png,F3.png 240V outlet, no cover and recessed to far in the wall. This is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F2.png | file://x:/photopub/docs/0000000667/068d7802-b711-4920-bd01-bcd41c8411c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47d9d401_777d_4dfa_990b_2827c7896087
ELIN-913917-2017 | UW-588357-2017 | 9/22/2017 8:47:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #F1.png,F2.png,F3.png 240V outlet, no cover and recessed to far in the wall. This is a fire and shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | F3.png | file://x:/photopub/docs/0000000667/8307b452-09b8-4d96-8a5c-19c9195800ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47d9d401_777d_4dfa_990b_2827c7896087
GAHE-916537-2017 | HE-589917-2017 | 9/25/2017 12:53:44 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane_tanks.png Propane cylinders and pressure regulator are installed too close to an air conditioning compressor. The electrical contacts inside of the air compressor are a source of ignition. If the cylinder relief valves or pressure regulator relief were to release propane vapour, the air conditioning compressor could provide a source of ignition and could possibly lead to a fire or explosion. | 4 | Ignition sources present with-in minimum distance required | Propane_tanks.png | file://x:/photopub/docs/0000000668/81525c7f-ca20-465a-a16f-2108a09bb80f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47d24f66_5486_4d5d_9fd3_b8053dfc40f1
EDOP-910604-2017 | 2037546 | 9/21/2017 10:26:00 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound |  |  |  |  | #Testing.png Blah blah blah |  |  | Testing.png | file://x:/photopub/docs/0000000666/c3c94cec-b599-4636-8cba-4e1669d1c3a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1856e12e_ea42_4524_92de_361f7741405f
BPVOP-849173-2017 | 3788624 | 9/20/2017 10:35:02 AM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2012_safety_valve_.png All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve on a 150psi steam boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2012_safety_valve_.png | file://x:/photopub/docs/0000000666/35fea2d5-bc21-4907-93ad-caebbb63e2bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D0F44757_458B_4DEA_80A9_926AA3AB395A
ELIN-913811-2017 | EL-566632-2017 | 9/21/2017 8:42:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 2 | #Temp_to_perm_service_with_no_lockable_cover.png In a new single family dwelling service connection assessment a 200 amp 120/240 volt panel was not provided with a lockable cover and the residence was not in lock up stage. This could result in a shock hazard situation. Picture attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Temp_to_perm_service_with_no_lockable_cover.png | file://x:/photopub/docs/0000000667/6d515b0d-4198-4b5e-8d84-2cbced64313e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bed26443_606d_4b8e_9dd8_5c65a9fce019
ELIN-912007-2017 | EL-586458-2017 | 9/26/2017 11:12:37 AM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | #Branch_Circuit.png In a Mobile Home Main Electrical Panel an old unused 30 amp branch breaker has been used to power a new 15 amp branch circuit. This poses a shock hazard to persons and potential mechanical damage to the electrical circuit and equipment as this 30 amp breaker does not adequately protect the 15 amp circuit and equipment. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Branch_Circuit.png | file://x:/photopub/docs/0000000669/9c3d161e-c6cf-4334-b712-3ddf59c37dd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b590d20_1b50_41f3_8b86_1616cb6aa640
GAIN-915764-2017 | GA-588305-2017 | 9/26/2017 12:59:30 PM | ASSESS: GA: Final | png | #asFound Rubber hose between tank and RV | GA052 | Unprotected temporary hose installations | 3 | 3 | #Hose_11.png,Hose_12.png,Hose_13.png Unprotected rubber gas line is currently laying on the ground. Could be struck or run over | 3 | Unprotected temporary hose installations | Hose_11.png | file://x:/photopub/docs/0000000669/732a05db-468f-4e3c-9bfa-569eaf14bb57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fefe8a_5d25_4345_82d2_4e2f01e40777
GAIN-915764-2017 | GA-588305-2017 | 9/26/2017 12:59:30 PM | ASSESS: GA: Final | png | #asFound | GA052 | Unprotected temporary hose installations | 3 | 3 | #Hose_11.png,Hose_12.png,Hose_13.png Unprotected rubber gas line is currently laying on the ground. Could be struck or run over | 3 | Unprotected temporary hose installations | Hose_12.png | file://x:/photopub/docs/0000000669/cdfdbf17-b547-4a56-adc2-ab092f373c0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fefe8a_5d25_4345_82d2_4e2f01e40777
GAIN-915764-2017 | GA-588305-2017 | 9/26/2017 12:59:30 PM | ASSESS: GA: Final | png | #asFound | GA052 | Unprotected temporary hose installations | 3 | 3 | #Hose_11.png,Hose_12.png,Hose_13.png Unprotected rubber gas line is currently laying on the ground. Could be struck or run over | 3 | Unprotected temporary hose installations | Hose_13.png | file://x:/photopub/docs/0000000669/2407c0b8-f2c1-498d-974a-eb3d8fd7d5fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30fefe8a_5d25_4345_82d2_4e2f01e40777
ELIN-889597-2017 | EL-570008-2017 | 9/26/2017 11:00:09 AM | ASSESS: EL: Service Connection | png | #asFound Service grounding plate electrode in earth has #6 AWG copper conductor installed but where copper #6 enters earth to connect to plate electrode the #6 copper is cut off below grade. The service grounding plate electrode is not connected to service by a continuous run of #6 copper grounding conductor to ground service properly. | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | #Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded1.png,Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded2.png,Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded3.png Found 120/240 volt 90 amp temporary construction service grounding plate electrode in earth has #6 AWG copper conductor installed to connect to plate electrode but the #6 copper is damaged and is cut off below grade. The service grounding plate electrode is not connected to service by a continuous run of #6 copper grounding conductor to ground service properly to plate electrode. When service is not grounded properly the system is a possible electrical shock hazard to people | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_grounding_conductor_is_cut_off_and_damaged_and_service_is_not_grounded1.png | file://x:/photopub/docs/0000000669/42126d89-1386-4599-9176-dde1bcdd6466.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7194961_b620_4830_8132_32b1e3eeb374
GAIN-903732-2017 | GA-582940-2017 | 9/20/2017 11:39:59 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #CPVC_and_wrong_glue.png -Wrong glue used on S636CPVC pipe and fittings. The use of wrong glue could potentially affect the life of the venting system causing premature failure of system, potentially releasing combustion products into living space. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | CPVC_and_wrong_glue.png | file://x:/photopub/docs/0000000666/842bc1c0-92f1-496e-85bf-3ad584139cd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fb0cb60_6528_439b_b722_14fcd9a8a186
ELHE-915059-2017 | HE-589182-2017 | 9/22/2017 12:52:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png Fire alarm life safety system heat detector is not installed on its junction box with wiring exposed to damage. Lack of fire alarm life safety system could delay egress in the case of a fire/ evacuation situation. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazard2.png | file://x:/photopub/docs/0000000667/9569c4e3-09de-47c6-8359-b984d701fbc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65831017_0719_45fb_92f8_62284f6c91ef
ELHE-915059-2017 | HE-589182-2017 | 9/22/2017 12:52:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png Fire alarm life safety system heat detector is not installed on its junction box with wiring exposed to damage. Lack of fire alarm life safety system could delay egress in the case of a fire/ evacuation situation. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazard4.png | file://x:/photopub/docs/0000000667/291a346d-5b7a-49ad-96c0-c949b642b3e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65831017_0719_45fb_92f8_62284f6c91ef
ELHE-915059-2017 | HE-589182-2017 | 9/22/2017 12:52:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png Fire alarm life safety system heat detector is not installed on its junction box with wiring exposed to damage. Lack of fire alarm life safety system could delay egress in the case of a fire/ evacuation situation. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazard3.png | file://x:/photopub/docs/0000000667/8836d9dc-76f6-489a-8170-1d770b56ed46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65831017_0719_45fb_92f8_62284f6c91ef
ELHE-915059-2017 | HE-589182-2017 | 9/22/2017 12:52:32 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png Fire alarm life safety system heat detector is not installed on its junction box with wiring exposed to damage. Lack of fire alarm life safety system could delay egress in the case of a fire/ evacuation situation. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazard1.png | file://x:/photopub/docs/0000000667/405f839b-168e-4599-a989-e66904d6eca5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65831017_0719_45fb_92f8_62284f6c91ef
EDOP-751881-2017 | 2048811 | 9/21/2017 | ASSESS: ED OP: RAP | png | #asFound Base of controller showing exposed electrical wires not properly secured | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | #Exposed_electrical_wires.png Exposed wires and not properly fastened or secured could lead to electrical shock or short circuit | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | Exposed_electrical_wires.png | file://x:/photopub/docs/0000000667/67bce914-974d-48c6-9e0b-8479e4723386.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__747440D4_29CD_474C_88F0_1DD2CF52D97A
EDOP-571686-2016 | 2041070 | 9/22/2017 11:58:14 AM | ASSESS: ED OP: RAP | png | #asFound Undersized rouging ropes | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Ropes_to_be_replaced.png The hoisting ropes lift and lower the elevator. These ropes are undersized and there is rouging which oxidation. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Ropes_to_be_replaced.png | file://x:/photopub/docs/0000000667/091f5396-b735-4869-9cab-cd15365e0a4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3B5AB20E_4BD2_4AE8_B015_C8443C234063
GAIN-844738-2017 | GA-550922-2017 | 9/21/2017 9:10:35 AM | ASSESS: GA: Final | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 2 | #524_6th_ave.png Gas meter is not supported and can fall over due to frost heaves which would cause a gas leak | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 524_6th_ave.png | file://x:/photopub/docs/0000000666/58da5ce7-873e-4fe0-a029-45ff85ff8dfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5d0d43a_675d_4e41_858a_157124f81714
ELIN-910851-2017 | EL-387572-2016 | 9/21/2017 2:00:19 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_bus.png Exposed energized electrical equipment in an area not accessible to unauthorized persons, panel fillers missing in energized panel board | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_bus.png | file://x:/photopub/docs/0000000667/37582f3d-1973-4bfd-80c7-86cebe0df59e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50ce15fe_e8d6_4d2d_ba0a_dd693c34a4af
ELIN-909997-2017 | EL-560510-2017 | 9/25/2017 10:50:21 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Smoke_detectors_on_general_purpose_lighting_circuit_.png In a new residence with a 100 amp 240 V single phase service the smoke and life safety system detectors are not connected on to a general purpose lighting Circuit. It is important to be able to monitor the life safety system devices with a branch circuit of this type so a person knows when the circuit feeding the life safety system devices has failed. This noncompliance can result in injury to purses there | 0 | No Created Hazard Identified | Smoke_detectors_on_general_purpose_lighting_circuit_.png | file://x:/photopub/docs/0000000669/6d7901a3-974b-481a-a55b-ea0f7203c185.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80d4e98f_f89f_4735_8fb6_08dba05e542a
ELIN-911617-2017 | EL-584180-2017 | 9/25/2017 11:43:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #No_bonding_b__no_bonding_bushing.png A New 200 amp 240 V single phase service to a residential dwelling has been installed. A metal conduit nipple has been used between the metre in the main service disconnecting means and has not been provided proper bonding to the grounding system. Bonding is essential to ensure that overcurrent devices will react in the event that eight fault occurs in the raceway. Injury to persons or damage to property can occur when this condition exists | 3 | Continuity Bonding; method for equipment is not adequate. | No_bonding_b__no_bonding_bushing.png | file://x:/photopub/docs/0000000669/8584c565-546d-4392-96bf-7cfca644aa3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e39785e_ba44_469c_8099_b4e649b953db
ELIN-910478-2017 | EL-577386-2017 | 9/26/2017 9:16:25 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound Bonding to device boxes and circuit incomplete | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Bonding_to_Rick.png A New house is being constructed. The grounding and bonding interconnections to the receptacles switches lighting smoke detectors and most other electrical equipment in the house was found to be incomplete at rough wiring stage of the installation. When electrical equipment is not properly bonded to ground electrical faults may not cause overcurrent protection to react correctly. This could lead to property damage or injury to persons | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_to_Rick.png | file://x:/photopub/docs/0000000669/44bfbabb-e430-491c-b760-f23e8d6b2965.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92b0c940_2d17_4238_a5e8_082b85e9fff8
GAIN-913850-2017 | GA-535106-2017 | 9/26/2017 11:29:37 AM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Piping_14.png,Piping_15.png Four gas lines containing valves in closed position without caps or plugs fitted. Accidental opening of valves would allow gas to enter the occupied space. Risk of explosion and or fire if source of ignition was present. Meter turned off and red tag attached by GSO. No fuel in use at this location at this time. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Piping_14.png | file://x:/photopub/docs/0000000669/48d09f34-cbcf-42d0-835b-3f5e69c8008d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97bcac2f_c525_42da_ac0a_963f403973d4
GAIN-913850-2017 | GA-535106-2017 | 9/26/2017 11:29:37 AM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | #Piping_14.png,Piping_15.png Four gas lines containing valves in closed position without caps or plugs fitted. Accidental opening of valves would allow gas to enter the occupied space. Risk of explosion and or fire if source of ignition was present. Meter turned off and red tag attached by GSO. No fuel in use at this location at this time. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Piping_15.png | file://x:/photopub/docs/0000000669/33fd535a-075c-4898-a076-11c3a0d55abd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97bcac2f_c525_42da_ac0a_963f403973d4
GAIN-913211-2017 | GA-587997-2017 | 9/22/2017 11:06:15 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #Liner2.png | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Liner2.png | file://x:/photopub/docs/0000000667/000bb3e6-a8ad-4acd-946c-a5b91da3da7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fa86981_0b87_4ec0_9c69_4c0a76c97845
ELIN-912606-2017 | EL-579658-2017 | 9/21/2017 3:07:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | #Pic5.png -Ground conductor #6 awg bare cu terminated on bond lug position in duplex meter base. May have Improper fault current path back to utility. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Pic5.png | file://x:/photopub/docs/0000000667/d014c05c-2793-43f6-bd6c-afa4590cc493.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c2caf2c_27cc_42e6_8f41_2bd2d9546f34
ELIN-912605-2017 | EL-579658-2017 | 9/21/2017 3:17:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Hazard_Picture.png,Pic_6.png Damage to non-metallic sheaths, conductor insulation and conductors pose a variety of risk including arcing and fire hazards. Damaging the conductor insulation and conductors may cause a week spot in the length of the cable where hazards like shock and fire become much greater due to the damage. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Pic_6.png | file://x:/photopub/docs/0000000667/7f4a6788-e0b4-42f4-bfa2-39c00cc5c3a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69cc1ee6_ff08_45fd_bd6f_012f85a3754b
ELIN-918167-2017 | EL-579574-2017 | 9/27/2017 1:28:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 3 | #Non-compliances_for_grounding_system1.png,Non-compliances_for_grounding_system2.png,Non-compliances_for_grounding_system3.png,Non-compliances_for_grounding_system4.png,Non-compliances_for_grounding_system5.png Found 120/240volt 100amp single phase service does not have grounding conductor terminated on supply side of service for grounding power supply system grounded conductor (identified/neutral conductor bar) as required. When service power supply system is not grounded the system is a possible shock hazard to people | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Non-compliances_for_grounding_system4.png | file://x:/photopub/docs/0000000670/92872d4e-4a60-4a31-b8c9-5eda13228ffd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778562d0_8db8_4064_a931_724b3320b24e
ELIN-918167-2017 | EL-579574-2017 | 9/27/2017 1:28:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 3 | #Non-compliances_for_grounding_system1.png,Non-compliances_for_grounding_system2.png,Non-compliances_for_grounding_system3.png,Non-compliances_for_grounding_system4.png,Non-compliances_for_grounding_system5.png Found 120/240volt 100amp single phase service does not have grounding conductor terminated on supply side of service for grounding power supply system grounded conductor (identified/neutral conductor bar) as required. When service power supply system is not grounded the system is a possible shock hazard to people | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Non-compliances_for_grounding_system2.png | file://x:/photopub/docs/0000000670/8fd17ff1-bae7-4b18-bf9d-d5d77869110d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778562d0_8db8_4064_a931_724b3320b24e
ELIN-918167-2017 | EL-579574-2017 | 9/27/2017 1:28:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 3 | #Non-compliances_for_grounding_system1.png,Non-compliances_for_grounding_system2.png,Non-compliances_for_grounding_system3.png,Non-compliances_for_grounding_system4.png,Non-compliances_for_grounding_system5.png Found 120/240volt 100amp single phase service does not have grounding conductor terminated on supply side of service for grounding power supply system grounded conductor (identified/neutral conductor bar) as required. When service power supply system is not grounded the system is a possible shock hazard to people | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Non-compliances_for_grounding_system1.png | file://x:/photopub/docs/0000000670/ecdb8b63-d930-4e33-8f38-9fa3ea411447.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778562d0_8db8_4064_a931_724b3320b24e
ELIN-915276-2017 | EL-587599-2017 | 9/25/2017 12:22:50 PM | ASSESS: EL: Service Connection | png | #asFound Grounding conductor terminated at the wrong location | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | #Termination_of.png Grounding conductor terminated at the wrong location, should A ground fault occur when someone is working near or within the vicinity of the electrical equipment, that person will not be at equal potential to the electrical equipment. The result is that person would receive a electrical shock. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Termination_of.png | file://x:/photopub/docs/0000000668/33e753c2-7631-461a-81c1-161345be5dae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7e0d2b9_c99f_46f1_8efc_b75beb980118
ELIN-916349-2017 | EL-263532-2015 | 9/26/2017 11:26:54 AM | ASSESS: EL: Final | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 3 | #G1.png,G2.png Point of attachment failed, new point of attachment not properly installed. This has resulted in strain on the conductors and terminations. This is a fire hazard. | 4 | Damage to equipment may result in overheating. | G1.png | file://x:/photopub/docs/0000000669/45027afb-72f1-4df3-a941-9e2a1c3200ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6252ff5_8004_42e0_a2ee_6b42a5a8ba01
ELIN-916985-2017 | EL-588970-2017 | 9/26/2017 2:42:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #H.png Receptacle located to close to the bathtub. This is a shock hazard. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | H.png | file://x:/photopub/docs/0000000669/b7624eb2-40d4-4ddc-aa26-f935bd7a6d87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d50df9e_beb7_4c85_9cc1_e87d5594042f
ELIN-916349-2017 | EL-263532-2015 | 9/26/2017 11:26:54 AM | ASSESS: EL: Final | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 3 | #G1.png,G2.png Point of attachment failed, new point of attachment not properly installed. This has resulted in strain on the conductors and terminations. This is a fire hazard. | 4 | Damage to equipment may result in overheating. | G2.png | file://x:/photopub/docs/0000000669/0fdf3a1f-49d3-4173-ab3f-922318337245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6252ff5_8004_42e0_a2ee_6b42a5a8ba01
ELIN-916608-2017 | EL-415150-2016 | 9/26/2017 10:27:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #F.png Cable exposed to damage. This is a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | F.png | file://x:/photopub/docs/0000000669/01d4d457-0c29-4384-a9d6-b1a8ec6a5302.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84cd224b_51b0_483d_9f5b_237d57c53320
ELIN-918167-2017 | EL-579574-2017 | 9/27/2017 1:28:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 3 | #Non-compliances_for_grounding_system1.png,Non-compliances_for_grounding_system2.png,Non-compliances_for_grounding_system3.png,Non-compliances_for_grounding_system4.png,Non-compliances_for_grounding_system5.png Found 120/240volt 100amp single phase service does not have grounding conductor terminated on supply side of service for grounding power supply system grounded conductor (identified/neutral conductor bar) as required. When service power supply system is not grounded the system is a possible shock hazard to people | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Non-compliances_for_grounding_system5.png | file://x:/photopub/docs/0000000670/f2502b2a-4be7-4536-8764-62a9f213163f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778562d0_8db8_4064_a931_724b3320b24e
ELIN-918167-2017 | EL-579574-2017 | 9/27/2017 1:28:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 3 | #Non-compliances_for_grounding_system1.png,Non-compliances_for_grounding_system2.png,Non-compliances_for_grounding_system3.png,Non-compliances_for_grounding_system4.png,Non-compliances_for_grounding_system5.png Found 120/240volt 100amp single phase service does not have grounding conductor terminated on supply side of service for grounding power supply system grounded conductor (identified/neutral conductor bar) as required. When service power supply system is not grounded the system is a possible shock hazard to people | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Non-compliances_for_grounding_system3.png | file://x:/photopub/docs/0000000670/da978c0d-ea4c-47cb-9d5c-ec7af045b09f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778562d0_8db8_4064_a931_724b3320b24e
GAIN-905134-2017 | GA-583487-2017 | 9/26/2017 9:53:22 AM | ASSESS: GA: Final | png | #asFound Vent | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent_.png At time of inspection vent installed too close to grade level, snow accumulation could cause system shut down. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_.png | file://x:/photopub/docs/0000000669/f5ffa9b9-6770-42c6-87dd-bb228329639a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6584d51_21d8_4e2d_b326_d3060856be3a
ELIN-911570-2017 | EL-563110-2017 | 9/27/2017 10:42:40 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop1.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop2.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop3.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop4.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop5.png When ungrounded conductor sizes are reduced from a larger size to a smaller size they are required to be protected by overcurrent devices. The exception in one case is where the conductors have an ampacity that is not less than the connected load, they do not exceed 3M in length, and they terminate in an overcurrent device that protected the conductors at the conductor's ampacity. This is required to prevent the conductor from being over loaded which can cause damage to the conductor insulation and a fault from the conductor to ground or to other ungrounded | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop3.png | file://x:/photopub/docs/0000000670/4bd759e4-f565-4c6c-86b1-cedd2681ac30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f566e19_0604_414b_a16f_42f2915280ea
ELIN-915394-2017 | EL-583757-2017 | 9/27/2017 8:35:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast_extends_1900mm_abov_e_the_supportting_wall1.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall2.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall3.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall4.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall5.png Over head service masts are normally part of an approved mast assembly complete with components that together must meet a CSA standard. The maximum unguyed projection of the mast can not exceed 1.5M. This is required to ensure the cantilever loa does not exceed the rating of the support member (mast) which can cause the mast to be pulled over or damaged. This installation for a new 200A for a house under construction has a mast assembly installed where the support member (mast) extends to a length of 1.9M above the above the supporting wall that it is secured to. Left uncorrected this is a potential shock and fire hazard if once the over head service supply conductors are installed the mast is unable to suppo | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast_extends_1900mm_abov_e_the_supportting_wall2.png | file://x:/photopub/docs/0000000670/aa429f87-b9e1-4242-9f9b-21a521720018.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6832d791_926b_4a5a_b466_9564cf7a92e5
ELIN-915394-2017 | EL-583757-2017 | 9/27/2017 8:35:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast_extends_1900mm_abov_e_the_supportting_wall1.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall2.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall3.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall4.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall5.png Over head service masts are normally part of an approved mast assembly complete with components that together must meet a CSA standard. The maximum unguyed projection of the mast can not exceed 1.5M. This is required to ensure the cantilever loa does not exceed the rating of the support member (mast) which can cause the mast to be pulled over or damaged. This installation for a new 200A for a house under construction has a mast assembly installed where the support member (mast) extends to a length of 1.9M above the above the supporting wall that it is secured to. Left uncorrected this is a potential shock and fire hazard if once the over head service supply conductors are installed the mast is unable to suppo | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast_extends_1900mm_abov_e_the_supportting_wall5.png | file://x:/photopub/docs/0000000670/3e564e01-ec9e-4469-9427-9702ab40e598.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6832d791_926b_4a5a_b466_9564cf7a92e5
EDIN-919325-2017 | ED-484383-2016 | 9/27/2017 7:54:21 PM | ASSESS: ED IN: Construction Use | png | #asFound Path to machine room lacks lighting | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | #MR_Lighting.png No lighting along the path from the stairwell to the machine room. Due to the lack of lighting along the path to the machine room may cause authorized elevator personal to trip and fall. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | MR_Lighting.png | file://x:/photopub/docs/0000000670/9429c30b-52ae-4ba3-bf4c-9f07c7d93870.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9817929e_8703_4474_a392_2a1a255ed924
ELIN-904353-2017 | EL-573967-2017 | 9/20/2017 | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box1.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box2.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box3.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box4.png Found 120 volt 15 amp non-metallic sheathed cable and its branch circuit conductors are energized and exposed and hanging free air out of the wall without a junction box and cover installed on end of conductors. When electrical equipment is energized and exposed with energized conductors not contained inside a junction box and cover, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box2.png | file://x:/photopub/docs/0000000668/7eb5a537-ec5a-4323-8a9d-77695f015669.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__771c2862_997d_4cb5_9147_865897df5578
ELIN-904353-2017 | EL-573967-2017 | 9/20/2017 | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box1.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box2.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box3.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box4.png Found 120 volt 15 amp non-metallic sheathed cable and its branch circuit conductors are energized and exposed and hanging free air out of the wall without a junction box and cover installed on end of conductors. When electrical equipment is energized and exposed with energized conductors not contained inside a junction box and cover, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box1.png | file://x:/photopub/docs/0000000668/88c44680-670b-4e53-ac90-a26bb22f5334.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__771c2862_997d_4cb5_9147_865897df5578
ELIN-911842-2017 | EL-557516-2017 | 9/26/2017 11:44:21 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMD_cable_run_UG1.png,NMD_cable_run_UG2.png NMD cable approved for dry and damp locations may deteriorate if installed in a wet location causing cable failure and potential fire or shock hazard | 3 | Conductors Equipment is not approved for the specific use. | NMD_cable_run_UG2.png | file://x:/photopub/docs/0000000669/bc8a6e98-7971-4ca2-952e-48e5faea5f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68ead50d_6d5a_4382_bee3_90c72e73006d
ELIN-920294-2017 | EL-592388-2017 | 9/29/2017 8:34:44 AM | ASSESS: EL: Service Connection | png | #asFound Screw in attachment point | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 2 | #S.png A screw in attachment point has been installed on a service. This style of attachment does not provide proper support of overhead conductors and is a shock and fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | S.png | file://x:/photopub/docs/0000000671/cd2dc29e-ec5a-4234-acc7-23d5343c0a9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba1eebc2_7c73_4869_bf88_ce2373373e64
ELIN-918882-2017 | EL-591127-2017 | 9/27/2017 | ASSESS: EL: Rough Wiring-Partial | png | #asFound Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors1.png,Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors2.png Found 2 sets of existing 120 volt energized branch circuits were altered while feeding two incandescent luminaires that are hanging energized from basement ceiling by conductors support only. When luminares, outlet boxes and cables are energized and are not supported properly, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors2.png | file://x:/photopub/docs/0000000671/233d8543-0263-4f5a-ac7c-f86947d05de3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5e0feaa_9f84_4f59_a992_48295e51d137
ELIN-918797-2017 | EL-574095-2017 | 9/28/2017 1:14:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #25mm_of_air_space_is_required1.png,25mm_of_air_space_is_required2.png,25mm_of_air_space_is_required3.png This assessment found that an air space of 25mm between heating ducts and wire are not present creating a fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 25mm_of_air_space_is_required1.png | file://x:/photopub/docs/0000000671/03174cb7-2912-49a5-aa55-82a3f16c2cea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314e8bda_706d_4ed4_8353_76b09f0d895a
ELIN-918797-2017 | EL-574095-2017 | 9/28/2017 1:14:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #25mm_of_air_space_is_required1.png,25mm_of_air_space_is_required2.png,25mm_of_air_space_is_required3.png This assessment found that an air space of 25mm between heating ducts and wire are not present creating a fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 25mm_of_air_space_is_required3.png | file://x:/photopub/docs/0000000671/37bbc67c-31e2-45fa-992b-63d86f6a7b62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314e8bda_706d_4ed4_8353_76b09f0d895a
BPVIN-895988-2017 | BPV-575023-2017 | 9/28/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP115 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | 4 | 4 | #Typical_Low_Water_Fuel_Cutoff.png I found an auxiliary low water fuel cutoff device not installed as required on a low pressure steam boiler to provide redundancy should the primary low water fuel cutoff device fail to operate during a low water condition in a boiler. The boiler has a specified minimum operating water level and should the water level drop to this point the fuel valve will automatically close preventing overheating of the boiler. Overheating of the boiler metal will lead to weakening of the metal and potential rupture of the boiler causing property damage and personnel injury or loss of life.. | 4 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | Typical_Low_Water_Fuel_Cutoff.png | file://x:/photopub/docs/0000000670/c0653168-2d17-4747-b43e-1e7f53891af2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f530e1b2_60a0_4f68_8823_c8a16d89c31e
ELIN-911570-2017 | EL-563110-2017 | 9/27/2017 10:42:40 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop1.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop2.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop3.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop4.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop5.png When ungrounded conductor sizes are reduced from a larger size to a smaller size they are required to be protected by overcurrent devices. The exception in one case is where the conductors have an ampacity that is not less than the connected load, they do not exceed 3M in length, and they terminate in an overcurrent device that protected the conductors at the conductor's ampacity. This is required to prevent the conductor from being over loaded which can cause damage to the conductor insulation and a fault from the conductor to ground or to other ungrounded | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop5.png | file://x:/photopub/docs/0000000670/7262d2f3-6889-4b93-a891-0cee764538f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f566e19_0604_414b_a16f_42f2915280ea
ELIN-915394-2017 | EL-583757-2017 | 9/27/2017 8:35:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast_extends_1900mm_abov_e_the_supportting_wall1.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall2.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall3.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall4.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall5.png Over head service masts are normally part of an approved mast assembly complete with components that together must meet a CSA standard. The maximum unguyed projection of the mast can not exceed 1.5M. This is required to ensure the cantilever loa does not exceed the rating of the support member (mast) which can cause the mast to be pulled over or damaged. This installation for a new 200A for a house under construction has a mast assembly installed where the support member (mast) extends to a length of 1.9M above the above the supporting wall that it is secured to. Left uncorrected this is a potential shock and fire hazard if once the over head service supply conductors are installed the mast is unable to suppo | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast_extends_1900mm_abov_e_the_supportting_wall3.png | file://x:/photopub/docs/0000000670/4f91fde6-f40e-45d3-a3aa-bc33d87c32ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6832d791_926b_4a5a_b466_9564cf7a92e5
BPVIN-919249-2017 | UW-587627-2017 | 9/19/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound year of build 1990 Age 27 years | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Age_verification_by_Name_plate.png Nondestructive examination should assess this vessels integrity, Local thin areas caused by internal corrosion could leak or cause catastrophic failure. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Age_verification_by_Name_plate.png | file://x:/photopub/docs/0000000670/40d04602-6fca-4bb5-836a-4a8721bc85f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae1ebdbf_4646_4968_92da_cc4e1b9f6112
ELIN-918923-2017 | UW-566784-2017 | 9/28/2017 7:06:22 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #W1.png,W2.png Doorbell transformer not grounded. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | W1.png | file://x:/photopub/docs/0000000670/b8564339-a43e-4cc6-b6f3-606a41ca0cd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2cdfa0_8579_48d3_9068_bb63b1596392
ELIN-918923-2017 | UW-566784-2017 | 9/28/2017 7:06:22 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #W1.png,W2.png Doorbell transformer not grounded. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | W2.png | file://x:/photopub/docs/0000000670/bb5645f3-5d8a-45a9-9b9b-887b5e2b92a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2cdfa0_8579_48d3_9068_bb63b1596392
ELIN-904353-2017 | EL-573967-2017 | 9/20/2017 | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box1.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box2.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box3.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box4.png Found 120 volt 15 amp non-metallic sheathed cable and its branch circuit conductors are energized and exposed and hanging free air out of the wall without a junction box and cover installed on end of conductors. When electrical equipment is energized and exposed with energized conductors not contained inside a junction box and cover, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box3.png | file://x:/photopub/docs/0000000668/375b3b96-dccd-42a7-a9bf-4e96044f8f0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__771c2862_997d_4cb5_9147_865897df5578
ELIN-904353-2017 | EL-573967-2017 | 9/20/2017 | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box1.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box2.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box3.png,Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box4.png Found 120 volt 15 amp non-metallic sheathed cable and its branch circuit conductors are energized and exposed and hanging free air out of the wall without a junction box and cover installed on end of conductors. When electrical equipment is energized and exposed with energized conductors not contained inside a junction box and cover, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_conductors_without_a_junction_box_and_cover_to_contain_wiring_in_box4.png | file://x:/photopub/docs/0000000668/50f58b50-a77c-4074-8f90-ccd356ca15e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__771c2862_997d_4cb5_9147_865897df5578
ELIN-911842-2017 | EL-557516-2017 | 9/26/2017 11:44:21 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #NMD_cable_run_UG1.png,NMD_cable_run_UG2.png NMD cable approved for dry and damp locations may deteriorate if installed in a wet location causing cable failure and potential fire or shock hazard | 3 | Conductors Equipment is not approved for the specific use. | NMD_cable_run_UG1.png | file://x:/photopub/docs/0000000669/da1455c7-9117-43df-b5a0-a44231de5fa4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68ead50d_6d5a_4382_bee3_90c72e73006d
ELIN-916258-2017 | EL-459050-2016 | 9/27/2017 8:36:01 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #NMD_cables_enetr_gutter_Box_without_mechanical_connectors.png Non-metallic type cables must be physically connected to the equipment they enter to prevent strain on conductor terminations and damage to the cables themselves | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | NMD_cables_enetr_gutter_Box_without_mechanical_connectors.png | file://x:/photopub/docs/0000000669/ad202ab1-847f-4e8a-972d-a9a7a6d83987.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000721c_25c0_4f3a_8dfc_da65866fabf3
EDOP-693001-2016 | 2048586 | 9/26/2017 10:40:41 AM | ASSESS: ED OP: RAP | png | #asFound Hoist ropes | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #hoist_ropes.png The hoist ropes are undersized and rouging which warrants the replacement | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Hoist_ropes.png | file://x:/photopub/docs/0000000669/5156783a-0dbb-42d3-97e5-a8d8a6f0bd7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9E3358DE_5572_4F33_85F9_52AE9B15A618
EDOP-693001-2016 | 2048586 | 9/26/2017 10:40:41 AM | ASSESS: ED OP: RAP | png | #asFound Undersized and rouged hoist ropes | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #hoist_ropes.png The hoist ropes are undersized and rouging which warrants the replacement | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | hoist_ropes.png | file://x:/photopub/docs/0000000669/570169cb-cf7a-42ba-8cca-f09d8416d28a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9E3358DE_5572_4F33_85F9_52AE9B15A618
ELIN-916970-2017 | EL-502495-2017 | 9/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers1.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers2.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers3.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers4.png,Front_of_the_new_house.png The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable electrical equipment that are plugged into receptacles. This installation for a new house was not provided with AFCI protection for the all 15A 120V receptacles and branch circuits throughout the house as is required. This is a potential fire hazard if an arcing fault occurs on the receptacle branch circuits from the | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers2.png | file://x:/photopub/docs/0000000669/e236f80f-f4a9-40ad-8718-c6fd56010a2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aedfbf7_f437_4c7e_8bf4_6d6b1b2e5f2c
ELIN-916970-2017 | EL-502495-2017 | 9/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers1.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers2.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers3.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers4.png,Front_of_the_new_house.png The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable electrical equipment that are plugged into receptacles. This installation for a new house was not provided with AFCI protection for the all 15A 120V receptacles and branch circuits throughout the house as is required. This is a potential fire hazard if an arcing fault occurs on the receptacle branch circuits from the | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers1.png | file://x:/photopub/docs/0000000669/a35dda69-f807-4d35-8a67-666c4d8e2898.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aedfbf7_f437_4c7e_8bf4_6d6b1b2e5f2c
ELIN-915944-2017 | EL-580066-2017 | 9/28/2017 11:30:18 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Subpanel_Cover_Missing1.png,Subpanel_Cover_Missing2.png An energized 100 amp 120/240 volt electrical panel does not have the panel cover in place to effectively cover/guard the energizes components. Without the panel cover there is nothing to prevent persons from contacting the energized components inside the panel. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Subpanel_Cover_Missing1.png | file://x:/photopub/docs/0000000671/68184335-1a31-4090-8591-c62a1bd26400.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4656a44f_77ea_4f01_97ab_9382fb1ad8f4
ELIN-915944-2017 | EL-580066-2017 | 9/28/2017 11:30:18 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Subpanel_Cover_Missing1.png,Subpanel_Cover_Missing2.png An energized 100 amp 120/240 volt electrical panel does not have the panel cover in place to effectively cover/guard the energizes components. Without the panel cover there is nothing to prevent persons from contacting the energized components inside the panel. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Subpanel_Cover_Missing2.png | file://x:/photopub/docs/0000000671/69fd9e43-e3eb-4a68-a2ab-5f7204bb5be4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4656a44f_77ea_4f01_97ab_9382fb1ad8f4
ELIN-911570-2017 | EL-563110-2017 | 9/27/2017 10:42:40 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop1.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop2.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop3.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop4.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop5.png When ungrounded conductor sizes are reduced from a larger size to a smaller size they are required to be protected by overcurrent devices. The exception in one case is where the conductors have an ampacity that is not less than the connected load, they do not exceed 3M in length, and they terminate in an overcurrent device that protected the conductors at the conductor's ampacity. This is required to prevent the conductor from being over loaded which can cause damage to the conductor insulation and a fault from the conductor to ground or to other ungrounded | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop1.png | file://x:/photopub/docs/0000000670/4b78f15e-04d3-45a7-a872-8749d9c7a5ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f566e19_0604_414b_a16f_42f2915280ea
ELIN-911570-2017 | EL-563110-2017 | 9/27/2017 10:42:40 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop1.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop2.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop3.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop4.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop5.png When ungrounded conductor sizes are reduced from a larger size to a smaller size they are required to be protected by overcurrent devices. The exception in one case is where the conductors have an ampacity that is not less than the connected load, they do not exceed 3M in length, and they terminate in an overcurrent device that protected the conductors at the conductor's ampacity. This is required to prevent the conductor from being over loaded which can cause damage to the conductor insulation and a fault from the conductor to ground or to other ungrounded | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop4.png | file://x:/photopub/docs/0000000670/04fcd044-dacc-4a20-88eb-4a22500482c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f566e19_0604_414b_a16f_42f2915280ea
ELIN-915394-2017 | EL-583757-2017 | 9/27/2017 8:35:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast_extends_1900mm_abov_e_the_supportting_wall1.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall2.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall3.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall4.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall5.png Over head service masts are normally part of an approved mast assembly complete with components that together must meet a CSA standard. The maximum unguyed projection of the mast can not exceed 1.5M. This is required to ensure the cantilever loa does not exceed the rating of the support member (mast) which can cause the mast to be pulled over or damaged. This installation for a new 200A for a house under construction has a mast assembly installed where the support member (mast) extends to a length of 1.9M above the above the supporting wall that it is secured to. Left uncorrected this is a potential shock and fire hazard if once the over head service supply conductors are installed the mast is unable to suppo | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast_extends_1900mm_abov_e_the_supportting_wall1.png | file://x:/photopub/docs/0000000670/d7d6924b-8554-4898-a60e-624c862b68f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6832d791_926b_4a5a_b466_9564cf7a92e5
ELIN-918857-2017 | EL-591381-2017 | 9/28/2017 12:37:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 2 | #Manufacturers_instructions_for_grounding_.png The ground wire was connected to the panel bonding terminal which could allow for a parallel path in the event of a fault causing potential overheating and equipment damage. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Manufacturers_instructions_for_grounding_.png | file://x:/photopub/docs/0000000670/b28fbadc-6469-46ee-9f96-ad06fcdd2727.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed91a312_5faa_4c43_937d_9edeee8bde94
GAIN-850518-2017 | GA-530573-2017 | 9/28/2017 8:21:30 AM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Missing_fire_valve.png Missing fire safety valve hen properly installed shuts off all gas entering the kitchen area to prevent a gas fed fire that can cause severe damage and loss of life | 4 | Missing mandatory safety controls | Missing_fire_valve.png | file://x:/photopub/docs/0000000670/7b8d8a6c-de37-4542-bf73-c669615f09c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca619a64_5669_4329_a537_ac92b34d4a9c
BPVIN-919627-2017 | UW-590426-2017 | 9/22/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #Leaking_Safety_Valve.png Due to valve leakage, valve may no operate at the set pressure and tank could over-pressurize. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leaking_Safety_Valve.png | file://x:/photopub/docs/0000000670/57e0ca6b-9eb0-4486-b363-d366a3ae5ed3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7ce099d_9aad_4046_9105_4f85236f4814
ELIN-828936-2017 | EL-265358-2015 | 9/26/2017 9:04:23 AM | ASSESS: EL: Final | png | #asFound | EL338 | Installation of electrical equipment Equipment is not approved for the specific use; specifically, the receptacle is undersized and not adequately protected. | 4 | 4 | #15A_receptacle_installed_on_a_20A_breaker.png 15 amp, 120 volt general use receptacle has been provided with a 20 amp overcurrent device that exceeds the ampere rating of the receptacle. This is a thermal issue. | 4 | Installation of electrical equipment Equipment is not approved for the specific use; specifically, the receptacle is undersized and not adequately protected. | 15A_receptacle_installed_on_a_20A_breaker.png | file://x:/photopub/docs/0000000670/1284a612-fa95-4cf9-9fcd-ddaa6b860b93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ee52e23_51ca_471d_8fe7_4bd3762a4ccb
GAIN-919654-2017 | GA-550995-2017 | 9/28/2017 9:00:05 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Water_heater_3.png Plastic water lines installed with less than the required 6'' clearance to type C vent. Possible risk of the lines melting due to exposure to temperatures above its rating. Fire risk, self extinguishing due to release of water. | 3 | Non compliant Type C Vent clearance | Water_heater_3.png | file://x:/photopub/docs/0000000670/4e463bc9-251f-49cd-a5ca-1e91e885f4ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfcbd6f8_78d2_4ed4_bc44_3d1bb46d685d
ELHE-919637-2017 | HE-591867-2017 | 9/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Service_arcing1.png,Service_arcing2.png - Main service switch feeding shows signs of arcing and melting. Other signs of age and lack of maintenance present as well. Switch is at high risk of failure and could lead to shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Service_arcing1.png | file://x:/photopub/docs/0000000671/e4795c0d-b7c4-4d92-bc86-cd86e706c3df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26be12a8_fa4b_48b3_92fc_bfa81147ba90
ELHE-919637-2017 | HE-591867-2017 | 9/27/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Service_arcing1.png,Service_arcing2.png - Main service switch feeding shows signs of arcing and melting. Other signs of age and lack of maintenance present as well. Switch is at high risk of failure and could lead to shock or fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Service_arcing2.png | file://x:/photopub/docs/0000000671/3bad7b8e-f5be-4a48-ae04-06756da60c28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26be12a8_fa4b_48b3_92fc_bfa81147ba90
ELIN-916970-2017 | EL-502495-2017 | 9/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers1.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers2.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers3.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers4.png,Front_of_the_new_house.png The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable electrical equipment that are plugged into receptacles. This installation for a new house was not provided with AFCI protection for the all 15A 120V receptacles and branch circuits throughout the house as is required. This is a potential fire hazard if an arcing fault occurs on the receptacle branch circuits from the | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers3.png | file://x:/photopub/docs/0000000669/ee7cc208-2be0-47f7-b0d6-2bbd1461f826.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aedfbf7_f437_4c7e_8bf4_6d6b1b2e5f2c
ELIN-916970-2017 | EL-502495-2017 | 9/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers1.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers2.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers3.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers4.png,Front_of_the_new_house.png The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable electrical equipment that are plugged into receptacles. This installation for a new house was not provided with AFCI protection for the all 15A 120V receptacles and branch circuits throughout the house as is required. This is a potential fire hazard if an arcing fault occurs on the receptacle branch circuits from the | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers4.png | file://x:/photopub/docs/0000000669/368f982a-5e82-44e6-abf2-0b9c1d1b950e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aedfbf7_f437_4c7e_8bf4_6d6b1b2e5f2c
ELIN-918882-2017 | EL-591127-2017 | 9/27/2017 | ASSESS: EL: Rough Wiring-Partial | png | #asFound Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors1.png,Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors2.png Found 2 sets of existing 120 volt energized branch circuits were altered while feeding two incandescent luminaires that are hanging energized from basement ceiling by conductors support only. When luminares, outlet boxes and cables are energized and are not supported properly, the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Existing_energized_luminares_and_outlet_boxes_hanging_by_energized_conductors1.png | file://x:/photopub/docs/0000000671/606cb986-8056-414f-977f-d1f714f20335.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5e0feaa_9f84_4f59_a992_48295e51d137
ELIN-918797-2017 | EL-574095-2017 | 9/28/2017 1:14:05 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #25mm_of_air_space_is_required1.png,25mm_of_air_space_is_required2.png,25mm_of_air_space_is_required3.png This assessment found that an air space of 25mm between heating ducts and wire are not present creating a fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 25mm_of_air_space_is_required2.png | file://x:/photopub/docs/0000000671/c2197529-550a-46ff-b18b-549848bcf517.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__314e8bda_706d_4ed4_8353_76b09f0d895a
ELIN-911570-2017 | EL-563110-2017 | 9/27/2017 10:42:40 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | #Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop1.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop2.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop3.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop4.png,Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop5.png When ungrounded conductor sizes are reduced from a larger size to a smaller size they are required to be protected by overcurrent devices. The exception in one case is where the conductors have an ampacity that is not less than the connected load, they do not exceed 3M in length, and they terminate in an overcurrent device that protected the conductors at the conductor's ampacity. This is required to prevent the conductor from being over loaded which can cause damage to the conductor insulation and a fault from the conductor to ground or to other ungrounded | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Under_sized_tap_conductors_from_100A_splitter_to_100A_load_center_in_the_detached_shop2.png | file://x:/photopub/docs/0000000670/0c199aa5-4d56-4be1-8867-8a537a9263a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f566e19_0604_414b_a16f_42f2915280ea
ELIN-915394-2017 | EL-583757-2017 | 9/27/2017 8:35:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #Service_mast_extends_1900mm_abov_e_the_supportting_wall1.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall2.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall3.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall4.png,Service_mast_extends_1900mm_abov_e_the_supportting_wall5.png Over head service masts are normally part of an approved mast assembly complete with components that together must meet a CSA standard. The maximum unguyed projection of the mast can not exceed 1.5M. This is required to ensure the cantilever loa does not exceed the rating of the support member (mast) which can cause the mast to be pulled over or damaged. This installation for a new 200A for a house under construction has a mast assembly installed where the support member (mast) extends to a length of 1.9M above the above the supporting wall that it is secured to. Left uncorrected this is a potential shock and fire hazard if once the over head service supply conductors are installed the mast is unable to suppo | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_mast_extends_1900mm_abov_e_the_supportting_wall4.png | file://x:/photopub/docs/0000000670/a6c4ca69-fd45-46e3-8d8f-1516b02f2647.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6832d791_926b_4a5a_b466_9564cf7a92e5
EDIN-920519-2017 | ED-483144-2016 | 9/28/2017 8:56:05 PM | ASSESS: ED IN: Construction Use | png | #asFound Top of car emergency exit hatch | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Emergency_Exit.png The top of car emergency exit is placed outside of the perimeter of the top of car handrail. If during an emergency rescue from the top of car, the passengers would require to climb over the handrail to a safer part of the top of car. This would introduce a fall hazard to the both passengers and emergency personal during evacuation from the elevator car | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Emergency_Exit.png | file://x:/photopub/docs/0000000670/d818d4d2-2947-413d-a8f1-c989c17d5665.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c786da9_38c9_46f6_9a59_ebb2307d8032
ELIN-916970-2017 | EL-502495-2017 | 9/25/2017 | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers1.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers2.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers3.png,Receptacle_branch_circuits_were_not_AFCI_protected_circuits_were_connected_to_non-AFCI_breakers4.png,Front_of_the_new_house.png The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable electrical equipment that are plugged into receptacles. This installation for a new house was not provided with AFCI protection for the all 15A 120V receptacles and branch circuits throughout the house as is required. This is a potential fire hazard if an arcing fault occurs on the receptacle branch circuits from the | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Front_of_the_new_house.png | file://x:/photopub/docs/0000000669/49dfb17d-dcef-4df5-8eca-a79f627326d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aedfbf7_f437_4c7e_8bf4_6d6b1b2e5f2c
ELIN-915268-2017 | EL-588440-2017 | 9/25/2017 2:17:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | #Garage_entrance.png The new detached garage does not include a light outside the exterior man-door entrance, this can lead to personnel injury issue and is labelled as a power supply/ interrupt condition | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Garage_entrance.png | file://x:/photopub/docs/0000000668/9d5c327c-acd6-4a4e-967a-54ce9e183861.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b108f6eb_4ae3_4ee1_956b_3374f9fe057b
ELIN-914857-2017 | EL-586678-2017 | 9/25/2017 1:42:52 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 3 | #Pole_service.png During the replacement of a damaged 100 amp 120/240 volt overhead service the contractor replaced the dip service feeder cable with a #2 aluminum conductor and did not provide a load calculation to support the use. With an unknown calculated load there is a chance of a Thermal issue could occur. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Pole_service.png | file://x:/photopub/docs/0000000668/9b4c09f9-63ed-409c-9709-fe3452d872c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5781fecf_59ec_4456_be63_c02840f6cc3b
ELIN-897942-2017 | EL-407922-2016 | 9/25/2017 12:18:51 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Panelboard.png In a new residential dwelling, 4x 15 amp various receptacle circuits are not protected by AFCI protection, this can lead to a thermal issue | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Panelboard.png | file://x:/photopub/docs/0000000668/7f5b8c52-0762-43ea-8ed9-8b0f3ea555ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94f7d6e4_9374_4271_8c71_8148fb9c4d72
ELIN-909346-2017 | EL-584809-2017 | 9/27/2017 11:23:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Conduit_entering_panel_without_bond_bushing_or_duct_seal_and_wet_location_cover_plate_without_extra_duty_marking_1.png,Conduit_entering_panel_without_bond_bushing_or_duct_seal_and_wet_location_cover_plate_without_extra_duty_marking_2.png Delete photo of wet location coverplate as "extra duty" mark is on cover. | 0 | No Created Hazard Identified | Conduit_entering_panel_without_bond_bushing_or_duct_seal_and_wet_location_cover_plate_without_extra_duty_marking_2.png | file://x:/photopub/docs/0000000670/823234a1-ee4f-4f97-adff-b0e804229c31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4926876_7118_4109_83a3_50caf177339e
ELIN-909346-2017 | EL-584809-2017 | 9/27/2017 11:23:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Conduit_entering_panel_without_bond_bushing_or_duct_seal_and_wet_location_cover_plate_without_extra_duty_marking_1.png,Conduit_entering_panel_without_bond_bushing_or_duct_seal_and_wet_location_cover_plate_without_extra_duty_marking_2.png Delete photo of wet location coverplate as "extra duty" mark is on cover. | 0 | No Created Hazard Identified | Conduit_entering_panel_without_bond_bushing_or_duct_seal_and_wet_location_cover_plate_without_extra_duty_marking_1.png | file://x:/photopub/docs/0000000670/ba9fe58c-e9ea-43a4-be66-46a7d820fe86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4926876_7118_4109_83a3_50caf177339e
ELIN-918232-2017 | EL-548374-2017 | 10/5/2017 11:14:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL333 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 2 | 2 | #Cables_in_contact_with_hot_air_ducts.png NMD type cables may be subject to insulation deterioration when in contact with hot air ducts | 2 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Cables_in_contact_with_hot_air_ducts.png | file://x:/photopub/docs/0000000674/cbf90f1e-3093-4ebe-8e4e-eaf87356b988.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b6d3975_2fc8_4fce_9953_bdb97b17765d
AMIN-926039-2017 | AM-595666-2017 | 10/6/2017 6:51:47 PM | ASSESS: AM IN: Inflatable Acceptance | png | #asFound Front attachments not anchored | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Inflatable_anchoring_inadequate_1.png,Inflatable_anchoring_inadequate_2.png,Inflatable_anchoring_inadequate_3.png Unit is not tethered to manufactures specification. Upper tethers set at angles of more than 45 degrees. Some anchor points are not anchored An inflatable not anchored appropriately risks being toppled in high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Inflatable_anchoring_inadequate_3.png | file://x:/photopub/docs/0000000675/1be32568-1bbf-464c-b601-64ef28ee76b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c63d24f8_736f_4f41_b32d_34c14e39690b
AMIN-926040-2017 | AM-595629-2017 | 10/6/2017 6:27:15 PM | ASSESS: AM IN: Inflatable Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Anchor_point_inadequate_1.png,Anchor_point_inadequate_2.png Unit is not tethered to manufactures specification. Spikes not at the minimum required depth Upper tethers set at angles of more than 45 degrees. Some anchor points are not anchored An inflatable not anchored appropriately risks being toppled in high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Anchor_point_inadequate_2.png | file://x:/photopub/docs/0000000675/681fb04c-9492-47f2-bb47-112b7bd2cf2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afce8de8_9b95_4a13_8351_a70517639a8d
AMIN-926039-2017 | AM-595666-2017 | 10/6/2017 6:51:47 PM | ASSESS: AM IN: Inflatable Acceptance | png | #asFound Lower tether points exceed 2' | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Inflatable_anchoring_inadequate_1.png,Inflatable_anchoring_inadequate_2.png,Inflatable_anchoring_inadequate_3.png Unit is not tethered to manufactures specification. Upper tethers set at angles of more than 45 degrees. Some anchor points are not anchored An inflatable not anchored appropriately risks being toppled in high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Inflatable_anchoring_inadequate_2.png | file://x:/photopub/docs/0000000675/21ad88d3-9846-4f49-9552-c54464ca5cb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c63d24f8_736f_4f41_b32d_34c14e39690b
AMIN-926040-2017 | AM-595629-2017 | 10/6/2017 6:27:15 PM | ASSESS: AM IN: Inflatable Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Anchor_point_inadequate_1.png,Anchor_point_inadequate_2.png Unit is not tethered to manufactures specification. Spikes not at the minimum required depth Upper tethers set at angles of more than 45 degrees. Some anchor points are not anchored An inflatable not anchored appropriately risks being toppled in high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Anchor_point_inadequate_1.png | file://x:/photopub/docs/0000000675/9a445b66-66e3-4b17-958c-9e632ef90f2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afce8de8_9b95_4a13_8351_a70517639a8d
BPVIN-926809-2017 | BPV-596045-2017 | 10/6/2017 12:29:12 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | #EXPANSION_TANKS.png Upon assessment of expansion tank (dimensions: length-0.70 meter and diameter-0.65 meter) with Maximum Allowable Working Pressure of 125psig it is determined that vessel is not firmly anchored to floor or braced. In the event of earthquake of significant scale vessel may trip or move and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | EXPANSION_TANKS.png | file://x:/photopub/docs/0000000675/70194de1-0b50-4d8f-9814-2ab7d166d727.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9de8d902_74f0_4f23_b066_9fb1169f79ef
ELIN-913911-2017 | EL-586061-2017 | 9/29/2017 10:48:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Loose_and_improper_conductor_termnations_at_new_service_panel1.png,Loose_and_improper_conductor_termnations_at_new_service_panel2.png,Loose_and_improper_conductor_termnations_at_new_service_panel3.png,Loose_and_improper_conductor_termnations_at_new_service_panel4.png,Loose_and_improper_conductor_termnations_at_new_service_panel5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This home owner installation for a new 200A service at an existing house had new service conductor terminations at the new service panel that were not terminated or tightened properly. The three #4/0 aluminum service conductor terminations at the service panel were inserted into the termination lugs without the use of anti-oxidant compound and without being tightened. The termination lu | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Loose_and_improper_conductor_termnations_at_new_service_panel3.png | file://x:/photopub/docs/0000000671/00d31720-29a3-4a28-a7ea-69a82a49a4dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b14d4a3b_c761_4840_9a89_710631726a97
ELIN-913911-2017 | EL-586061-2017 | 9/29/2017 10:48:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Loose_and_improper_conductor_termnations_at_new_service_panel1.png,Loose_and_improper_conductor_termnations_at_new_service_panel2.png,Loose_and_improper_conductor_termnations_at_new_service_panel3.png,Loose_and_improper_conductor_termnations_at_new_service_panel4.png,Loose_and_improper_conductor_termnations_at_new_service_panel5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This home owner installation for a new 200A service at an existing house had new service conductor terminations at the new service panel that were not terminated or tightened properly. The three #4/0 aluminum service conductor terminations at the service panel were inserted into the termination lugs without the use of anti-oxidant compound and without being tightened. The termination lu | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Loose_and_improper_conductor_termnations_at_new_service_panel1.png | file://x:/photopub/docs/0000000671/689dbe07-1bb4-4f33-9ba9-4c75e41342e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b14d4a3b_c761_4840_9a89_710631726a97
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Breakers conductors for heating equipment second floor bathroom energized breakers. Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. Owner was stepping on this in floor heating equipment with owner's sock covered bare feet | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png | file://x:/photopub/docs/0000000674/330826bb-7710-4033-8e79-29343752bea3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png | file://x:/photopub/docs/0000000674/ab36812f-149b-4e2e-a970-5b71e0c5eaeb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
EDOP-924448-2017 | 2048751 | 10/4/2017 1:50:59 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound Deteriorating handrail | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | #Handrail_1.png When the escalator handrail is deteriorating the handrail becomes unsafe | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Handrail_1.png | file://x:/photopub/docs/0000000675/8eeb5c3c-ebfb-4cf8-ae20-159b96190693.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5f8db3f_2f81_46d9_80aa_0a9f2fc1ba43
ELIN-923492-2017 | EL-592706-2017 | 10/5/2017 10:45:20 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Residential_receptacles.png The new construction of a residential dwelling includes temporary receptacles installed without GFCI protection, this can lead to both a shock and thermal hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Residential_receptacles.png | file://x:/photopub/docs/0000000675/d548f29e-4613-4af4-a90c-1bef1c439ba6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd86aee6_cc58_49c3_953a_56e65d2e7605
ELIN-923546-2017 | EL-587015-2017 | 10/5/2017 12:09:52 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | #Residential_secondary_ground_installation.png A new residential construction is fed 125 amps 120/240 with underground cable with bonding conductor and has included a secondary grounding installation causing a parallel path for current to flow, this can lead to a shock hazard | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Residential_secondary_ground_installation.png | file://x:/photopub/docs/0000000675/dd7d6149-5b2d-4dfd-960d-bf2478f5b520.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca7cc26a_e7d2_45ec_af4f_0c6aeeb42c8c
ELIN-922906-2017 | EL-570311-2017 | 10/2/2017 4:23:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Plywood_mounting_bracket1.png,Plywood_mounting_bracket2.png At a new recreational property, a new 100amp 240volt 1phase service and distribution equipment was found placed onto a sheet of oversized plywood and not effectively bolted to pole. This can lead to an "Equipment Damage" situation. Pic attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Plywood_mounting_bracket2.png | file://x:/photopub/docs/0000000673/ae5520c1-75c7-4732-ba1a-ef28883f024e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fcc36af_5b00_4e8d_ad2f_5d0015d94000
ELIN-922906-2017 | EL-570311-2017 | 10/2/2017 4:23:22 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | #Plywood_mounting_bracket1.png,Plywood_mounting_bracket2.png At a new recreational property, a new 100amp 240volt 1phase service and distribution equipment was found placed onto a sheet of oversized plywood and not effectively bolted to pole. This can lead to an "Equipment Damage" situation. Pic attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Plywood_mounting_bracket1.png | file://x:/photopub/docs/0000000673/7c3e4abb-d6a7-4612-ba60-1443b7c780ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fcc36af_5b00_4e8d_ad2f_5d0015d94000
EDMA-923130-2017 | ED-492243-2017 | 10/2/2017 9:25:51 PM | ASSESS: ED MA: Acceptance | png | #asFound Fire alarm relays | ED032 | Safety controls/circuits installed incorrectly bypassed or failed . No other system in place that will detect this. (e.g. e-stop button bypassed) Risk Reg ED-02 | 5 | 5 | #Fire_alarm_relays.png The alarm activation relays that causes the elevators to respond to a fire signal was not programmed correctly causing the elevators not to respond at all to fire alarm initiating devices. When a fire activates the alarm alarm initiating device does not respond to cause the elevator to take passengers away from the source of the fire. | 5 | Safety controls/circuits installed incorrectly bypassed or failed . No other system in place that will detect this. (e.g. e-stop button bypassed) Risk Reg ED-02 | Fire_alarm_relays.png | file://x:/photopub/docs/0000000672/087b2a5f-b1b9-46be-b4cf-bbd47cfe8b5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__765c2d02_1b5f_4046_a2d2_ad828ded26c8
EDMA-923131-2017 | ED-492251-2017 | 10/2/2017 9:40:56 PM | ASSESS: ED MA: Acceptance | png | #asFound Fire alarm initiating device relays | ED032 | Safety controls/circuits installed incorrectly bypassed or failed . No other system in place that will detect this. (e.g. e-stop button bypassed) Risk Reg ED-02 | 5 | 5 | #FAID_relays.png The alarm activation relays that causes the elevators to respond to a fire signal was not programmed correctly causing the elevators not to respond at all to fire alarm initiating devices. When a fire activates the alarm alarm initiating device does not respond to cause the elevator to take passengers away from the source of the fire. | 5 | Safety controls/circuits installed incorrectly bypassed or failed . No other system in place that will detect this. (e.g. e-stop button bypassed) Risk Reg ED-02 | FAID_relays.png | file://x:/photopub/docs/0000000672/c805c456-13d4-4522-ae43-ae64843e914b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29868e84_6823_44c9_b8d8_1d265b8eb1f6
AMIN-926039-2017 | AM-595666-2017 | 10/6/2017 6:51:47 PM | ASSESS: AM IN: Inflatable Acceptance | png | #asFound Upper tethers set at angles exceeding 45 degrees | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | #Inflatable_anchoring_inadequate_1.png,Inflatable_anchoring_inadequate_2.png,Inflatable_anchoring_inadequate_3.png Unit is not tethered to manufactures specification. Upper tethers set at angles of more than 45 degrees. Some anchor points are not anchored An inflatable not anchored appropriately risks being toppled in high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Inflatable_anchoring_inadequate_1.png | file://x:/photopub/docs/0000000675/7b699077-5c7c-4b1c-88dc-c877026af2ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c63d24f8_736f_4f41_b32d_34c14e39690b
ELIN-913911-2017 | EL-586061-2017 | 9/29/2017 10:48:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Loose_and_improper_conductor_termnations_at_new_service_panel1.png,Loose_and_improper_conductor_termnations_at_new_service_panel2.png,Loose_and_improper_conductor_termnations_at_new_service_panel3.png,Loose_and_improper_conductor_termnations_at_new_service_panel4.png,Loose_and_improper_conductor_termnations_at_new_service_panel5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This home owner installation for a new 200A service at an existing house had new service conductor terminations at the new service panel that were not terminated or tightened properly. The three #4/0 aluminum service conductor terminations at the service panel were inserted into the termination lugs without the use of anti-oxidant compound and without being tightened. The termination lu | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Loose_and_improper_conductor_termnations_at_new_service_panel2.png | file://x:/photopub/docs/0000000671/4800bc07-a0e4-493f-b15f-1210c632b6a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b14d4a3b_c761_4840_9a89_710631726a97
ELIN-913911-2017 | EL-586061-2017 | 9/29/2017 10:48:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Loose_and_improper_conductor_termnations_at_new_service_panel1.png,Loose_and_improper_conductor_termnations_at_new_service_panel2.png,Loose_and_improper_conductor_termnations_at_new_service_panel3.png,Loose_and_improper_conductor_termnations_at_new_service_panel4.png,Loose_and_improper_conductor_termnations_at_new_service_panel5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This home owner installation for a new 200A service at an existing house had new service conductor terminations at the new service panel that were not terminated or tightened properly. The three #4/0 aluminum service conductor terminations at the service panel were inserted into the termination lugs without the use of anti-oxidant compound and without being tightened. The termination lu | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Loose_and_improper_conductor_termnations_at_new_service_panel4.png | file://x:/photopub/docs/0000000671/3550aaac-8a7c-4a89-ac67-7e82ac2a6c62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b14d4a3b_c761_4840_9a89_710631726a97
ELIN-913911-2017 | EL-586061-2017 | 9/29/2017 10:48:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Loose_and_improper_conductor_termnations_at_new_service_panel1.png,Loose_and_improper_conductor_termnations_at_new_service_panel2.png,Loose_and_improper_conductor_termnations_at_new_service_panel3.png,Loose_and_improper_conductor_termnations_at_new_service_panel4.png,Loose_and_improper_conductor_termnations_at_new_service_panel5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This home owner installation for a new 200A service at an existing house had new service conductor terminations at the new service panel that were not terminated or tightened properly. The three #4/0 aluminum service conductor terminations at the service panel were inserted into the termination lugs without the use of anti-oxidant compound and without being tightened. The termination lu | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Loose_and_improper_conductor_termnations_at_new_service_panel5.png | file://x:/photopub/docs/0000000671/7f87ccd1-f911-47a3-971a-0cdf09288c94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b14d4a3b_c761_4840_9a89_710631726a97
ELIN-924935-2017 | UW-595014-2017 | 10/4/2017 4:30:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #H1.png,H2.png,H3.png,H4.png Energized overhead service conductors were found at grade level. This poses a serious risk of personal injury (shock) and property damage (thermal event) resulting from failure of system protection measures. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | H2.png | file://x:/photopub/docs/0000000674/93b6b8eb-d3e3-4bbd-aea1-e97bd802cc8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da35f194_9723_4c73_b45f_9faa685041d6
ELIN-924935-2017 | UW-595014-2017 | 10/4/2017 4:30:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #H1.png,H2.png,H3.png,H4.png Energized overhead service conductors were found at grade level. This poses a serious risk of personal injury (shock) and property damage (thermal event) resulting from failure of system protection measures. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | H3.png | file://x:/photopub/docs/0000000674/7860da7e-15be-4d41-ab7e-4d74bedb0cb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da35f194_9723_4c73_b45f_9faa685041d6
ELIN-924935-2017 | UW-595014-2017 | 10/4/2017 4:30:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound Service conductors at grade | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #H1.png,H2.png,H3.png,H4.png Energized overhead service conductors were found at grade level. This poses a serious risk of personal injury (shock) and property damage (thermal event) resulting from failure of system protection measures. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | H4.png | file://x:/photopub/docs/0000000674/0d3c6d46-5e47-493f-b830-7cbbf501a213.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da35f194_9723_4c73_b45f_9faa685041d6
GAIN-926801-2017 | GA-331019-2016 | 10/6/2017 11:23:04 AM | ASSESS: GA: Final | png | #asFound Furnace missing return air | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Return_air_.png Photo was sent by a licensed contractor, hazard is products of combustion can enter conditioned space from water heater | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Return_air_.png | file://x:/photopub/docs/0000000675/8695a028-c53d-4815-bbec-b4293c6cb2af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d42c3f98_a537_4a3e_97c9_bf746393aadc
ELIN-909179-2017 | EL-570311-2017 | 10/2/2017 2:56:42 PM | ASSESS: EL: Final | png | #asFound | EL338 | Installation of electrical equipment Equipment is not approved for the specific use; specifically, the receptacle is undersized and not adequately protected. | 4 | 4 | #Receptacle_.png At a new recreation property, a 15amp 120volt exterior receptacle was found with an oversized over-current protection breaker in place. This can lead to a "Thermal Effect" condition . Pic attached | 4 | Installation of electrical equipment Equipment is not approved for the specific use; specifically, the receptacle is undersized and not adequately protected. | Receptacle_.png | file://x:/photopub/docs/0000000672/4a70afee-b602-45bf-8a5c-748d4e9450ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a755ea3_108f_4e1d_a5a7_d61802d61663
ELIN-921708-2017 | EL-584932-2017 | 10/2/2017 1:17:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | #Jamaica_TCS.png Service is mounted too high to be readily accessible and not adequately weatherproofed. Service is not safe for connection due to tree interference and point of attachment is installed on wrong side of pole. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Jamaica_TCS.png | file://x:/photopub/docs/0000000672/5324423a-7a78-41e1-af76-332183aea1ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02c2b584_d6d6_484d_b286_e0be0756ba12
GAWP-910491-2017 | GA-530221-2017 | 10/6/2017 9:52:57 AM | ASSESS: GA Work In Progress | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Missing_regulator.png Gas supplied to home is 2 psi, equipment is designed to operate at 7-14" wc, over firing of appliances occurred hen home owner attempted to operate range, extreme burning hazard and possible explosions may result from this missing regulator. | 4 | Appliance regulator not installed, incorrect delivery pressure | Missing_regulator.png | file://x:/photopub/docs/0000000675/b4942fdf-2a90-4742-98f0-7317cd86fd36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbb513f7_ff5d_4ab7_b291_24b1483f325d
ELIN-923677-2017 | EL-591429-2017 | 10/5/2017 8:51:41 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #unfilled_holes_in_back_of_panel.png In a single family dwelling service upgrade a 200 amp 120/240 volt panel board was found to have uncovered openings exposing it to moisture and insect ingress. This could result in the equipment becoming damaged. Picture attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | unfilled_holes_in_back_of_panel.png | file://x:/photopub/docs/0000000674/bc85a33f-302f-4518-9f76-349edfd729cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9414ad77_2962_40e4_84f6_8e71e8aaddb4
ELIN-925485-2017 | EL-592789-2017 | 10/6/2017 1:02:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Lower_receptacle_not_GFCI_protected.png GFCI protection of general use receptacles helps in reducing shock hazards | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Lower_receptacle_not_GFCI_protected.png | file://x:/photopub/docs/0000000675/0984abd9-a08b-4fa8-8d69-478b323c0429.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__193501f4_74c6_4beb_bfde_72f4d5cef0ae
ELIN-920467-2017 | EL-574907-2017 | 10/4/2017 | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #NMSC_in_contact_with_duct.png Non-metallic sheathed cable is required to be installed in locations with an ambient temperature not exceeding 30 Â°C. When the cable is installed adjacent to heating ducts, a 50mm clearance or thermal barrier is required. This is required so that the increased temperature from the heating duct does not cause the cable to exceed the temperature rating of the cable which could lead to insulation breakdown of the conductor. In this installation in a single family dwelling, non-metallic sheathed cable was installed where the cable came in contact with the heating ducts at several locations. When this cable is energized and under load, the conductor insulation could break down and cause a risk of a fire or equipment breakdown. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_in_contact_with_duct.png | file://x:/photopub/docs/0000000674/6c26eb46-9879-4d9b-9fe9-d676eeb7a8f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbf89591_ec3f_4d64_9a58_26d6c34acc24
BPVIN-927425-2017 | BPV-516365-2017 | 9/29/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound Valve installed in the horizontal position and is not a T & P valve | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | #Safety_valve_mounted_incorrectly.png Due to the valve being mounted incorrectly it may fail to function as intended by the manufacturer, and may fail to open at the set pressure or may remain open after relieving a overpressure event. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Safety_valve_mounted_incorrectly.png | file://x:/photopub/docs/0000000675/c225994b-fe06-4616-8b8e-09ce66e743c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__736fd1af_d07a_4069_9401_35cd586dc37e
ELIN-924032-2017 | EL-586365-2017 | 10/4/2017 9:38:37 AM | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | #Q.png An outlet box is not firmly secured to a stud. This outlet box is fed with nonmetallic sheathed cable which the box is hanging from. This is a shock and fire hazard | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Q.png | file://x:/photopub/docs/0000000673/690ac625-f58f-458d-855e-8decc605e8f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8fb0608_06f0_4077_9b05_9c4dfc6aae52
ELHE-923397-2017 | HE-593986-2017 | 10/2/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png,Hazard6.png Overhead communications cable without adequate separation from line voltage wiring creating a potential shock hazard for telecommunication workers. | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hazard6.png | file://x:/photopub/docs/0000000673/de3fad1d-f1fa-4d02-9f42-a83a720292e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2aec50_03a1_4b06_8988_304ee6bf19bf
ELHE-923397-2017 | HE-593986-2017 | 10/2/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png,Hazard6.png Overhead communications cable without adequate separation from line voltage wiring creating a potential shock hazard for telecommunication workers. | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hazard2.png | file://x:/photopub/docs/0000000673/21794b8b-15b8-4c82-b0cc-f97ca98b2182.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2aec50_03a1_4b06_8988_304ee6bf19bf
ELHE-923397-2017 | HE-593986-2017 | 10/2/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png,Hazard6.png Overhead communications cable without adequate separation from line voltage wiring creating a potential shock hazard for telecommunication workers. | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hazard5.png | file://x:/photopub/docs/0000000673/b54ef85e-3315-4bbe-9e1d-f1510a5dc31d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2aec50_03a1_4b06_8988_304ee6bf19bf
BPVOP-923902-2017 | 2271461 | 10/3/2017 2:15:55 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP137 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | 4 | 3 | #Temperature__and_pressure_relief_valve.png Upon assessment of domestic hot water storage (3m long and 1.5m diameter) it is determined that temperature and pressure relief valve set pressure exceeds Maximum Allowable Working Pressure (MAWP) of the vessel. Vessel may be subjected to pressure above MAWP if operating control fails. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.1.1 Safeties will not function - Pressure Relief Device set pressure higher than minimum applicable setting required to provide over pressure protection | Temperature__and_pressure_relief_valve.png | file://x:/photopub/docs/0000000673/66ef8b7a-455e-4683-9428-29fc9f1dbcc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad3e3464_0906_4cf2_9841_2e45b9738693
BPVIN-917499-2017 | BPV-589960-2017 | 9/29/2017 10:21:30 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound PSV outlet header | BP112 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping under size | 3 | 3 | #PSV_outlet_hdr.png 3 relief valve outlet pipes, all 3/4" are dumping into a header also 3/4" in size. Code says the cross sectional area of the header has to equal the sum of the area of all outlet pipes coming into it. If 2 or all 3 valves were to open at once, the header could not handle the flow and a possible overpressure scenario could result. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping under size | PSV_outlet_hdr.png | file://x:/photopub/docs/0000000672/f0868b05-1add-4ccf-9e3c-ae64acae74ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__580c76b1_ee28_40f8_a9f3_64620fb2e6c0
ELIN-922939-2017 | EL-590389-2017 | 10/4/2017 1:01:52 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Unapproved_panel_cover_with_openings_around_main_breaker_.png Panel cover is not the original panel cover and has openings around the main breaker. This condition could result in the occupants coming into accidental contact with energized parts and receiving an electrical shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Unapproved_panel_cover_with_openings_around_main_breaker_.png | file://x:/photopub/docs/0000000674/1df2f8e9-9ba8-4742-8350-272c7a54494f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4bdcf2d_2dc7_4f59_801c_b11162e527af
ELHE-923397-2017 | HE-593986-2017 | 10/2/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png,Hazard6.png Overhead communications cable without adequate separation from line voltage wiring creating a potential shock hazard for telecommunication workers. | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hazard1.png | file://x:/photopub/docs/0000000673/a1674a8b-8d82-4963-8d5f-95130c89ed9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2aec50_03a1_4b06_8988_304ee6bf19bf
ELHE-923397-2017 | HE-593986-2017 | 10/2/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png,Hazard6.png Overhead communications cable without adequate separation from line voltage wiring creating a potential shock hazard for telecommunication workers. | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hazard3.png | file://x:/photopub/docs/0000000673/28b0b7f0-777d-4fc9-aa2f-53d81f1148fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2aec50_03a1_4b06_8988_304ee6bf19bf
ELHE-923397-2017 | HE-593986-2017 | 10/2/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 | #Hazard1.png,Hazard2.png,Hazard3.png,Hazard4.png,Hazard5.png,Hazard6.png Overhead communications cable without adequate separation from line voltage wiring creating a potential shock hazard for telecommunication workers. | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hazard4.png | file://x:/photopub/docs/0000000673/6a250800-77f0-477f-8038-0b74432ccc81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a2aec50_03a1_4b06_8988_304ee6bf19bf
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__7.png | file://x:/photopub/docs/0000000674/83cfd23d-2362-4204-9cb8-6d298cb6f8ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png | file://x:/photopub/docs/0000000674/75bb08ea-acf1-4a64-a3ae-c597a3b10f2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png | file://x:/photopub/docs/0000000674/e7ee7a9e-019c-4d96-b1be-f849fc9fbf76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__8.png | file://x:/photopub/docs/0000000674/d05c37de-297b-4498-861b-3f272d574007.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__1.png | file://x:/photopub/docs/0000000674/9697ffb0-1dc2-4919-b5c8-b5e1baee0181.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_7.png | file://x:/photopub/docs/0000000674/6c871402-095a-485c-bda7-6b9e06350f83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_6.png | file://x:/photopub/docs/0000000674/16fa47dd-9781-4fab-9bf4-7211e6f814df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png | file://x:/photopub/docs/0000000674/a4787be2-03ad-4af2-89e7-b262581232fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png | file://x:/photopub/docs/0000000674/ae629b2b-9cb0-44a6-ae53-4b92e8aa5239.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__2.png | file://x:/photopub/docs/0000000674/60aeebbb-780c-4edd-ad85-7839061af987.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_5.png | file://x:/photopub/docs/0000000674/80c46076-02ca-49d6-9e15-dd5e53c2b7c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
BPVOP-923649-2017 | 3199246 | 10/3/2017 10:48:47 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2006_SRV.png,2006__SRV.png All safety relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve installed in 2006 on a 160psi hot water boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2006_SRV.png | file://x:/photopub/docs/0000000675/705ce646-0b72-4241-a155-9e22e6d38e32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3a445a_1443_4fa3_a2c7_b3aa0426e280
BPVOP-923747-2017 | 3199250 | 10/5/2017 2:09:20 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #SRV_2006.png Maximum service intervals for safety relief valves on hot water storage tanks is every 3 years.I found no record of service or replacement for safety valve installed in 2006 on a 150psi hot water storage tank. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV_2006.png | file://x:/photopub/docs/0000000675/216f33c1-4b55-4400-b74c-16af93f5f8d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bde0b9ae_f5ca_43fd_aa31_967645d9652d
BPVOP-923746-2017 | 3199251 | 10/5/2017 2:37:32 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2006_srv_.png Maximum service intervals for safety relief valves on hot water storage tanks is every 3 years.I found no record of service or replacement for safety valve installed in 2006 on a 150psi hot water storage tank. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2006_srv_.png | file://x:/photopub/docs/0000000675/072895f6-8391-4c93-a00d-a7dfd9861c8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__579edaad_224f_41a6_ae53_4ef3a5cd3524
BPVOP-923651-2017 | 3199247 | 10/3/2017 11:09:32 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2006__SRV.png Maximum service intervals for safety relief valves on hot water boilers operating up to 160psi and 250F is every 6 years.I found no record of service or replacement for safety relief valve installed in 2006 on a 160psi hot water boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2006__SRV.png | file://x:/photopub/docs/0000000675/b00fc694-a347-4884-81d0-40da46a38b0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__889e4830_70e0_4cbd_8fa1_b5c22d7d7edd
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png | file://x:/photopub/docs/0000000674/e6d580ac-7d1e-4a5e-b640-183e0e133de3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_10.png | file://x:/photopub/docs/0000000674/eb9571b4-ce27-41a9-8372-06d769d5b7e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png | file://x:/photopub/docs/0000000674/52129704-a949-4741-841e-817ee904b1f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__3.png | file://x:/photopub/docs/0000000674/e529f5dc-7ea6-49a0-b344-90220ee7e76e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png | file://x:/photopub/docs/0000000674/fa4bcbec-74c8-46ce-9f69-54e5d93a9499.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELIN-911370-2017 | EL-240889-2015 | 10/5/2017 10:26:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #High_Voltge1.png,High_Voltge2.png Concrete encased high-voltage feeders were improperly labeled. It was hazardous because the labelling in place could be painted over, thus concealing the associated risk inside the concrete. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | High_Voltge1.png | file://x:/photopub/docs/0000000674/41f55982-c018-4168-bace-4bd41fd7bf5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3906d141_9f35_4c34_aa10_2d848329be3b
ELIN-911370-2017 | EL-240889-2015 | 10/5/2017 10:26:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #High_Voltge1.png,High_Voltge2.png Concrete encased high-voltage feeders were improperly labeled. It was hazardous because the labelling in place could be painted over, thus concealing the associated risk inside the concrete. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | High_Voltge2.png | file://x:/photopub/docs/0000000674/ad218c18-c88c-466f-b34f-6c0a7631de7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3906d141_9f35_4c34_aa10_2d848329be3b
BPVOP-924103-2017 | 3157862 | 10/5/2017 10:37:59 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Overdue_PRD.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 5 years. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_PRD.png | file://x:/photopub/docs/0000000674/bf2fcb50-78a4-4ae9-8ef2-c480626e6196.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa147f6a_3561_4701_a62a_2c092d51557f
ELHE-920447-2017 | HE-592520-2017 | 9/29/2017 3:49:20 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL294 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #K.png Open holes in panel. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | K.png | file://x:/photopub/docs/0000000671/092af4b8-6dd9-45ec-b8b8-03cd0e283b46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52dc22ff_85d4_443d_8a0f_9b70871394c8
EDRI-924441-2017 | ED-542228-2017 | 10/4/2017 9:36:09 AM | ASSESS: ED RI: Initial | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Missing_hoarding.png Construction hoists require walls built around them in areas workers can access. This hoist did not have a wall built beside it on landing two, leaving workers exposed to the hoist as it drives by. | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Missing_hoarding.png | file://x:/photopub/docs/0000000674/7822d32e-2f07-4b48-a5a5-73c372cdc06e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6789ea28_2f4e_4565_b7c8_1f6555ea5ac6
ELIN-906732-2017 | EL-305792-2015 | 9/27/2017 8:05:25 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #2_x_ranges_fed_with_10_copper.png In a new dwelling 2 50 amp electric ranges were found, one in use and one other incomplete, fed with 30 amp conductors connected to 50 amp circuit breakers. The conductors were rated a maximum of 30 amps, subsequently the circuits were able to be loaded much more than the capacity of the conductors. Damage to equipment, structures, or injury to person can result as a failure to the system in this scenario. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 2_x_ranges_fed_with_10_copper.png | file://x:/photopub/docs/0000000672/7c2c4b02-c197-4b95-898d-6b50816aa7bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1a1f2e1_ba58_4d68_990f_d13024492be7
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png | file://x:/photopub/docs/0000000674/f86feb3a-2f2a-4216-98fc-36258130e909.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_9.png | file://x:/photopub/docs/0000000674/287d6081-4b6e-4392-ad03-343056b04035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELIN-921165-2017 | EL-465951-2016 | 10/2/2017 2:16:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Un_grounded_neutral1.png,Un_grounded_neutral2.png Service neutral has not been grounded for a grounded AC system. Possibility for a high impedance to the ground not maintaining equal potential plane in the event of a fault to ground. Possibility for shock. | 4 | Installation Grounding; conductor is not continuous. | Un_grounded_neutral1.png | file://x:/photopub/docs/0000000672/a2c64d2a-039a-4e52-a0dd-827167a4b4d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b1a55d_bc14_4edd_96f1_4753f74b6029
ELIN-921165-2017 | EL-465951-2016 | 10/2/2017 2:16:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Un_grounded_neutral1.png,Un_grounded_neutral2.png Service neutral has not been grounded for a grounded AC system. Possibility for a high impedance to the ground not maintaining equal potential plane in the event of a fault to ground. Possibility for shock. | 4 | Installation Grounding; conductor is not continuous. | Un_grounded_neutral2.png | file://x:/photopub/docs/0000000672/4e6b82e3-be1a-4b85-ac03-df80ba0036b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b1a55d_bc14_4edd_96f1_4753f74b6029
ELIN-924360-2017 | EL-563119-2017 | 10/5/2017 11:41:12 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Bonding_required.png This assessment found that the metal gas piping is not bonded to ground creating a fire hazard in a fault situation | 3 | Equipment Gas line, cast or water pipe has not been bonded | Bonding_required.png | file://x:/photopub/docs/0000000674/b839a756-2927-404c-871e-18f181a774ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1ab8d1d_9ed0_4320_a141_63db6501254a
ELOP-847240-2017 | EL-538162-2017 | 10/5/2017 2:10:24 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #Tripped_breaker1.png,Tripped_breaker2.png Circuit breaker has tripped repeatedly and may lead to a overheat or fire condition if not addressed. | 3 | Protection and control Loading of distribution equipment exceeded | Tripped_breaker2.png | file://x:/photopub/docs/0000000674/6591bebf-11e1-4650-b74c-805101fe938b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F889741E_AAEB_47BB_B416_2BBBACAE414A
ELOP-847240-2017 | EL-538162-2017 | 10/5/2017 2:10:24 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | #Tripped_breaker1.png,Tripped_breaker2.png Circuit breaker has tripped repeatedly and may lead to a overheat or fire condition if not addressed. | 3 | Protection and control Loading of distribution equipment exceeded | Tripped_breaker1.png | file://x:/photopub/docs/0000000674/52ff6bc5-7890-4eee-9f82-abd450d1ae83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F889741E_AAEB_47BB_B416_2BBBACAE414A
BPVOP-793305-2017 | 2273483 | 9/28/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #ASME_plate_.png During the inspection of a Hot Water Boiler with MAWP of 60 psig was found that there is no Low Water Cutoff Device installed. This can contribute to the failure of the boiler in case of a low water condition. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | ASME_plate_.png | file://x:/photopub/docs/0000000673/8a7a62e5-12da-4e8e-956f-675de2d9693c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da233314_8043_4b7e_a13a_217ac76f22de
BPVOP-786050-2017 | 2258060 | 9/28/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | #Handholes_1.png,Handholes_2.png,Handholes_3.png During the external inspection of a HP Steam Boiler with MAWP of 150 psig heavy corrosion was discovered on the shell metal around the hand holes to the point material was peeling off. This is compromising the pressure boundary which could lead to a uncontrolled high pressure steam release and the failure of the boiler. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | Handholes_2.png | file://x:/photopub/docs/0000000673/9527ef1d-8e25-4c32-8f30-62d14cb540d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__133c161d_bf68_43be_859c_1931e5760795
BPVOP-786050-2017 | 2258060 | 9/28/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | #Handholes_1.png,Handholes_2.png,Handholes_3.png During the external inspection of a HP Steam Boiler with MAWP of 150 psig heavy corrosion was discovered on the shell metal around the hand holes to the point material was peeling off. This is compromising the pressure boundary which could lead to a uncontrolled high pressure steam release and the failure of the boiler. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | Handholes_3.png | file://x:/photopub/docs/0000000673/7ad42d0f-0eed-48c9-8d2b-2cda05d246fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__133c161d_bf68_43be_859c_1931e5760795
BPVOP-786050-2017 | 2258060 | 9/28/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | #Handholes_1.png,Handholes_2.png,Handholes_3.png During the external inspection of a HP Steam Boiler with MAWP of 150 psig heavy corrosion was discovered on the shell metal around the hand holes to the point material was peeling off. This is compromising the pressure boundary which could lead to a uncontrolled high pressure steam release and the failure of the boiler. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | Handholes_1.png | file://x:/photopub/docs/0000000673/f3d9f71b-144b-4919-a4f5-7a80eff6e19f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__133c161d_bf68_43be_859c_1931e5760795
ELIN-919160-2017 | EL-482417-2016 | 10/2/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_under_mobile_home1.png,ACWU_under_mobile_home2.png Service cables are to be run on the outside of the building except when entering to connect to the service panel. The service cable is allowed a maximum of 1.5 meters inside the building unless the cable is encased in minimum 50mm of concrete. This requirement is to reduce the risk of fire because the service cable lacks effective over current protection. In this service cable installation for a mobile home, the armoured cable was installed a total length of 7 m under the home before entering the panel. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_under_mobile_home1.png | file://x:/photopub/docs/0000000673/cff34856-565d-4738-9c84-cbfdc6ed2574.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb7769d7_00b1_4077_ab79_334e33068da3
ELIN-919160-2017 | EL-482417-2016 | 10/2/2017 | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #ACWU_under_mobile_home1.png,ACWU_under_mobile_home2.png Service cables are to be run on the outside of the building except when entering to connect to the service panel. The service cable is allowed a maximum of 1.5 meters inside the building unless the cable is encased in minimum 50mm of concrete. This requirement is to reduce the risk of fire because the service cable lacks effective over current protection. In this service cable installation for a mobile home, the armoured cable was installed a total length of 7 m under the home before entering the panel. When energized, there is a risk of fire hazard inside the dwelling if there was a fault condition on the cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | ACWU_under_mobile_home2.png | file://x:/photopub/docs/0000000673/e700ecab-bfa3-40ba-bed2-28d77ae7b6bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb7769d7_00b1_4077_ab79_334e33068da3
ELHE-923553-2017 | HE-591867-2017 | 10/4/2017 12:48:51 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | #Canopie.png Cables pinched under canopy could cause damage to conductors leading to arcing and risk of fire | 4 | Installation of electrical equipment Fixtures without suitable support. | Canopie.png | file://x:/photopub/docs/0000000674/d8eb07cd-ffc7-4018-842a-66b6fa1168ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e89fced_471f_427c_b27b_73d2dd462c70
GAUP-921361-2017 | UW-592962-2017 | 10/2/2017 9:12:49 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Regulators.png Gas pressure regulator with relief installed outdoors within three feet of a source of ignition. This could lead to a fire or explosion if the regulator were to relief gas through it's vent in an overpressure situation. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Regulators.png | file://x:/photopub/docs/0000000672/bc27ac73-cfce-4d66-814a-65f019a4b68a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8fdc7aa_67fb_44ea_bcb9_084f0935cca1
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat device heat control unit which is faulty and not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setting resulting in space heater being on fully at all times. When electrical equipment such as a thermostat is faulty or damaged and does not work properly as per approved use and specifications of the electrical product, the electrical equipment is a possible electrical fire hazard to people and property. Thermostat is off to lowest heat setting possible and baseboard heater is still full ON and heating and is a fire hazard | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png | file://x:/photopub/docs/0000000673/2bdc33ce-69df-4d60-9e29-dd303bf81ee8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png | file://x:/photopub/docs/0000000673/deba01da-a086-4c29-b4f2-d17685f1f411.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
GAHE-926609-2017 | HE-595904-2017 | 10/6/2017 10:29:40 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_location.png An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device installed in the tank begins to vent, and explosion or fire could occur if the heat pump cycled on simultaneously causing and arc and providing ignition to the propane. | 4 | Ignition sources present with-in minimum distance required | Tank_location.png | file://x:/photopub/docs/0000000675/aec6d455-8ead-436c-98d7-040931cc6b03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0578d033_a4df_4ebd_be86_805dc115458f
ELIN-925901-2017 | EL-568470-2017 | 10/5/2017 1:57:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Service_conduit.png - Service conduit installed in outside wall with no protection, very likely could have a nail go through conduit and hit the BC Hydro conductors. These conductors are unprotected from fuses or breakers in very dangerous if they were to arc within the wood frame wall. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_conduit.png | file://x:/photopub/docs/0000000675/856b50af-cc61-4349-8250-7fc7825f6698.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c335c018_7f3f_430a_b48d_5c741baa8b98
BPVOP-790251-2017 | 2285860 | 9/28/2017 10:25:56 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #ASME_Plate.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years as well as the NDT was not performed as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | ASME_Plate.png | file://x:/photopub/docs/0000000673/0e533e60-6efa-4788-888c-7a295d413bfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1d97b67_07fa_4e9f_b0c3_1995b2e493b1
ELIN-921042-2017 | EL-589696-2017 | 10/3/2017 11:33:38 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #Kitchen_Outlets.png In the new home kitchen area an insufficient amount of 15 or 20 amp 120 volt receptacle locations has been supplied for the counter area. This could result in the use of extension cords in order to use appliances on the working areas, this poses a shock hazard and potential damage to the electrical equipment. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_Outlets.png | file://x:/photopub/docs/0000000673/e3b97283-694b-4b37-88b7-997d434f6523.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2db96937_09bc_4e3b_a596_ce095f514132
ELIN-916221-2017 | EL-456168-2016 | 10/3/2017 4:34:03 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Sewage_pump_out_no_approvals1.png,Sewage_pump_out_no_approvals2.png The installation of the sewage pump-out systems located within 4 meters of fuel pumps on marine docks does not bear any identification labels or approval labels for use in Canada or Hazardous locations, this could lead to equipment damage | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Sewage_pump_out_no_approvals1.png | file://x:/photopub/docs/0000000673/5aca03d3-9338-4893-822d-64aa71ffbeaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c32686e_b585_4d76_a625_c7a7f3728de9
ELIN-916221-2017 | EL-456168-2016 | 10/3/2017 4:34:03 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Sewage_pump_out_no_approvals1.png,Sewage_pump_out_no_approvals2.png The installation of the sewage pump-out systems located within 4 meters of fuel pumps on marine docks does not bear any identification labels or approval labels for use in Canada or Hazardous locations, this could lead to equipment damage | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Sewage_pump_out_no_approvals2.png | file://x:/photopub/docs/0000000673/f51835cc-9db7-45d7-8693-59137e9dccc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c32686e_b585_4d76_a625_c7a7f3728de9
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat device heat control unit which is faulty and not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setting resulting in space heater being on fully at all times. When electrical equipment such as a thermostat is faulty or damaged and does not work properly as per approved use and specifications of the electrical product, the electrical equipment is a possible electrical fire hazard to people and property. Thermostat is off to lowest heat setting possible and baseboard heater is still full ON and heating and is a fire hazard | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png | file://x:/photopub/docs/0000000673/a0774457-d765-4283-b152-a5e752bb89e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat device heat control unit which is faulty and not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setting resulting in space heater being on fully at all times. When electrical equipment such as a thermostat is faulty or damaged and does not work properly as per approved use and specifications of the electrical product, the electrical equipment is a possible electrical fire hazard to people and property. | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png | file://x:/photopub/docs/0000000673/975ba5d8-6faf-48aa-801f-7e26ee4b5c73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
ELIN-921064-2017 | EL-520419-2017 | 10/3/2017 11:40:21 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Light_switch_within_reach_of_bathtub_.png Light switch is within reach of bathtub. This is a possible shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Light_switch_within_reach_of_bathtub_.png | file://x:/photopub/docs/0000000673/b3837b67-8047-44b1-9d19-8054783047d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b540068_f622_49c5_b78e_2386337e3adb
ELIN-921131-2017 | EL-546190-2017 | 10/2/2017 5:13:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL038 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3 | 3 | #Subpanel_beside_Main_Panel.png A new 200 amp 120/240 volt panel fed from a new service has been located in the same building and beside another 100 amp 120/240 volt panel fed from a different service. This poses a shock hazard to persons and potential mechanical damage to the electrical equipment as the two different systems could accidentally be connected to each other. | 3 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | Subpanel_beside_Main_Panel.png | file://x:/photopub/docs/0000000672/26573d65-9a8e-445c-b334-d7f4be84b3f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__979db990_26fd_4131_85ea_01e1fdd732f6
GAIN-900743-2017 | GA-510267-2017 | 10/4/2017 4:13:51 PM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | #Venting_termination.png Unglued venting termination found | 5 | Special venting system not glued or connected as per certified instructions | Venting_termination.png | file://x:/photopub/docs/0000000674/b7afb945-a518-4184-ad31-7270b348b9bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd7e5a08_9307_442e_b9d9_40574872e89c
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png | file://x:/photopub/docs/0000000673/0f23327b-7fc8-4b0e-a6e9-5cf23e26094b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat device heat control unit which is faulty and not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setting resulting in space heater being on fully at all times. When electrical equipment such as a thermostat is faulty or damaged and does not work properly as per approved use and specifications of the electrical product, the electrical equipment is a possible electrical fire hazard to people and property. Thermostat is off to lowest heat setting possible and baseboard heater is still full ON and heating and is a fire hazard | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png | file://x:/photopub/docs/0000000673/38aa6cc9-d51f-4f45-b0d4-aa6daccc548d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png | file://x:/photopub/docs/0000000673/b3d97300-7690-43ad-85aa-51b80d2cc146.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
ELHE-921388-2017 | HE-592862-2017 | 9/29/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL163 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant1.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant2.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant3.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant4.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant5.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant6.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant7.png,Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png Found 240 volt 15 amp 2 pole breaker feeding power to baseboard space heater and its thermostat heating control device which is faulty electrical equipment and is not working properly. The thermostat does not control or shut off power to space heater when thermostat heat setting is at its lowest possible setti | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Space_heater_thermostat_is_damaged_faulty_and_not_working_properly_is_non-compliant8.png | file://x:/photopub/docs/0000000673/fcf69051-c4d5-4c40-aa4d-a0b5a621062e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc3953b_cdc8_4175_a214_609ee2787e11
GAIN-895004-2017 | GA-277974-2015 | 10/2/2017 1:59:36 PM | ASSESS: GA: Final | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Ignition_source.png Propane tank with relief device was found installed next to a heat pump condensing unit. The heat pump creates an arc each time the appliance is cycled on. This would provide a source of ignition if propane started to vent from the relief device and could result in an explosion or fire. | 4 | Ignition sources present with-in minimum distance required | Ignition_source.png | file://x:/photopub/docs/0000000672/14652f61-871e-47d4-8ebe-765505c6393d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f48e5d05_aa3a_44a6_ab9f_4a2b15169f0f
GAIN-895002-2017 | 5339764 | 10/2/2017 1:28:24 PM | ASSESS: GA: Rough-In | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Source_of_ignition_.png Propane tank with relief device was found installed next to a heat pump condensing unit. The heat pump creates an arc each time the appliance is cycled on. This would provide a source of ignition if propane started to vent from the relief device and could result in an explosion or fire. | 4 | Ignition sources present with-in minimum distance required | Source_of_ignition_.png | file://x:/photopub/docs/0000000672/b01f531b-dcc5-49e3-8f8b-57b58546e81a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d99c1b1_3691_4d61_872d_0c79ba729fc5
GAHE-922684-2017 | HE-593593-2017 | 10/2/2017 12:56:26 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound Propane tank with relief device was found installed next to a heat pump condensing unit. The heat pump creates an arc each time the appliance is cycled on. This would provide a source of ignition if propane started to vent from the relief device and could result in an explosion or fire. | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_clearnce.png Propane tank with relief device was found installed next to a heat pump condensing unit. The heat pump creates an arc each time the appliance is cycled on. This would provide a source of ignition if propane started to vent from the relief device and could result in an explosion or fire. | 4 | Ignition sources present with-in minimum distance required | Tank_clearnce.png | file://x:/photopub/docs/0000000672/3417d24a-e662-4c9c-a531-ffe8a209baaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7767a9d3_0f4f_486c_832c_a630175591db
ELIN-924935-2017 | UW-595014-2017 | 10/4/2017 4:30:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | #H1.png,H2.png,H3.png,H4.png Energized overhead service conductors were found at grade level. This poses a serious risk of personal injury (shock) and property damage (thermal event) resulting from failure of system protection measures. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | H1.png | file://x:/photopub/docs/0000000674/e22aa38e-4a67-4960-a5ae-c168c92bd49d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da35f194_9723_4c73_b45f_9faa685041d6
ELIN-923991-2017 | EL-377806-2016 | 10/3/2017 4:37:34 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #System_ground.png At a new addition to an existing lumber mill, a 480volt 100amp transformer was found without a ground conductor installed to the "Y" point of the transformer. This can lead to a "Thermal Effect" condition. Pic attached | 4 | Installation Grounding; conductor is not continuous. | System_ground.png | file://x:/photopub/docs/0000000675/b9e2bc92-d2cc-49b4-a490-ef3071d87ba0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e6746a9_3ebe_42aa_b251_d2a9c2d74a61
ELIN-924598-2017 | EL-479036-2016 | 10/6/2017 12:13:34 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Installation_site.png Plane and specifications must be provided when requested by a Safety Officer to assist in determining Code compliance and overall safety of the installation | 0 | No Created Hazard Identified | Installation_site.png | file://x:/photopub/docs/0000000675/e6fae628-69bd-4388-8e9a-6e8b49fee974.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__564ef8eb_cc54_45b4_a3dc_975499867714
ELIN-923911-2017 | EL-554907-2017 | 10/4/2017 2:02:02 PM | ASSESS: EL: Final | png | #asFound | EL034 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not located as close as practicable to point of conductor entry into building | 3 | 3 | #Service_enclosed_in_wall.png This assessment found that the consumer raceway is enclosed creating a potential fire hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not located as close as practicable to point of conductor entry into building | Service_enclosed_in_wall.png | file://x:/photopub/docs/0000000674/86e19f99-718c-4a5b-a2b6-fc5cf0c4d558.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3349b50e_12a9_4b28_8057_f047fb78f431
ELIN-925072-2017 | EL-595067-2017 | 10/6/2017 9:35:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | #Pic5.png Un-fused consumer service cables are run to the service entrance box greater then 1.5M. The greater the cable length the more opportunity to mechanical damage to consumer service cables. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Pic5.png | file://x:/photopub/docs/0000000675/9017483f-26d2-488f-a541-bf5ff072ddab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b714aa93_87b5_4b53_8040_5169dbad997a
ELIN-911741-2017 | EL-579373-2017 | 10/6/2017 3:14:15 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #No_certification_mark1.png,No_certification_mark2.png Electrical equipment for use in BC must bear evidence of a mark or label of an accredited certification agency recognized by the Standards Council of Canada. During an inspection of a residential dwelling, five 240V / 600W horticultural lights were found installed in a room. No evidence of a certification mark or label could be found on these fixtures. Light fixtures not certified by an certification agency could be a potential fire or shock hazard to persons using these fixtures. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_certification_mark2.png | file://x:/photopub/docs/0000000675/a8412a28-fce9-4ca8-bb40-46b1ffcd8da5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afb7f14c_cde4_486a_899c_882054e13541
ELIN-911741-2017 | EL-579373-2017 | 10/6/2017 3:14:15 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #No_certification_mark1.png,No_certification_mark2.png Electrical equipment for use in BC must bear evidence of a mark or label of an accredited certification agency recognized by the Standards Council of Canada. During an inspection of a residential dwelling, five 240V / 600W horticultural lights were found installed in a room. No evidence of a certification mark or label could be found on these fixtures. Light fixtures not certified by an certification agency could be a potential fire or shock hazard to persons using these fixtures. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_certification_mark1.png | file://x:/photopub/docs/0000000675/d9f1466a-6897-4c28-b419-711b90e7d610.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afb7f14c_cde4_486a_899c_882054e13541
GAHE-926669-2017 | HE-595956-2017 | 10/6/2017 10:33:04 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_condensing_unit.png An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the propane tank relief device begins to vent, an explosion or fire could occur if the heat pump cycled on simultaneously causing an arc and providing a source of ignition to the propane. | 4 | Ignition sources present with-in minimum distance required | Tank_condensing_unit.png | file://x:/photopub/docs/0000000675/99ed361c-cf25-4dd7-ba09-a56886c83785.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b63d61b6_e18e_4466_9c9a_71779e1ba5bf
BPVOP-918529-2017 | 2884336 | 10/6/2017 2:00:28 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_valve_.png A low pressure steam boiler with a maximum allowable working pressure of 15 psig, there was evidence when the safety valve was last serviced or replaced. Potential exists for an incident to occur due to a safety device failing to operate. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_.png | file://x:/photopub/docs/0000000675/ee31ed03-53b1-4932-a161-82641c17d604.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__F700AEFD_8AF0_456D_A101_7ED11D1BC5AB
GAIN-924896-2017 | GA-536010-2017 | 10/6/2017 10:04:22 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent.png The as-found condition is that a single wall type C vent is not installed with the minimum clearance to combustible material. The potential hazard is that the temperature of the flue gas in the type C vent will cause the material to combust, creating a fire hazard. | 3 | Non compliant Type C Vent clearance | Vent.png | file://x:/photopub/docs/0000000675/cd9dcf94-5658-41af-a41e-0ded8bbe7aa4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb6284d9_f450_47e9_b170_2c2da129fefe
ELIN-926087-2017 | EL-590515-2017 | 10/6/2017 7:53:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL323 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 3 | 3 | #Mechanical_protection.png In an existing residential property, a new outbuilding has a s125amp 240volt 1phase supply service feeder cable entering the building without adequate mechanical protection in place. This can lead to an "Equipment Damage" scenario. Pic attached | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Mechanical_protection.png | file://x:/photopub/docs/0000000675/c90c866d-dda0-4a03-b12f-318a7f084ccb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef13813_ee68_4dea_a663_7f210fb44461
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png | file://x:/photopub/docs/0000000674/09881778-6550-4e3f-b27c-cb0205520c6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Breakers conductors for heating equipment second floor bathroom energized breakers. Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. Owner was stepping on this in floor heating equipment with owner's sock covered bare feet | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png | file://x:/photopub/docs/0000000674/c7755c08-2657-402f-9ac3-8bb6b6fd8e0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
GAHE-926807-2017 | HE-596072-2017 | 10/6/2017 1:06:48 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Heatpump_location.png An 80 gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on simultaneously causing an arc and providing ignition to the propane. | 4 | Ignition sources present with-in minimum distance required | Heatpump_location.png | file://x:/photopub/docs/0000000675/40b5a8d0-8d35-450a-a650-0a0cc1d53b6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60857f10_1337_45a2_b76f_c9b90d624872
GAHE-926838-2017 | HE-596085-2017 | 10/6/2017 1:21:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane_.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Propane_.png | file://x:/photopub/docs/0000000675/2bd96639-b602-4b2e-8a03-72841f8418a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d40b2e60_f0ba_49fc_8c86_418bb1fd7ccd
GAHE-926844-2017 | HE-596089-2017 | 10/6/2017 1:33:49 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #AC_condenser.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | AC_condenser.png | file://x:/photopub/docs/0000000675/aecfc32d-ae8e-4781-9f42-1c9999507099.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8a13607_7d90_45ad_adb6_31425f2ac8da
ELIN-922116-2017 | EL-581752-2017 | 10/2/2017 11:59:24 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #Receptacle_spacing.png 15 amp, 120 volt general use receptacles are installed so that along a point of the floor line there is a greater distance of 1.8 meters from the receptacles. This is a thermal issue. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacle_spacing.png | file://x:/photopub/docs/0000000673/73dde8f8-b367-4935-9957-9868f83dd87e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17b16fda_bb87_4c72_a921_54f66fcc0133
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png | file://x:/photopub/docs/0000000674/23b3a011-6391-4ddc-a768-04317e34e8ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_8.png | file://x:/photopub/docs/0000000674/2f3fb090-eb50-4bac-ab04-6215da1f6a90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__4.png | file://x:/photopub/docs/0000000674/204afb20-d12e-4a76-aa8f-27e089b855ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__5.png | file://x:/photopub/docs/0000000674/a8a9f91d-b93d-4632-87ad-e5576b979fbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png | file://x:/photopub/docs/0000000674/7eac2761-58f6-4228-9330-027b73ac9ba4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device__6.png | file://x:/photopub/docs/0000000674/55523ba7-392f-4c84-8623-2925683c8eea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png | file://x:/photopub/docs/0000000674/8d4e3498-4234-4b10-b370-837beec88c01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_4.png | file://x:/photopub/docs/0000000674/fd87c594-95b8-4287-860f-8193a414a193.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png | file://x:/photopub/docs/0000000674/94756b50-0e60-47d2-9665-9dc99b429478.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELHE-923689-2017 | HE-594202-2017 | 10/3/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device3.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device4.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device5.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device6.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device7.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device8.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device9.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device10.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_2.png,Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_3.png,Improper_extension_cord_fixture | 4 | Conductors, Misuse of flexible cords. | Improper_extension_cord_fixture_cord_power_bar_and_multi-outlet_device_1.png | file://x:/photopub/docs/0000000674/8886fab4-073a-47d7-afcc-0f8bbe8f7b78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2808becc_b545_4b41_a69c_5f723369ac4a
ELIN-923582-2017 | EL-236306-2015 | 10/4/2017 12:41:04 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #GFCI_required_by_sink.png This assessment found that no GFCI protection within 1m of a sink, creating a shock hazard | 3 | Conductors Equipment is not approved for the specific use. | GFCI_required_by_sink.png | file://x:/photopub/docs/0000000674/97b7c54b-ce29-44e3-8f50-45b2027b6c81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66fb1ea5_6a5e_4a99_86ed_f3630e6b83be
GAHE-926978-2017 | HE-596200-2017 | 10/6/2017 2:31:49 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane_.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Propane_.png | file://x:/photopub/docs/0000000675/76cd5ab0-6db1-4410-a4f2-15fafa9e20a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b93380b_c81d_4381_9939_a6f722178d98
GAHE-926979-2017 | HE-596203-2017 | 10/6/2017 4:14:01 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Condenser_.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Condenser_.png | file://x:/photopub/docs/0000000675/c914d176-113e-469b-80c2-f6e3fd62ba1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7708a9c_58fd_4ba3_b857_60a13601e0f1
ELOP-805835-2017 | EL-520090-2017 | 10/4/2017 5:49:19 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL187 | General Construction Outdoor: inadequate clearances. | 3 | 3 | #Seaton2.png The code requires that dielectric liquid filled transformers be installed a minimum of 6 meters from combustible material. This prevents combustible material from combusting during a fault or overload. This transformer is installed near combustable material and could be a fire hazard. | 3 | General Construction Outdoor: inadequate clearances. | Seaton2.png | file://x:/photopub/docs/0000000676/acb357d9-bcc6-4226-be0b-b931f6ec8f6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__DDD04E0E_E738_49C6_BE72_8D409ACAEE64
BPVIN-925489-2017 | UW-595288-2017 | 10/5/2017 | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 | #Safety_relief_mounting_.png Observed Safety Relief Valve mounted in the horizontal position. | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Safety_relief_mounting_.png | file://x:/photopub/docs/0000000675/62657522-1ba3-4839-b31c-16c216b351f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57ad13f1_a738_4eb2_b1dd_ec0172aa4e60
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. Owner was stepping on this in floor heating equipment with owner's sock covered bare feet | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png | file://x:/photopub/docs/0000000674/993eb2eb-c82b-49ac-ac9d-6a38ed73d3b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png | file://x:/photopub/docs/0000000674/9d78fa02-c9c5-4534-bfe6-9d1ede6ecf7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
ELHE-924736-2017 | HE-594876-2017 | 10/4/2017 12:22:52 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Bottom_of_panel_is_rusty.png There is evidence of panel having been wet. This compromises the overcurrent protection and is a possible shock/fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Bottom_of_panel_is_rusty.png | file://x:/photopub/docs/0000000674/ea92ed80-a48d-4c99-9c28-e64aee5471e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8408f0ca_0988_4c92_ae92_939dd464e5ca
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Breakers conductors for heating equipment second floor bathroom energized breakers. Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. Owner was stepping on this in floor heating equipment with owner's sock covered bare feet | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png | file://x:/photopub/docs/0000000674/b62de352-262c-459d-a45b-2cd069e960f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
ELIN-919967-2017 | EL-505487-2017 | 10/5/2017 2:38:33 PM | ASSESS: EL: Final | png | #asFound Found 240 volt branch circuit conductors for space heating equipment are connected to branch circuit breakers of which breakers may be turned on and energized for load end electrical equipment. The load end of the above electrical equipment have exposed conductors that are not contained in electrical equipment enclosures and are not completed electrical work for all electrical equipment. When 240 volt conductors are exposed and could become energized, the electrical equipment is a possible electrical fire or shock hazard to people and property. Owner was stepping on this in floor heating equipment with owner's sock covered bare feet | EL308 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers5.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers6.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers7.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers9.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers12.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers13.png,Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers14.png Found 240 volt branch circuit conductors for in-floor space heating cable se | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Non-compliances_as_all_electrical_equipment_is_not_completed_work_and_is_connected_to_energized_circuit_breakers8.png | file://x:/photopub/docs/0000000674/17012a79-71be-437d-bd95-6112f3129fa2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac8daeb3_54ed_419e_8941_5ea194e859d2
GAIN-926024-2017 | GA-515116-2017 | 10/6/2017 10:26:30 AM | ASSESS: GA: Final | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | #Notinterlocked.png The as found condition is there was no interlock between the boiler safety circuit and mechanically supplied combustion air. The as found hazard is if the mechanical air supply fails , operation of the boilers could depressurize the room and lead to products of combustion being drawn back into the structure. | 3 | Mechanical Air/ventilation supply present, missing interlock | Notinterlocked.png | file://x:/photopub/docs/0000000675/766dd6bc-7c1d-4fa7-a265-78b4ca955d93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc18b8b6_abdb_4247_b196_4b6ff97c7e1a
ELIN-881966-2017 | EL-566788-2017 | 10/6/2017 11:54:34 AM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #NMD90_not_terminated_within_an_outlet_box.png 15 amp, 120 volt branch circuit wiring is not terminated within a box. This is a thermal issue. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | NMD90_not_terminated_within_an_outlet_box.png | file://x:/photopub/docs/0000000676/654951f0-fda7-4172-88f1-a1ae96e128ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a798d560_e1e7_4b16_a3db_369078c69b03
ELIN-924562-2017 | EL-546715-2017 | 10/5/2017 11:36:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #Ground_terminated_to_enclosure.png 200 amp, 120/240 volt underground dual meter base has the ground conductor terminated within meter base. Ground conductor is not terminated on neutral conductor. This could cause equipment damage. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_terminated_to_enclosure.png | file://x:/photopub/docs/0000000676/abd53734-4715-4786-bfe8-bdb63150a78f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cec67b1b_7d4e_46c8_8522_0721ee884b3a
GAHE-931378-2017 | HE-598403-2017 | 10/16/2017 3:09:47 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | #Canwest_tank.png Propane tank installed beside building, 10 foot clearance requirement not met. Clearance required in event of a propane leak or fire to reduce exposure. | 3 | Clearance to combustibles not maintained | Canwest_tank.png | file://x:/photopub/docs/0000000679/6f22c3e1-4fae-4243-827e-df83b29963c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d1ea10d_44d1_4fab_bbf7_f46d38e2aa5e
ELIN-908336-2017 | EL-575919-2017 | 10/6/2017 11:17:59 AM | ASSESS: EL: Final | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | #Receptacle_with_reverse_polarity.png 15 amp, 120 volt general use receptacles has the polarity reversed. This is a thermal issue. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Receptacle_with_reverse_polarity.png | file://x:/photopub/docs/0000000676/4836fea2-43a0-48cb-909a-f2b331ecfdbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6381d52_4564_4147_8e76_532ac3dc7466
GAHE-931377-2017 | HE-598402-2017 | 10/16/2017 1:26:31 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | #Tank_adjacent.png Propane tank installed adjacent to mobile home and 10 foot clearance not met. In event of fire or leak, could be too close to building | 3 | Clearance to combustibles not maintained | Tank_adjacent.png | file://x:/photopub/docs/0000000679/ee390973-9cc6-4e8c-b837-4560fb012580.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9da1ba4a_2bd3_403e_abbf_141345eb7d72
BPVOP-924042-2017 | BPV-153620-2014 | 10/3/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #SV.png During the external inspection of a HP Steam Boiler with MAWP of 150 psig, it was discovered that the Safety Valve was leaking from the drain hole. This can lead to malfunctioning of the Safety Valve and the failure to protect the boiler in case of an overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | SV.png | file://x:/photopub/docs/0000000676/8af1e6c7-1131-4f87-8532-e4f6e328d85e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9be32d88_9836_403e_82c7_527e38ba5f59
BPVOP-928475-2017 | 4149140 | 10/3/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #Flow_switch1.png,Flow_switch2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the flow switch has signs of heavy leakage. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Flow_switch1.png | file://x:/photopub/docs/0000000676/bc9e541c-d2ea-4e85-94b0-1e26ac3f5cea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__756511f9_e65f_468b_98c0_b4afec27e57c
BPVOP-928475-2017 | 4149140 | 10/3/2017 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #Flow_switch1.png,Flow_switch2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the flow switch has signs of heavy leakage. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Flow_switch2.png | file://x:/photopub/docs/0000000676/f3afa86e-39a9-4132-84f9-9f6a70110f1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__756511f9_e65f_468b_98c0_b4afec27e57c
BPVOP-923986-2017 | BPV-153619-2014 | 10/3/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #Overall.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 160 psig, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Overall.png | file://x:/photopub/docs/0000000676/c8faa087-ca05-4713-ad66-b0e3a75452f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__463fac44_811f_4082_a476_c34cb1bee4af
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment4.png | file://x:/photopub/docs/0000000676/209920d1-9c70-4ac5-914c-7fad1aeeefff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment11.png | file://x:/photopub/docs/0000000676/febd7003-5089-4f4f-b4a9-3c38344e3952.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment10.png | file://x:/photopub/docs/0000000676/fa824e92-9cb7-4c28-b667-5a2038dbdebe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment8.png | file://x:/photopub/docs/0000000676/b75abdf1-099e-4864-a6ac-488495d796ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment1.png | file://x:/photopub/docs/0000000676/044ea57e-9aba-483e-8db1-7dc38ca07dd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment5.png | file://x:/photopub/docs/0000000676/484d2ba4-cfba-4dd1-a244-d07533c302bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_6.png | file://x:/photopub/docs/0000000676/006580d9-4b7b-4bfe-a5c4-2a722f6f6c18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment9.png | file://x:/photopub/docs/0000000676/206550c2-4f37-4275-93b8-eabcf93f59aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment2.png | file://x:/photopub/docs/0000000676/682b85f9-d0c8-4b75-b4a5-d532af034219.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_1.png | file://x:/photopub/docs/0000000676/e1e6060b-4761-48ee-a286-d6d640b1b22f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
GAIN-924896-2017 | GA-536010-2017 | 10/6/2017 10:04:22 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent.png The as-found condition is that a single wall type C vent is not installed with the minimum clearance to combustible material. The potential hazard is that the temperature of the flue gas in the type C vent will cause the material to combust, creating a fire hazard. | 3 | Non compliant Type C Vent clearance | Vent.png | file://x:/photopub/docs/0000000676/c5d91d1a-bb08-4817-9ad1-cea596d653ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb6284d9_f450_47e9_b170_2c2da129fefe
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_11.png | file://x:/photopub/docs/0000000676/92003242-330c-4625-bdb3-0673a32e0514.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_10.png | file://x:/photopub/docs/0000000676/65631d34-1dc0-4557-bc41-a2bb054c32fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_4.png | file://x:/photopub/docs/0000000676/29873967-dce1-45ab-b05e-9f9df1b7ced7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_5.png | file://x:/photopub/docs/0000000676/eddc3781-cd5f-4a91-8982-605c1d75d50e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_8.png | file://x:/photopub/docs/0000000676/04f61f9a-d378-48ec-965c-73c16f25cede.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_9.png | file://x:/photopub/docs/0000000676/5243ff94-9840-4bbb-9338-5e2bb7ebd25d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_3.png | file://x:/photopub/docs/0000000676/0d69a8d9-3612-46c7-956d-29c6cb3ff277.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment3.png | file://x:/photopub/docs/0000000676/0b8a2a58-140f-4b78-8771-ec3bfbecd980.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_7.png | file://x:/photopub/docs/0000000676/011ad068-9491-459c-9bf6-7b029fc03bd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment7.png | file://x:/photopub/docs/0000000676/b4ecc3b2-80c5-4d56-b136-caba92bb87af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
ELIN-928336-2017 | EL-544877-2017 | 10/10/2017 5:50:21 PM | ASSESS: EL: Final | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #HV_unit_sub_1.png,HV_unit_sub_2.png,HV_unit_sub_3.png,HV_unit_sub_4.png,HV_unit_sub_5.png,HV_unit_sub_6.png,HV_unit_sub_7.png,HV_unit_sub_8.png,HV_unit_sub_9.png,HV_unit_sub_10.png,HV_unit_sub_11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This is a potential shock, arc flash, and fire hazard if the equipment fails catastrophically and needs to be co | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | HV_unit_sub_2.png | file://x:/photopub/docs/0000000676/c34388ac-b066-44f8-b2e3-83568acb2a83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067b4b45_a7e9_4962_95bc_883fa8a41e5e
ELOP-922841-2017 | EL-057475-2013 | 10/10/2017 5:28:56 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL303 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | 5 | 5 | #High_voltage_equipment1.png,High_voltage_equipment2.png,High_voltage_equipment3.png,High_voltage_equipment4.png,High_voltage_equipment5.png,High_voltage_equipment6.png,High_voltage_equipment7.png,High_voltage_equipment8.png,High_voltage_equipment9.png,High_voltage_equipment10.png,High_voltage_equipment11.png High voltage equipment is required to be installed in such a manner that the equipment will not have the internal components subject to moisture, dust or other contaminants. This is required to prevent the equipment from getting corroded and dirty which can cause high voltage tracking over insulators and line to ground or line to line electrical faults. This installation at a grocery store has a 25KV 1000KVA high voltage outdoor unit substation that is exhibiting audible crackling and hissing sounds from within the equipment load break switch. This equipment has had moisture, corrosion, and contamination problems in the past which have caused equipment failure due to an electrical fault to ground. This | 5 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, continued use is not authorized. | High_voltage_equipment6.png | file://x:/photopub/docs/0000000676/d8564c39-f663-434f-be3b-57d1b5e5f177.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24a5ce85_d019_47da_b9a5_81aaefb7d797
BPVOP-923649-2017 | 3199246 | 10/3/2017 10:48:47 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2006_SRV.png,2006__SRV.png All safety relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve installed in 2006 on a 160psi hot water boiler. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2006__SRV.png | file://x:/photopub/docs/0000000676/52a69e64-3864-434e-aaa6-f88a13e11cac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f3a445a_1443_4fa3_a2c7_b3aa0426e280
GAIN-933372-2017 | GA-514572-2017 | 10/17/2017 1:57:07 PM | ASSESS: GA: Final | JPG | #asFound | GA088 | Relief style regulator/device allowed to vent within building/confined space | 5 | 5 | #IMG_0984.JPG A gas pressure regulator with an internal overpressure relief device was installed in the mechanical room of an elementary school. If the regulator failed and the downstream gas pressure exceeded the set point of the internal relief device the regulator would vent out the excess gas through the vent opening and into the mechanical room. The mechanical room contains three gas fuelled appliance which draw their air from the room. If enough gas was to escape the gas appliances could become a source of ignition and cause a fire or explosion. | 5 | Relief style regulator/device allowed to vent within building/confined space | IMG_0984.JPG | file://x:/photopub/docs/0000000680/743202e7-8972-477a-9857-db6bace43982.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c692454_0f9b_4923_98a2_cb230f102d5f
GAHE-935246-2017 | HE-600441-2017 | 10/17/2017 2:36:45 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank_relief.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Tank_relief.png | file://x:/photopub/docs/0000000680/d0ecb981-466a-43fa-9797-4692d820d073.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ff849ae_cde0_4a97_8c9d_eecac77b7341
GAHE-935261-2017 | HE-600453-2017 | 10/17/2017 2:56:02 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane__relief.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Propane__relief.png | file://x:/photopub/docs/0000000680/4b7ea318-9643-4bb1-ab49-4cbe498a02ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fff07f03_3dfc_4778_9d2d_94c3ace951e0
BPVOP-934954-2017 | 2268223 | 10/17/2017 10:46:18 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #Leaky_safety_valve.png Upon assessment of low pressure steam boiler with 30 square meters of heating surface, it is determined that safety valve is leaking. Leaky safety may result in complete failure of safety valve with likelihood of severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leaky_safety_valve.png | file://x:/photopub/docs/0000000680/2c5ed6f7-8375-4328-a8c8-b1f93039b35e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33b441af_043b_48e2_b5a7_fa10cf9a0c4a
GAIN-895010-2017 | GA-391254-2016 | 10/17/2017 10:34:58 AM | ASSESS: GA: Final | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Tank.png | file://x:/photopub/docs/0000000680/19f7d889-e22c-4f00-b444-93d73d72f485.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e798dae_80b2_4549_8b7d_bb1e16bc10bb
ELIN-932925-2017 | EL-567204-2017 | 10/16/2017 10:56:14 AM | ASSESS: EL: Final | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 2 | 3 | #Grounding_connction.png Loose system grounding wire | 2 | Continuity Bonding; conductor is not properly sized. | Grounding_connction.png | file://x:/photopub/docs/0000000680/1621bdf0-0680-45ba-b980-45bed2d33111.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfeddb01_6bdf_46b6_8483_940767b1de34
ELHE-924919-2017 | HE-594993-2017 | 10/10/2017 7:59:09 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | #Feeder_Conductors.png Feeder conductors emerging from the overhead service pipe have degraded enough to expose bare aluminium. It is hazardous because the conductors are exposed & accidental contact may result in shock or fire. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Feeder_Conductors.png | file://x:/photopub/docs/0000000679/f0651f61-de8c-44c7-bf8c-3b7e0f515740.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e70d024_b45a_4362_917e_504a7b93ba12
GAHE-937256-2017 | HE-601490-2017 | 10/19/2017 7:10:42 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | Dual stage regulator and rubber hose installed below liquid valves of propane tanks. This arrangement creates the possibility of liquid migration to inlet of regulator causing damage to regulator and downstream appliances. | 4 | 1st stage regulator installed below container liquid level | Regulator_liquid.png | file://x:/photopub/docs/0000000682/1663cad9-ac0d-459d-8f74-f17bf13c543a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff672ff1_8c94_4532_962a_daf34c75ad6e
EDOP-942705-2017 | 2051003 | 10/25/2017 2:05:49 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED007 | Defects found where the required strength may no longer exist | 5 | 5 | #Cracks_in_steps1.png,Cracks_in_steps2.png Cracks in the metal of the structural portion of the escalator steps were found. If there is a crack that spends it could cause a serious incident. | 4 | Defects found where the required strength may no longer exist | Cracks_in_steps1.png | file://x:/photopub/docs/0000000684/48887823-997f-4860-9e3b-53008c023743.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23a9a431_c10b_4b29_9d66_28d147861759
GAHE-936173-2017 | HE-600984-2017 | 10/18/2017 11:09:30 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Vent.png The as found condition is a stainless steel venting system on a commercial boiler was found with collapsed sections. The as found hazard is collapsed venting due to poor combustion, which can cause the compression fit connections to be compromised possibly subjecting any workers to carbon monoxide toxicity. | 3 | Leaking or failing special venting system (Minor) | Vent.png | file://x:/photopub/docs/0000000681/7771181b-3f45-404b-a89d-0e54004b1103.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e16a7f40_5c61_4d1d_9ed4_8af69e9b03f6
GAUP-931375-2017 | UW-598401-2017 | 10/18/2017 9:14:55 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Underground_g1.png,Underground_g2.png Type G copper installed and buried underground from propane tank to site office. Type G copper not rated for underground use and could be damaged causing no gas flow or a leak releasing uncontrollable propane and cause a fire or explosion causing bodily damage or property damage. | 3 | Non-compliant material/fittings installed | Underground_g1.png | file://x:/photopub/docs/0000000681/c177eb20-47e1-47d5-8570-0f396727715a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93ca4f14_b582_4597_bbd1_fbc482de42b4
GAUP-931375-2017 | UW-598401-2017 | 10/18/2017 9:14:55 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Underground_g1.png,Underground_g2.png Type G copper installed and buried underground from propane tank to site office. Type G copper not rated for underground use and could be damaged causing no gas flow or a leak releasing uncontrollable propane and cause a fire or explosion causing bodily damage or property damage. | 3 | Non-compliant material/fittings installed | Underground_g2.png | file://x:/photopub/docs/0000000681/7dfc3575-1409-4941-8251-cb37b1867662.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93ca4f14_b582_4597_bbd1_fbc482de42b4
ELIN-938802-2017 | EL-399358-2016 | 10/24/2017 10:26:30 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Pump_system1.png,Pump_system2.png,Pump_system3.png The new installation of a submersible pump cable is run in open wall studs and not installed in conduit within the building plus is exposed to mechanical damage. This along with the overcurrent device being oversized is a thermal hazard | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Pump_system1.png | file://x:/photopub/docs/0000000684/0f0bc09f-4c78-470c-b919-2a673aec3ef7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__590274d0_031f_4c1a_8521_dfdd1c6209c5
ELIN-938802-2017 | EL-399358-2016 | 10/24/2017 10:26:30 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Pump_system1.png,Pump_system2.png,Pump_system3.png The new installation of a submersible pump cable is run in open wall studs and not installed in conduit within the building plus is exposed to mechanical damage. This along with the overcurrent device being oversized is a thermal hazard | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Pump_system2.png | file://x:/photopub/docs/0000000684/01104698-d326-4efc-afee-4b668fe15893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__590274d0_031f_4c1a_8521_dfdd1c6209c5
ELIN-938802-2017 | EL-399358-2016 | 10/24/2017 10:26:30 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Pump_system1.png,Pump_system2.png,Pump_system3.png The new installation of a submersible pump cable is run in open wall studs and not installed in conduit within the building plus is exposed to mechanical damage. This along with the overcurrent device being oversized is a thermal hazard | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Pump_system3.png | file://x:/photopub/docs/0000000684/764d3494-6721-4e03-920e-8297bf63b9af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__590274d0_031f_4c1a_8521_dfdd1c6209c5
ELIN-941497-2017 | EL-589087-2017 | 10/25/2017 11:29:00 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Floor_outlets_boxes_typical_of_4.png The new installation of 4x 15 amp 120 volt floor plastic boxes in a wood floor for outlets of a renovated office space does not use the approved floor mounting boxes and this can lead to a thermal hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Floor_outlets_boxes_typical_of_4.png | file://x:/photopub/docs/0000000684/e9ff86f1-797c-4e67-9686-ba7ba80bd216.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07724bc7_db00_4bb5_9f4c_90455cefd620
EDOP-942705-2017 | 2051003 | 10/25/2017 2:05:49 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED007 | Defects found where the required strength may no longer exist | 5 | 5 | #Cracks_in_steps1.png,Cracks_in_steps2.png Cracks in the metal of the structural portion of the escalator steps were found. If there is a crack that spends it could cause a serious incident. | 4 | Defects found where the required strength may no longer exist | Cracks_in_steps2.png | file://x:/photopub/docs/0000000684/8006f9bc-b193-4e10-893a-094746413d94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23a9a431_c10b_4b29_9d66_28d147861759
GAIN-933770-2017 | GA-592042-2017 | 10/18/2017 11:28:35 AM | ASSESS: GA: Final | png | #asFound Gas was detected at location (c) as identified on parts breakdown. | GA153 | Gas leakage at appliance controls | 5 | 5 | #Uptown_boiler_parts_breakdown.png Gas detected at fan intake opening. Gas valve appears to be leaking past shutoff. Risk of fuel accumulating in combustion chamber during off cycle. Risk of fire and or explosion. | 5 | Gas leakage at appliance controls | Uptown_boiler_parts_breakdown.png | file://x:/photopub/docs/0000000681/26c5ed98-3884-4db5-b4b6-080a2248bc27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__165c8778_9817_4e83_a57b_6a124e10b308
GAIN-934979-2017 | GA-600208-2017 | 10/18/2017 11:07:32 AM | ASSESS: GA: Final | png | #asFound | GA064 | Gas leak readily detectable, able to pinpoint and isolate at source | 4 | 4 | #Gas_leak.png Gas line has a audible gas leak downstream of the shutoff within 10 feet to a source of ignition. This could lead to a fire or explosion. | 4 | Gas leak readily detectable, able to pinpoint and isolate at source | Gas_leak.png | file://x:/photopub/docs/0000000681/fc6ed8d0-0f13-4a22-be61-1166a0d8fb29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43d57078_d376_4687_ae81_3d3d6fef3cf7
GAWP-939931-2017 | GA-563366-2017 | 10/23/2017 9:55:54 AM | ASSESS: GA Work In Progress | png | #asFound | GA143 | Open junction box with line voltage not accessible to public | 3 | 3 | #Open_wire_nuts.png,Wirenuts.png Open connections( wire nuts) located in accessible location on the appliance. Risk of accidental contact with energized conductors. Possible shock hazard. | 3 | Open junction box with line voltage not accessible to public | Wirenuts.png | file://x:/photopub/docs/0000000683/9873c973-711c-415c-b36d-31fa50a23e1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83404e20_c71e_42da_b0df_93624a9de14f
ELIN-936239-2017 | EL-601013-2017 | 10/23/2017 3:39:19 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png Exposed conductors, this is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A2.png | file://x:/photopub/docs/0000000683/5c422fe3-6efe-4d3e-8c34-3734f9f7a3cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4a6a1d8_5546_489b_b0d9_c36ba62e3a2b
GAUP-942592-2017 | UW-604354-2017 | 10/25/2017 12:25:13 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Exhaust_and_comb_air_too_close_to_relief.png Venting for a gas furnace is installed within minimum distances of Gas Regulator relief. In colder tempuratures condensation from exhaust fumes could block relief vent for Gas Regulator possible causing an over pressure scenario in piping system. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Exhaust_and_comb_air_too_close_to_relief.png | file://x:/photopub/docs/0000000684/a4fe99c7-8863-4fba-9ef1-4135f7a3d574.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ca07840_20bd_4fb5_aaa2_df38978d59e2
GAUP-935125-2017 | UW-600340-2017 | 10/17/2017 2:34:18 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Regulator.png Regulator vents on a rooftop are not pointing down or terminating above anticipated snow loads. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Regulator.png | file://x:/photopub/docs/0000000681/359633eb-7d01-413a-86a5-35a0e00e1570.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3fbc1c7_d83d_44ce_8fd6_450d67178edc
GAIN-932362-2017 | GA-594948-2017 | 10/18/2017 1:15:32 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Water_heater_vent_1.png Single wall vent connector for water heater passes through the furnace room wall in direct contact with combustible wood 2x4 framing. This could lead to a fire. | 3 | Non compliant Type C Vent clearance | Water_heater_vent_1.png | file://x:/photopub/docs/0000000681/d7a2d15d-15c4-414a-801f-d59edf4a53cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7950b72d_d1ed_4828_a100_b560a33a3de2
GAUP-917367-2017 | UW-590408-2017 | 10/19/2017 11:29:49 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Sidewallterminations1.png,Sidewallterminations2.png,Sidewallterminations3.png | 2 | Side wall vent termination not compliant with installation instructions | Sidewallterminations1.png | file://x:/photopub/docs/0000000682/fdf191c7-6dca-442d-b050-3a411a477d23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0129be9_1900_4a96_919e_17640f62ef0c
GAUP-917367-2017 | UW-590408-2017 | 10/19/2017 11:29:49 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Sidewallterminations1.png,Sidewallterminations2.png,Sidewallterminations3.png | 2 | Side wall vent termination not compliant with installation instructions | Sidewallterminations2.png | file://x:/photopub/docs/0000000682/14605560-d046-45d5-a2ff-4668d81253fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0129be9_1900_4a96_919e_17640f62ef0c
GAIN-917741-2017 | GA-510455-2017 | 10/19/2017 10:00:24 AM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Boiler_vent_1680_hwy33.png,1680hwy331.png,1680hwy332.png,1680hwy333.png Found 4" pvc pipe vent on IBC boiler. Manufacturers instructions clearly state 636 cpvc required. The installed vent material could over heat causing the pipe and joints to fail allowing products of combustion to escape. This could result in loss of property, serious injury, or death. | 3 | Leaking or failing special venting system (Minor) | 1680hwy333.png | file://x:/photopub/docs/0000000682/b129fea4-c1e2-4626-854c-d715ca18264c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a224e7ad_66ae_4820_9a4c_1518dea03f90
GAIN-917741-2017 | GA-510455-2017 | 10/19/2017 10:00:24 AM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Boiler_vent_1680_hwy33.png,1680hwy331.png,1680hwy332.png,1680hwy333.png Found 4" pvc pipe vent on IBC boiler. Manufacturers instructions clearly state 636 cpvc required. The installed vent material could over heat causing the pipe and joints to fail allowing products of combustion to escape. This could result in loss of property, serious injury, or death. | 3 | Leaking or failing special venting system (Minor) | Boiler_vent_1680_hwy33.png | file://x:/photopub/docs/0000000682/7ce8a987-a4a2-4749-93b9-315b0b1a0dbf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a224e7ad_66ae_4820_9a4c_1518dea03f90
GAIN-917741-2017 | GA-510455-2017 | 10/19/2017 10:00:24 AM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Boiler_vent_1680_hwy33.png,1680hwy331.png,1680hwy332.png,1680hwy333.png Found 4" pvc pipe vent on IBC boiler. Manufacturers instructions clearly state 636 cpvc required. The installed vent material could over heat causing the pipe and joints to fail allowing products of combustion to escape. This could result in loss of property, serious injury, or death. | 3 | Leaking or failing special venting system (Minor) | 1680hwy332.png | file://x:/photopub/docs/0000000682/d2629ba6-ec85-493b-a2ed-a68b941579b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a224e7ad_66ae_4820_9a4c_1518dea03f90
GAIN-917741-2017 | GA-510455-2017 | 10/19/2017 10:00:24 AM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | #Boiler_vent_1680_hwy33.png,1680hwy331.png,1680hwy332.png,1680hwy333.png Found 4" pvc pipe vent on IBC boiler. Manufacturers instructions clearly state 636 cpvc required. The installed vent material could over heat causing the pipe and joints to fail allowing products of combustion to escape. This could result in loss of property, serious injury, or death. | 3 | Leaking or failing special venting system (Minor) | 1680hwy331.png | file://x:/photopub/docs/0000000682/0896015a-8270-4e3b-a858-561f6be92a57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a224e7ad_66ae_4820_9a4c_1518dea03f90
GAUP-940251-2017 | UW-602951-2017 | 10/24/2017 12:15:41 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #921_foothill1.png,921_foothill2.png,921_foothill3.png At time of inspection venting tables clearly defined vent too small for appliance, this condition can cause furnace malfunction | 3 | Appliance not installed according to installation instructions | 921_foothill2.png | file://x:/photopub/docs/0000000684/5fa3aa67-a21d-4812-8c8a-e78a914e9111.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b83f6fa8_37b9_408d_af1c_0d15191376c8
GAUP-940251-2017 | UW-602951-2017 | 10/24/2017 12:15:41 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #921_foothill1.png,921_foothill2.png,921_foothill3.png At time of inspection venting tables clearly defined vent too small for appliance, this condition can cause furnace malfunction | 3 | Appliance not installed according to installation instructions | 921_foothill1.png | file://x:/photopub/docs/0000000684/13f8a157-20df-406b-9de4-5b0b520f9a9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b83f6fa8_37b9_408d_af1c_0d15191376c8
GAUP-940251-2017 | UW-602951-2017 | 10/24/2017 12:15:41 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound 3 | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #921_foothill1.png,921_foothill2.png,921_foothill3.png At time of inspection venting tables clearly defined vent too small for appliance, this condition can cause furnace malfunction | 3 | Appliance not installed according to installation instructions | 921_foothill3.png | file://x:/photopub/docs/0000000684/e838acdc-8b21-42dd-a84d-751ae02bf923.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b83f6fa8_37b9_408d_af1c_0d15191376c8
BPVIN-933820-2017 | BPV-598642-2017 | 10/20/2017 12:13:18 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Remote_Shutdown_Switch.png The remote shutdown switch allows the equipment operator to safely shutdown the boilers at a safe distance should the boiler be experiencing major fault conditions such as a pressure boundary failure. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Remote_Shutdown_Switch.png | file://x:/photopub/docs/0000000682/207ede75-369f-42fd-80fb-15008187603f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddcfe433_46b9_439a_a503_22be2baec375
BPVOP-936209-2017 | 4587028 | 10/18/2017 11:17:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #2010_PRV_.png Maximum service intervals for pressure relief valves on pressure vessels is 5 years .I found no record of annual testing or replacement for pressure relief valve installed in 2010 on a 200psi air receiver mounted with machine. Potential exists for a pressure relief valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 2010_PRV_.png | file://x:/photopub/docs/0000000681/8162dfe4-7d4d-4ed5-8219-0d14fdf2def9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f05a694_1b47_406b_89e7_f1c66481b8d3
ELIN-938884-2017 | EL-505487-2017 | 10/24/2017 9:24:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #Hazard.png Bonding conductors of multiple cables are not suitably terminated together which may cause the continuity of the bonding conductors at the splice to become loose. | 3 | Continuity Bonding; method for equipment is not adequate. | Hazard.png | file://x:/photopub/docs/0000000684/f2b65f79-703c-4b31-81a1-5ea346a99ac9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28cb22eb_a98d_453e_9908_730c0785dc38
ELIN-938511-2017 | EL-601907-2017 | 10/24/2017 3:00:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hazard1.png Panelboard is not rated for service entrance which may cause a shock hazard if no protective barrier is there for the un-fused consumer service conductors. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hazard1.png | file://x:/photopub/docs/0000000684/542b65e9-e063-4bea-a824-6738ceba3e7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70d8f501_43a1_4580_a0ca_0886a070bb06
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco11.png | file://x:/photopub/docs/0000000683/631545ac-699c-46a8-b3fe-e85f2ee401ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco15.png | file://x:/photopub/docs/0000000683/4cd3e73f-8878-476e-8d8e-81488a7e3e6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco8.png | file://x:/photopub/docs/0000000683/8d211d3f-a6c5-49f8-9ea3-ab4e6a8bfc57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco9.png | file://x:/photopub/docs/0000000683/abc10487-e2b9-44c1-aedb-2ae4e23b5d4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco2.png | file://x:/photopub/docs/0000000683/d928582e-5ee6-45da-9759-dd42535f717a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco4.png | file://x:/photopub/docs/0000000683/9477b444-3ad7-4004-abeb-3c42d6db4081.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco1.png | file://x:/photopub/docs/0000000683/278a9170-ffc8-483e-be89-f32360611435.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco6.png | file://x:/photopub/docs/0000000683/3e55a052-67e0-4ec8-a6e6-81b99406c8a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco13.png | file://x:/photopub/docs/0000000683/2dd4aeac-bc27-4a65-ae18-c444ed71dba7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco5.png | file://x:/photopub/docs/0000000683/243d095b-0e33-4aeb-bce9-6166700462cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco10.png | file://x:/photopub/docs/0000000683/c90ef855-e9a8-4958-b9a4-d4a02ecd9652.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco14.png | file://x:/photopub/docs/0000000683/0fbd6f76-4027-46d6-a8cd-2461913dcec2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco7.png | file://x:/photopub/docs/0000000683/add01535-0c17-421f-bf45-e9aafc39e928.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco12.png | file://x:/photopub/docs/0000000683/b5f110d5-cf5d-4b94-8c8b-a92e33453216.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
BPVOP-937377-2017 | 2252559 | 10/19/2017 10:44:08 AM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Boiler_tube_sheet_lwco1.png,Boiler_tube_sheet_lwco2.png,Boiler_tube_sheet_lwco3.png,Boiler_tube_sheet_lwco4.png,Boiler_tube_sheet_lwco5.png,Boiler_tube_sheet_lwco6.png,Boiler_tube_sheet_lwco7.png,Boiler_tube_sheet_lwco8.png,Boiler_tube_sheet_lwco9.png,Boiler_tube_sheet_lwco10.png,Boiler_tube_sheet_lwco11.png,Boiler_tube_sheet_lwco12.png,Boiler_tube_sheet_lwco13.png,Boiler_tube_sheet_lwco14.png,Boiler_tube_sheet_lwco15.png Each automatically fired hot water boiler shall have an automatic low-water fuel cutoff with manual reset and shall be so located as to automatically cut off the fuel supply when the surface of the water falls below the safe permissible water level established by the boiler manufacturer. I found that a low water cut-off device on a 30psi hot water boiler failed to stop the boiler fuel combustion process under low water level conditions. This resulted in overheating of the boiler fire tubes and failure to contain pressure and water level in the boiler. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Boiler_tube_sheet_lwco3.png | file://x:/photopub/docs/0000000683/3f4b3320-0588-4062-8179-e9e5241ca61a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94876c1b_7a8f_4353_9869_3f85cf7e6c6a
GAIN-935402-2017 | GA-567410-2017 | 10/20/2017 8:13:00 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Condensate_trap.png Furnace not installed to manufacture instructions. Insufficient service clearance and condensate trap not relocated for horizontal installation. Products of combustion may enter the occupied space due to insufficient water seal in trap. Possible carbon monoxide risk. | 3 | Appliance not installed according to installation instructions | Condensate_trap.png | file://x:/photopub/docs/0000000682/29925ce9-e898-4cbb-aa43-9332276dd75b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d12c5533_7307_462e_98a5_eba47362e62b
GAIN-931891-2017 | GA-585754-2017 | 10/19/2017 12:53:34 PM | ASSESS: GA: Rough-In | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Royal_range_4.png,Royal_range.png Un certified gas range. Not certified to a recognized standard with respects to construction and operation. Possible unsafe appliance. | 3 | Uncertified appliance connected to gas supply but not in service | Royal_range.png | file://x:/photopub/docs/0000000682/a0c9891f-7f3b-486c-a6eb-d5311f3e408c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5ed1e80_6a15_4fcd_986c_54c964640ba8
GAWP-939931-2017 | GA-563366-2017 | 10/23/2017 9:55:54 AM | ASSESS: GA Work In Progress | png | #asFound | GA143 | Open junction box with line voltage not accessible to public | 3 | 3 | #Open_wire_nuts.png,Wirenuts.png Open connections( wire nuts) located in accessible location on the appliance. Risk of accidental contact with energized conductors. Possible shock hazard. | 3 | Open junction box with line voltage not accessible to public | Open_wire_nuts.png | file://x:/photopub/docs/0000000683/a6101f65-b8a4-45be-9fbe-ba20bb1d5168.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83404e20_c71e_42da_b0df_93624a9de14f
GAHE-940099-2017 | HE-598640-2017 | 10/23/2017 11:48:42 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | #Solitudes.png Fittings inside the living space of a fifth wheel trailer, propane leak can occur causing fire and or explosion | 3 | Non-certified appliance connector | Solitudes.png | file://x:/photopub/docs/0000000683/f88754d0-0aee-446f-8831-aa02f548b996.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f4b9269_5954_4b56_ac89_1aed9d79a576
ELIN-936871-2017 | EL-595854-2017 | 10/20/2017 9:36:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | #Hazard.png Circuit breaker is broken this may cause a fire or shock hazard if its function is compromised due to the damage. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Hazard.png | file://x:/photopub/docs/0000000683/19154497-f8bb-455f-b6d3-40cca970253c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24cbca54_0cc9_413b_9354_c4ca208dc315
BPVIN-929854-2017 | BPV-588964-2017 | 10/20/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnect.png | file://x:/photopub/docs/0000000683/c9cb714e-2d82-480d-a651-6a081614c437.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8fb9126_f770_449b_b930_b6c3402c3fc1
GAHE-937465-2017 | HE-601619-2017 | 10/19/2017 11:27:53 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane_tank.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Propane_tank.png | file://x:/photopub/docs/0000000681/849fa220-f070-4d11-97e9-ab32a44ee5a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af2a394d_ee26_4307_952e_15db765a4c6a
ELIN-936665-2017 | EL-601278-2017 | 10/20/2017 4:43:38 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle1.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle2.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle3.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle4.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle5.png Branch circuits are required to be properly sized for the equipment they supply. This is required to ensure the conductors and overcurrent devices are not overloaded during use. This installation at a used mobile home has a 30A 120/240V branch circuit installed for 50A 120/240V range receptacle. A range receptacle requires a minimum 40A rated branch circuit. This is a potential fire hazard if the branch circuit is overloaded and the 30A circuit breaker or branch circuit conductors and terminations are thermally damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle2.png | file://x:/photopub/docs/0000000682/49eeade5-aaa1-4471-a403-3ea7ff8282f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce58a6c_93a0_4b26_8203_ee463e9e2f8a
ELIN-936665-2017 | EL-601278-2017 | 10/20/2017 4:43:38 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle1.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle2.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle3.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle4.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle5.png Branch circuits are required to be properly sized for the equipment they supply. This is required to ensure the conductors and overcurrent devices are not overloaded during use. This installation at a used mobile home has a 30A 120/240V branch circuit installed for 50A 120/240V range receptacle. A range receptacle requires a minimum 40A rated branch circuit. This is a potential fire hazard if the branch circuit is overloaded and the 30A circuit breaker or branch circuit conductors and terminations are thermally damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle4.png | file://x:/photopub/docs/0000000682/09dba456-0936-4002-bba7-7081dbf67226.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce58a6c_93a0_4b26_8203_ee463e9e2f8a
BPVIN-920203-2017 | BPV-589409-2017 | 10/20/2017 11:55:09 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Non_lockable_disconnect_switch.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no lockable disconnect switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Non_lockable_disconnect_switch.png | file://x:/photopub/docs/0000000683/7f2878d1-04fc-4295-8d88-c20cf938e1fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ba1700b_d729_429e_a9ff_726b505fd036
GAHE-937238-2017 | HE-601478-2017 | 10/19/2017 9:16:23 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Propane_relief.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Propane_relief.png | file://x:/photopub/docs/0000000681/28053ae9-feda-4fd8-baeb-460a2402ac89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae024345_ecab_42f3_89a4_43ca09047c8d
GAIN-931891-2017 | GA-585754-2017 | 10/19/2017 12:53:34 PM | ASSESS: GA: Rough-In | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Royal_range_4.png,Royal_range.png Un certified gas range. Not certified to a recognized standard with respects to construction and operation. Possible unsafe appliance. | 3 | Uncertified appliance connected to gas supply but not in service | Royal_range_4.png | file://x:/photopub/docs/0000000682/ddbacd6d-fe98-4710-be8e-c4e44f9705f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5ed1e80_6a15_4fcd_986c_54c964640ba8
GAIN-920947-2017 | GA-528032-2017 | 10/19/2017 10:14:38 AM | ASSESS: GA: Final | png | #asFound aArcadia fireplace 2 | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 3 | #Arcadia_firplace_2.png,Fireplace_3.png Log set installed into masonry firebox with damper not permanently secured in full open position. Products of combustion may not properly vent into the chimney. Risk of Carbon Monoxide entering the occupied space if effective draft is not maintained while appliance is in operation. | 4 | Gas log set installed with damper not permanently secured in open position | Arcadia_firplace_2.png | file://x:/photopub/docs/0000000682/fb08c331-b9df-43fe-8496-0c476e399b78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86212375_3174_40f7_857a_c2a692c07a14
GAIN-920947-2017 | GA-528032-2017 | 10/19/2017 10:14:38 AM | ASSESS: GA: Final | png | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 3 | #Arcadia_firplace_2.png,Fireplace_3.png Log set installed into masonry firebox with damper not permanently secured in full open position. Products of combustion may not properly vent into the chimney. Risk of Carbon Monoxide entering the occupied space if effective draft is not maintained while appliance is in operation. | 4 | Gas log set installed with damper not permanently secured in open position | Fireplace_3.png | file://x:/photopub/docs/0000000682/a2789759-8d76-4c75-931c-85970442ef84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__86212375_3174_40f7_857a_c2a692c07a14
BPVOP-886630-2017 | 2255535 | 10/19/2017 11:43:04 AM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Boiler.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no remote shutdown switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler.png | file://x:/photopub/docs/0000000682/c1e89145-7d85-46a0-9ebe-848ea5e2a298.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__CDC4A910_BCBA_46C9_9508_C1DC09608348
GAIN-929545-2017 | GA-571935-2017 | 10/23/2017 5:21:54 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | #Pietro_limiter.png Pietro Fiotentini 2 psi to inches regulator with vent limiter installed outdoors. Vent limiter not rated for outdoor use and could be blocked and cause malfunction of the regulator and deliver incorrect pressure to the appliance, | 3 | Regulator vent not terminated as per manufacturers instruction | Pietro_limiter.png | file://x:/photopub/docs/0000000684/3263cc63-c4b2-4d96-8919-0aa3d7bd2be0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79f2a2d4_8fff_481d_84e6_a8ff4192c32e
BPVHE-936181-2017 | HE-600985-2017 | 10/18/2017 2:16:36 PM | ASSESS: BPV HE: Hazard Elimination Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Venting1.png,Venting2.png During the inspection of a HP Steam boiler with MAWP of 150 psig I found that the venting is dislodged from the boiler allowing the combustion gases to enter the room freely. This could endanger the lives of any person occupying the area. | 4 | 5.1.0 In service proc/process - Casing leakage | Venting1.png | file://x:/photopub/docs/0000000681/9941ce8c-8874-4cd7-9b52-5898811cff1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2caed50_5899_4c0c_9752_0bdf2a668b12
BPVHE-936181-2017 | HE-600985-2017 | 10/18/2017 2:16:36 PM | ASSESS: BPV HE: Hazard Elimination Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | #Venting1.png,Venting2.png During the inspection of a HP Steam boiler with MAWP of 150 psig I found that the venting is dislodged from the boiler allowing the combustion gases to enter the room freely. This could endanger the lives of any person occupying the area. | 4 | 5.1.0 In service proc/process - Casing leakage | Venting2.png | file://x:/photopub/docs/0000000681/884346d5-86d3-4197-bc5e-718af1338ddc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2caed50_5899_4c0c_9752_0bdf2a668b12
ELIN-936665-2017 | EL-601278-2017 | 10/20/2017 4:43:38 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle1.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle2.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle3.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle4.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle5.png Branch circuits are required to be properly sized for the equipment they supply. This is required to ensure the conductors and overcurrent devices are not overloaded during use. This installation at a used mobile home has a 30A 120/240V branch circuit installed for 50A 120/240V range receptacle. A range receptacle requires a minimum 40A rated branch circuit. This is a potential fire hazard if the branch circuit is overloaded and the 30A circuit breaker or branch circuit conductors and terminations are thermally damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle1.png | file://x:/photopub/docs/0000000682/79c5b2bc-3fed-442d-abef-8c282d5a12c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce58a6c_93a0_4b26_8203_ee463e9e2f8a
ELIN-936665-2017 | EL-601278-2017 | 10/20/2017 4:43:38 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle1.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle2.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle3.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle4.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle5.png Branch circuits are required to be properly sized for the equipment they supply. This is required to ensure the conductors and overcurrent devices are not overloaded during use. This installation at a used mobile home has a 30A 120/240V branch circuit installed for 50A 120/240V range receptacle. A range receptacle requires a minimum 40A rated branch circuit. This is a potential fire hazard if the branch circuit is overloaded and the 30A circuit breaker or branch circuit conductors and terminations are thermally damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle3.png | file://x:/photopub/docs/0000000682/e42f9804-8471-446f-b452-6fd9c21516b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce58a6c_93a0_4b26_8203_ee463e9e2f8a
ELIN-936665-2017 | EL-601278-2017 | 10/20/2017 4:43:38 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle1.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle2.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle3.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle4.png,Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle5.png Branch circuits are required to be properly sized for the equipment they supply. This is required to ensure the conductors and overcurrent devices are not overloaded during use. This installation at a used mobile home has a 30A 120/240V branch circuit installed for 50A 120/240V range receptacle. A range receptacle requires a minimum 40A rated branch circuit. This is a potential fire hazard if the branch circuit is overloaded and the 30A circuit breaker or branch circuit conductors and terminations are thermally damaged. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Used_mobile_home_has_a_30A_120_240V_rated_branch_circuit_for_the_range_receptacle5.png | file://x:/photopub/docs/0000000682/7d963c8a-70a2-4281-973a-7442783f7cca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce58a6c_93a0_4b26_8203_ee463e9e2f8a
ELIN-936239-2017 | EL-601013-2017 | 10/23/2017 3:39:19 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #A1.png,A2.png Exposed conductors, this is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A1.png | file://x:/photopub/docs/0000000683/37e5bf55-cff7-4d75-b89b-8cf6770b1fc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4a6a1d8_5546_489b_b0d9_c36ba62e3a2b
GAIN-942402-2017 | GA-587504-2017 | 10/25/2017 9:54:19 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 4 | #Venting_mobile.png Exhaust and combustion air piping not completed and furnace in operation. Water could enter the furnace burner chamber and flue gasses could recirculate from exhaust into combustion air. Water could damage the burner or furnace and furnace will not work when blocked by snow and the recirculation of exhaust gas could introduce products of combustion into the house. | 5 | Special venting system not glued or connected as per certified instructions | Venting_mobile.png | file://x:/photopub/docs/0000000684/290f84ea-fae2-4772-b1bb-7bea7f602c2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fab4c28a_ccd8_49fa_b85e_45ec34049098
GAUP-917367-2017 | UW-590408-2017 | 10/19/2017 11:29:49 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | #Sidewallterminations1.png,Sidewallterminations2.png,Sidewallterminations3.png | 2 | Side wall vent termination not compliant with installation instructions | Sidewallterminations3.png | file://x:/photopub/docs/0000000682/3cdf1b48-6d83-4517-9342-e7c366da93eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0129be9_1900_4a96_919e_17640f62ef0c
BPVOP-939831-2017 | 2291641 | 10/19/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP013 | 1.0.1 Temp/Pressure ratings not met - Support design inadequate for all loadings | 4 | 4 | #Blowdown_tank_.png On assessment of a blowdown tank pressure vessel, it was determined there was no evidence of any mounting supports installed in consideration of seismic loading. This creates risk to personnel and equipment if the tank became unsupported and ruptured it's hot liquid contents. | 4 | 1.0.1 Temp/Pressure ratings not met - Support design inadequate for all loadings | Blowdown_tank_.png | file://x:/photopub/docs/0000000683/1950352d-1d7a-4885-b16c-a1ba049e4239.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39918716_d4a2_4e60_bc44_09ae975182fb
GAIN-939441-2017 | GA-602001-2017 | 10/25/2017 12:36:36 PM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Water_heater_venting1.png,Water_heater_venting2.png Furnace upgraded to high efficiency, existing single wall chimney capped with duct tape and water heater only appliance ran into masonry chimney with no liner. Products of combustion could enter the residence due to the water heater spilling out of draft hood, causing carbon monoxide poisoning. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Water_heater_venting1.png | file://x:/photopub/docs/0000000684/1d4985a2-5b1d-4b35-b389-bfa4d7d6b9ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076d9aeb_02e7_4700_820e_9df26ee04a88
GAIN-939441-2017 | GA-602001-2017 | 10/25/2017 12:36:36 PM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Water_heater_venting1.png,Water_heater_venting2.png Furnace upgraded to high efficiency, existing single wall chimney capped with duct tape and water heater only appliance ran into masonry chimney with no liner. Products of combustion could enter the residence due to the water heater spilling out of draft hood, causing carbon monoxide poisoning. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Water_heater_venting2.png | file://x:/photopub/docs/0000000684/6a1a1904-d781-4595-a52e-4d4c728d3a6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__076d9aeb_02e7_4700_820e_9df26ee04a88
GAIN-936860-2017 | GA-594051-2017 | 10/25/2017 3:44:11 PM | ASSESS: GA: Rough-In | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Rating_plate.png The as-found condition is that the supply gas pressure serving commercial cooking equipment is in excess of the rated pressure of the appliances. The potential hazard is that the appliances will over-fire and operate in an unsafe manner, creating a risk of fire and explosion. | 4 | Appliance regulator not installed, incorrect delivery pressure | Rating_plate.png | file://x:/photopub/docs/0000000684/176ca5c0-079e-459a-a72c-fc02c13f768b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79ffd0f9_1123_4812_8fdf_6dd54e0bd10e
GAWP-940661-2017 | GA-508672-2017 | 10/23/2017 5:30:42 PM | ASSESS: GA Work In Progress | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #HYBRID_3.png Appliance vent termination located inside of minimum required zone. Failure of the regulator located on the gas meter could result in the release of high pressure gas. Fuel could enter the appliance through the exhaust termination and into the combustion chamber. Risk of fire if a source of ignition was present. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | HYBRID_3.png | file://x:/photopub/docs/0000000683/477f8ae3-7f51-41d6-baa7-039f0a7a9e2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9da3e6b7_70b7_4fe2_a223_de8b8f020a46
BPVOP-805613-2017 | 2302146 | 10/18/2017 11:23:22 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #Safety_Relief_Valve_leaking1.png,Safety_Relief_Valve_leaking2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was leaking significantly.. This can contribute to the failure of the Safety Relief Valve and consequently not protecting the boiler in case of overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Safety_Relief_Valve_leaking2.png | file://x:/photopub/docs/0000000683/b76c0d89-42c4-4146-9f8a-8e6110336b92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1a5f344_35de_47ed_8aed_a1d8ae964233
BPVOP-805613-2017 | 2302146 | 10/18/2017 11:23:22 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | #Safety_Relief_Valve_leaking1.png,Safety_Relief_Valve_leaking2.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was leaking significantly.. This can contribute to the failure of the Safety Relief Valve and consequently not protecting the boiler in case of overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Safety_Relief_Valve_leaking1.png | file://x:/photopub/docs/0000000683/7722eb75-8f13-4855-b9c5-ca995a643f4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1a5f344_35de_47ed_8aed_a1d8ae964233
ELOP-928497-2017 | 432 | 10/23/2017 8:50:24 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL298 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Exposed_busses_on_MCC__2.png In an operating permit assessment of a veneer mill a 480 volt motor control center was found to be missing a cover potentially exposing energized copper busses. At time of assessment this portion of the veneer mill was not energized. This could result in a shock hazard situation. Picture attached. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_busses_on_MCC__2.png | file://x:/photopub/docs/0000000683/389edca0-c764-4f13-828d-42861d8a229a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36a70dfb_a1c1_405f_8dd6_8deaff0c5068
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows6.png | file://x:/photopub/docs/0000000684/64c6a0a8-3247-4359-a60f-fb8f4c73cee7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows3.png | file://x:/photopub/docs/0000000684/19f7dcdd-a8e5-4b50-855d-ec18938b91fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows2.png | file://x:/photopub/docs/0000000684/e5c92a4b-f9d2-403f-ab7f-3e23ae5c159e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows1.png | file://x:/photopub/docs/0000000684/53c778cd-96b7-4995-8773-9cd511bdf628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows4.png | file://x:/photopub/docs/0000000684/60d3f0f1-24ea-49de-b299-e638f9189437.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows5.png | file://x:/photopub/docs/0000000684/322d2202-ea1e-478d-a32a-30219d4afd99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
ELIN-938680-2017 | EL-448415-2016 | 10/24/2017 12:40:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #No_floor_receptacles_in_floor_to_ceiling_windows1.png,No_floor_receptacles_in_floor_to_ceiling_windows2.png,No_floor_receptacles_in_floor_to_ceiling_windows3.png,No_floor_receptacles_in_floor_to_ceiling_windows4.png,No_floor_receptacles_in_floor_to_ceiling_windows5.png,No_floor_receptacles_in_floor_to_ceiling_windows6.png,No_floor_receptacles_in_floor_to_ceiling_windows7.png In a new single family dwelling, general use 15 amp 120 volt receptacles have not been installed in the floor where windows go from floor to ceiling. This could result in a thermal effect condition. Pictures attached. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_floor_receptacles_in_floor_to_ceiling_windows7.png | file://x:/photopub/docs/0000000684/d2ee0f3d-bf28-4865-8162-a78a04dfa565.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d8f80bd_728a_4e83_aafd_2cbd95e4b5cb
GAIN-905070-2017 | GA-569109-2017 | 10/24/2017 11:47:46 AM | ASSESS: GA: Final | png | #asFound | GA100 | Hazards created by exhaust fans | 3 | 3 | #Water_heater_3.png Commercial water heating spilling products of combustion due to space being in negative condition. Products of combustion entering occupied area of building. Risk of Carbon Monoxide | 3 | Hazards created by exhaust fans | Water_heater_3.png | file://x:/photopub/docs/0000000684/239540db-72b7-4575-982b-2989c85df8f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7450156_1eaf_4ebf_9ecb_eacab8bd5049
ELIN-940400-2017 | EL-602096-2017 | 10/24/2017 2:36:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL307 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Panel_entry_.png The installation of a 100 amp 120/240 volt Temporary service located on a pole has the consumer service conduit entering through the top of the enclosure through a separately drilled hole and not through the normal required hub entry. The conduit is not sealed and therefore can allow moisture to enter the main breaker portion of the panelboard, this will lead to an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Panel_entry_.png | file://x:/photopub/docs/0000000684/54c85479-8770-47a7-b0ba-276082396c87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__863bd71c_9294_4a34_b203_2be9c6eca170
ELIN-935098-2017 | EL-596896-2017 | 10/23/2017 2:07:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 3 | 3 | #No_ground_wire_installed.png This assessment found that grounding was not done correctly creating a shock hazard | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_ground_wire_installed.png | file://x:/photopub/docs/0000000683/3125cc0e-4ae3-467e-b47f-5a72f1814dbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__835d319c_8054_402a_a198_db6e47313afd
ELIN-940094-2017 | EL-594922-2017 | 10/26/2017 8:26:07 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Hazard1.png RPVC is tight against sheathing with un-fused conductors inside. While siding and finishing nails and other penetrating device's may puncture the RPVC which may damage the conductors inside. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Hazard1.png | file://x:/photopub/docs/0000000685/35c425cb-d44d-4efa-93b1-8ee7124f0f05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__852ee4e0_2757_4909_b116_b03843adfab2
GAIN-935995-2017 | GA-600628-2017 | 10/24/2017 9:49:17 AM | ASSESS: GA: Rough-In | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #C-vent_clearance_to_combustibles.png Single wall vent connector is installed too close to combustible building materials. This could lead to a fire in the home. | 3 | Non compliant Type C Vent clearance | C-vent_clearance_to_combustibles.png | file://x:/photopub/docs/0000000684/4da96d70-ae39-4b11-8c6c-96dad9ea34e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41ee78b4_4057_4691_95c4_a80aad4f9901
ELIN-943467-2017 | EL-360367-2016 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hazard.png The protective barrier is missing in the load centre exposing energized bussing. This may cause a possible shock hazard to anyone turning on or off the breakers. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hazard.png | file://x:/photopub/docs/0000000685/462979d7-6981-420b-a70d-0bb5db7a3107.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33de0d9b_bc13_4854_be14_3ebae035e106
GAIN-937955-2017 | GA-598433-2017 | 10/26/2017 10:28:34 AM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | #Cast_bushing_.png 1.25" X 1" cast black iron reducing bushing installed on gas piping system. Due to the thin wall and lower strength of cast black iron there is a risk of the bushing cracking. Risk of fuel leak caused by a cracked fitting. | 3 | Non-compliant material/fittings installed | Cast_bushing_.png | file://x:/photopub/docs/0000000685/865c681c-8a20-453d-9bb1-18cec549f4ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4296c6a_3e11_4b13_9d01_660f9b0f3357
GAIN-835194-2017 | GA-499642-2017 | 10/17/2017 11:28:23 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #6to12venting_thnroughtoroof.png Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive. The 12" vent through to the roof termination is oversized for the water where the 6" vent connects to it at the base, no provisions were made to decrease this size. In turn could lead to improper drafting of appliance depending on weather conditions causing improper firing and a potential CO issue. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 6to12venting_thnroughtoroof.png | file://x:/photopub/docs/0000000681/15164e37-ef22-47cf-a1d8-65eb07a24b4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f95eabaf_6f11_443e_b965_925d48608457
GAHE-941837-2017 | HE-603919-2017 | 10/25/2017 11:01:10 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA100 | Hazards created by exhaust fans | 3 | 3 | #Rum_runners.png Flue gas spilling from draft hood due to negative conditions created by exhaust fan. Products of combustion entering occupied space . Risk of exposure to carbon monoxide. | 3 | Hazards created by exhaust fans | Rum_runners.png | file://x:/photopub/docs/0000000684/fd5c894c-8f94-46f0-a93f-2ed276a8ffa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dcfe6ca_fec5_4b9b_9f7a_dbb2868a639d
GAHE-940608-2017 | HE-603197-2017 | 10/23/2017 4:04:47 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Tank.png -An 80 Gallon propane tank was found installed very close to a heat pump condensing unit feeding a residential home. In the event that the relief device begins to vent, an explosion or fire could occur if the heat pump cycled on causing an arc and providing ignition for the propane. | 4 | Ignition sources present with-in minimum distance required | Tank.png | file://x:/photopub/docs/0000000683/ea600158-f4e7-4ab7-a72c-3a8361cd6cc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d3d2e89_2a25_46f2_9dfb_ad96d32a5d2f
BPVOP-949249-2017 | 3117261 | 11/1/2017 4:59:55 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_Relief_Valve.png Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was overdue as per CSA B51. This can contribute to the failure of the boiler safeties. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000689/67ce4275-ac1e-4f66-a825-f217242afd51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__184a3451_17a8_4b07_99f2_5bcd8e18a65d
ELIN-946030-2017 | EL-551671-2017 | 10/31/2017 7:55:07 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | #No_protection_plate_for_consumer_service_cable_and_conduit.png In a new residential single family dwelling the 200 amp 120/240 volt consumer service cable and conduit were found not to have a protection plate installed on the exterior of the residence. This could result in an equipment damage condition. Picture attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | No_protection_plate_for_consumer_service_cable_and_conduit.png | file://x:/photopub/docs/0000000688/6a6c9afa-31b4-4108-a08c-8b2144c4c0e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0da66c8_c0c1_48df_af68_3e0f877ede86
EDOP-440115-2015 | 2045757 | 10/31/2017 | ASSESS: ED OP: RAP | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Skirt_panel_worn.png The skirt panel is located next to the steps on the escalator. If they have a rough surface a shoe can get caught between the step and the skirt causing serious injury. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Skirt_panel_worn.png | file://x:/photopub/docs/0000000689/e016264f-e06e-4207-aea3-23a0ea5973b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__CCD9AB1D_5EB1_4546_9E65_5BF8903CDEA7
EDOP-440116-2015 | 2045758 | 10/31/2017 | ASSESS: ED OP: RAP | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Worn_skirt_panels.png The skirt panel is located next to steps of the escalator. If the skirt panel is worn a shoe can get caught between the step and the skirt panel causing serious injury. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Worn_skirt_panels.png | file://x:/photopub/docs/0000000689/ca0e2443-6074-48b2-99cd-baa6a21d0988.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D1D64A0F_0B5A_4EEF_824C_8993B4C4E1B1
EDOP-440117-2015 | 2045759 | 10/31/2017 | ASSESS: ED OP: RAP | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Worn_skirt_panels1.png The skirt panel is located next to steps of the escalator. If the skirt panel is worn a shoe can get caught between the step and the skirt panel causing serious injury. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Worn_skirt_panels1.png | file://x:/photopub/docs/0000000689/fac77f3c-5f4b-4256-9ecb-2d7dc4d1fd0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22089274_2235_458D_AF2B_4E8B3D568898
ELHE-944891-2017 | HE-606101-2017 | 10/27/2017 2:43:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord.png Under the crawl space of a dwelling this assessment found an extension cord spliced to an underground street light circuit. Extension cord is not approved for this use and may overheat posing a fire hazard. | 4 | Conductors, Misuse of flexible cords. | Extension_cord.png | file://x:/photopub/docs/0000000686/8813e391-3e30-4709-8028-4c1013715271.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3ff3cdc_0b87_4566_8b07_0070450877bf
ELIN-934705-2017 | EL-595124-2017 | 10/26/2017 11:29:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Connection_Point1.png,Connection_Point2.png An overhead 100 amp 120/240 volt Service Connection point to the weatherhead is accessible from persons standing on the ground, this poses a shock hazard and potential mechanical damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Connection_Point1.png | file://x:/photopub/docs/0000000685/53dcad45-a95a-4366-bc15-503d276ccf3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a61a4206_28fc_4658_b53a_d8f2a1090ea2
ELIN-934705-2017 | EL-595124-2017 | 10/26/2017 11:29:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Connection_Point1.png,Connection_Point2.png An overhead 100 amp 120/240 volt Service Connection point to the weatherhead is accessible from persons standing on the ground, this poses a shock hazard and potential mechanical damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Connection_Point2.png | file://x:/photopub/docs/0000000685/3c413839-a6c4-49bb-9c5c-c63e6689cbab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a61a4206_28fc_4658_b53a_d8f2a1090ea2
EDOP-948940-2017 | 4221-0 | 10/30/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | #4221_1.png,4221_2.png,4221_3.png,4221_4.png Hoist cables have stretched below allowable specifications and left unattended may increase a safety hazard. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 4221_4.png | file://x:/photopub/docs/0000000689/187a50f5-3761-409f-85b4-4d110207f429.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06b0992c_c8aa_4cfb_8892_6a6ed0489580
GAHE-943728-2017 | HE-605264-2017 | 10/26/2017 2:29:00 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA065 | Gas leak readily detectable, (strong odor) unable to pin point or isolate, utility/fuel supplier and first responder notification required | 5 | 5 | #Underground_gas_line__damage1.png,Underground_gas_line__damage2.png,Underground_gas_line__damage3.png During the pressure test of an installation of piping to existing undergound gas line a leak in existing pipe was found. Gas line was isolated and checked for leak, multiple locations found. There could be a catastrophic event if the leaking gas line was to catch fire. | 5 | Gas leak readily detectable, (strong odor) unable to pin point or isolate, utility/fuel supplier and first responder notification required | Underground_gas_line__damage1.png | file://x:/photopub/docs/0000000685/ea4bc86e-4798-46bf-84d1-40822570b772.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57dc0529_fe4c_4ea3_9e9f_70143991c2d7
GAHE-943728-2017 | HE-605264-2017 | 10/26/2017 2:29:00 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA065 | Gas leak readily detectable, (strong odor) unable to pin point or isolate, utility/fuel supplier and first responder notification required | 5 | 5 | #Underground_gas_line__damage1.png,Underground_gas_line__damage2.png,Underground_gas_line__damage3.png During the pressure test of an installation of piping to existing undergound gas line a leak in existing pipe was found. Gas line was isolated and checked for leak, multiple locations found. There could be a catastrophic event if the leaking gas line was to catch fire. | 5 | Gas leak readily detectable, (strong odor) unable to pin point or isolate, utility/fuel supplier and first responder notification required | Underground_gas_line__damage3.png | file://x:/photopub/docs/0000000685/b6860049-dc5b-4076-8807-ead13cc730ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57dc0529_fe4c_4ea3_9e9f_70143991c2d7
GAHE-943728-2017 | HE-605264-2017 | 10/26/2017 2:29:00 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA065 | Gas leak readily detectable, (strong odor) unable to pin point or isolate, utility/fuel supplier and first responder notification required | 5 | 5 | #Underground_gas_line__damage1.png,Underground_gas_line__damage2.png,Underground_gas_line__damage3.png During the pressure test of an installation of piping to existing undergound gas line a leak in existing pipe was found. Gas line was isolated and checked for leak, multiple locations found. There could be a catastrophic event if the leaking gas line was to catch fire. | 5 | Gas leak readily detectable, (strong odor) unable to pin point or isolate, utility/fuel supplier and first responder notification required | Underground_gas_line__damage2.png | file://x:/photopub/docs/0000000685/20faac6e-1e14-41f7-824c-4b7cc3e6cef2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57dc0529_fe4c_4ea3_9e9f_70143991c2d7
ELIN-940175-2017 | EL-567932-2017 | 10/30/2017 10:01:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Main_service_switch1.png,Main_service_switch2.png,Main_service_switch3.png The installation of a new 200 amp 120/240 volt service includes a mounting of a meterbase and main fused disconnect beside each other on a pole install with no additional structural installation to help support the fused disconnect mounted in mid air beside the pole. This will eventually lead to weakening of the existing mounting structure and expose the installation to an equipment damage issue. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Main_service_switch2.png | file://x:/photopub/docs/0000000687/e16f937f-2592-4bcb-93cf-a4b2a663d27f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__151f7f24_5daa_4c88_94a7_e354bb816453
ELIN-940175-2017 | EL-567932-2017 | 10/30/2017 10:01:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Main_service_switch1.png,Main_service_switch2.png,Main_service_switch3.png The installation of a new 200 amp 120/240 volt service includes a mounting of a meterbase and main fused disconnect beside each other on a pole install with no additional structural installation to help support the fused disconnect mounted in mid air beside the pole. This will eventually lead to weakening of the existing mounting structure and expose the installation to an equipment damage issue. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Main_service_switch1.png | file://x:/photopub/docs/0000000687/ef2c31bb-d0a8-4ea8-a526-3c3f21877468.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__151f7f24_5daa_4c88_94a7_e354bb816453
ELIN-928288-2017 | EL-275546-2015 | 10/30/2017 10:50:28 AM | ASSESS: EL: Final | png | #asFound | EL304 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | 3 | 3 | #Main_panel.png The 200 amp 120/240 volt main panelboard located in the 'detached and locked shed' does not have a 2" knock out filler installed. This can lead to a shock hazard | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | Main_panel.png | file://x:/photopub/docs/0000000687/faf16b2a-171d-4ffa-a280-a78419e62da7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dad17229_aa08_4c55_baa6_6569120f4242
ELIN-940175-2017 | EL-567932-2017 | 10/30/2017 10:01:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Main_service_switch1.png,Main_service_switch2.png,Main_service_switch3.png The installation of a new 200 amp 120/240 volt service includes a mounting of a meterbase and main fused disconnect beside each other on a pole install with no additional structural installation to help support the fused disconnect mounted in mid air beside the pole. This will eventually lead to weakening of the existing mounting structure and expose the installation to an equipment damage issue. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Main_service_switch3.png | file://x:/photopub/docs/0000000687/e3d4cea6-37c7-4e98-8157-2e7ac57932d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__151f7f24_5daa_4c88_94a7_e354bb816453
BPVIN-947924-2017 | BPV-391970-2016 | 11/2/2017 8:36:58 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | #7.png Safety relief valves are installed in horizontal positions instead of vertical positions. Potential exists for an incident as the Safety relief valves may not functioning because of the wrong installation | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 7.png | file://x:/photopub/docs/0000000689/c7cbfdd2-9aa6-4241-82f6-43133dc0d7e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ffe722db_61cc_4ffe_b761_7726b372eb93
EDOP-948940-2017 | 4221-0 | 10/30/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | #4221_1.png,4221_2.png,4221_3.png,4221_4.png Hoist cables have stretched below allowable specifications and left unattended may increase a safety hazard. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 4221_1.png | file://x:/photopub/docs/0000000689/2ff1531f-7c9a-4876-913e-7ec5e815cf12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06b0992c_c8aa_4cfb_8892_6a6ed0489580
EDOP-948940-2017 | 4221-0 | 10/30/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | #4221_1.png,4221_2.png,4221_3.png,4221_4.png Hoist cables have stretched below allowable specifications and left unattended may increase a safety hazard. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 4221_2.png | file://x:/photopub/docs/0000000689/5f25e7ec-e6ef-4bc6-bc91-bd10bed51d85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06b0992c_c8aa_4cfb_8892_6a6ed0489580
EDOP-948940-2017 | 4221-0 | 10/30/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED003 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 3 | 3 | #4221_1.png,4221_2.png,4221_3.png,4221_4.png Hoist cables have stretched below allowable specifications and left unattended may increase a safety hazard. | 3 | Suspected wear or defects that are; Likely to progress and affects a safety critical component | 4221_3.png | file://x:/photopub/docs/0000000689/e7a8e69a-8074-4f24-9fb7-539e949eafcb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06b0992c_c8aa_4cfb_8892_6a6ed0489580
ELIN-945976-2017 | EL-556738-2017 | 10/31/2017 10:48:22 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL252 | Category 2 Equipment is not approved for the specific use or location. | 3 | 3 | #Too_tight_staple.png Incorrect staples were used (too small) on the wires installed in wood frame construction. It is hazardous because the wire was stapled too tightly creating a potential hot spot which could lead to a fire. | 3 | Category 2 Equipment is not approved for the specific use or location. | Too_tight_staple.png | file://x:/photopub/docs/0000000687/2c5ae37c-c02e-479d-9321-4de7238463f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76241c0e_94f7_4537_9c2d_81c3b183a9bd
ELIN-942610-2017 | EL-536726-2017 | 10/27/2017 1:46:29 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #Expansion_needed.png This assessment found that no expansion joints were used, creating a fire or shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Expansion_needed.png | file://x:/photopub/docs/0000000686/3fb76075-fe9c-428e-b769-8cd02e605608.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63982378_6e23_4cea_9181_074cd5af819e
ELIN-943485-2017 | EL-593729-2017 | 10/27/2017 3:33:22 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Hazard1.png -Energized conductors that are not suitably terminated in a box may cause a shock hazard if grabbed or unintentionally hit. If the wire nut becomes dislodged from the live conductor a greater shock hazard may be present. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Hazard1.png | file://x:/photopub/docs/0000000687/28ad9495-89ef-4049-9e9f-7190420c5c47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a64061d9_b6a0_4632_8ad9_3c18cff49c0d
ELIN-948619-2017 | UW-607913-2017 | 11/1/2017 4:22:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | #A.png Overhead conductors not properly supported or attached. This is a fire and shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | A.png | file://x:/photopub/docs/0000000689/c9fea17a-cdf1-48f4-a601-12697773ad06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94bc05d6_2dae_4f5d_9e16_68c20694c432
GAIN-946441-2017 | GA-603727-2017 | 11/1/2017 9:45:05 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | #Union_leak_4.png Small fuel leak at union for direct fired make up air located outdoors. Gas leaking at union Risk of fire if a source of ignition was available and Lower explosive limit(LEL) was present. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Union_leak_4.png | file://x:/photopub/docs/0000000689/7dfe8651-3aed-4970-8955-a42c14032e8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8bf121a_45f0_4ef8_9550_ce43f21cc81d
ELHE-946390-2017 | HE-606746-2017 | 10/30/2017 11:38:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #Damaged_service1.png,Damaged_service2.png This assessment found that the service was damaged in a storm, putting stress on the service conductors creating a fire and shock hazard | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Damaged_service1.png | file://x:/photopub/docs/0000000687/7fa334da-00e0-4239-809c-6ee99899e34e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5be90269_a629_46ab_97cb_88c4185e837a
ELHE-946348-2017 | HE-606713-2017 | 10/30/2017 11:27:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL301 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Service_conductors_are_exposed1.png,Service_conductors_are_exposed2.png,Service_conductors_are_exposed3.png This assessment found that exposed conductor below the meter base, that creates a fire and shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | Service_conductors_are_exposed3.png | file://x:/photopub/docs/0000000687/0b303396-2315-48c9-afb2-371aaaa454f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce15363_2954_4cda_9974_fb7994d8d2d5
ELHE-946348-2017 | HE-606713-2017 | 10/30/2017 11:27:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL301 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Service_conductors_are_exposed1.png,Service_conductors_are_exposed2.png,Service_conductors_are_exposed3.png This assessment found that exposed conductor below the meter base, that creates a fire and shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | Service_conductors_are_exposed2.png | file://x:/photopub/docs/0000000687/c6f9d4e9-b600-46a5-a659-611c43e74415.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce15363_2954_4cda_9974_fb7994d8d2d5
ELHE-946390-2017 | HE-606746-2017 | 10/30/2017 11:38:15 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | #Damaged_service1.png,Damaged_service2.png This assessment found that the service was damaged in a storm, putting stress on the service conductors creating a fire and shock hazard | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Damaged_service2.png | file://x:/photopub/docs/0000000687/a4fda767-b1ee-4914-a6b1-75bb188907fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5be90269_a629_46ab_97cb_88c4185e837a
ELHE-946348-2017 | HE-606713-2017 | 10/30/2017 11:27:21 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL301 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Service_conductors_are_exposed1.png,Service_conductors_are_exposed2.png,Service_conductors_are_exposed3.png This assessment found that exposed conductor below the meter base, that creates a fire and shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | Service_conductors_are_exposed1.png | file://x:/photopub/docs/0000000687/15fdc69c-d2f9-4b31-b71d-f6e08ef68b18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ce15363_2954_4cda_9974_fb7994d8d2d5
ELHE-947880-2017 | HE-607503-2017 | 10/30/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL302 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, repairs are necessary; Low voltage service equipment has been compromised, continued use is not authorized | 4 | 4 | #Rotten_meter_pole1.png,Rotten_meter_pole2.png,Rotten_meter_pole3.png Meter pole has rotted to the point where it will no longer hold the screws for the support straps of the service conduit. The pole is now a hazard to nearby trailers as it is no longer sound and can come down on top of neighbouring trailers. This could cause structural damage and also pose a risk of electrical shock as the overhead lines are still connected to the pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, repairs are necessary; Low voltage service equipment has been compromised, continued use is not authorized | Rotten_meter_pole3.png | file://x:/photopub/docs/0000000689/6035d9b3-532f-4fe4-bb99-cba09b3a1a43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4097e622_d6bf_43a4_8425_c28f36199092
ELIN-939624-2017 | EL-599748-2017 | 10/25/2017 8:53:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL200 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no procedures. | 5 | 5 | #Meter_with_cut_hydro_tag1.png,Meter_with_cut_hydro_tag2.png,New_200A_panel_installed.png The BC Electrical Code does not allow repairs or alterations to be carried out on energized equipment except where complete disconnection of the equipment is not feasible. This requirement is to protect workers from injury and prevent damage to equipment. During an assessment for a 200A service upgrade to a single family dwelling, the safety officer found that the electrician had removed the existing energized electrical meter to connect the new service conductors in the meter base. The electrician was not authorized by hydro to remove this meter. The energized terminals inside the meter base were a potential shock hazard to the electrician. An electrical arc flash hazard also exists if the meter is removed under load or metal comes in contact with the energized terminals in the meter base. The arc flash has the potential to injure the worker, damage the equipment, and create a fire inside this dwelling. | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no procedures. | New_200A_panel_installed.png | file://x:/photopub/docs/0000000686/4abe903d-1528-4336-9927-77a07aa5d4ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e648fb0d_32fe_4089_815c_2fe413251ee5
ELIN-939624-2017 | EL-599748-2017 | 10/25/2017 8:53:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL200 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no procedures. | 5 | 5 | #Meter_with_cut_hydro_tag1.png,Meter_with_cut_hydro_tag2.png,New_200A_panel_installed.png The BC Electrical Code does not allow repairs or alterations to be carried out on energized equipment except where complete disconnection of the equipment is not feasible. This requirement is to protect workers from injury and prevent damage to equipment. During an assessment for a 200A service upgrade to a single family dwelling, the safety officer found that the electrician had removed the existing energized electrical meter to connect the new service conductors in the meter base. The electrician was not authorized by hydro to remove this meter. The energized terminals inside the meter base were a potential shock hazard to the electrician. An electrical arc flash hazard also exists if the meter is removed under load or metal comes in contact with the energized terminals in the meter base. The arc flash has the potential to injure the worker, damage the equipment, and create a fire inside this dwelling. | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no procedures. | Meter_with_cut_hydro_tag2.png | file://x:/photopub/docs/0000000686/0f049942-6565-47c1-b4bf-f05cb001b308.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e648fb0d_32fe_4089_815c_2fe413251ee5
ELIN-939624-2017 | EL-599748-2017 | 10/25/2017 8:53:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL200 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no procedures. | 5 | 5 | #Meter_with_cut_hydro_tag1.png,Meter_with_cut_hydro_tag2.png,New_200A_panel_installed.png The BC Electrical Code does not allow repairs or alterations to be carried out on energized equipment except where complete disconnection of the equipment is not feasible. This requirement is to protect workers from injury and prevent damage to equipment. During an assessment for a 200A service upgrade to a single family dwelling, the safety officer found that the electrician had removed the existing energized electrical meter to connect the new service conductors in the meter base. The electrician was not authorized by hydro to remove this meter. The energized terminals inside the meter base were a potential shock hazard to the electrician. An electrical arc flash hazard also exists if the meter is removed under load or metal comes in contact with the energized terminals in the meter base. The arc flash has the potential to injure the worker, damage the equipment, and create a fire inside this dwelling. | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no procedures. | Meter_with_cut_hydro_tag1.png | file://x:/photopub/docs/0000000686/fd09221c-f0eb-458a-abcd-6956a3f578c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e648fb0d_32fe_4089_815c_2fe413251ee5
ELIN-812481-2017 | EL-293890-2015 | 10/26/2017 9:01:13 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Temporary_energized_receptacle.png The use of an existing 15 amp 120 volt receptacle on the main floor has metal box laying loose on the floor in an open area, no cover plate, missing knock out filler with NMSC exposed to mechanical damage, this creates a shock and thermal hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Temporary_energized_receptacle.png | file://x:/photopub/docs/0000000686/d731b67c-69bb-4c0e-929d-99d00ff89e3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4424430d_9130_47c5_8cc2_66ec5524a5a9
ELIN-945608-2017 | EL-532835-2017 | 11/1/2017 12:37:55 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material1.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material2.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material3.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material4.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material5.png The front edges of outlet boxes are required to be installed flush with combustible materials. This is required to ensure devices that are installed on outlet boxes are contained within the box and the internal wiring, connections, and devices are not in contact with or otherwise exposed to combustible material. This installation at a new house has an exterior receptacle that is installed on an outlet box that is recessed approximately 4cm back from the combustible wood material around it. This is a potential fire hazard if the receptacle, receptacle terminations, wiring, or circuit connections fail and over heat and the | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material3.png | file://x:/photopub/docs/0000000689/f152fc60-4815-4b99-bafa-c9f85f158969.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__081921fe_0a80_4676_a6ed_5428c6043250
ELIN-945608-2017 | EL-532835-2017 | 11/1/2017 12:37:55 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material1.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material2.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material3.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material4.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material5.png The front edges of outlet boxes are required to be installed flush with combustible materials. This is required to ensure devices that are installed on outlet boxes are contained within the box and the internal wiring, connections, and devices are not in contact with or otherwise exposed to combustible material. This installation at a new house has an exterior receptacle that is installed on an outlet box that is recessed approximately 4cm back from the combustible wood material around it. This is a potential fire hazard if the receptacle, receptacle terminations, wiring, or circuit connections fail and over heat and the | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material4.png | file://x:/photopub/docs/0000000689/eb07d1b2-e022-40d5-81fb-3831e4424ada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__081921fe_0a80_4676_a6ed_5428c6043250
GAIN-930897-2017 | GA-583425-2017 | 10/31/2017 3:34:12 PM | ASSESS: GA: Rough-In | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #Concentric_too_close.png Mechanical air intake for appliances is installed too close gas regulator relief outlet. In an overpressure scenario gas regulator relief will relieve gas and the mechanical air supply can suck gas through intake into appliance causing a possible explosion inside combustion chamber | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Concentric_too_close.png | file://x:/photopub/docs/0000000688/7077d871-b1ee-4f23-8b34-e22dc2f03e9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fb3873d_8f8d_47d9_9712_5488c6266da8
ELIN-945608-2017 | EL-532835-2017 | 11/1/2017 12:37:55 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material1.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material2.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material3.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material4.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material5.png The front edges of outlet boxes are required to be installed flush with combustible materials. This is required to ensure devices that are installed on outlet boxes are contained within the box and the internal wiring, connections, and devices are not in contact with or otherwise exposed to combustible material. This installation at a new house has an exterior receptacle that is installed on an outlet box that is recessed approximately 4cm back from the combustible wood material around it. This is a potential fire hazard if the receptacle, receptacle terminations, wiring, or circuit connections fail and over heat and the | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material2.png | file://x:/photopub/docs/0000000689/7cd1af2a-bad5-423d-b8c4-064b45f0f67d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__081921fe_0a80_4676_a6ed_5428c6043250
ELIN-944615-2017 | UW-605858-2017 | 10/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_panel_in_garage1.png,Existing_panel_in_garage2.png,100A_breaker_bottom_panel.png,Fixtures1.png,Fixtures2.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The existing 100 A, 120/240V, single phase, combination panel had 2 pole 100A, breaker added for a sub-panel for the horticultural operation. The branch wiring for the horticultural lights was also non-compliant. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Existing_panel_in_garage1.png | file://x:/photopub/docs/0000000686/8f49ce56-4344-4535-b392-c516981c0b82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7ca3b1_a121_4c1e_8ddf_f1aad2a3447f
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png | file://x:/photopub/docs/0000000686/269105af-6f5a-4271-9f43-516d151461d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png | file://x:/photopub/docs/0000000686/f3f4b134-b430-4479-926c-bd5986ca4f4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png | file://x:/photopub/docs/0000000686/b11d6015-5984-4816-a1fa-c20d214c71c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943259-2017 | EL-572931-2017 | 10/27/2017 12:47:23 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #F1.png,F2.png Heat pump feeder not terminated. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | F1.png | file://x:/photopub/docs/0000000687/53407861-0124-4dbf-85ca-48fee469386f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c86263e8_73b6_4e0d_bff0_76aed08dd0d0
ELIN-943259-2017 | EL-572931-2017 | 10/27/2017 12:47:23 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #F1.png,F2.png Heat pump feeder not terminated. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | F2.png | file://x:/photopub/docs/0000000687/0894e857-a355-4cac-a6fb-0d2913b88e27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c86263e8_73b6_4e0d_bff0_76aed08dd0d0
ELIN-945376-2017 | EL-486862-2017 | 10/30/2017 11:35:33 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Kitchen_counter_receptacle_beside_sink.png Receptacle beside sink is not gfci protected. GFCI protection is required for receptacles in these locations in order to sense leakage currents that may exist when electrical equipment comes in contact with water. GFCI protection is required to de-energize equipment and avoid electrical shock and fire in the case of a fault. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Kitchen_counter_receptacle_beside_sink.png | file://x:/photopub/docs/0000000687/d86da217-0998-47d1-9cbb-592aa89e7a24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__849d6500_e960_4676_84f5_6570cfcd9420
ELIN-945608-2017 | EL-532835-2017 | 11/1/2017 12:37:55 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material1.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material2.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material3.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material4.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material5.png The front edges of outlet boxes are required to be installed flush with combustible materials. This is required to ensure devices that are installed on outlet boxes are contained within the box and the internal wiring, connections, and devices are not in contact with or otherwise exposed to combustible material. This installation at a new house has an exterior receptacle that is installed on an outlet box that is recessed approximately 4cm back from the combustible wood material around it. This is a potential fire hazard if the receptacle, receptacle terminations, wiring, or circuit connections fail and over heat and the | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material1.png | file://x:/photopub/docs/0000000689/602a255e-d93d-4b29-a2d4-360a5a6b59a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__081921fe_0a80_4676_a6ed_5428c6043250
ELIN-944615-2017 | UW-605858-2017 | 10/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_panel_in_garage1.png,Existing_panel_in_garage2.png,100A_breaker_bottom_panel.png,Fixtures1.png,Fixtures2.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The existing 100 A, 120/240V, single phase, combination panel had 2 pole 100A, breaker added for a sub-panel for the horticultural operation. The branch wiring for the horticultural lights was also non-compliant. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Fixtures1.png | file://x:/photopub/docs/0000000686/b1101e0b-b2ec-421e-a20f-b018dbc04cea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7ca3b1_a121_4c1e_8ddf_f1aad2a3447f
ELIN-944615-2017 | UW-605858-2017 | 10/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_panel_in_garage1.png,Existing_panel_in_garage2.png,100A_breaker_bottom_panel.png,Fixtures1.png,Fixtures2.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The existing 100 A, 120/240V, single phase, combination panel had 2 pole 100A, breaker added for a sub-panel for the horticultural operation. The branch wiring for the horticultural lights was also non-compliant. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Existing_panel_in_garage2.png | file://x:/photopub/docs/0000000686/58185a5b-15d0-463f-97bf-cf276b82f98a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7ca3b1_a121_4c1e_8ddf_f1aad2a3447f
ELIN-944615-2017 | UW-605858-2017 | 10/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_panel_in_garage1.png,Existing_panel_in_garage2.png,100A_breaker_bottom_panel.png,Fixtures1.png,Fixtures2.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The existing 100 A, 120/240V, single phase, combination panel had 2 pole 100A, breaker added for a sub-panel for the horticultural operation. The branch wiring for the horticultural lights was also non-compliant. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 100A_breaker_bottom_panel.png | file://x:/photopub/docs/0000000686/bb9f8cbb-536a-4a9b-9818-bf96696c83d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7ca3b1_a121_4c1e_8ddf_f1aad2a3447f
ELIN-944615-2017 | UW-605858-2017 | 10/25/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | #Existing_panel_in_garage1.png,Existing_panel_in_garage2.png,100A_breaker_bottom_panel.png,Fixtures1.png,Fixtures2.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The existing 100 A, 120/240V, single phase, combination panel had 2 pole 100A, breaker added for a sub-panel for the horticultural operation. The branch wiring for the horticultural lights was also non-compliant. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Fixtures2.png | file://x:/photopub/docs/0000000686/f15cefe2-a5f4-4ab0-a8fa-c676826e0ae8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f7ca3b1_a121_4c1e_8ddf_f1aad2a3447f
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png | file://x:/photopub/docs/0000000686/0a1c4c39-5665-486b-ba29-d8a8d6800a19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
GAIN-927880-2017 | GA-579318-2017 | 10/30/2017 1:30:48 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | #Meter_clearance__2.png Mechanical intake to a appliance installed 36" from meter relief opening. A failure of the regulator would allow high pressure gas to be released. Fuel could be drawn into the appliance intake resulting in a over fire condition. Risk of carbon monoxide production or possible fire. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Meter_clearance__2.png | file://x:/photopub/docs/0000000687/bbc76752-d66a-484b-8234-9dcd570db5b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8300a084_e28a_4dfc_a80e_b5ba625ea9b5
PROP-870998-2017 | 2224220 | 11/1/2017 9:13:32 AM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Diesel_tank_spillage.png Diesel fuel had pooled on the main tank in the drive machine room, if not removed, could pose a fire hazard | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Diesel_tank_spillage.png | file://x:/photopub/docs/0000000688/4ca1c728-7199-4223-9874-8af789ee764d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__A5280B9B_3C1B_451E_956B_293BE062341A
ELIN-943460-2017 | EL-594922-2017 | 10/26/2017 11:09:14 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL314 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Pic-hazard.png Improper installation of electrical construction heater. Wire is "slipped" underneath panel cover and terminating under a 40A breaker without any strain relief or support. Conductors could be pinched against metal causing a shock and fire hazard. If the heater is pulled it would cause strain on the breaker terminals. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Pic-hazard.png | file://x:/photopub/docs/0000000685/7a6f29ac-70d3-4bb8-ba62-31aea35a003d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d519326f_fbef_4d0b_8743_33ea2cd27b23
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png | file://x:/photopub/docs/0000000686/27b1bb1a-4cf7-4310-8721-2d03079f9ba7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png | file://x:/photopub/docs/0000000686/1a5aba7f-62d3-41e4-baea-e9d755940d35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png | file://x:/photopub/docs/0000000686/38f4b15c-4f4e-4711-829d-1a6b89176000.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELHE-946736-2017 | HE-606996-2017 | 10/30/2017 6:50:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_Mast1.png,Service_Mast2.png The overhead 200 amp 120/240 volt service feed to the home attaches to a Mast above the roof line which is bent allowing the overhead conductors to lower enough for possible contact by persons. This poses a shock hazard to persons and mechanical damage to the Service Equipment is already present. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_Mast1.png | file://x:/photopub/docs/0000000687/48b1530e-7fc4-4c21-b475-8a75a280ae00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65e30261_4072_4b60_8020_c853194cdea4
ELHE-946736-2017 | HE-606996-2017 | 10/30/2017 6:50:43 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_Mast1.png,Service_Mast2.png The overhead 200 amp 120/240 volt service feed to the home attaches to a Mast above the roof line which is bent allowing the overhead conductors to lower enough for possible contact by persons. This poses a shock hazard to persons and mechanical damage to the Service Equipment is already present. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_Mast2.png | file://x:/photopub/docs/0000000687/6a83943f-0409-4c32-8af9-791a16a647f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65e30261_4072_4b60_8020_c853194cdea4
ELIN-943425-2017 | EL-604826-2017 | 10/30/2017 | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL310 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | 3 | 3 | #Hazard.png Unused breaker openings in panelboard are not filled this may cause a shock or fire hazard if a person comes in contact with the energized bus or if material enters the opening causing a arc. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | Hazard.png | file://x:/photopub/docs/0000000687/af4137f1-a475-44da-b61a-a3389401694c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50bdd86f_f1e4_4fe1_b698_106711fa285d
BPVOP-938252-2017 | BPV-331092-2016 | 10/24/2017 2:20:42 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Boiler_log_book_1.png,Boiler_log_book_2.png,Boiler_log_book_3.png A power engineer must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 70m2 low pressure steam boiler during afternoon and night shifts while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_log_book_1.png | file://x:/photopub/docs/0000000687/5982ef35-e11f-4008-8e0f-664856cce859.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5b06897_16ba_412e_baa3_bfad19e84b9c
BPVOP-938252-2017 | BPV-331092-2016 | 10/24/2017 2:20:42 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Boiler_log_book_1.png,Boiler_log_book_2.png,Boiler_log_book_3.png A power engineer must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 70m2 low pressure steam boiler during afternoon and night shifts while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_log_book_3.png | file://x:/photopub/docs/0000000687/54ca553f-a28f-4c93-8f76-06b98a956d1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5b06897_16ba_412e_baa3_bfad19e84b9c
BPVOP-938252-2017 | BPV-331092-2016 | 10/24/2017 2:20:42 PM | ASSESS: BPV OP: Compliance Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Boiler_log_book_1.png,Boiler_log_book_2.png,Boiler_log_book_3.png A power engineer must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 70m2 low pressure steam boiler during afternoon and night shifts while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_log_book_2.png | file://x:/photopub/docs/0000000687/641dac0b-5d61-4174-8ecf-df90b661d74c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5b06897_16ba_412e_baa3_bfad19e84b9c
BPVIN-943815-2017 | UW-605312-2017 | 10/27/2017 8:11:29 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | #Low_Water_Fuel_Cutoff_Device.png The hot water heating boiler was not fitted with a low water fuel cutoff device. The purpose of this device is to protect the boiler from overheating should the water level within the boiler drop to an unacceptable level. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Low_Water_Fuel_Cutoff_Device.png | file://x:/photopub/docs/0000000686/3d76beab-a7b1-4adc-b527-8580791752f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2465b61d_beb5_47ef_8653_7a7712218731
ELIN-945608-2017 | EL-532835-2017 | 11/1/2017 12:37:55 PM | ASSESS: EL: Final | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | #Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material1.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material2.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material3.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material4.png,Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material5.png The front edges of outlet boxes are required to be installed flush with combustible materials. This is required to ensure devices that are installed on outlet boxes are contained within the box and the internal wiring, connections, and devices are not in contact with or otherwise exposed to combustible material. This installation at a new house has an exterior receptacle that is installed on an outlet box that is recessed approximately 4cm back from the combustible wood material around it. This is a potential fire hazard if the receptacle, receptacle terminations, wiring, or circuit connections fail and over heat and the | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Exterior_receptacle_box_recessed_4_cm_back_from_combustible_wood_material5.png | file://x:/photopub/docs/0000000689/35675e69-1df9-4151-a60b-d915bfdb1e71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__081921fe_0a80_4676_a6ed_5428c6043250
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png | file://x:/photopub/docs/0000000686/ef8960ae-81c5-4022-973c-275836e92e2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png | file://x:/photopub/docs/0000000686/35c11218-9c6f-4a41-b486-d2fa575a7d1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
GAIN-947431-2017 | GA-421103-2016 | 10/31/2017 10:38:54 AM | ASSESS: GA: Final | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | #Gibbins_6.png Propane cylinder installed with less than the minimum required clearance to a source of ignition. Risk of fuel released during filling and over pressure condition coming into contact with ignition source. Risk of fire. | 4 | Ignition sources present with-in minimum distance required | Gibbins_6.png | file://x:/photopub/docs/0000000687/bbe953f1-69ca-4bed-be86-f41ff20fd8d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d2d3042_7b16_4291_84b3_190dd1431f79
ELHE-947880-2017 | HE-607503-2017 | 10/30/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL302 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, repairs are necessary; Low voltage service equipment has been compromised, continued use is not authorized | 4 | 4 | #Rotten_meter_pole1.png,Rotten_meter_pole2.png,Rotten_meter_pole3.png Meter pole has rotted to the point where it will no longer hold the screws for the support straps of the service conduit. The pole is now a hazard to nearby trailers as it is no longer sound and can come down on top of neighbouring trailers. This could cause structural damage and also pose a risk of electrical shock as the overhead lines are still connected to the pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, repairs are necessary; Low voltage service equipment has been compromised, continued use is not authorized | Rotten_meter_pole2.png | file://x:/photopub/docs/0000000689/d93b8110-b26f-4173-b91d-8219ce2e460a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4097e622_d6bf_43a4_8425_c28f36199092
ELHE-947880-2017 | HE-607503-2017 | 10/30/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL302 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, repairs are necessary; Low voltage service equipment has been compromised, continued use is not authorized | 4 | 4 | #Rotten_meter_pole1.png,Rotten_meter_pole2.png,Rotten_meter_pole3.png Meter pole has rotted to the point where it will no longer hold the screws for the support straps of the service conduit. The pole is now a hazard to nearby trailers as it is no longer sound and can come down on top of neighbouring trailers. This could cause structural damage and also pose a risk of electrical shock as the overhead lines are still connected to the pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage service equipment has been damaged and is now compromised, repairs are necessary; Low voltage service equipment has been compromised, continued use is not authorized | Rotten_meter_pole1.png | file://x:/photopub/docs/0000000689/99c51b6d-ff4c-4396-b622-48d4d5b1fa11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4097e622_d6bf_43a4_8425_c28f36199092
ELOP-652634-2016 | EL-097057-2014 | 10/31/2017 1:36:30 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 4 | #Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile1.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile2.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile3.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile4.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile5.png Over head high voltage power lines are required to be installed and maintained with proper clearances from grade level. This is required to prevent contact with the cables that can potentially shock/electrocute persons and/or cause damage to equipment, property, and the power lines. This installation at a mill site has 25KV 3 phase over head power lines that are not located 6.1M above grade level. The grade clearance has been reduced to approximately 3.5 - 4M from the top of a saw dust pile to the over head power lines. This is a potential shock hazard if persons or machinery operating on the saw dust pile contact the energized lines. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile5.png | file://x:/photopub/docs/0000000688/57f2a8ea-8e87-4b37-bfa3-d33bb8523b44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8EF56908_02B0_4C22_9A72_4397E02B0621
ELIN-928238-2017 | EL-587775-2017 | 10/27/2017 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_Attachment1.png,Service_Attachment2.png A new 200 amp 120/240 volt overhead service has been installed on the exterior of a shop but the point of attachment to the roof and the weatherhead are located at the bottom of the sloped roof. This poses potential mechanical damage to the overhead service conductors as snow sliding down the roof can pull the attachment and weatherhead away from the building disconnecting the service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_Attachment2.png | file://x:/photopub/docs/0000000686/fa7069d0-d07c-4995-9ed2-c047df1c8147.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f8415b5_26e8_4379_b033_d0f83a6c211e
ELIN-942941-2017 | EL-604606-2017 | 10/27/2017 11:52:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | #Floor_Heat.png In the bathrooms of a new home under construction, thermostat locations have been provided with strings down to the floor area for future installation and fishing of the non-heating leads from the electric 20 amp 120 volt heating mats placed under the flooring. This poses potential mechanical damage to the heating leads when fished up through the interior of the completed wall. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | Floor_Heat.png | file://x:/photopub/docs/0000000686/4e494c76-b90f-474a-b780-0fe6616f3eaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1073c29_041d_4291_8cde_4559747a020c
ELIN-928238-2017 | EL-587775-2017 | 10/27/2017 12:34:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_Attachment1.png,Service_Attachment2.png A new 200 amp 120/240 volt overhead service has been installed on the exterior of a shop but the point of attachment to the roof and the weatherhead are located at the bottom of the sloped roof. This poses potential mechanical damage to the overhead service conductors as snow sliding down the roof can pull the attachment and weatherhead away from the building disconnecting the service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_Attachment1.png | file://x:/photopub/docs/0000000686/677a4995-1988-4fdf-b187-e94e09043b8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f8415b5_26e8_4379_b033_d0f83a6c211e
ELIN-943879-2017 | UW-605390-2017 | 10/26/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hazard.png Knockouts in spitter have not been filled. The unused openings may cause a shock or fire hazard if conductive material enters the spitter accidentally through the unfilled opening or a shock hazard if energized conductors inside are contacted by a person through the unfilled opening. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hazard.png | file://x:/photopub/docs/0000000686/68bd5dfd-0152-4e5e-99b4-99c315ecc98f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecb4aea4_3aa3_4640_9e93_a9ad08a583b3
ELIN-933641-2017 | EL-591490-2017 | 11/1/2017 2:37:03 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | #Consumer_service_conductor.png The consumer service cable is not supported with any straps | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Consumer_service_conductor.png | file://x:/photopub/docs/0000000689/b7cb9dfe-2db4-4c28-9c67-053eecff2fcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd9fcbfb_58ca_40f0_9f16_ac84b41866fb
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png | file://x:/photopub/docs/0000000686/61b66e2b-2193-4406-a49b-be9a5d798971.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png | file://x:/photopub/docs/0000000686/3e901cce-cf18-4253-892a-ea51fc996bf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png | file://x:/photopub/docs/0000000686/408e8aac-1447-4140-ad49-4572253a86ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELOP-652634-2016 | EL-097057-2014 | 10/31/2017 1:36:30 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 4 | #Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile1.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile2.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile3.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile4.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile5.png Over head high voltage power lines are required to be installed and maintained with proper clearances from grade level. This is required to prevent contact with the cables that can potentially shock/electrocute persons and/or cause damage to equipment, property, and the power lines. This installation at a mill site has 25KV 3 phase over head power lines that are not located 6.1M above grade level. The grade clearance has been reduced to approximately 3.5 - 4M from the top of a saw dust pile to the over head power lines. This is a potential shock hazard if persons or machinery operating on the saw dust pile contact the energized lines. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile2.png | file://x:/photopub/docs/0000000688/34798071-de3c-409e-9417-1489441e08d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8EF56908_02B0_4C22_9A72_4397E02B0621
ELIN-948622-2017 | EL-586677-2017 | 11/1/2017 2:27:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_100a_electrical_panel_with_no_covers.png,Horse_housed_in_ancillary_building.png Protective covers were left off of unsupervised energized 240 volt 100a electrical panel located in a residential dwelling ancillary building being used to house livestock and accessible to unqualified persons, increasing the probability of accidental contact with energized electrical conductors and bus bars that could have resulted in electrical shock upon contact. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Horse_housed_in_ancillary_building.png | file://x:/photopub/docs/0000000689/2dbd9a9c-fe2a-4b8c-8ab7-9dff40a8a13d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51c6385a_46c3_49dd_bcb8_0b7adf218c24
ELIN-948622-2017 | EL-586677-2017 | 11/1/2017 2:27:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_100a_electrical_panel_with_no_covers.png,Horse_housed_in_ancillary_building.png Protective covers were left off of unsupervised energized 240 volt 100a electrical panel located in a residential dwelling ancillary building being used to house livestock and accessible to unqualified persons, increasing the probability of accidental contact with energized electrical conductors and bus bars that could have resulted in electrical shock upon contact. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_100a_electrical_panel_with_no_covers.png | file://x:/photopub/docs/0000000689/1db7ef7a-1a9c-455c-bab1-fae79c199e8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51c6385a_46c3_49dd_bcb8_0b7adf218c24
GAUP-946894-2017 | UW-593201-2017 | 10/31/2017 1:25:34 PM | ASSESS: GA UP: Regulated Work WO Permit | jpg | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #IMG_0460.jpg While assessing an unpermitted boiler installation I found a boiler installed too close to an adjacent wall. Over time, the heat generated from the boiler will cause the wood in the wall to pyrolyze until it ignites causing a fire in the wall behind the boiler. | 3 | Clearance to combustible not met | IMG_0460.jpg | file://x:/photopub/docs/0000000688/82275207-6b7b-442b-a9c9-d8d441296be2.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e3d547b_60e1_4fb6_a1df_293c7a8c0d66
ELIN-943848-2017 | EL-549864-2017 | 10/25/2017 | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | #Exposed_and_rodent_damaged_non-metallic_sheathed_cables1.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables2.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables3.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables4.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables5.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables7.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables8.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables9.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables10.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables11.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables12.png,Exposed_and_rodent_damaged_non-metallic_sheathed_cables13.png Electrical cables have jackets and their conductors have insulation on them. The jackets and conductor insulation are required to be undamaged and intact. This is required to prevent persons or objects from contacting energize | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_and_rodent_damaged_non-metallic_sheathed_cables6.png | file://x:/photopub/docs/0000000686/2508191e-b107-47b2-9fe2-9314ad2254cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9d1f5b_2fd3_4cba_9e08_d85de8c89cbd
ELOP-652634-2016 | EL-097057-2014 | 10/31/2017 1:36:30 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 4 | #Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile1.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile2.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile3.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile4.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile5.png Over head high voltage power lines are required to be installed and maintained with proper clearances from grade level. This is required to prevent contact with the cables that can potentially shock/electrocute persons and/or cause damage to equipment, property, and the power lines. This installation at a mill site has 25KV 3 phase over head power lines that are not located 6.1M above grade level. The grade clearance has been reduced to approximately 3.5 - 4M from the top of a saw dust pile to the over head power lines. This is a potential shock hazard if persons or machinery operating on the saw dust pile contact the energized lines. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile3.png | file://x:/photopub/docs/0000000688/581e9d6e-0a3b-4c52-bbea-e57ff2974930.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8EF56908_02B0_4C22_9A72_4397E02B0621
ELOP-652634-2016 | EL-097057-2014 | 10/31/2017 1:36:30 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 4 | #Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile1.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile2.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile3.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile4.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile5.png Over head high voltage power lines are required to be installed and maintained with proper clearances from grade level. This is required to prevent contact with the cables that can potentially shock/electrocute persons and/or cause damage to equipment, property, and the power lines. This installation at a mill site has 25KV 3 phase over head power lines that are not located 6.1M above grade level. The grade clearance has been reduced to approximately 3.5 - 4M from the top of a saw dust pile to the over head power lines. This is a potential shock hazard if persons or machinery operating on the saw dust pile contact the energized lines. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile1.png | file://x:/photopub/docs/0000000688/825ddab3-b2c6-4821-b1f0-1d85fdcbb33f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8EF56908_02B0_4C22_9A72_4397E02B0621
GAIN-941299-2017 | GA-599458-2017 | 11/1/2017 2:33:36 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Unsecured_gas_lines.png Gas lines extending from regulators are unsupported. They may damage the regulators or shut off valves if gas lines are exposed to strain or mechanical damage. This could lead to a gas leak in the building possibly causing a fire or explosion. | 2 | Physical protection of piping and tubing absent. | Unsecured_gas_lines.png | file://x:/photopub/docs/0000000689/fc7c632a-4dfa-43f7-8d98-56fad42213e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e021b98_0a49_4814_a192_b8c4b14ca77a
GAIN-942484-2017 | GA-600208-2017 | 11/1/2017 1:39:17 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | #Propane_regulator_vent_piping.png Regulator venting run with plastic piping. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Propane_regulator_vent_piping.png | file://x:/photopub/docs/0000000689/b475bfa4-ebaf-4397-946b-185d48b8884c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18bbf526_475f_4022_8c89_a58ff7087420
ELOP-652634-2016 | EL-097057-2014 | 10/31/2017 1:36:30 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 4 | #Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile1.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile2.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile3.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile4.png,Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile5.png Over head high voltage power lines are required to be installed and maintained with proper clearances from grade level. This is required to prevent contact with the cables that can potentially shock/electrocute persons and/or cause damage to equipment, property, and the power lines. This installation at a mill site has 25KV 3 phase over head power lines that are not located 6.1M above grade level. The grade clearance has been reduced to approximately 3.5 - 4M from the top of a saw dust pile to the over head power lines. This is a potential shock hazard if persons or machinery operating on the saw dust pile contact the energized lines. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Reduced_clearances_for_over_head_power_line_over_a_saw_dust_pile4.png | file://x:/photopub/docs/0000000688/00021f2e-e6f4-4477-89c3-687043148253.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8EF56908_02B0_4C22_9A72_4397E02B0621
GAIN-947664-2017 | GA-583905-2017 | 10/31/2017 3:16:19 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Piping_exterior.png Black iron piping not sleeved or wrapped through exterior wall which could result in premature failure of piping by water | 2 | Physical protection of piping and tubing absent. | Piping_exterior.png | file://x:/photopub/docs/0000000688/80f6d348-6d59-4001-87d6-0da647f614a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b040bb21_065b_4a93_9066_9c9bb3959806
EDOP-948445-2017 | 7908 | 10/30/2017 | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED028 | Defect that results in loss of control but means of detection and/or stopping means are functional | 4 | 4 | #7908.png Traction drive sheave has worn below OEM specifications causing hoist cables to lose traction | 4 | Defect that results in loss of control but means of detection and/or stopping means are functional | 7908.png | file://x:/photopub/docs/0000000689/4813ce04-50fe-42ef-ab49-f8b27da540cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4293d3e9_ae64_46a8_849a_b3bb65c28ddd
GAIN-938414-2017 | GA-602132-2017 | 11/1/2017 12:34:43 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Meter.png Meter and piping installed in driveway with no protection. Protection required to protect meter and piping from physical damage from vehicle | 2 | Physical protection of piping and tubing absent. | Meter.png | file://x:/photopub/docs/0000000689/309adf6b-f232-4e05-afae-08037a544d85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69c97388_e6df_49ab_844f_84ac808f6f10
ELIN-938784-2017 | EL-600563-2017 | 10/26/2017 8:04:50 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #G1.png,G2.png,G3.png 50 receptacle rated for max #4 awg at 60 degrees fed with #3 awg, 90 degree wire. This is a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | G3.png | file://x:/photopub/docs/0000000689/c348ff42-d760-415b-80f3-86f7d354c692.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8acb5c8_3d3b_4bbd_bf7b_af5b0572330e
ELIN-938784-2017 | EL-600563-2017 | 10/26/2017 8:04:50 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #G1.png,G2.png,G3.png 50 receptacle rated for max #4 awg at 60 degrees fed with #3 awg, 90 degree wire. This is a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | G1.png | file://x:/photopub/docs/0000000689/69ae3af6-3f1b-4bc4-be45-30754dcf039b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8acb5c8_3d3b_4bbd_bf7b_af5b0572330e
ELIN-938784-2017 | EL-600563-2017 | 10/26/2017 8:04:50 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #G1.png,G2.png,G3.png 50 receptacle rated for max #4 awg at 60 degrees fed with #3 awg, 90 degree wire. This is a fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | G2.png | file://x:/photopub/docs/0000000689/d198c2b2-4ec0-4c69-bb3b-22b236033536.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8acb5c8_3d3b_4bbd_bf7b_af5b0572330e
ELIN-936811-2017 | EL-601368-2017 | 11/2/2017 4:09:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wires_too_close_to_face_of_stud1.png,Wires_too_close_to_face_of_stud2.png,Wires_too_close_to_face_of_stud3.png,Wires_too_close_to_face_of_stud4.png Cables are required to be installed 32mm from the face of structural members they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation for a new house under construction had a 2c#14NMD90 installed through a 2x6 exterior stud wall that terminated at either side if the the garage wall into the exterior sconce fixture boxes. The cable(s) passed through the wall stud closer than 32mm from the face of the stud (flush with the stud). This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wires_too_close_to_face_of_stud2.png | file://x:/photopub/docs/0000000689/cb9faaf7-83d9-4d4e-a298-99869c88ac53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4de10af_d5be_4851_b8ff_9f1cc0d47331
ELIN-936811-2017 | EL-601368-2017 | 11/2/2017 4:09:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wires_too_close_to_face_of_stud1.png,Wires_too_close_to_face_of_stud2.png,Wires_too_close_to_face_of_stud3.png,Wires_too_close_to_face_of_stud4.png Cables are required to be installed 32mm from the face of structural members they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation for a new house under construction had a 2c#14NMD90 installed through a 2x6 exterior stud wall that terminated at either side if the the garage wall into the exterior sconce fixture boxes. The cable(s) passed through the wall stud closer than 32mm from the face of the stud (flush with the stud). This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wires_too_close_to_face_of_stud3.png | file://x:/photopub/docs/0000000689/068f9753-7b03-4bf2-92a1-f59528914e32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4de10af_d5be_4851_b8ff_9f1cc0d47331
ELIN-947742-2017 | EL-570447-2017 | 11/2/2017 3:41:59 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Devices_rated_for_copper_connection1.png,Devices_rated_for_copper_connection2.png,Devices_rated_for_copper_connection3.png When aluminum conductors are connected to a device, the device must be approved for use with the aluminum. This is because when an aluminum conductor is terminated on a copper terminal, the dissimilar metals create a chemical reaction which causes oxidization of the metals. Also the the aluminum and copper expand and contract differently which can cause the connection to loosen. During a final assessment of an existing condo that had been renovated, new receptacles, switches and light fixtures were installed by a contractor. The devices were only rated for copper connections but the conductors on the second floor were aluminum. The devices connected to the aluminum wire could eventually oxidize and loosen which would cause a high resistance and the connection to heat up. This heat build up can cause equipment failure and has the potential to create a fire hazard in this dwelling. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Devices_rated_for_copper_connection1.png | file://x:/photopub/docs/0000000689/88777710-d6b4-4ba3-9403-985b50a753f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b778d067_f912_4657_9595_474d81131394
ELIN-936811-2017 | EL-601368-2017 | 11/2/2017 4:09:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wires_too_close_to_face_of_stud1.png,Wires_too_close_to_face_of_stud2.png,Wires_too_close_to_face_of_stud3.png,Wires_too_close_to_face_of_stud4.png Cables are required to be installed 32mm from the face of structural members they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation for a new house under construction had a 2c#14NMD90 installed through a 2x6 exterior stud wall that terminated at either side if the the garage wall into the exterior sconce fixture boxes. The cable(s) passed through the wall stud closer than 32mm from the face of the stud (flush with the stud). This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wires_too_close_to_face_of_stud4.png | file://x:/photopub/docs/0000000689/c48c0782-783d-4e80-87e7-423dc25111f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4de10af_d5be_4851_b8ff_9f1cc0d47331
ELIN-947742-2017 | EL-570447-2017 | 11/2/2017 3:41:59 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Devices_rated_for_copper_connection1.png,Devices_rated_for_copper_connection2.png,Devices_rated_for_copper_connection3.png When aluminum conductors are connected to a device, the device must be approved for use with the aluminum. This is because when an aluminum conductor is terminated on a copper terminal, the dissimilar metals create a chemical reaction which causes oxidization of the metals. Also the the aluminum and copper expand and contract differently which can cause the connection to loosen. During a final assessment of an existing condo that had been renovated, new receptacles, switches and light fixtures were installed by a contractor. The devices were only rated for copper connections but the conductors on the second floor were aluminum. The devices connected to the aluminum wire could eventually oxidize and loosen which would cause a high resistance and the connection to heat up. This heat build up can cause equipment failure and has the potential to create a fire hazard in this dwelling. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Devices_rated_for_copper_connection2.png | file://x:/photopub/docs/0000000689/8f893a81-b1bd-4343-a15b-1d3827b2625d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b778d067_f912_4657_9595_474d81131394
ELIN-947742-2017 | EL-570447-2017 | 11/2/2017 3:41:59 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Devices_rated_for_copper_connection1.png,Devices_rated_for_copper_connection2.png,Devices_rated_for_copper_connection3.png When aluminum conductors are connected to a device, the device must be approved for use with the aluminum. This is because when an aluminum conductor is terminated on a copper terminal, the dissimilar metals create a chemical reaction which causes oxidization of the metals. Also the the aluminum and copper expand and contract differently which can cause the connection to loosen. During a final assessment of an existing condo that had been renovated, new receptacles, switches and light fixtures were installed by a contractor. The devices were only rated for copper connections but the conductors on the second floor were aluminum. The devices connected to the aluminum wire could eventually oxidize and loosen which would cause a high resistance and the connection to heat up. This heat build up can cause equipment failure and has the potential to create a fire hazard in this dwelling. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Devices_rated_for_copper_connection3.png | file://x:/photopub/docs/0000000689/9a497123-6b77-4a40-a7db-9a59dc10ae7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b778d067_f912_4657_9595_474d81131394
GAHE-946770-2017 | HE-607011-2017 | 10/31/2017 5:27:39 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #Tank_location.png Propane tank placed beside electrical, source of ignition present during filling of the tank with liquid level gauge. | 2 | Installation clearances or set backs to propane containers not met | Tank_location.png | file://x:/photopub/docs/0000000688/3cebaa81-6b75-4dfa-89ed-a58537a08ecb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83542bce_8e0a_4846_99bb_3a5409564208
ELIN-942843-2017 | EL-604575-2017 | 10/31/2017 1:28:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | #Protection_.png This assessment found that the service cable was installed in a manner that would subject it to nails from baseboard installers. This cable is unfused from Hydro and poses a higher fire hazard then with fused cables. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Protection_.png | file://x:/photopub/docs/0000000688/48e358d1-0e2b-4c1c-a182-180d507b4738.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20adf80a_1755_4f07_b72b_a56209e4c8a9
ELIN-946825-2017 | EL-568034-2017 | 10/31/2017 2:15:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #F1.png,F2.png Equipment is not rated for conditions of use. This is a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | F1.png | file://x:/photopub/docs/0000000688/7ff07e54-a4a0-431e-9f46-9960dc908577.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f342c4a_f2f4_4fcf_9c95_45103e8e965d
ELIN-946825-2017 | EL-568034-2017 | 10/31/2017 2:15:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #F1.png,F2.png Equipment is not rated for conditions of use. This is a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | F2.png | file://x:/photopub/docs/0000000688/c3bb8da3-ed4b-4291-aee7-fdc238616a63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f342c4a_f2f4_4fcf_9c95_45103e8e965d
ELIN-947872-2017 | UW-607516-2017 | 10/27/2017 12:58:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Hazard11.png,Hazard12.png Power pedestals are rated for 50A. Installing a 60A breaker instead of the 50A breaker voids the manufactures certification. This exceeds the manufactures ratings and may cause the product to fail and may cause a fire or shock hazard | 3 | Protection and control Loading of distribution equipment exceeded. | Hazard11.png | file://x:/photopub/docs/0000000689/a6d87d47-4e9f-401e-a1a0-3a2c5e1c47b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e645746d_a059_49be_a0c8_59b0dbce37b6
ELIN-947872-2017 | UW-607516-2017 | 10/27/2017 12:58:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Hazard11.png,Hazard12.png Power pedestals are rated for 50A. Installing a 60A breaker instead of the 50A breaker voids the manufactures certification. This exceeds the manufactures ratings and may cause the product to fail and may cause a fire or shock hazard | 3 | Protection and control Loading of distribution equipment exceeded. | Hazard12.png | file://x:/photopub/docs/0000000689/332c19a7-6d14-439b-a19a-7bb6a269492f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e645746d_a059_49be_a0c8_59b0dbce37b6
GAIN-944563-2017 | GA-604905-2017 | 10/30/2017 10:47:15 AM | ASSESS: GA: Rough-In | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Stock_pot.png Used uncertified stock pot burner has been connected for use at a new location (commecial Kitchen)The Safety Standards Act requires that only certified gas appliances can be installed in Canada. This is a very old appliance at the end of its life and if it were to fail it could cause a building fire | 3 | Uncertified appliance connected to gas supply but not in service | Stock_pot.png | file://x:/photopub/docs/0000000687/3fe4fb4b-489b-4639-9e22-6338911e49d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3734ccc_06e6_48de_bfc8_085671e15ecd
ELIN-936811-2017 | EL-601368-2017 | 11/2/2017 4:09:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Wires_too_close_to_face_of_stud1.png,Wires_too_close_to_face_of_stud2.png,Wires_too_close_to_face_of_stud3.png,Wires_too_close_to_face_of_stud4.png Cables are required to be installed 32mm from the face of structural members they pass through. This is required to help prevent damage to cables from nails, screws and other fasteners during or after construction. This installation for a new house under construction had a 2c#14NMD90 installed through a 2x6 exterior stud wall that terminated at either side if the the garage wall into the exterior sconce fixture boxes. The cable(s) passed through the wall stud closer than 32mm from the face of the stud (flush with the stud). This is a fire and shock hazard if the service cable gets damaged by fasteners or gets accidentally cut into during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wires_too_close_to_face_of_stud1.png | file://x:/photopub/docs/0000000689/0872c7c2-e9b0-47e8-9b0e-8d0e5b3b00ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4de10af_d5be_4851_b8ff_9f1cc0d47331
ELIN-947657-2017 | EL-600158-2017 | 11/1/2017 11:34:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Missing_filler_plates.png The installation of a temporary 200 amp 120/240 volt service panel is missing 2 breaker filler plates, the service is not energized but this would become a shock hazard if energized | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_filler_plates.png | file://x:/photopub/docs/0000000689/4cbb1b82-3ff9-4556-aed8-2c178d635062.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2c675fd_c46a_4e90_80dd_0b2fd683d978
ELIN-946613-2017 | EL-606852-2017 | 11/1/2017 2:41:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL341 | Outlet boxes are not approved their intended use or environment. | 2 | 2 | #Plastic_receptacle_box.png The use of a plastic NMSC 2 gang box for receptacles is designed for side mounting to stud construction mainly in residential are not approved for surface mounting and is exposed to mechanical damage and this is an equipment damage issue. | 2 | Outlet boxes are not approved their intended use or environment. | Plastic_receptacle_box.png | file://x:/photopub/docs/0000000689/de736239-416f-4ed4-b4a2-2aa43fd53ba8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0da4c8e_e0b6_4677_bb56_711162151597
EDOP-440118-2015 | 2045760 | 10/31/2017 | ASSESS: ED OP: RAP | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | #Worn_out_skirt_panel.png The skirt panel is located next to steps of the escalator. If the skirt panel is worn a shoe can get caught between the step and the skirt panel causing serious injury. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Worn_out_skirt_panel.png | file://x:/photopub/docs/0000000689/9ce5e9e8-8cde-4d1a-850a-2b98c7838c59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7C4C0D46_0618_4505_BB98_A7C9A0A72243
ELIN-944280-2017 | EL-555098-2017 | 11/1/2017 4:53:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Improper_temporary_heater_installation1.png,Improper_temporary_heater_installation2.png,Improper_temporary_heater_installation3.png,Improper_temporary_heater_installation4.png,Improper_temporary_heater_installation5.png,Improper_temporary_heater_installation6.png Cables used for temporary construction heaters are required to be entered into panels using approved connectors. Cables are also required to be the proper type where subject to mechanical damage. Splices between cable conductors and temporary heater cords must be made inside approved boxes with covers. These are requirements that are intended to ensure the safe installation and operation of temporary heaters for use during construction. This installation had a temporary heater installed in a new house under construction. The heater was supplied by a cable that was entering into the panel without a connector and pinched between the panel enclosure and the panel cover. The non-metallic sheathed cable was run through a wall and along the floor and up s | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Improper_temporary_heater_installation4.png | file://x:/photopub/docs/0000000689/21e50956-7e68-4b0e-a63b-a11104d20005.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09c23351_2f09_4578_8c9d_20d455ba0770
ELIN-944280-2017 | EL-555098-2017 | 11/1/2017 4:53:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Improper_temporary_heater_installation1.png,Improper_temporary_heater_installation2.png,Improper_temporary_heater_installation3.png,Improper_temporary_heater_installation4.png,Improper_temporary_heater_installation5.png,Improper_temporary_heater_installation6.png Cables used for temporary construction heaters are required to be entered into panels using approved connectors. Cables are also required to be the proper type where subject to mechanical damage. Splices between cable conductors and temporary heater cords must be made inside approved boxes with covers. These are requirements that are intended to ensure the safe installation and operation of temporary heaters for use during construction. This installation had a temporary heater installed in a new house under construction. The heater was supplied by a cable that was entering into the panel without a connector and pinched between the panel enclosure and the panel cover. The non-metallic sheathed cable was run through a wall and along the floor and up s | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Improper_temporary_heater_installation1.png | file://x:/photopub/docs/0000000689/8738bcff-8404-4418-ba6c-08650ef38cc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09c23351_2f09_4578_8c9d_20d455ba0770
ELIN-944280-2017 | EL-555098-2017 | 11/1/2017 4:53:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Improper_temporary_heater_installation1.png,Improper_temporary_heater_installation2.png,Improper_temporary_heater_installation3.png,Improper_temporary_heater_installation4.png,Improper_temporary_heater_installation5.png,Improper_temporary_heater_installation6.png Cables used for temporary construction heaters are required to be entered into panels using approved connectors. Cables are also required to be the proper type where subject to mechanical damage. Splices between cable conductors and temporary heater cords must be made inside approved boxes with covers. These are requirements that are intended to ensure the safe installation and operation of temporary heaters for use during construction. This installation had a temporary heater installed in a new house under construction. The heater was supplied by a cable that was entering into the panel without a connector and pinched between the panel enclosure and the panel cover. The non-metallic sheathed cable was run through a wall and along the floor and up s | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Improper_temporary_heater_installation3.png | file://x:/photopub/docs/0000000689/bbde2f93-3b0d-49fe-99a7-f03b5e5d82f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09c23351_2f09_4578_8c9d_20d455ba0770
ELIN-944280-2017 | EL-555098-2017 | 11/1/2017 4:53:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Improper_temporary_heater_installation1.png,Improper_temporary_heater_installation2.png,Improper_temporary_heater_installation3.png,Improper_temporary_heater_installation4.png,Improper_temporary_heater_installation5.png,Improper_temporary_heater_installation6.png Cables used for temporary construction heaters are required to be entered into panels using approved connectors. Cables are also required to be the proper type where subject to mechanical damage. Splices between cable conductors and temporary heater cords must be made inside approved boxes with covers. These are requirements that are intended to ensure the safe installation and operation of temporary heaters for use during construction. This installation had a temporary heater installed in a new house under construction. The heater was supplied by a cable that was entering into the panel without a connector and pinched between the panel enclosure and the panel cover. The non-metallic sheathed cable was run through a wall and along the floor and up s | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Improper_temporary_heater_installation6.png | file://x:/photopub/docs/0000000689/90862e87-aa53-4e78-b48d-a21ccbf4c7b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09c23351_2f09_4578_8c9d_20d455ba0770
ELIN-944280-2017 | EL-555098-2017 | 11/1/2017 4:53:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Improper_temporary_heater_installation1.png,Improper_temporary_heater_installation2.png,Improper_temporary_heater_installation3.png,Improper_temporary_heater_installation4.png,Improper_temporary_heater_installation5.png,Improper_temporary_heater_installation6.png Cables used for temporary construction heaters are required to be entered into panels using approved connectors. Cables are also required to be the proper type where subject to mechanical damage. Splices between cable conductors and temporary heater cords must be made inside approved boxes with covers. These are requirements that are intended to ensure the safe installation and operation of temporary heaters for use during construction. This installation had a temporary heater installed in a new house under construction. The heater was supplied by a cable that was entering into the panel without a connector and pinched between the panel enclosure and the panel cover. The non-metallic sheathed cable was run through a wall and along the floor and up s | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Improper_temporary_heater_installation2.png | file://x:/photopub/docs/0000000689/335ce8f2-abb5-4966-84f1-27fce38a14ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09c23351_2f09_4578_8c9d_20d455ba0770
ELIN-944280-2017 | EL-555098-2017 | 11/1/2017 4:53:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Improper_temporary_heater_installation1.png,Improper_temporary_heater_installation2.png,Improper_temporary_heater_installation3.png,Improper_temporary_heater_installation4.png,Improper_temporary_heater_installation5.png,Improper_temporary_heater_installation6.png Cables used for temporary construction heaters are required to be entered into panels using approved connectors. Cables are also required to be the proper type where subject to mechanical damage. Splices between cable conductors and temporary heater cords must be made inside approved boxes with covers. These are requirements that are intended to ensure the safe installation and operation of temporary heaters for use during construction. This installation had a temporary heater installed in a new house under construction. The heater was supplied by a cable that was entering into the panel without a connector and pinched between the panel enclosure and the panel cover. The non-metallic sheathed cable was run through a wall and along the floor and up s | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Improper_temporary_heater_installation5.png | file://x:/photopub/docs/0000000689/b632a2de-073f-425d-918f-97fb3d5b4354.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09c23351_2f09_4578_8c9d_20d455ba0770
ELIN-947859-2017 | EL-574103-2017 | 11/2/2017 12:20:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Wire_too_close_to_heating_ducts1.png,Wire_too_close_to_heating_ducts2.png,Wire_too_close_to_heating_ducts3.png,Wire_too_close_to_heating_ducts4.png This assessment found that wire in close proximity to heating ducts, creating a fire hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Wire_too_close_to_heating_ducts1.png | file://x:/photopub/docs/0000000689/0d71be33-9868-42aa-9023-18d1ef8c2e46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9664e3a2_40c3_4307_806a_36e86fdbcec6
ELIN-947859-2017 | EL-574103-2017 | 11/2/2017 12:20:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Wire_too_close_to_heating_ducts1.png,Wire_too_close_to_heating_ducts2.png,Wire_too_close_to_heating_ducts3.png,Wire_too_close_to_heating_ducts4.png This assessment found that wire in close proximity to heating ducts, creating a fire hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Wire_too_close_to_heating_ducts3.png | file://x:/photopub/docs/0000000689/e9d951a4-eace-48bf-a07b-58a378c02995.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9664e3a2_40c3_4307_806a_36e86fdbcec6
ELIN-947859-2017 | EL-574103-2017 | 11/2/2017 12:20:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Wire_too_close_to_heating_ducts1.png,Wire_too_close_to_heating_ducts2.png,Wire_too_close_to_heating_ducts3.png,Wire_too_close_to_heating_ducts4.png This assessment found that wire in close proximity to heating ducts, creating a fire hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Wire_too_close_to_heating_ducts4.png | file://x:/photopub/docs/0000000689/96ebbe93-d029-4dcd-885e-57079ced6d94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9664e3a2_40c3_4307_806a_36e86fdbcec6
ELIN-947859-2017 | EL-574103-2017 | 11/2/2017 12:20:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Wire_too_close_to_heating_ducts1.png,Wire_too_close_to_heating_ducts2.png,Wire_too_close_to_heating_ducts3.png,Wire_too_close_to_heating_ducts4.png This assessment found that wire in close proximity to heating ducts, creating a fire hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Wire_too_close_to_heating_ducts2.png | file://x:/photopub/docs/0000000689/90d4329e-aee7-42ca-90db-cb16233f6499.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9664e3a2_40c3_4307_806a_36e86fdbcec6
GAHE-948975-2017 | HE-608225-2017 | 11/6/2017 1:24:33 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 | #Base_wood.png Cylinder installed on wooden base and below ground level. Wood will rot and provide an unstable support and cylinder could fall over. | 2 | Container not set upon compliant base | Base_wood.png | file://x:/photopub/docs/0000000691/733a0891-8fb8-4fc9-9cf7-d4ce479028fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__505eb419_9813_4aca_b990_3c4e473cac39
GAIN-955601-2017 | GA-593063-2017 | 11/8/2017 1:19:10 PM | ASSESS: GA: Rough-In | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Oven.png Oven not certified as a package installed. Possible Fire and or explosion may result. | 3 | Uncertified appliance connected to gas supply but not in service | Oven.png | file://x:/photopub/docs/0000000694/655b7bae-ebeb-46f1-ab1c-9a2203f95b1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54143139_d60d_46fa_bb4c_832cc544a061
ELIN-952932-2017 | EL-452773-2016 | 11/7/2017 12:09:10 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Energized_panel1.png,Energized_panel2.png Panel cover missing. Energized switches and receptacles left hanging out of the wall | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Energized_panel1.png | file://x:/photopub/docs/0000000693/9a27c52e-4548-476e-9fb2-6f767c838b71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__628f8eef_b9f0_4a4d_965f_7043657e8854
ELIN-948596-2017 | EL-606006-2017 | 11/6/2017 12:12:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #No_GFCI.png The installation of a Temporary Operating service includes the installation of 3x 20 amp 120 volt receptacles without any GFCI protection provided, this can lead to a shock hazard | 3 | Conductors Equipment is not approved for the specific use. | No_GFCI.png | file://x:/photopub/docs/0000000691/b7c3929f-a216-47fe-98c3-f1769361ff59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0ef8299_02b7_499f_a3fe_e36876ada418
ELIN-953179-2017 | EL-583642-2017 | 11/9/2017 11:01:45 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Cover_Plates1.png,Cover_Plates2.png,Cover_Plates3.png 120 volt 15 amp light boxes are open, and receptacles and switches have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Cover_Plates3.png | file://x:/photopub/docs/0000000694/87dac00d-9c91-4169-82e7-6a8528a58c6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__047a93f6_a478_4025_bb79_136a220492c3
ELIN-953179-2017 | EL-583642-2017 | 11/9/2017 11:01:45 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Cover_Plates1.png,Cover_Plates2.png,Cover_Plates3.png 120 volt 15 amp light boxes are open, and receptacles and switches have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Cover_Plates2.png | file://x:/photopub/docs/0000000694/cb5ae98a-58c1-4383-bf23-f4799880a562.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__047a93f6_a478_4025_bb79_136a220492c3
ELIN-953179-2017 | EL-583642-2017 | 11/9/2017 11:01:45 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Cover_Plates1.png,Cover_Plates2.png,Cover_Plates3.png 120 volt 15 amp light boxes are open, and receptacles and switches have not been provided with cover plates in areas where the wiring and connections are accessible to the general public. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Cover_Plates1.png | file://x:/photopub/docs/0000000694/9fbb4081-8798-4339-aabf-d14fba8ff512.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__047a93f6_a478_4025_bb79_136a220492c3
BPVOP-949459-2017 | 2262103 | 11/2/2017 12:14:27 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP221 | 5.1.2 Validation: work performed - Mandatory testing non-compliant with code or standard | 3 | 3 | #Superheater_tube.png On assessment of a HP pressure steam boiler with a maximum working pressure of 1090 psig and a maximum working temperature of 850 Fahrenheit, the hydrostatic test revealed an additional pin hole leak on a superheater tube. This creates risk to personnel and equipment. | 3 | 5.1.2 Validation: work performed - Mandatory testing non-compliant with code or standard | Superheater_tube.png | file://x:/photopub/docs/0000000690/ceb89cb0-74e7-4d58-907d-fdbd517437f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71c26446_0b91_4dd2_a143_be35883e1438
GAHE-954466-2017 | HE-611107-2017 | 11/8/2017 8:19:48 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | #Furnace_venting.png Furnace venting run in unapproved material. This may lead to cracking of the venting allowing the flue products to enter the home and possibly lead to carbon monoxide exposure for the occupants. | 3 | Unapproved venting material | Furnace_venting.png | file://x:/photopub/docs/0000000693/b5c5aeab-d3cd-41b9-9526-dd9202595de1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a05af47b_543b_4a9b_90cd_35987301315f
ELIN-948951-2017 | EL-404538-2016 | 11/7/2017 4:04:23 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Hazard.png,Hazard2.png Exposed energized conductor may cause a shock hazard if a person accidentally or purposely touches the energized conductor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Hazard2.png | file://x:/photopub/docs/0000000692/0336a787-f454-4948-acb2-023365279b5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6882c25f_4c12_4a3f_a81d_f73ad0b679e8
BPVOP-095964-2013 | 2253687 | 10/20/2017 | ASSESS: BPV OP: RAP (for recert insp) Boiler | JPG | #asFound | BP088 | 2.0.1 Control system may overrun - Calibration out of date | 2 | 3 | #Ammonia_sensor_calibration.png,Photo-2017-10-20-15-38-36_8174.JPG,Photo-2017-10-20-15-38-31_8173.JPG Ammonia sensors beyond 1 year calibration. | 2 | 2.0.1 Control system may overrun - Calibration out of date | Photo-2017-10-20-15-38-36_8174.JPG | file://x:/photopub/docs/0000000692/a595cec6-c407-4662-b4b8-c462c314f29f.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3E7D2151_8DB1_431C_89E8_110393C9B69E
BPVOP-095964-2013 | 2253687 | 10/20/2017 | ASSESS: BPV OP: RAP (for recert insp) Boiler | JPG | #asFound | BP088 | 2.0.1 Control system may overrun - Calibration out of date | 2 | 3 | #Ammonia_sensor_calibration.png,Photo-2017-10-20-15-38-36_8174.JPG,Photo-2017-10-20-15-38-31_8173.JPG Ammonia sensors beyond 1 year calibration. | 2 | 2.0.1 Control system may overrun - Calibration out of date | Photo-2017-10-20-15-38-31_8173.JPG | file://x:/photopub/docs/0000000692/0243bcb9-e7c5-4df5-873b-b23590563f70.JPG | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3E7D2151_8DB1_431C_89E8_110393C9B69E
GAIN-954303-2017 | GA-610987-2017 | 11/8/2017 12:24:43 PM | ASSESS: GA: Final | png | #asFound | GA008 | Tank/cylinder not installed on RV/Vehicle in a safe compliant manner | 3 | 3 | #RV_and_tank.png Recreational vehicle has been installed in a permanent location and connected to an external propane tank but has not been installed according to the B-149 code. If existing regulator were to fail due to liquid propane migrating to regulator or through normal operation this would compromise the appliances in the recreational vehicle potentially causing a gas leak and or fire | 3 | Tank/cylinder not installed on RV/Vehicle in a safe compliant manner | RV_and_tank.png | file://x:/photopub/docs/0000000693/31850ad4-8e56-42f4-acde-fafa3fa0eca5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6d4ff3a_2c43_4163_bb42_d73800ada939
ELOP-922755-2017 | 5241350 | 11/8/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Over_heated_lamp_holder_type_fixtures_1.png,Over_heated_lamp_holder_type_fixtures_2.png Lighting fixtures are designed, tested, rated, and approved to operate at specified wattages and operating conditions. If wattages are exceeded or operating conditions are different from what the fixture is approved for damage to the fixture can occur and fire hazards can be created. This installation at a shake and shingle mill had lamp holder type light fixtures installed in a lunch room and a saw sharpening area. The fixtures were thermally damaged around the area that the bulb screws in and were damaged to the point where they were not suitable for use. The fixtures may have been over lamped at one time (had bulbs that exceeded the allowable wattage) or had bulbs installed in them that they were not approved for the fixture type (ie: heat lamps). This caused the fixtures to be over heated and created a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Over_heated_lamp_holder_type_fixtures_2.png | file://x:/photopub/docs/0000000694/9e40656e-2095-4aae-a61d-4195be0167d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d5d7a12_389e_4b7b_ac9e_1011769da068
ELIN-950290-2017 | UW-609023-2017 | 11/2/2017 3:25:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | #Service.png The service equipment is installed on a post not an approved pole. The service conductors could possibly be damaged by the service equipment due to damage received by the service disconnect. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Service.png | file://x:/photopub/docs/0000000690/c2a20c34-9328-4a84-ae72-98cdf046d034.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73e3ebce_746b_4650_a94a_0a346dcb8744
BPVOP-948714-2017 | 2258060 | 11/4/2017 2:46:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #S_facing_lower_handhole1.png,S_facing_lower_handhole2.png,S_facing_lower_handhole3.png During the internal inspection of a HP Steam Boiler with MAWP of 150 psig it was found that at the South facing lower handhole the shell metal shows thinning estimated at 40% wall thickness. This can contribute to failure to the pressure boundary of the shell. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | S_facing_lower_handhole2.png | file://x:/photopub/docs/0000000691/6694294c-b913-47a6-ad2a-52404ed642e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6793d6f6_7868_408b_84bb_c35fa203e9fa
BPVOP-948714-2017 | 2258060 | 11/4/2017 2:46:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #S_facing_lower_handhole1.png,S_facing_lower_handhole2.png,S_facing_lower_handhole3.png During the internal inspection of a HP Steam Boiler with MAWP of 150 psig it was found that at the South facing lower handhole the shell metal shows thinning estimated at 40% wall thickness. This can contribute to failure to the pressure boundary of the shell. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | S_facing_lower_handhole1.png | file://x:/photopub/docs/0000000691/7add81e9-0e84-4447-952a-d5ac7a25bfff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6793d6f6_7868_408b_84bb_c35fa203e9fa
BPVOP-948714-2017 | 2258060 | 11/4/2017 2:46:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | #S_facing_lower_handhole1.png,S_facing_lower_handhole2.png,S_facing_lower_handhole3.png During the internal inspection of a HP Steam Boiler with MAWP of 150 psig it was found that at the South facing lower handhole the shell metal shows thinning estimated at 40% wall thickness. This can contribute to failure to the pressure boundary of the shell. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | S_facing_lower_handhole3.png | file://x:/photopub/docs/0000000691/6b23af51-460a-4e8b-967d-c3108fe6cbb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6793d6f6_7868_408b_84bb_c35fa203e9fa
ELOP-915665-2017 | EL-562210-2017 | 11/2/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Extension_cord_run_through_steel_stud_wall1.png,Extension_cord_run_through_steel_stud_wall2.png,Extension_cord_run_through_steel_stud_wall3.png Extension cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. They are not intended to be used in the place of permanent wiring and outlets. Flexible cords are not intended to be fastened to structures or run through holes in floors, walls, or ceilings. This is not permitted because equipment that is designed, evaluated, approved and labeled for use as portable equipment for temporary use is more susceptible to mechanical damage and overloading which can create shock and fire hazards. This installation at a seniors independent living facility has a flexible extension cord that has been plugged into a 15A 120V receptacle. The cord was run along and through a steel stud wall to provide power to a theatre audio system. The jacket of the cord was damaged by the sharp edge of the stee | 4 | Conductors, Misuse of flexible cords. | Extension_cord_run_through_steel_stud_wall2.png | file://x:/photopub/docs/0000000690/a4601ec8-9843-4ac7-9f79-1c94ffa8a1d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D17B44EE_9419_407F_ABCC_E8404CC85075
ELOP-915665-2017 | EL-562210-2017 | 11/2/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Extension_cord_run_through_steel_stud_wall1.png,Extension_cord_run_through_steel_stud_wall2.png,Extension_cord_run_through_steel_stud_wall3.png Extension cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. They are not intended to be used in the place of permanent wiring and outlets. Flexible cords are not intended to be fastened to structures or run through holes in floors, walls, or ceilings. This is not permitted because equipment that is designed, evaluated, approved and labeled for use as portable equipment for temporary use is more susceptible to mechanical damage and overloading which can create shock and fire hazards. This installation at a seniors independent living facility has a flexible extension cord that has been plugged into a 15A 120V receptacle. The cord was run along and through a steel stud wall to provide power to a theatre audio system. The jacket of the cord was damaged by the sharp edge of the stee | 4 | Conductors, Misuse of flexible cords. | Extension_cord_run_through_steel_stud_wall3.png | file://x:/photopub/docs/0000000690/aa1cd363-5c67-4409-9514-56338f44e3de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D17B44EE_9419_407F_ABCC_E8404CC85075
ELOP-915665-2017 | EL-562210-2017 | 11/2/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | #Extension_cord_run_through_steel_stud_wall1.png,Extension_cord_run_through_steel_stud_wall2.png,Extension_cord_run_through_steel_stud_wall3.png Extension cords are intended and approved to be used for temporary connection between receptacles, portable appliances, and electrical equipment. They are not intended to be used in the place of permanent wiring and outlets. Flexible cords are not intended to be fastened to structures or run through holes in floors, walls, or ceilings. This is not permitted because equipment that is designed, evaluated, approved and labeled for use as portable equipment for temporary use is more susceptible to mechanical damage and overloading which can create shock and fire hazards. This installation at a seniors independent living facility has a flexible extension cord that has been plugged into a 15A 120V receptacle. The cord was run along and through a steel stud wall to provide power to a theatre audio system. The jacket of the cord was damaged by the sharp edge of the stee | 4 | Conductors, Misuse of flexible cords. | Extension_cord_run_through_steel_stud_wall1.png | file://x:/photopub/docs/0000000690/e6ac066b-014e-47b3-af13-d0ab1e8c8c93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D17B44EE_9419_407F_ABCC_E8404CC85075
GAHE-947363-2017 | HE-607174-2017 | 11/3/2017 8:14:54 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #Mercury_switch.png Flame switch removed from primary control circuit wiring for fireplace. The removal of the switch has increased the flame response time that provides auto shutoff of the gas valve. Risk of delayed ignition due to pilot valve remaining open after flame signal is lost. Delayed ignition could result in fireplace glass spalling into occupied area. | 4 | Missing mandatory safety controls | Mercury_switch.png | file://x:/photopub/docs/0000000690/df992489-4357-4b82-9ee1-50bc54c31334.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__faaeae64_6bed_493e_80e3_8958fe419559
ELIN-950254-2017 | UW-609000-2017 | 11/2/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Breaker_space_open.png Open breaker space on an energized panel leaving exposed electrical parts and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Breaker_space_open.png | file://x:/photopub/docs/0000000692/3a2f9d34-1f57-4113-9cc7-dd4499416909.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be63c50_a54c_4dcd_9c73_ade351a162f4
ELIN-952961-2017 | EL-490636-2017 | 11/7/2017 3:24:34 PM | ASSESS: EL: Final | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Energized_outlets_without_coverplates_1.png,Energized_outlets_without_coverplates_2.png Device boxes with and without devices did not have coverplates on them. This condition could expose occupants to a potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Energized_outlets_without_coverplates_2.png | file://x:/photopub/docs/0000000693/4f6fb736-5136-48a0-8099-155116e1d77b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb469de_64d6_462f_8b72_5adcff810b66
ELIN-952961-2017 | EL-490636-2017 | 11/7/2017 3:24:34 PM | ASSESS: EL: Final | png | #asFound | EL289 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Energized_outlets_without_coverplates_1.png,Energized_outlets_without_coverplates_2.png Device boxes with and without devices did not have coverplates on them. This condition could expose occupants to a potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Energized_outlets_without_coverplates_1.png | file://x:/photopub/docs/0000000693/540d6111-32a6-40ca-a975-da3248d7a91a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cb469de_64d6_462f_8b72_5adcff810b66
ELIN-952984-2017 | EL-609793-2017 | 11/8/2017 7:28:09 AM | ASSESS: EL: Service Connection | png | #asFound | EL325 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3 | 3 | #No_sealing_ring_installed_on_conduit.png In a temporary construction service, the 200 amp 120/240 volt consumer service raceway entering the side of the panelboard, located outdoors, did not have a sealing ring to protect the panelboard from ingress of moisture. This could result in an equipment damage condition. Picture attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_sealing_ring_installed_on_conduit.png | file://x:/photopub/docs/0000000694/708ed79e-e3f3-4498-9e0b-f0032653b3f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4928436f_7b07_4356_a2f5_e01b42caeaaa
GAIN-933024-2017 | GA-599228-2017 | 11/6/2017 10:21:16 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Mechanical_air_too_close.png Mechanical Air for an appliance installed too close to a regulator relief vent. In an overpressure scenario regulator will relieve pressure through relief vent. Natural gas will then be sucked through the mechanical air into appliance causing an overfired situation or an explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Mechanical_air_too_close.png | file://x:/photopub/docs/0000000691/f3b1a8ac-b357-47a9-b617-0a03f08f7b82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__009eca37_70a4_41c4_b6c5_c5a91025338b
GAIN-941518-2017 | GA-531475-2017 | 11/3/2017 9:41:15 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Gas_piping.png Gas piping installed on the exterior of the building without expansion loops. This may lead to undue stress on the piping due to linear expansion and the possibility of a gas leak. | 2 | Physical protection of piping and tubing absent. | Gas_piping.png | file://x:/photopub/docs/0000000690/c65815b2-66a8-40fd-a1e6-6daf8cf0e7d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9cfdf13_a914_4c7a_b8ac_a98a5ab0bce5
GAHE-951065-2017 | HE-609497-2017 | 11/3/2017 2:09:10 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #Water_heater_relief_valve1.png,Water_heater_relief_valve2.png Hot water tank temperature/ pressure relief valve jammed against furnace plenum. This would not allow the relief valve to relieve excess water pressure from inside the tank. If the tank pressure was to get too high the water tank could explode causing injury or death. | 4 | Incorrect use of safety controls (Example: bypass limit) | Water_heater_relief_valve1.png | file://x:/photopub/docs/0000000690/2f28520c-d68f-47ca-a82b-0068256ef982.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8ded7ed_517e_4ada_a504_93a39e41692e
GAHE-951065-2017 | HE-609497-2017 | 11/3/2017 2:09:10 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA147 | Incorrect use of safety controls (Example: bypass limit) | 4 | 4 | #Water_heater_relief_valve1.png,Water_heater_relief_valve2.png Hot water tank temperature/ pressure relief valve jammed against furnace plenum. This would not allow the relief valve to relieve excess water pressure from inside the tank. If the tank pressure was to get too high the water tank could explode causing injury or death. | 4 | Incorrect use of safety controls (Example: bypass limit) | Water_heater_relief_valve2.png | file://x:/photopub/docs/0000000690/58dd53e5-6cbf-44ad-a684-eaf44a6278bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8ded7ed_517e_4ada_a504_93a39e41692e
ELOP-922755-2017 | 5241350 | 11/8/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Over_heated_lamp_holder_type_fixtures_1.png,Over_heated_lamp_holder_type_fixtures_2.png Lighting fixtures are designed, tested, rated, and approved to operate at specified wattages and operating conditions. If wattages are exceeded or operating conditions are different from what the fixture is approved for damage to the fixture can occur and fire hazards can be created. This installation at a shake and shingle mill had lamp holder type light fixtures installed in a lunch room and a saw sharpening area. The fixtures were thermally damaged around the area that the bulb screws in and were damaged to the point where they were not suitable for use. The fixtures may have been over lamped at one time (had bulbs that exceeded the allowable wattage) or had bulbs installed in them that they were not approved for the fixture type (ie: heat lamps). This caused the fixtures to be over heated and created a potential fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Over_heated_lamp_holder_type_fixtures_1.png | file://x:/photopub/docs/0000000694/4c24c175-6bb4-4ca2-bb29-0002d3596a39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d5d7a12_389e_4b7b_ac9e_1011769da068
BPVIN-950899-2017 | BPV-608756-2017 | 11/7/2017 11:55:26 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #Disconnect.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no lockable disconnect switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Disconnect.png | file://x:/photopub/docs/0000000692/54716cb4-f0ee-42fa-a563-682a4afbebfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f22ec6dc_f9c8_4596_b6fa_04d397adeefe
ELIN-951376-2017 | EL-594792-2017 | 11/6/2017 4:36:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Neutral_conductor_not_adequately_tightened1.png,Neutral_conductor_not_adequately_tightened2.png,Neutral_conductor_not_adequately_tightened3.png,Neutral_conductor_not_adequately_tightened4.png,Neutral_conductor_not_adequately_tightened5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the electrical equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 200A service at a new house under construction had a service conductor termination at the service panel that was not terminated or tightened properly. The #250 kcmil aluminum service neutral conductor termination at the service panel was not adequately tightened. The termination lug had a threaded hex type fastener that was intended to fasten the conductor securely into the lug. The hex fastener was not tightened adequately to provide a soli | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Neutral_conductor_not_adequately_tightened4.png | file://x:/photopub/docs/0000000691/78a2fc75-6cef-4f89-ba35-55d84cf19ff9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ace87257_c2cd_46c1_9b8e_3ff696118fc1
ELIN-953106-2017 | EL-607315-2017 | 11/8/2017 1:36:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Main_shed_service_70_main_with_60_amp_feeder_for_residence1.png,Main_shed_service_70_main_with_60_amp_feeder_for_residence2.png,Main_shed_service_70_main_with_60_amp_feeder_for_residence3.png The installation of a new residence with a 60 amp 120/240 volt sub fed from another existing service on site has a calculated load requiring a 100 amp service. The service is not sufficient for the calculated load and this will lead to a thermal issue | 3 | Protection and control Loading of distribution equipment exceeded. | Main_shed_service_70_main_with_60_amp_feeder_for_residence2.png | file://x:/photopub/docs/0000000694/63ba5d4c-29b1-47c4-8181-c6d1955c8ed1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6702f509_b4a0_400c_8bfb_a4598ac1b3a8
ELIN-955098-2017 | EL-611290-2017 | 11/9/2017 10:33:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #Inadequate_protection_from_weather_1.png,Inadequate_protection_from_weather_2.png,Inadequate_protection_from_weather_3.png,Inadequate_protection_from_weather_4.png | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Inadequate_protection_from_weather_2.png | file://x:/photopub/docs/0000000694/9b4349f6-8bf7-4ad0-a8bd-ea2998757d64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293800d3_9427_4359_b0fd_8790526509f1
ELIN-955098-2017 | EL-611290-2017 | 11/9/2017 10:33:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #Inadequate_protection_from_weather_1.png,Inadequate_protection_from_weather_2.png,Inadequate_protection_from_weather_3.png,Inadequate_protection_from_weather_4.png | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Inadequate_protection_from_weather_4.png | file://x:/photopub/docs/0000000694/b03d687a-112c-4738-ab9c-337058249ece.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293800d3_9427_4359_b0fd_8790526509f1
ELIN-955098-2017 | EL-611290-2017 | 11/9/2017 10:33:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #Inadequate_protection_from_weather_1.png,Inadequate_protection_from_weather_2.png,Inadequate_protection_from_weather_3.png,Inadequate_protection_from_weather_4.png | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Inadequate_protection_from_weather_1.png | file://x:/photopub/docs/0000000694/1ba5843b-2bfe-4dc1-8bfe-6233e33f0bda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293800d3_9427_4359_b0fd_8790526509f1
ELIN-955098-2017 | EL-611290-2017 | 11/9/2017 10:33:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | #Inadequate_protection_from_weather_1.png,Inadequate_protection_from_weather_2.png,Inadequate_protection_from_weather_3.png,Inadequate_protection_from_weather_4.png | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Inadequate_protection_from_weather_3.png | file://x:/photopub/docs/0000000694/1d567188-74a9-4c36-b778-1c6fa961e5a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293800d3_9427_4359_b0fd_8790526509f1
ELIN-950498-2017 | EL-595856-2017 | 11/4/2017 11:16:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Not_bonded.png Gas bond This assessment found the gas pipe installed without the required bond jumper. There is a risk of the pipe becoming energized from internal circuits or lightening; thereby presenting a fire and shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Not_bonded.png | file://x:/photopub/docs/0000000691/131ef184-b3d4-424c-bb6b-b13dbac36f13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5460769e_459b_49e9_9539_93e8a5760478
BPOP-935364-2017 | BPV-455029-2015 | 10/26/2017 6:25:00 PM | ASSESS: Propane PV: Periodic | png | #asFound | GA024 | No protection Low traffic | 3 | 3 | #Clearances.png | 3 | No protection Low traffic | Clearances.png | file://x:/photopub/docs/0000000693/93d2af75-5af4-4481-956f-8670f2260d90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fc9f664_5bab_4560_8b2d_2438866d0974
ELIN-951376-2017 | EL-594792-2017 | 11/6/2017 4:36:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Neutral_conductor_not_adequately_tightened1.png,Neutral_conductor_not_adequately_tightened2.png,Neutral_conductor_not_adequately_tightened3.png,Neutral_conductor_not_adequately_tightened4.png,Neutral_conductor_not_adequately_tightened5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the electrical equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 200A service at a new house under construction had a service conductor termination at the service panel that was not terminated or tightened properly. The #250 kcmil aluminum service neutral conductor termination at the service panel was not adequately tightened. The termination lug had a threaded hex type fastener that was intended to fasten the conductor securely into the lug. The hex fastener was not tightened adequately to provide a soli | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Neutral_conductor_not_adequately_tightened3.png | file://x:/photopub/docs/0000000691/a4d9af42-2811-485a-928c-8c1e53270ff3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ace87257_c2cd_46c1_9b8e_3ff696118fc1
ELIN-951376-2017 | EL-594792-2017 | 11/6/2017 4:36:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Neutral_conductor_not_adequately_tightened1.png,Neutral_conductor_not_adequately_tightened2.png,Neutral_conductor_not_adequately_tightened3.png,Neutral_conductor_not_adequately_tightened4.png,Neutral_conductor_not_adequately_tightened5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the electrical equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 200A service at a new house under construction had a service conductor termination at the service panel that was not terminated or tightened properly. The #250 kcmil aluminum service neutral conductor termination at the service panel was not adequately tightened. The termination lug had a threaded hex type fastener that was intended to fasten the conductor securely into the lug. The hex fastener was not tightened adequately to provide a soli | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Neutral_conductor_not_adequately_tightened5.png | file://x:/photopub/docs/0000000691/ad7b198d-5a24-4fd9-ac97-0b7015bef255.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ace87257_c2cd_46c1_9b8e_3ff696118fc1
ELIN-951376-2017 | EL-594792-2017 | 11/6/2017 4:36:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Neutral_conductor_not_adequately_tightened1.png,Neutral_conductor_not_adequately_tightened2.png,Neutral_conductor_not_adequately_tightened3.png,Neutral_conductor_not_adequately_tightened4.png,Neutral_conductor_not_adequately_tightened5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the electrical equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 200A service at a new house under construction had a service conductor termination at the service panel that was not terminated or tightened properly. The #250 kcmil aluminum service neutral conductor termination at the service panel was not adequately tightened. The termination lug had a threaded hex type fastener that was intended to fasten the conductor securely into the lug. The hex fastener was not tightened adequately to provide a soli | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Neutral_conductor_not_adequately_tightened2.png | file://x:/photopub/docs/0000000691/977e71ef-8914-4d24-a53b-b6debd143481.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ace87257_c2cd_46c1_9b8e_3ff696118fc1
ELIN-951376-2017 | EL-594792-2017 | 11/6/2017 4:36:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | #Neutral_conductor_not_adequately_tightened1.png,Neutral_conductor_not_adequately_tightened2.png,Neutral_conductor_not_adequately_tightened3.png,Neutral_conductor_not_adequately_tightened4.png,Neutral_conductor_not_adequately_tightened5.png Termination of electrical conductors must be made up tight according to the manufacturers torque specifications related to the electrical equipment involved. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation of a new 200A service at a new house under construction had a service conductor termination at the service panel that was not terminated or tightened properly. The #250 kcmil aluminum service neutral conductor termination at the service panel was not adequately tightened. The termination lug had a threaded hex type fastener that was intended to fasten the conductor securely into the lug. The hex fastener was not tightened adequately to provide a soli | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Neutral_conductor_not_adequately_tightened1.png | file://x:/photopub/docs/0000000691/661d0f7e-db70-4e7b-8d88-335aad2c252e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ace87257_c2cd_46c1_9b8e_3ff696118fc1
ELIN-948951-2017 | EL-404538-2016 | 11/7/2017 4:04:23 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | #Hazard.png,Hazard2.png Exposed energized conductor may cause a shock hazard if a person accidentally or purposely touches the energized conductor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Hazard.png | file://x:/photopub/docs/0000000692/f552d1ae-e36c-441f-a31b-9881ee1f943c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6882c25f_4c12_4a3f_a81d_f73ad0b679e8
ELIN-953106-2017 | EL-607315-2017 | 11/8/2017 1:36:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Main_shed_service_70_main_with_60_amp_feeder_for_residence1.png,Main_shed_service_70_main_with_60_amp_feeder_for_residence2.png,Main_shed_service_70_main_with_60_amp_feeder_for_residence3.png The installation of a new residence with a 60 amp 120/240 volt sub fed from another existing service on site has a calculated load requiring a 100 amp service. The service is not sufficient for the calculated load and this will lead to a thermal issue | 3 | Protection and control Loading of distribution equipment exceeded. | Main_shed_service_70_main_with_60_amp_feeder_for_residence1.png | file://x:/photopub/docs/0000000694/6d902b1e-be51-43b8-a4a0-82441c9ba21b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6702f509_b4a0_400c_8bfb_a4598ac1b3a8
ELIN-953106-2017 | EL-607315-2017 | 11/8/2017 1:36:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | #Main_shed_service_70_main_with_60_amp_feeder_for_residence1.png,Main_shed_service_70_main_with_60_amp_feeder_for_residence2.png,Main_shed_service_70_main_with_60_amp_feeder_for_residence3.png The installation of a new residence with a 60 amp 120/240 volt sub fed from another existing service on site has a calculated load requiring a 100 amp service. The service is not sufficient for the calculated load and this will lead to a thermal issue | 3 | Protection and control Loading of distribution equipment exceeded. | Main_shed_service_70_main_with_60_amp_feeder_for_residence3.png | file://x:/photopub/docs/0000000694/6027e900-1b80-4672-bee1-26c71f7d3cd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6702f509_b4a0_400c_8bfb_a4598ac1b3a8
ELIN-952934-2017 | EL-585954-2017 | 11/8/2017 8:32:21 AM | ASSESS: EL: Final | png | #asFound | EL342 | Improper installation or location of equipment, Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Motor_connection_box.png 20 Horsepower motor connection box lid is damage/bent. The attachment screws are missing and the cover has been secured with electrical tape. There are gaps between the lid and the box. The location of the box is susceptible to moisture and debris, moisture and debris may cause deterioration of internal wiring or overheating issues in the future, a risk of fire, shock and equipment failure exists. | 3 | Improper installation or location of equipment, Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Motor_connection_box.png | file://x:/photopub/docs/0000000693/1d28dc6d-a45d-4a09-8a6d-e5294961d0df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98943c14_af56_4454_9bc1_633eb6da1c34
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png | file://x:/photopub/docs/0000000693/a0d12f8a-4f5d-4fd3-939b-7bd00a38f2e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png | file://x:/photopub/docs/0000000693/6fcbc112-7236-457e-ac19-4ae08d10c489.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png | file://x:/photopub/docs/0000000693/da5917af-b51a-469c-b9e0-b8873f50ac3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house25.png | file://x:/photopub/docs/0000000693/5206e9e9-f5f3-4bda-8ea1-33be0ab9954f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELIN-952288-2017 | EL-610012-2017 | 11/7/2017 10:55:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL307 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #One_of_the_many_holes_cut_into_csa3_r_panel.png A 200 amp 240 volt weatherproof panel has had holes cut into it for mounting and for entry of cables. Factory approved weatherproof equipment is designed to have openings provided by the manufacturer only. Field alteration of weatherproof equipment can result in damage to the equipment or injury to persons due to water ingress, insect invasion,and other contamination entering the weatherproof equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | One_of_the_many_holes_cut_into_csa3_r_panel.png | file://x:/photopub/docs/0000000692/d92d9add-8c22-4458-8eb8-cf101cfbae7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc44ab1e_c3e5_41e4_b106_c4cc74e98c15
ELIN-949991-2017 | EL-606269-2017 | 11/6/2017 12:34:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Outlets_and_Breakers1.png,Outlets_and_Breakers2.png In a new 100 amp 120/240 volt electrical service panel, 15 amp wire has been used to connect 20 amp receptacles to 20 amp breakers. This poses a shock hazard and potential damage to the electrical components as the wiring may not be capable of the imposed fault current or the same levels of ampacity as the outlets and breakers. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Outlets_and_Breakers2.png | file://x:/photopub/docs/0000000691/e80de0bf-3c0f-4d5c-80a7-d083da63bfb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78753b63_23d3_48ee_9ff9_71630f78a1e8
ELIN-949991-2017 | EL-606269-2017 | 11/6/2017 12:34:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Outlets_and_Breakers1.png,Outlets_and_Breakers2.png In a new 100 amp 120/240 volt electrical service panel, 15 amp wire has been used to connect 20 amp receptacles to 20 amp breakers. This poses a shock hazard and potential damage to the electrical components as the wiring may not be capable of the imposed fault current or the same levels of ampacity as the outlets and breakers. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Outlets_and_Breakers1.png | file://x:/photopub/docs/0000000691/3fc2ea91-a374-4de0-9d52-78b0e7239ff3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78753b63_23d3_48ee_9ff9_71630f78a1e8
GAIN-685929-2016 | GA-436391-2016 | 11/6/2017 11:34:56 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | #Water_heater.png The as-found condition is that a water heater and furnace have been installed without adequate combustion air supply. The potential hazard is that the appliances will be starved of air when in operation, causing a poor air/gas mixture which could result in the production of harmful emissions such as Carbon Monoxide. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Water_heater.png | file://x:/photopub/docs/0000000692/4ff5e204-dac7-42e8-ac4b-4240ffeab677.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72ecb06c_3ec7_4ccb_92af_896f959f201f
GAIN-949852-2017 | GA-608610-2017 | 11/6/2017 1:57:02 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | #Reg_below__liquid.png System regulator installed below liquid level of cylinder. Risk of liquid propane entering regulator which has a vapour rating only. Physical damage to internal component of the regulator caused by the liquid could result in downstream pressures ,in excess of system design. Risk of the appliance being over fired resulting in the production of carbon monoxide. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Reg_below__liquid.png | file://x:/photopub/docs/0000000691/ed970f24-ff99-4b13-92c9-b8fc0ecfc649.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bfdf1e1_1bd5_4557_800a_3b47805f242d
GAIN-949036-2017 | GA-589429-2017 | 11/6/2017 2:53:17 PM | ASSESS: GA: Rough-In | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 2 | #Vent_termination.png | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_termination.png | file://x:/photopub/docs/0000000691/a8ea121a-50ab-43f1-8547-779ca130d737.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10a1bdd6_8c08_47b7_8e2f_88711faa0280
GAIN-948447-2017 | GA-606353-2017 | 11/6/2017 3:36:58 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Mechanical_air_too_close.png Mechanical Air for an appliance installed too close to a regulator relief vent. In an overpressure scenario, regulator will relieve pressure through relief vent. Natural gas will the n be sucked through the mechanical air inlet into appliance causing an over fired situation or an explosion | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Mechanical_air_too_close.png | file://x:/photopub/docs/0000000691/ab7f4f71-9d04-4d1b-a412-d2b3ca8db933.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea5c157a_8b6d_4d38_b23b_4a2936907d17
GAUP-955339-2017 | UW-611537-2017 | 11/8/2017 10:42:43 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Copper_gas_line.png Type G Copper gas line directly buried in the ground from meter location to house. This type of copper is not approved to be directly buried. This may lead to a damaged underground line and a potential gas leak. | 3 | Code prohibited practices or materials | Copper_gas_line.png | file://x:/photopub/docs/0000000693/dee9fb7c-4104-4358-bd57-255565afd4c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20d935e6_7436_47c5_8fd2_579efdf57fbd
BPOP-952658-2017 | BPV-455110-2015 | 11/6/2017 10:44:16 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | #Tank_1.png,Tank_2.png Propane tank installed against wooden fence and building wall. Propane tank clearance from combustibles required in event of a fire for protection | 3 | Clearance to combustibles not maintained | Tank_2.png | file://x:/photopub/docs/0000000691/6dfe0059-9932-4df0-9633-3c50b067509d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b17f1488_7587_4d1f_97cd_8ce9bcbb0297
BPOP-952658-2017 | BPV-455110-2015 | 11/6/2017 10:44:16 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | #Tank_1.png,Tank_2.png Propane tank installed against wooden fence and building wall. Propane tank clearance from combustibles required in event of a fire for protection | 3 | Clearance to combustibles not maintained | Tank_1.png | file://x:/photopub/docs/0000000691/d9f3889a-9c67-4108-9f0c-417764793cc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b17f1488_7587_4d1f_97cd_8ce9bcbb0297
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house23.png | file://x:/photopub/docs/0000000693/6ca96ba1-d664-42c8-8e83-17d67fb335b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png | file://x:/photopub/docs/0000000693/3d5c7c20-acd1-4e6e-8ee0-cd4e1436c926.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
GAHE-954286-2017 | HE-610983-2017 | 11/7/2017 11:41:38 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | #Piping_supports2.png Gas piping supports have come undone | 2 | Physical protection of piping and tubing absent. | Piping_supports2.png | file://x:/photopub/docs/0000000692/c89e374d-9e2f-4b21-bd18-e42931429a03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fae6e38_45a0_40df_9754_f6f6ec9d24d8
ELIN-943462-2017 | EL-600982-2017 | 11/7/2017 11:05:27 AM | ASSESS: EL: Final | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | #NMWU_installed_in_main_consumer_service_conductor_compartment.png In a residential single family dwelling air conditioner installation the 30 amp 120/240 volt branch circuit conductor was installed through the main consumer service conductor compartment of the panel. This could result in an equipment damage condition. Picture attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | NMWU_installed_in_main_consumer_service_conductor_compartment.png | file://x:/photopub/docs/0000000692/98bee4aa-22de-4e87-b3cb-1a7743329338.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ccc545f_4a93_490f_b83d_4c4bf234dc21
ELIN-950195-2017 | EL-607495-2017 | 11/7/2017 8:40:21 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Kitchen_counter_receptacle_without_GFCI_protection.png In a residential single family dwelling renovation a 15 amp 120 volt kitchen counter receptacle was added without GFCI protection. This could result in a thermal effect condition. Picture attached. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Kitchen_counter_receptacle_without_GFCI_protection.png | file://x:/photopub/docs/0000000692/4c124768-c300-44f7-bbbd-b6a4240a7fe9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11323a4d_d452_49e3_8e8f_09a8ac2e2614
ELIN-953518-2017 | EL-555066-2017 | 11/7/2017 7:48:47 AM | ASSESS: EL: Service Connection | png | #asFound | EL323 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 3 | 3 | #No_mechanical_protection_for_ACWU.png In a new residential single family dwelling, the 200 amp 120/240 volt consumer service cable did not have mechanical protection provided where it exits the earth on the exterior of the residence. This could result in an equipment damage condition. Picture attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | No_mechanical_protection_for_ACWU.png | file://x:/photopub/docs/0000000692/b93275ee-2fa0-436f-a362-c9fdaa976bc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__364c1172_3620_43b6_8ebf_be072f3a9b0b
GAIN-944493-2017 | GA-603538-2017 | 11/6/2017 1:14:49 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Photo.png The as found condition is a Furnace was installed without a slope as required by manufacturers installation Instructions. The as found hazard is excessive accumulation of condensate can lead to premature failure of the heat exchanger concurrently leading to inhabitants possibly being subjected to carbon monoxide toxicity. | 3 | Appliance not installed according to installation instructions | Photo.png | file://x:/photopub/docs/0000000691/e3ce3204-3707-4120-a605-44122e834db4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7931fe6f_88c9_4dd0_8c31_0095cc4291ff
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png | file://x:/photopub/docs/0000000693/a09fd586-01fa-4edd-9456-1526b7dc3407.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png | file://x:/photopub/docs/0000000693/09a84cd2-e0e1-4c2f-a800-0019f7368480.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house19.png | file://x:/photopub/docs/0000000693/9ed9a82c-87ca-49fb-a3ce-b626312bcc5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house21.png | file://x:/photopub/docs/0000000693/4974a5a8-6aea-43b3-94da-e069f7b1c3e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png | file://x:/photopub/docs/0000000693/aa4d6ff3-5d43-4cdc-ab62-c6609479b935.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELIN-954555-2017 | EL-516511-2017 | 11/7/2017 | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | #Hazard1.png,Hazard2.png Conductors are not suitably protected with properly sized overcurrent protection. This may cause the conductors to heat up and may fail if they carry more current then the conductors are rated for. This may cause a fire or shock hazard. | 4 | Protection and control Interrupt ratings are not adequate for the installation | Hazard2.png | file://x:/photopub/docs/0000000693/d9c04db5-e654-45a3-b544-c3e4c6fd80f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5a97459_614c_4929_af85_e519b1da9ae5
ELIN-954555-2017 | EL-516511-2017 | 11/7/2017 | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | #Hazard1.png,Hazard2.png Conductors are not suitably protected with properly sized overcurrent protection. This may cause the conductors to heat up and may fail if they carry more current then the conductors are rated for. This may cause a fire or shock hazard. | 4 | Protection and control Interrupt ratings are not adequate for the installation | Hazard1.png | file://x:/photopub/docs/0000000693/33b37797-0185-4156-9a77-a863cbfe434d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5a97459_614c_4929_af85_e519b1da9ae5
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png | file://x:/photopub/docs/0000000693/b6d07aa2-ad86-4f43-b4d8-0726edc94c30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house16.png | file://x:/photopub/docs/0000000693/b27015d9-cad6-44b9-9919-14c887df6afb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png | file://x:/photopub/docs/0000000693/21fcaaa0-6531-46fa-b1de-63426f46ac08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house27.png | file://x:/photopub/docs/0000000693/a61bbe81-f2d8-4742-873a-f370435042cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png | file://x:/photopub/docs/0000000693/b09ee88a-2456-4454-867a-88b0a9be6fa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house17.png | file://x:/photopub/docs/0000000693/067a3264-b9dc-4319-890d-5777d674c60f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house30.png | file://x:/photopub/docs/0000000693/7087916d-ca99-47a1-b65c-4e02764e073a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELIN-951789-2017 | EL-609172-2017 | 11/7/2017 2:02:17 PM | ASSESS: EL: Final | png | #asFound | EL168 | Protection and control Ratings are not adequate. | 3 | 3 | #Hot_Tub_specs.png The installation of a new Beachcomber Hot Tub that requires a 40 amp overcurrent device is protected by a 2pole 50 amp 120/240 volt GFCI overcurrent (OC) device, this OC device exceeds both the Hot Tub specifications and the #8 cu NMWU 60 degree rated branch circuit conductors, this can lead to a thermal issue | 3 | Protection and control Ratings are not adequate. | Hot_Tub_specs.png | file://x:/photopub/docs/0000000693/f9c2099e-4992-47a3-bab6-134376fc365a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7160ef0_9240_40fd_a2ee_4ee5179c2851
ELIN-951379-2017 | EL-609672-2017 | 11/9/2017 9:48:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service_disconnect_1.png,Service_disconnect_2.png The repair installation of a damaged overhead 60 amp 120/240 volt service for a trailer disconnect is not approved for use as service entrance rated equipment in Canada, this could lead to an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_disconnect_2.png | file://x:/photopub/docs/0000000694/a48aff98-7730-4130-955d-0bff501e757b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8feae1ae_a599_4d3a_bebd_0e19b73a4148
ELIN-951379-2017 | EL-609672-2017 | 11/9/2017 9:48:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | #Service_disconnect_1.png,Service_disconnect_2.png The repair installation of a damaged overhead 60 amp 120/240 volt service for a trailer disconnect is not approved for use as service entrance rated equipment in Canada, this could lead to an equipment damage issue | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_disconnect_1.png | file://x:/photopub/docs/0000000694/897d91c1-68e4-446d-9990-e7a0b8a45d9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8feae1ae_a599_4d3a_bebd_0e19b73a4148
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png | file://x:/photopub/docs/0000000693/c546b4ef-0d69-4de3-bac9-5f5ffbe1fb76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house22.png | file://x:/photopub/docs/0000000693/567cdbc5-1867-47bf-86a1-0fe91c1dbed4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle3.png | file://x:/photopub/docs/0000000691/39cd8860-a229-413a-ae0a-fa40f11840ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house26.png | file://x:/photopub/docs/0000000693/0fd3a5a7-03d0-4fef-82a4-1012c3e0f389.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png | file://x:/photopub/docs/0000000693/15b26071-d6a4-4caf-a7dd-f2b012449c1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle8.png | file://x:/photopub/docs/0000000691/78b4660a-18fd-4f4a-9972-fe03dcf08589.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle2.png | file://x:/photopub/docs/0000000691/3068c444-43eb-491f-a5f8-2003ab991d35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
BPVOP-095964-2013 | 2253687 | 10/20/2017 | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound calibration sticker for ammonia sensors at time of assessment. | BP088 | 2.0.1 Control system may overrun - Calibration out of date | 2 | 3 | #Ammonia_sensor_calibration.png,Photo-2017-10-20-15-38-36_8174.JPG,Photo-2017-10-20-15-38-31_8173.JPG Ammonia sensors beyond 1 year calibration. | 2 | 2.0.1 Control system may overrun - Calibration out of date | Ammonia_sensor_calibration.png | file://x:/photopub/docs/0000000691/104953dc-24d2-4c8f-b77e-47e1695338b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3E7D2151_8DB1_431C_89E8_110393C9B69E
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle5.png | file://x:/photopub/docs/0000000691/fd652f1f-2b20-4e6b-aeee-6b795ab1cbf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png | file://x:/photopub/docs/0000000693/8b19af1c-4c74-4bae-afce-fad0730f11d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png | file://x:/photopub/docs/0000000693/29eaeea4-ee3f-4ac8-83b0-488062a5234a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png | file://x:/photopub/docs/0000000693/590ec534-12e7-4878-8186-91b059ff99a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house24.png | file://x:/photopub/docs/0000000693/7d74fadf-7c72-4f35-8310-3f453985ee56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house29.png | file://x:/photopub/docs/0000000693/a27175c7-b571-48a1-81ed-096036802890.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house28.png | file://x:/photopub/docs/0000000693/e86dec07-fe0a-462d-bdb1-743f6939026b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle6.png | file://x:/photopub/docs/0000000691/2aa0be54-5381-4a1b-93fd-94f4fc6545eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle1.png | file://x:/photopub/docs/0000000691/01189631-dfd6-4cb9-81c5-f59a29790973.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle4.png | file://x:/photopub/docs/0000000691/9451c906-1c4f-4880-b28e-204e92adf5f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELOP-937065-2017 | 199 | 11/3/2017 | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | #Thermally_damaged_receptacle1.png,Thermally_damaged_receptacle2.png,Thermally_damaged_receptacle3.png,Thermally_damaged_receptacle4.png,Thermally_damaged_receptacle5.png,Thermally_damaged_receptacle6.png,Thermally_damaged_receptacle7.png,Thermally_damaged_receptacle8.png Receptacles are required to be maintained in proper working order. When receptacles are over loaded they can become over heated and thermally damaged and in turn adjacent surfaces and structures can be thermally damaged. In some cases this can cause fires. This installation at a healing center gymnasium had a 15A 120V receptacle that was thermally damaged which also damaged the surrounding wooden structure where the receptacle was installed. The receptacle was still energized at the time of the inspection and was immediately made safe by disconnection and removal by a qualified electrical worker. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Thermally_damaged_receptacle7.png | file://x:/photopub/docs/0000000691/0d05e4f9-7ba6-4db6-8287-85f1a62afc65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2313F5A6_79EC_478A_A65B_46AD9699C7BB
ELIN-950532-2017 | EL-609183-2017 | 11/6/2017 4:17:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Hazard1.png Un-used breaker positions in panel board are not filled. This may cause a shock hazard to people operating breakers. It may cause a shock / fire hazard if conductive materials enter the un-filled openings. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Hazard1.png | file://x:/photopub/docs/0000000692/bd286e40-cc59-4cad-8b17-66f3adfce522.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecfe45b3_41b8_434b_8813_4bc605a0eafe
ELHE-955425-2017 | HE-611649-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Hazard.png Outlet box covers are not installed leaving exposed electrical conductors and a potential shock hazard. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Hazard.png | file://x:/photopub/docs/0000000694/14949566-79ca-41f3-a537-fad64e339c02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15d70a1b_fc1d_40fa_9b31_46ed3709406a
ELIN-949180-2017 | EL-592527-2017 | 11/7/2017 4:36:47 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound No connection to ground at time of inspection this picture was on opposite side from new service | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 3 | 3 | #Hazard1.png -Grounding electrode was not present at time of inspection not ensuring a low impedance path to ground. Grounding is for the safety of people and property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Hazard1.png | file://x:/photopub/docs/0000000692/fc295626-6624-4a61-a3c3-9f14dcb6c08e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4896fb80_b980_4f40_a19f_f356e6fc45c3
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house18.png | file://x:/photopub/docs/0000000693/2491c858-49e1-4947-85e4-a05b429676e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELHE-953211-2017 | HE-610467-2017 | 11/7/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house1.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house2.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house3.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house4.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house5.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house6.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house7.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house8.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house9.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house10.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house11.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house12.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house13.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house14.png,Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house15.png,Open_energiz | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_cabel__wiring_outlet_boxes_in_addtion_to_house20.png | file://x:/photopub/docs/0000000693/fcafe004-6f06-40f7-a06b-ad504a9a2a2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b62ab40b_13ec_4317_98ae_241c71dc9cd0
ELIN-956943-2017 | UW-612460-2017 | 11/9/2017 4:41:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Distribution1.png,Distribution2.png,Distribution3.png,Distribution4.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 40A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Distribution1.png | file://x:/photopub/docs/0000000694/0209dd46-1bd1-4f54-8bb2-3558050f7e73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae388dc4_8515_4d7c_a8e7_2b26cf26afdb
ELIN-956943-2017 | UW-612460-2017 | 11/9/2017 4:41:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Distribution1.png,Distribution2.png,Distribution3.png,Distribution4.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 40A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Distribution2.png | file://x:/photopub/docs/0000000694/edbd8397-d805-4378-97a6-7cfafad32b39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae388dc4_8515_4d7c_a8e7_2b26cf26afdb
ELIN-956943-2017 | UW-612460-2017 | 11/9/2017 4:41:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Distribution1.png,Distribution2.png,Distribution3.png,Distribution4.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 40A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Distribution4.png | file://x:/photopub/docs/0000000694/6789a016-9b97-45fb-aeb7-288f23079e16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae388dc4_8515_4d7c_a8e7_2b26cf26afdb
ELIN-956943-2017 | UW-612460-2017 | 11/9/2017 4:41:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Distribution1.png,Distribution2.png,Distribution3.png,Distribution4.png Before any regulated electrical work begins, it is required that a electrical permit be obtained. Once an electrical permit is in place, inspections are to be requested for each phase of electrical work before proceeding to the next phase. In this installation at a single family home, electrical equipment was installed for a horticultural project without a permit and without inspections. The Existing 200 A, 120/240V, single phase, combination panel had 2 x 100A, 1 x 60A, and 1 x 40A two pole breakers added for sub-panels. The additional loads from the sub-panels could create an overload condition on the main electrical panel or the incoming electrical service and cause damage to the equipment. The damaged electrical equipment has the potential to create a fire hazard within this dwelling. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Distribution3.png | file://x:/photopub/docs/0000000694/aeefca0f-1481-4720-af4a-59ab4a6a7917.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae388dc4_8515_4d7c_a8e7_2b26cf26afdb
GAIN-943438-2017 | GA-601638-2017 | 11/2/2017 10:52:27 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent.png The as-found condition is that a vent serving a water heater is located too close to combustible material. The hazard is that the high heat of the vent could potentially cause cause the combustible material to catch fire, creating a risk to occupants in the building. | 3 | Non compliant Type C Vent clearance | Vent.png | file://x:/photopub/docs/0000000691/b9f1b2b6-b97c-46d7-b04a-364fc3fe4040.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0064f6e2_365e_4a04_b9a8_a5398ad8dcaa
ELIN-953205-2017 | EL-591146-2017 | 11/8/2017 2:31:46 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #Service_Conduit.png The underground conduit feeding the new 200 amp 120/240 volt electrical service has not been covered with the correct amount of soil, leaving the conduit easily accessible from the current grade. This poses a shock hazard to persons who could come in contact with this conduit, and potential mechanical damage to the electrical Service Conduit and Equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Service_Conduit.png | file://x:/photopub/docs/0000000694/42af8ac7-2d14-4ca3-83d5-e4fef0878a30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65543562_ff5a_4c86_90c4_14167eee8ee0
GAIN-871264-2017 | GA-514470-2017 | 10/23/2017 11:52:00 AM | ASSESS: GA: Final | png | #asFound propane regulator | GA054 | Code prohibited practices or materials | 3 | 3 | #Propane_regulator.png Photos showed regulator not protected from damage, this condition could cause damage from weather | 3 | Code prohibited practices or materials | Propane_regulator.png | file://x:/photopub/docs/0000000694/2e9d17d4-b9a1-434d-b2c2-1169f8d0043a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50ccaacc_2a6d_415c_a029_130f9f682b6f
GAIN-943830-2017 | GA-510630-2017 | 11/9/2017 1:56:34 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #BBQ_Install1.png,BBQ_Install2.png,BBQ_Install3.png,BBQ_Install4.png,BBQ_Install5.png,BBQ_Install6.png Built in BBQ and stock pot cooker installed under combustible material. In the event of a fire the surrounding combustible material may catch fire causing property damage | 3 | Clearance to combustible not met | BBQ_Install1.png | file://x:/photopub/docs/0000000694/b4b8b80f-4983-49a3-b5c5-5901ab26bd99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7c73b8_4ba9_4ce8_b063_381a0f282ee7
GAIN-943830-2017 | GA-510630-2017 | 11/9/2017 1:56:34 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #BBQ_Install1.png,BBQ_Install2.png,BBQ_Install3.png,BBQ_Install4.png,BBQ_Install5.png,BBQ_Install6.png Built in BBQ and stock pot cooker installed under combustible material. In the event of a fire the surrounding combustible material may catch fire causing property damage | 3 | Clearance to combustible not met | BBQ_Install3.png | file://x:/photopub/docs/0000000694/ae59d3d8-1972-400f-9fa5-9e811e9f0b8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7c73b8_4ba9_4ce8_b063_381a0f282ee7
GAIN-943830-2017 | GA-510630-2017 | 11/9/2017 1:56:34 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #BBQ_Install1.png,BBQ_Install2.png,BBQ_Install3.png,BBQ_Install4.png,BBQ_Install5.png,BBQ_Install6.png Built in BBQ and stock pot cooker installed under combustible material. In the event of a fire the surrounding combustible material may catch fire causing property damage | 3 | Clearance to combustible not met | BBQ_Install6.png | file://x:/photopub/docs/0000000694/8afae1bf-d086-49b2-85cd-caae3aa279b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7c73b8_4ba9_4ce8_b063_381a0f282ee7
GAIN-943830-2017 | GA-510630-2017 | 11/9/2017 1:56:34 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #BBQ_Install1.png,BBQ_Install2.png,BBQ_Install3.png,BBQ_Install4.png,BBQ_Install5.png,BBQ_Install6.png Built in BBQ and stock pot cooker installed under combustible material. In the event of a fire the surrounding combustible material may catch fire causing property damage | 3 | Clearance to combustible not met | BBQ_Install2.png | file://x:/photopub/docs/0000000694/94b5033f-834b-4153-9f77-39bd4bd3a0a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7c73b8_4ba9_4ce8_b063_381a0f282ee7
GAIN-943830-2017 | GA-510630-2017 | 11/9/2017 1:56:34 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #BBQ_Install1.png,BBQ_Install2.png,BBQ_Install3.png,BBQ_Install4.png,BBQ_Install5.png,BBQ_Install6.png Built in BBQ and stock pot cooker installed under combustible material. In the event of a fire the surrounding combustible material may catch fire causing property damage | 3 | Clearance to combustible not met | BBQ_Install4.png | file://x:/photopub/docs/0000000694/effd54d4-f640-4a36-8dab-205f0f32dfcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7c73b8_4ba9_4ce8_b063_381a0f282ee7
GAIN-943830-2017 | GA-510630-2017 | 11/9/2017 1:56:34 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | #BBQ_Install1.png,BBQ_Install2.png,BBQ_Install3.png,BBQ_Install4.png,BBQ_Install5.png,BBQ_Install6.png Built in BBQ and stock pot cooker installed under combustible material. In the event of a fire the surrounding combustible material may catch fire causing property damage | 3 | Clearance to combustible not met | BBQ_Install5.png | file://x:/photopub/docs/0000000694/40f2d97e-322c-44c2-97b8-a19960b8d3ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7c73b8_4ba9_4ce8_b063_381a0f282ee7
ELIN-961982-2017 | UW-615055-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazard1.png,Hazard2.png Fire alarm remote annunciators without evidence of periodic testing, signs of water ingress and signs of deterioration to the enclosure plexi-glass limiting viewing ability. Without proper viewing ability and function of the remote annunciators, emergency personnel may not be able to address emergencies effectively creating a potential hazard to persons and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazard1.png | file://x:/photopub/docs/0000000697/ffec5438-7cc4-42f8-b6f4-225893ee75a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c19146ef_9305_4c8f_8697_8ddace07cc89
ELIN-961982-2017 | UW-615055-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazard1.png,Hazard2.png Fire alarm remote annunciators without evidence of periodic testing, signs of water ingress and signs of deterioration to the enclosure plexi-glass limiting viewing ability. Without proper viewing ability and function of the remote annunciators, emergency personnel may not be able to address emergencies effectively creating a potential hazard to persons and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazard2.png | file://x:/photopub/docs/0000000697/710ff665-67c6-4f31-91ab-77c29b22ff81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c19146ef_9305_4c8f_8697_8ddace07cc89
GAIN-936861-2017 | GA-594051-2017 | 11/16/2017 10:37:44 AM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Stock_pot_burner.png The as-found condition is that a stock pot burner installed in a commercial kitchen has been connected to a gas supply that is greater than the maximum rated pressure of the appliance. The potential hazard is that the stock pot burner will overfire, creating a risk of fire and equipment damage. | 4 | Appliance regulator not installed, incorrect delivery pressure | Stock_pot_burner.png | file://x:/photopub/docs/0000000697/9a1c133e-b8c4-4b8c-a202-b8efdbb50d4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b67ac8aa_0869_44e1_8ce7_a317d527ebc1
ELIN-958429-2017 | EL-594221-2017 | 11/16/2017 12:59:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 3 | #Consumer_service_conduit_not_bonded.png In a commercial pump house service upgrade the consumer service conduit containing the 200 amp 120/208 volt service conductors was found not to be properly bonded to ground. This could result in a shock hazard condition. Picture attached. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Consumer_service_conduit_not_bonded.png | file://x:/photopub/docs/0000000697/9c1e66e7-165f-4fd3-818f-39238c1476c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc799e52_7370_45a6_bfe3_89a1d0ea88b1
ELIN-963522-2017 | EL-615388-2017 | 11/20/2017 11:19:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL339 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 | #Hazard_1.png 15A rated duplex GFCI receptacles are protected by a circuit breaker having a higher amperage rating the receptacles may not be able to handle 20A. | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Hazard_1.png | file://x:/photopub/docs/0000000699/7ab9c520-cb2d-4f82-b6a2-aa9200f27968.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e82d4a5_6180_45c9_bdd7_0aedcbf843d5
ELIN-963816-2017 | EL-591938-2017 | 11/20/2017 1:43:36 PM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 | #Hazard.png,Hazard2.png Working area in front of and above panel has not been provided and may cause a risk to personal working or operating panelboard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Hazard2.png | file://x:/photopub/docs/0000000699/28d0f699-6ed5-4a1a-9487-2b457cdb7930.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__656cdcae_f61d_4fbf_a6cc_66dc25f5a723
ELIN-963816-2017 | EL-591938-2017 | 11/20/2017 1:43:36 PM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 | #Hazard.png,Hazard2.png Working area in front of and above panel has not been provided and may cause a risk to personal working or operating panelboard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Hazard.png | file://x:/photopub/docs/0000000699/4b783511-e71b-4f32-887a-79492558e062.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__656cdcae_f61d_4fbf_a6cc_66dc25f5a723
BPOP-936501-2017 | BPV-472188-2015 | 11/10/2017 10:42:01 AM | ASSESS: Propane PV: Periodic | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | #Tank.png Tank installed up against outbuilding wall. | 2 | Installation clearances or set backs to propane containers not met | Tank.png | file://x:/photopub/docs/0000000695/2f216a1b-9486-408d-8b81-65cc4927c152.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de0d117c_de6d_4d3e_9b71_83ebd747d00b
ELIN-921012-2017 | EL-376280-2016 | 11/15/2017 9:32:26 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | #Tamper_resistant_plugs_required_in_dwelling_units.png This assessment found that Tamper resistant outlets have not been provided creating a shock hazard. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Tamper_resistant_plugs_required_in_dwelling_units.png | file://x:/photopub/docs/0000000696/b216b80f-2266-423a-8e04-2c6d88f2be8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1488c63_5868_4a0d_ad82_6f89aa1b9406
ELIN-953353-2017 | EL-206281-2015 | 11/17/2017 2:35:39 PM | ASSESS: EL: Final | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | #F.png Kitchen counter receptacles located within 1.5m of the kitchen sink are not GFCI protected, they are also 15 Amp rated receptacles and have been terminated on a 20 Amp branch circuit over current device. This poses a serious risk an individual ( Shock) and property damage through a thermal event (fire). | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | F.png | file://x:/photopub/docs/0000000699/aa2a1f04-e9e0-45a8-86fb-582257950aed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47d5b923_2b71_425a_8b10_6e593b6e4c33
PROP-871026-2017 | PR-312459-2015 | 11/15/2017 8:09:46 AM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | #Smoke_alrm_installation_.png Smoke alarms are not installed, therefore will not annunciate if a fire were to start. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Smoke_alrm_installation_.png | file://x:/photopub/docs/0000000697/557273bd-a70a-4866-8f4b-8110c277308e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__793248E4_FA9E_4638_9321_DFEAD7393A42
ELIN-962087-2017 | UW-615140-2017 | 11/15/2017 2:40:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL349 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Hazard.png Covers removed on energized control device leaving exposed electrical terminals and conductors and a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Hazard.png | file://x:/photopub/docs/0000000698/5fa5ee05-89bf-4164-8c3b-c523949a2653.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b34e086_699d_4094_89b4_9abd3a2e209e
GAIN-961110-2017 | GA-610299-2017 | 11/17/2017 12:00:03 PM | ASSESS: GA: Final | png | #asFound | GA070 | Undersized hose or appliance connector | 3 | 3 | #Gas_cnnector.png Gas connector connected to appliance is undersized for BTU Input of appliance. The appliance will be under Fired causing system failures inside appliance | 3 | Undersized hose or appliance connector | Gas_cnnector.png | file://x:/photopub/docs/0000000698/5f18f67c-eb42-4ced-9f85-7dd75954001e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f94fcb53_867f_4c50_aea0_8c7c947f9657
ELIN-957785-2017 | UW-612977-2017 | 11/3/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #No_device_box.png An additional, and not interconnected, smoke detector had been added by a previous homeowner to what had been an unfinished basement. The smoke detector was wired directly to a branch circuit cable which had been extended from a nearby switch box. No device box was installed to contain the splice. In the event of a fault at this splice location, thermal energy would not be contained and could potentially ignite nearby wooden structural members. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | No_device_box.png | file://x:/photopub/docs/0000000696/aebd3486-8cc4-411f-ad65-e689233c7903.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28757a5f_b258_4800_9866_9a0b949cbc3d
ELIN-954226-2017 | EL-386778-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Coverplates1.png,Coverplates2.png 120 volt 15 amp junction boxes, switches and receptacles have not been provided with cover plates in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Coverplates2.png | file://x:/photopub/docs/0000000695/b74b87a5-4292-495c-a320-ac6820702fe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d5fc352_85fb_4210_9ba3_292790f8e7bd
ELIN-942649-2017 | EL-506841-2017 | 11/10/2017 11:35:06 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Panel.png An energized 200 amp 120/240 volt electrical panel does not have the panel cover installed effectively covering or guarding to components inside which could become easily energized by operation of the Main Breaker which is not locked in the off position. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel.png | file://x:/photopub/docs/0000000695/75542926-3b1e-4af5-af57-56fcdabdd996.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__802090b2_a9b2_4421_bb98_addc4f44aed1
ELIN-954226-2017 | EL-386778-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Coverplates1.png,Coverplates2.png 120 volt 15 amp junction boxes, switches and receptacles have not been provided with cover plates in areas where the wiring and connections are accessible. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Coverplates1.png | file://x:/photopub/docs/0000000695/75d73405-337e-4bda-81a4-3af1043b6771.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d5fc352_85fb_4210_9ba3_292790f8e7bd
ELIN-962889-2017 | EL-569373-2017 | 11/20/2017 1:25:23 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3 | 2 | #Bonding_screw1.png,Bonding_screw2.png Bonding screw left in sub panel, could cause circulating current, or shock hazard | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Bonding_screw1.png | file://x:/photopub/docs/0000000699/127c2f24-b7ff-4613-be99-3ede891f3efc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__187d39d3_d4b0_4e11_a339_f76de9fbf430
ELOP-956293-2017 | 5363402 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Hazard1.png,Hazard2.png Energized 120 volt terminals and conductors are accessible in a control panel within an electrical room inside a lockable hinged door creating a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Hazard1.png | file://x:/photopub/docs/0000000697/32692225-9df5-40a5-8a01-64e7da0abdf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c836c703_e819_4c7c_b25b_eb3b7f590fc4
ELOP-956293-2017 | 5363402 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL299 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Hazard1.png,Hazard2.png Energized 120 volt terminals and conductors are accessible in a control panel within an electrical room inside a lockable hinged door creating a potential shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Hazard2.png | file://x:/photopub/docs/0000000697/f4aed78b-23b7-4e4a-b0ec-5e086e549253.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c836c703_e819_4c7c_b25b_eb3b7f590fc4
ELIN-954522-2017 | EL-368474-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exposed_wiring_in_the_shop-garage_building1.png,Exposed_wiring_in_the_shop-garage_building2.png,Exposed_wiring_in_the_shop-garage_building3.png,Exposed_wiring_in_the_shop-garage_building4.png,Exposed_wiring_in_the_shop-garage_building5.png Cables installed in locations where they may be subject to mechanical damage need to be approved for the location or they need to be protected in an acceptable manner. This is required to prevent the cable jacket and inner conductor insulation from mechanical damage during and after construction. This installation for a recently completed new house and detached shop/garage building had NMD90 cables (non-metallic sheathed cables) installed inside of a 2â€ x 6â€ exterior stud wall in a detached shop/garage building. The cables passed through the wall studs and were installed correctly however the walls remained open and unfinished at the time the final inspection was requested. Various items including some sharp and/or heavy metal items were being stored inside the wall | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_wiring_in_the_shop-garage_building2.png | file://x:/photopub/docs/0000000695/da7795f3-f14d-4e1e-bd1e-827c3b4bec74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c43648a_9261_4470_8887_34ae358320f7
ELIN-954522-2017 | EL-368474-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exposed_wiring_in_the_shop-garage_building1.png,Exposed_wiring_in_the_shop-garage_building2.png,Exposed_wiring_in_the_shop-garage_building3.png,Exposed_wiring_in_the_shop-garage_building4.png,Exposed_wiring_in_the_shop-garage_building5.png Cables installed in locations where they may be subject to mechanical damage need to be approved for the location or they need to be protected in an acceptable manner. This is required to prevent the cable jacket and inner conductor insulation from mechanical damage during and after construction. This installation for a recently completed new house and detached shop/garage building had NMD90 cables (non-metallic sheathed cables) installed inside of a 2â€ x 6â€ exterior stud wall in a detached shop/garage building. The cables passed through the wall studs and were installed correctly however the walls remained open and unfinished at the time the final inspection was requested. Various items including some sharp and/or heavy metal items were being stored inside the wall | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_wiring_in_the_shop-garage_building4.png | file://x:/photopub/docs/0000000695/28f8466f-4ba4-41d1-9e95-02f67951fa4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c43648a_9261_4470_8887_34ae358320f7
ELIN-954522-2017 | EL-368474-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exposed_wiring_in_the_shop-garage_building1.png,Exposed_wiring_in_the_shop-garage_building2.png,Exposed_wiring_in_the_shop-garage_building3.png,Exposed_wiring_in_the_shop-garage_building4.png,Exposed_wiring_in_the_shop-garage_building5.png Cables installed in locations where they may be subject to mechanical damage need to be approved for the location or they need to be protected in an acceptable manner. This is required to prevent the cable jacket and inner conductor insulation from mechanical damage during and after construction. This installation for a recently completed new house and detached shop/garage building had NMD90 cables (non-metallic sheathed cables) installed inside of a 2â€ x 6â€ exterior stud wall in a detached shop/garage building. The cables passed through the wall studs and were installed correctly however the walls remained open and unfinished at the time the final inspection was requested. Various items including some sharp and/or heavy metal items were being stored inside the wall | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_wiring_in_the_shop-garage_building1.png | file://x:/photopub/docs/0000000695/280cb734-cfbf-4bd9-8136-03b0d6e536f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c43648a_9261_4470_8887_34ae358320f7
ELIN-954522-2017 | EL-368474-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exposed_wiring_in_the_shop-garage_building1.png,Exposed_wiring_in_the_shop-garage_building2.png,Exposed_wiring_in_the_shop-garage_building3.png,Exposed_wiring_in_the_shop-garage_building4.png,Exposed_wiring_in_the_shop-garage_building5.png Cables installed in locations where they may be subject to mechanical damage need to be approved for the location or they need to be protected in an acceptable manner. This is required to prevent the cable jacket and inner conductor insulation from mechanical damage during and after construction. This installation for a recently completed new house and detached shop/garage building had NMD90 cables (non-metallic sheathed cables) installed inside of a 2â€ x 6â€ exterior stud wall in a detached shop/garage building. The cables passed through the wall studs and were installed correctly however the walls remained open and unfinished at the time the final inspection was requested. Various items including some sharp and/or heavy metal items were being stored inside the wall | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_wiring_in_the_shop-garage_building5.png | file://x:/photopub/docs/0000000695/18bb8387-144c-4808-8257-ea84e7d3e34d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c43648a_9261_4470_8887_34ae358320f7
ELIN-954808-2017 | EL-559510-2017 | 11/9/2017 12:29:58 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Hazard1.png Luminaire above bathtub is not approved for use in a damp location. The light bulb can be changed while standing in the bathtub without a barrier. This may cause a shock hazard if the light bulb is changed with or without water in the bath tub. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Hazard1.png | file://x:/photopub/docs/0000000695/32081248-49e2-4261-aa00-af27e2870725.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a291fa2_a311_469d_987a_961dbc1c28a6
GAIN-959146-2017 | GA-609722-2017 | 11/14/2017 10:53:07 AM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Vent.png At time of inspection venting of water heater terminated into a exciting chimney, this condition can cause damage to chimney. | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Vent.png | file://x:/photopub/docs/0000000696/77cb6873-8b93-404c-8443-90748343cabd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0dfeeb3_ad81_421c_b4fb_12e6805d7106
ELIN-960894-2017 | EL-583384-2017 | 11/16/2017 10:52:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | #Pic4.png Ground plate is not buried to the correct depth at time of inspection. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Pic4.png | file://x:/photopub/docs/0000000697/76f160c6-a0f5-4e31-9b00-5b8e89ea7362.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f59dc1c_54eb_48af_8cc3_eef0db5f4eda
ELIN-960893-2017 | EL-563279-2017 | 11/16/2017 8:47:17 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | #Wrong_staple_for_conductor_size.png 30 amp, 120/240 volt non-metallic-sheathed cable is support by straps not approved for cable. This is a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Wrong_staple_for_conductor_size.png | file://x:/photopub/docs/0000000697/e21ae1e1-5e33-4aeb-8a0f-d47df23213ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f10841dc_087b_47e6_a1dc_7c012447776e
ELIN-947290-2017 | EL-265358-2015 | 11/16/2017 12:51:28 PM | ASSESS: EL: Final | png | #asFound | EL338 | Installation of electrical equipment Equipment is not approved for the specific use; specifically, the receptacle is undersized and not adequately protected. | 4 | 4 | #15_amp_receptacle_installed_with_a_20_amp_overcurrent_device.png 15 amp, 120 volt receptacle installed on a branch circuit that is protected by a 20 amp overcurrent device. This is a thermal issue. | 4 | Installation of electrical equipment Equipment is not approved for the specific use; specifically, the receptacle is undersized and not adequately protected. | 15_amp_receptacle_installed_with_a_20_amp_overcurrent_device.png | file://x:/photopub/docs/0000000697/d937ad88-3dc5-48e7-a216-ef30b2b07a80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6433628d_88ab_4e29_86ec_d2f070b32e6d
ELIN-948816-2017 | EL-595253-2017 | 11/15/2017 2:18:32 PM | ASSESS: EL: Service Connection | png | #asFound the service ground conductor is terminated in the branch circuit compartment bonding bus, this is the wrong grounding location and crosses the protective barrier | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | #Incorrect_service_ground.png The system ground conductor is terminated on a bond bus in the branch circuit compartment. The system is not correctly grounded and the ground conductor crosses the protective barrier between compartments. | 4 | Installation Grounding; conductor is not continuous. | Incorrect_service_ground.png | file://x:/photopub/docs/0000000697/7774357a-0e63-440e-9a17-926307dff69b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f93c3b4c_4177_4a1a_90ef_0ba246b345c4
GAHE-960604-2017 | HE-614295-2017 | 11/15/2017 2:26:28 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent_connector.png Single wall vent connector installed too close to a combustible wall. They may eventually lead to a fire. | 3 | Non compliant Type C Vent clearance | Vent_connector.png | file://x:/photopub/docs/0000000696/d3aed363-9790-46e1-8959-8a5a33fbfaca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02a0086e_6c21_4c0b_b077_e6fdc071dcff
ELIN-957909-2017 | EL-613088-2017 | 11/15/2017 8:26:10 AM | ASSESS: EL: Service Connection | png | #asFound | EL324 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 3 | 3 | #Unprotected_consumer_service_supply_conductor.png In a new single family dwelling the 200 amp 120/240 volt consumer service supply conductor was left exposed laying on top of the ground and was subject to mechanical damage. This could result in a equipment damage and shock condition. Picture attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Unprotected_consumer_service_supply_conductor.png | file://x:/photopub/docs/0000000697/78fc960d-30ac-4408-b76f-ab3c96ec8b94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a28f2dc_7363_4f05_9637_1c701eb38cfe
ELIN-957659-2017 | EL-605648-2017 | 11/15/2017 7:29:09 AM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #No_lockable_cover_provided.png In a new single family dwelling a 125 amp 120/240 volt main distribution panel was found to not have a lockable cover installed and the residence was not in lock up stage. This could result in a shock hazard condition. Picture attached. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | No_lockable_cover_provided.png | file://x:/photopub/docs/0000000697/c1873e44-13ec-4751-9133-ac38ad108f6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17aeacba_c115_4d74_8a9d_908c5476e988
ELIN-958856-2017 | EL-613259-2017 | 11/14/2017 5:56:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Main_Panel4.png A 400 amp 120/240 volt Panel has been connected to a 200 amp Cable and Meterbase. This poses a shock hazard and potential damage to the electrical components because the service conductors could be overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Main_Panel1.png | file://x:/photopub/docs/0000000696/3f0c6419-a3e6-4296-8787-648dcc260cb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0734efa_e138_4720_98ae_aa5894432d45
ELIN-958856-2017 | EL-613259-2017 | 11/14/2017 5:56:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Main_Panel4.png A 400 amp 120/240 volt Panel has been connected to a 200 amp Cable and Meterbase. This poses a shock hazard and potential damage to the electrical components because the service conductors could be overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Main_Panel4.png | file://x:/photopub/docs/0000000696/639b95c5-8160-4bc6-9766-f9382076e4bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0734efa_e138_4720_98ae_aa5894432d45
ELIN-958856-2017 | EL-613259-2017 | 11/14/2017 5:56:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Main_Panel4.png A 400 amp 120/240 volt Panel has been connected to a 200 amp Cable and Meterbase. This poses a shock hazard and potential damage to the electrical components because the service conductors could be overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Main_Panel2.png | file://x:/photopub/docs/0000000696/90b942dd-4740-4c86-a18d-43eb58ae7713.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0734efa_e138_4720_98ae_aa5894432d45
ELIN-958856-2017 | EL-613259-2017 | 11/14/2017 5:56:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 3 | 3 | #Main_Panel1.png,Main_Panel2.png,Main_Panel3.png,Main_Panel4.png A 400 amp 120/240 volt Panel has been connected to a 200 amp Cable and Meterbase. This poses a shock hazard and potential damage to the electrical components because the service conductors could be overloaded. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Main_Panel3.png | file://x:/photopub/docs/0000000696/843ab434-1298-4124-a4dd-1217c9a61cee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0734efa_e138_4720_98ae_aa5894432d45
ELIN-953158-2017 | EL-487021-2017 | 11/15/2017 11:21:04 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | #Panelboard.png The electric heat installation in a new SFD was wired with #14awg cable and protected by 20 amp 240 volt overcurrent devices, this can lead to a thermal issue on the cable | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Panelboard.png | file://x:/photopub/docs/0000000696/8bcbb03c-dc50-4c45-ace7-4530f316bf37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65cf529e_209e_423b_8c42_145f6cee28bf
ELIN-953451-2017 | EL-525362-2017 | 11/15/2017 3:24:42 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Eaton_Main_Panel1.png,Eaton_Main_Panel2.png In a new 200 amp 120/240 volt Eaton brand Panel, Individual Breaker from another manufacturer have been installed and are not compatible with the Eaton Panel. This voids the warranty of the panel and poses a potential shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Eaton_Main_Panel1.png | file://x:/photopub/docs/0000000697/c698fd08-9a5e-4ed1-84b1-58592c5f9fd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40b7a1fa_1dc6_4ea6_9da8_b340b7a23ec8
ELIN-953451-2017 | EL-525362-2017 | 11/15/2017 3:24:42 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | #Eaton_Main_Panel1.png,Eaton_Main_Panel2.png In a new 200 amp 120/240 volt Eaton brand Panel, Individual Breaker from another manufacturer have been installed and are not compatible with the Eaton Panel. This voids the warranty of the panel and poses a potential shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Eaton_Main_Panel2.png | file://x:/photopub/docs/0000000697/afa4cef2-abb8-49cc-bf29-713f188e70bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40b7a1fa_1dc6_4ea6_9da8_b340b7a23ec8
ELIN-956969-2017 | EL-612480-2017 | 11/14/2017 4:44:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | #DB2_cable.png This assessment found that the service cable was installed above grade in a conduit approved only for underground. This conduit is light duty and subject to damage. This cable is unfused from Hydro and poses a fire and shock hazard if damaged. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | DB2_cable.png | file://x:/photopub/docs/0000000696/abf75fd3-7418-4131-a634-d1ef57121f3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34be33f8_0315_45ff_b89c_1cfd380b35cf
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png | file://x:/photopub/docs/0000000697/0f2d3f14-71de-4915-9a0b-c3f3bb23fda4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png | file://x:/photopub/docs/0000000697/3ce3082d-7e68-49c7-9b90-c1d9d5d94c76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png | file://x:/photopub/docs/0000000697/3da6eb9c-f86f-40c5-be33-f6e928da0c62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
GAIN-956532-2017 | GA-584730-2017 | 11/14/2017 1:40:55 PM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Rating_plate.png The as found condition is that the gas pressure serving 2 ranges is higher than the appliances are rated for. The potential hazard is the appliances are over fired which has the potential for a kitchen fire and delayed ignition of the burners injuring the operator of the appliance. | 4 | Appliance regulator not installed, incorrect delivery pressure | Rating_plate.png | file://x:/photopub/docs/0000000696/1d1da145-5b76-468b-89fe-62c8de13a417.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__abeeb83c_5c0a_4ea8_9b20_e600e64cafc2
ELIN-958237-2017 | EL-353398-2016 | 11/14/2017 4:44:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Hazard2.png Exposed conductors in wire nut spices may cause a fire or shock hazard if pushed into device boxes and may contact a conductor of different polarity or grounded metal. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Hazard2.png | file://x:/photopub/docs/0000000696/858e585a-d56d-4309-a217-644adcbceae2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3e57142_95d4_473b_9ea3_e607da3c6006
ELIN-957936-2017 | EL-583384-2017 | 11/14/2017 1:20:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | #Hazard1.png De-Energized Service cables are not protected and may be damaged prior to installation of service equipment. | 0 | No Created Hazard Identified | Hazard1.png | file://x:/photopub/docs/0000000696/d4885712-0112-4740-bb24-ba2658df1fd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d51f74d_3f6b_4b0f_b9d7_b091843bcf97
ELIN-956528-2017 | EL-580996-2017 | 11/10/2017 1:20:00 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | #Receptacle_missing.png This assessment found that a receptacle on the island with a greater dimension of 600mm and 300mm is missing, this can create a shock hazard for appliances pluged in the other plug across the sink. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Receptacle_missing.png | file://x:/photopub/docs/0000000695/125a4683-e2cc-441f-ba95-54893e44cc3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__808d0dd3_9b0b_497e_97a0_c17b45042fff
ELIN-922834-2017 | EL-559063-2017 | 11/14/2017 1:25:27 PM | ASSESS: EL: Final | png | #asFound | EL288 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_filler_missing.png A panel filler is not installed in main distribution panel. It is reasonable to assume that accidental contact of the live parts of panel pose a possible shock hazard | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_filler_missing.png | file://x:/photopub/docs/0000000696/07e02f8b-fc2a-406f-a5f2-8238aa742e22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42212e6a_9ddb_4435_95cb_e13006c2bd72
ELIN-956989-2017 | EL-589474-2017 | 11/14/2017 3:24:50 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | #Support_required.png The outlet boxes required support on two sides. There could be damage during the drywall installation that could become a shock hazard if the boxes are damaged. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Support_required.png | file://x:/photopub/docs/0000000696/35df8023-4dd0-4505-a9c5-02e98c40c823.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff63dd81_0680_4b8a_9b7c_a1658ff4334e
ELIN-958862-2017 | EL-496885-2017 | 11/17/2017 12:59:16 PM | ASSESS: EL: Final | png | #asFound | EL325 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3 | 3 | #Improper_and_unapproved_neutral_termination1.png,Improper_and_unapproved_neutral_termination2.png,Improper_and_unapproved_neutral_termination3.png,Improper_and_unapproved_neutral_termination4.png Termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a house being upgraded and renovated had a 100A sub-panel feeder cable neutral conductor termination that was not approved for use with the panel that it was installed in. The termination lug was a solderless lug that was not approved for installation on the neutral bus within the particular panel that it was installed in. This may cause a poor connection that can not be installed and tightened adequately. Left uncorrected this is a fire hazard if the conductor termination becomes over he | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Improper_and_unapproved_neutral_termination1.png | file://x:/photopub/docs/0000000698/a36ee30d-0e35-4156-a86c-3d9ca47b9572.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a4af276_db8d_4c59_bde6_31e0f62d6da7
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png | file://x:/photopub/docs/0000000697/a9c9b11e-636d-4a94-9ec6-792f316400c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png | file://x:/photopub/docs/0000000697/c4f3e271-9327-4f21-b8ee-68ce5b37b94f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
ELIN-954522-2017 | EL-368474-2016 | 11/10/2017 | ASSESS: EL: Final | png | #asFound | EL329 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | #Exposed_wiring_in_the_shop-garage_building1.png,Exposed_wiring_in_the_shop-garage_building2.png,Exposed_wiring_in_the_shop-garage_building3.png,Exposed_wiring_in_the_shop-garage_building4.png,Exposed_wiring_in_the_shop-garage_building5.png Cables installed in locations where they may be subject to mechanical damage need to be approved for the location or they need to be protected in an acceptable manner. This is required to prevent the cable jacket and inner conductor insulation from mechanical damage during and after construction. This installation for a recently completed new house and detached shop/garage building had NMD90 cables (non-metallic sheathed cables) installed inside of a 2â€ x 6â€ exterior stud wall in a detached shop/garage building. The cables passed through the wall studs and were installed correctly however the walls remained open and unfinished at the time the final inspection was requested. Various items including some sharp and/or heavy metal items were being stored inside the wall | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_wiring_in_the_shop-garage_building3.png | file://x:/photopub/docs/0000000695/f7167ab0-465f-4692-8e34-9af0d3ac86fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c43648a_9261_4470_8887_34ae358320f7
GAHE-962128-2017 | HE-615175-2017 | 11/16/2017 1:26:09 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 2 | #Underground_3.png,Underground.png Gas line entering building below grade. Gas leak could follow space surrounding pipe and enter building. Risk of explosion and or fire. | 3 | Underground piping entering a building below grade (unapproved) | Underground_3.png | file://x:/photopub/docs/0000000697/1af1e423-1e4e-4887-99c5-44323b65e141.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98b310fd_81b5_4fcc_9c8b_a2aea44035df
GAIN-915135-2017 | GA-589256-2017 | 11/14/2017 2:06:09 PM | ASSESS: GA: Final | png | #asFound Five feet showing on tape measure. | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Vent_clearance.png Mechanical appliance intake installed with 50% of the required separation to meter relief. Failure of the relief device on the meter would result in the release of high pressure gas in the vicinity of the appliance intake. This gas vapour could be through the appliance intake into the combustion chamber. Risk of over fire condition resulting in the production of carbon monoxide or damage to the firebox of appliance. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Vent_clearance.png | file://x:/photopub/docs/0000000696/82aaa421-3c6b-4dd0-b07a-f656f4c6a75d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95a1a007_ace8_4cb9_8b4f_241dfcb35e6d
BPVOP-868278-2017 | 2282230 | 11/7/2017 11:17:31 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | #ASME_plate_and_PRD.png Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver with MAWP of 200 psig, I found a Pressure Relief Device not replaced within the last 3 years and the NDT was not done as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety order not followed. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | ASME_plate_and_PRD.png | file://x:/photopub/docs/0000000695/491dcde0-9a5a-4dd5-a66d-8d2e6324f74b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68abfb94_574d_4630_8a09_cc02adbb9610
BPVOP-956487-2017 | BPV 00000028319-2013 | 11/9/2017 10:44:51 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Log_book_enrtries_5th_class_certificate1.png,Log_book_enrtries_5th_class_certificate2.png,Log_book_enrtries_5th_class_certificate3.png,Log_book_enrtries_5th_class_certificate4.png,Log_book_enrtries_5th_class_certificate5.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 175kw class B2 Refrigeration plant during the evening and night shifts while the plant was operating. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Log_book_enrtries_5th_class_certificate1.png | file://x:/photopub/docs/0000000695/53826e4f-d36b-4dda-8ee0-2de20ab5b878.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b034dea9_35f3_4ca1_8ca0_d3d69c372806
BPVOP-956487-2017 | BPV 00000028319-2013 | 11/9/2017 10:44:51 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Log_book_enrtries_5th_class_certificate1.png,Log_book_enrtries_5th_class_certificate2.png,Log_book_enrtries_5th_class_certificate3.png,Log_book_enrtries_5th_class_certificate4.png,Log_book_enrtries_5th_class_certificate5.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 175kw class B2 Refrigeration plant during the evening and night shifts while the plant was operating. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Log_book_enrtries_5th_class_certificate2.png | file://x:/photopub/docs/0000000695/4f034bf2-cca3-48a7-8b52-dcbd834b842c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b034dea9_35f3_4ca1_8ca0_d3d69c372806
BPVOP-956487-2017 | BPV 00000028319-2013 | 11/9/2017 10:44:51 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Log_book_enrtries_5th_class_certificate1.png,Log_book_enrtries_5th_class_certificate2.png,Log_book_enrtries_5th_class_certificate3.png,Log_book_enrtries_5th_class_certificate4.png,Log_book_enrtries_5th_class_certificate5.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 175kw class B2 Refrigeration plant during the evening and night shifts while the plant was operating. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Log_book_enrtries_5th_class_certificate3.png | file://x:/photopub/docs/0000000695/a8c30b2c-b0bf-49d4-ba9c-9e56bd7ce2f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b034dea9_35f3_4ca1_8ca0_d3d69c372806
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png | file://x:/photopub/docs/0000000697/a91db767-cc5a-4d84-9852-43dad6f2f6e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
GAIN-960046-2017 | UW-614066-2017 | 11/14/2017 7:44:28 PM | ASSESS: GA: Final | png | #asFound Furnace not installed to manufacturers instruction | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Furnace_.png Found furnace in service without any evidence of permit or safe start up. If the furnace is not set up properly and all safeties aren't checked, there could be a failure and the unit would not shut off properly, thus creating a hazard leading to damage and possible injury. | 3 | Appliance not installed according to installation instructions | Furnace_.png | file://x:/photopub/docs/0000000696/8247660a-0237-457c-b032-6eb9d4994640.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbfdef0e_b606_4325_a602_6714aaf626a2
GAIN-921449-2017 | GA-593016-2017 | 11/15/2017 4:23:29 PM | ASSESS: GA: Final | png | #asFound | GA114 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | 3 | 3 | #Oversized_common_venting.png Common venting used to vent flue gases of Furnace and Water Heater. Common vent is 6 inches in diameter. Furnace venting has been removed from common vent leaving a 4 inch vent connected to 6 inch common vent. Venting of the hot water heater is now oversized and under certain conditions flue gases could cool down too quickly inside vent and spill through draft hood of water heater into home possibly causing CO poisoning to occupants | 3 | Atmospheric venting system oversized, appliance vents in prime condition non compliant with Gas Directive | Oversized_common_venting.png | file://x:/photopub/docs/0000000697/41e490af-4c3f-458e-b416-fe1f7e12791d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26c41e87_4d22_4de9_999f_d1d54922720d
ELIN-961624-2017 | EL-568282-2017 | 11/17/2017 7:27:26 AM | ASSESS: EL: Service Connection | png | #asFound | EL324 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 3 | 3 | #No_mechanical_protection_provided_for_ACWU.png In a new single family dwelling the 200 amp 120/240 volt consumer service cable is subject to mechanical damage and no protection plate has been provided. This could result in an equipment damage condition. Photo attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | No_mechanical_protection_provided_for_ACWU.png | file://x:/photopub/docs/0000000698/a36d3239-14cb-4ad3-aad3-9b823ab497fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c91c1df9_97f6_4e58_ba80_20ab2fe4fb68
GAIN-957625-2017 | GA-591119-2017 | 11/10/2017 1:06:55 PM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | #Underground_PE_pipe.png The as-found hazard is an underground polyethylene piping system was found installed passing below a wall. The as-found hazard is if the wall settles on the underground piping, the side wall could be punctured causing a undetectable gas leak. If the gas accumulates in an area with an ignition source, and explosion could occur. | 3 | Code prohibited practices or materials | Underground_PE_pipe.png | file://x:/photopub/docs/0000000695/bb409ff7-cf87-48d4-9fc6-7e2724d89dfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37e13c75_8dc4_4e3d_9251_60dbd61feebe
BPVOP-956487-2017 | BPV 00000028319-2013 | 11/9/2017 10:44:51 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Log_book_enrtries_5th_class_certificate1.png,Log_book_enrtries_5th_class_certificate2.png,Log_book_enrtries_5th_class_certificate3.png,Log_book_enrtries_5th_class_certificate4.png,Log_book_enrtries_5th_class_certificate5.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 175kw class B2 Refrigeration plant during the evening and night shifts while the plant was operating. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Log_book_enrtries_5th_class_certificate4.png | file://x:/photopub/docs/0000000695/8793b500-8d25-48c4-a47f-9ae663c08ecd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b034dea9_35f3_4ca1_8ca0_d3d69c372806
BPVOP-956487-2017 | BPV 00000028319-2013 | 11/9/2017 10:44:51 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | #Log_book_enrtries_5th_class_certificate1.png,Log_book_enrtries_5th_class_certificate2.png,Log_book_enrtries_5th_class_certificate3.png,Log_book_enrtries_5th_class_certificate4.png,Log_book_enrtries_5th_class_certificate5.png The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a 175kw class B2 Refrigeration plant during the evening and night shifts while the plant was operating. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Log_book_enrtries_5th_class_certificate5.png | file://x:/photopub/docs/0000000695/67c61055-5eac-4c6b-bf16-b062881a52a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b034dea9_35f3_4ca1_8ca0_d3d69c372806
GAIN-954061-2017 | GA-592856-2017 | 11/16/2017 4:35:38 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | #No_Extension.png Intertherm co-axle venting system has no flue extension and installed in snow region. Combustion air could be blocked by snow and furnace will not work. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | No_Extension.png | file://x:/photopub/docs/0000000698/8be91edc-0d23-4ba9-a294-f07c4c912d5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8797d451_a77e_4807_8a91_460938120ceb
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png | file://x:/photopub/docs/0000000697/16f956c4-d6fb-4e6e-bb4e-5947440bd77a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png | file://x:/photopub/docs/0000000697/b3b5e263-78dd-400f-8bb4-b3bac6c00745.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
ELOP-922774-2017 | EL-298722-2015 | 11/15/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL359 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor2.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor3.png,Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors1.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors2.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors3.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors4.png,Conveyor_motor_connection_box_has_detached_from_the_motor_and_is_hanging_from_the_motor_conductors5.png Motors have connection boxes that contain the branch circuit conduc | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage equipment has been damaged and is now compromised, repairs are necessary. | Damaged_and_improperly_installed_motor_connection_box_cover_for_the_dust_collection_system_blower_motor1.png | file://x:/photopub/docs/0000000697/63e58cc2-1e9c-48e3-a1d9-1434787d7784.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d8791c3_b110_4fa2_8352_8242661a686d
GAUP-962296-2017 | UW-615300-2017 | 11/16/2017 3:47:37 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound Apologize, other photo got deleted somehow, cannot get access to roof, however mechanical ical air supply is directly above this reg relief | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | #Reg_relief.png Relief vent from a regulator is installed too close to a Mechanical air inlet of an appliance. In an over pressure scenario the relief will relief the pressure and the Mechanical air will suck gas into the building through the appliance, possibly causing an explosion inside the building | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Reg_relief.png | file://x:/photopub/docs/0000000697/8834dbde-520f-4afe-9d55-9e83037eeba6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad8150ed_18cc_46b5_b7d9_ec653f577a88
EDIN-960976-2017 | ED-483689-2016 | 11/15/2017 3:11:34 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | #Unit_413092.png Inadequate lighting provide at top and bottom elevator landing sills. Approximately 20 lx ( Minimum 100 lx required). | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Unit_413092.png | file://x:/photopub/docs/0000000697/df6c7ab5-6ffa-4fb3-b503-dc5890f92cf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33fd271b_dfdc_433d_a70c_931d67765492
ELIN-962738-2017 | UW-615426-2017 | 11/17/2017 10:25:07 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Flexible_cord_permanebet_substitute.png Flexible cord operating at 120 volts and 20 amps was found being used as a substitute for permanent wiring and was feeding permanent electrical equipment. Flexible cord when used in this way can deteriorate over time energizing metal structures or causing arc fault damage to combustible surfaces and can result in injury to persons or damage to structures. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_permanebet_substitute.png | file://x:/photopub/docs/0000000699/8ca08362-a534-4378-b46a-183a88e70216.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9dd2494_ce1d_4ee8_9018_d13e09bf8008
ELIN-962736-2017 | UW-615435-2017 | 11/20/2017 10:35:45 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL351 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Sign_no_approval_.png A new LED market display sign operating at 120 volts and 30 amps was found installed at fuel and market business. The sign was mounted to an exterior metal sign structure accessible to the public. The sign had been manufactured using a number of components, but had not undergone overall certification for the assembly. Without an overall certification mark the equipment has not been retested for minimum safety. Equipment can fail and in this case create a risk for injury to persons or damage to property. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Sign_no_approval_.png | file://x:/photopub/docs/0000000699/3dc7d956-df9f-436f-aede-b2e0f144620f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7c07689_c4ad_4562_bfbd_0166be33a068
ELIN-963148-2017 | UW-615684-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #Hazard1.png,Hazard2.png Storage materials are placed within 1 meter of the front of the electrical panels preventing clear and safe access to deenergize circuit breakers in case of emergency. | 1 | General Working space or dedicated space is being used for storage | Hazard1.png | file://x:/photopub/docs/0000000699/2b0515c7-0c79-4ab3-b152-4311ef3cb5e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36644290_cc6c_4277_a261_5a0b3881fea7
ELIN-963148-2017 | UW-615684-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | #Hazard1.png,Hazard2.png Storage materials are placed within 1 meter of the front of the electrical panels preventing clear and safe access to deenergize circuit breakers in case of emergency. | 1 | General Working space or dedicated space is being used for storage | Hazard2.png | file://x:/photopub/docs/0000000699/eede4be6-3fdb-4882-b1ac-498827433dc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36644290_cc6c_4277_a261_5a0b3881fea7
EDIN-960933-2017 | ED-483693-2016 | 11/15/2017 7:51:32 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | #Lighting.png All landings does not have adequate lighting which could result trips/slips/falls by passengers | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Lighting.png | file://x:/photopub/docs/0000000697/b5e940c7-53b8-49a9-9c95-90a469afe87c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab9985d9_45bf_46bd_aa25_49ffe3a84947
ELIN-961630-2017 | EL-503039-2017 | 11/16/2017 11:28:55 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL296 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | #Panel_enclosed_within_plywood_box.png Dry type panel boards must be protected from the weather by installing in suitable weatherproof enclosures. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_enclosed_within_plywood_box.png | file://x:/photopub/docs/0000000698/c1827b2b-d3f1-45e5-a64d-1bdad4b62ff0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33da8ed6_7369_44ed_b2f2_5dd5845c07e3
ELIN-960278-2017 | EL-591938-2017 | 11/16/2017 2:08:19 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Hazard1.png Receptacle is within 1.5M of sink and is not GFCI protected. This may be a shock hazard to people using electrical equipment or products around the sink. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Hazard1.png | file://x:/photopub/docs/0000000697/71c76ef5-4604-4753-89e6-8f40b716c2e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f43e6f3c_6c68_46bc_8a9f_216e7512524b
ELIN-958408-2017 | EL-607713-2017 | 11/14/2017 12:20:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_receptacles1.png,Energized_receptacles2.png,Energized_receptacles3.png,Energized_receptacles4.png The installation/ complete renovation of an existing residence includes multiple energized 20 amp 120 volt circuited receptacles without coverplates or insulated protection of energized parts, this is a shock hazard. The site is not occupied by persons and is under construction, completely lockable. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_receptacles2.png | file://x:/photopub/docs/0000000696/9fe75f9a-57d8-4b1f-807c-222427b1b85e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb808ee_b421_4329_bbf3_bbe3855e618b
ELIN-958408-2017 | EL-607713-2017 | 11/14/2017 12:20:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_receptacles1.png,Energized_receptacles2.png,Energized_receptacles3.png,Energized_receptacles4.png The installation/ complete renovation of an existing residence includes multiple energized 20 amp 120 volt circuited receptacles without coverplates or insulated protection of energized parts, this is a shock hazard. The site is not occupied by persons and is under construction, completely lockable. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_receptacles1.png | file://x:/photopub/docs/0000000696/c7b0ecea-b7b4-46cd-a291-d536f4e33338.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb808ee_b421_4329_bbf3_bbe3855e618b
ELIN-958408-2017 | EL-607713-2017 | 11/14/2017 12:20:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_receptacles1.png,Energized_receptacles2.png,Energized_receptacles3.png,Energized_receptacles4.png The installation/ complete renovation of an existing residence includes multiple energized 20 amp 120 volt circuited receptacles without coverplates or insulated protection of energized parts, this is a shock hazard. The site is not occupied by persons and is under construction, completely lockable. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_receptacles3.png | file://x:/photopub/docs/0000000696/d1c371cc-c28b-489e-a3af-97cad25ade85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb808ee_b421_4329_bbf3_bbe3855e618b
ELIN-958408-2017 | EL-607713-2017 | 11/14/2017 12:20:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | #Energized_receptacles1.png,Energized_receptacles2.png,Energized_receptacles3.png,Energized_receptacles4.png The installation/ complete renovation of an existing residence includes multiple energized 20 amp 120 volt circuited receptacles without coverplates or insulated protection of energized parts, this is a shock hazard. The site is not occupied by persons and is under construction, completely lockable. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_receptacles4.png | file://x:/photopub/docs/0000000696/6d20760b-d8d0-4026-8311-7aa2fa7069df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb808ee_b421_4329_bbf3_bbe3855e618b
GAHE-962128-2017 | HE-615175-2017 | 11/16/2017 1:26:09 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 2 | #Underground_3.png,Underground.png Gas line entering building below grade. Gas leak could follow space surrounding pipe and enter building. Risk of explosion and or fire. | 3 | Underground piping entering a building below grade (unapproved) | Underground.png | file://x:/photopub/docs/0000000698/069f0cae-414b-4cac-b5da-ca892d7b5e8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98b310fd_81b5_4fcc_9c8b_a2aea44035df
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards3.png | file://x:/photopub/docs/0000000698/92afcd64-18fa-4e0d-8c7a-a248d3ccf8b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards5.png | file://x:/photopub/docs/0000000698/5545d249-4817-41ee-90d3-eb55e88835d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards6.png | file://x:/photopub/docs/0000000698/41b95184-c84f-47ec-847a-4034c695758a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards4.png | file://x:/photopub/docs/0000000698/d91f9b5d-fd04-4519-85eb-2f8246a8b16d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards1.png | file://x:/photopub/docs/0000000698/34ab3a46-dbe2-4ca5-a048-2b1a4e75099a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards9.png | file://x:/photopub/docs/0000000698/b4f558f3-db0c-42bc-8258-de253b975e5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards7.png | file://x:/photopub/docs/0000000698/f75632f5-5da3-4042-937c-e7621b3bda18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards8.png | file://x:/photopub/docs/0000000698/70c1b9a3-6fde-4a61-a9b3-5bba1f637dce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards2.png | file://x:/photopub/docs/0000000698/63cb9180-8c3a-4e0a-befe-244072137a9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
ELIN-963138-2017 | UW-615671-2017 | 11/15/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | #Hazards1.png,Hazards2.png,Hazards3.png,Hazards4.png,Hazards5.png,Hazards6.png,Hazards7.png,Hazards8.png,Hazards9.png,Hazards10.png Existing fire alarm remote annunciators are installed in outdoor locations which the enclosures do not have evidence of being approved for. Remote annunciators are vital for emergency personnel to identify the area and type of emergencies on site to protect personnel and property. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | Hazards10.png | file://x:/photopub/docs/0000000698/fe90526e-9b12-4e58-8e11-a960305ba86e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076e5b8_8521_4c7b_bc79_6801b243bee7
GAIN-961098-2017 | GA-588263-2017 | 11/17/2017 3:31:15 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | #Too_close.png Mechanical Air for an appliance installed too close to a regulator relief vent. In an overpressure scenario, regulator will relieve pressure through relief vent. Natural gas will then be sucked through the mechanical air inlet into appliance causing an over fired situation or an explosion | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Too_close.png | file://x:/photopub/docs/0000000698/b8259b3d-5804-4db7-aba6-0c458d0c5134.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37a557e0_9fac_4619_89a9_94fc928c7649
GAIN-960125-2017 | GA-614097-2017 | 11/17/2017 10:59:26 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent1.png,Vent2.png,Vent3.png The as found hazard is the vent termination is not within minimum clearance from a mechanical air intake. This is hazardous as products of combustion can enter the occupied building space | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent1.png | file://x:/photopub/docs/0000000698/c5749662-67ac-46c8-84c7-a86902fe2f0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21974cb5_52da_4d03_982c_b466a327f4a0
GAIN-960125-2017 | GA-614097-2017 | 11/17/2017 10:59:26 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent1.png,Vent2.png,Vent3.png The as found hazard is the vent termination is not within minimum clearance from a mechanical air intake. This is hazardous as products of combustion can enter the occupied building space | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent2.png | file://x:/photopub/docs/0000000698/5dab2f2b-4450-4c1b-8972-8c13ef2d0509.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21974cb5_52da_4d03_982c_b466a327f4a0
GAIN-960125-2017 | GA-614097-2017 | 11/17/2017 10:59:26 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Vent1.png,Vent2.png,Vent3.png The as found hazard is the vent termination is not within minimum clearance from a mechanical air intake. This is hazardous as products of combustion can enter the occupied building space | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent3.png | file://x:/photopub/docs/0000000698/6019d0cb-268b-4c73-83d5-a622a6a102a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21974cb5_52da_4d03_982c_b466a327f4a0
GAIN-961257-2017 | GA-602190-2017 | 11/20/2017 9:14:40 AM | ASSESS: GA: Final | png | #asFound Single wall vent connector installed in combustible joist space. | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent_connector.png Single wall vent connectors are too close to combustible material. This could lead to a fire. | 3 | Non compliant Type C Vent clearance | Vent_connector.png | file://x:/photopub/docs/0000000699/accf5b61-887b-4724-acc8-71a6ae95c83a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__376b9e3e_7cc5_49da_9743_d81fcdb30613
GAIN-947549-2017 | GA-436141-2016 | 11/17/2017 7:54:20 AM | ASSESS: GA: Rough-In | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | #Regultors.png The as-found condition is that regulators have been installed in a non-ventilated ceiling space. The potential hazard is that the regulators will relieve and leak gas into a drop ceiling space where an ignition source could cause a risk of fire and explosion. | 3 | Vent limiter style regulator not installed in a ventilated space | Regultors.png | file://x:/photopub/docs/0000000698/bb0c4f4c-022c-46b1-bae0-aa1ae5c9c707.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__899a7f76_0c9d_406e_9f30_43eb4615365e
GAIN-954495-2017 | GA-569109-2017 | 11/17/2017 2:22:01 PM | ASSESS: GA: Final | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | #Rum_runner_water_heater.png Spillage of flue products from hot water tank. Products of combustion entering occupied space. Risk of exposure to carbon monoxide. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Rum_runner_water_heater.png | file://x:/photopub/docs/0000000699/c6426985-2ef7-43d2-afbc-51880a02177e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7687fd80_c5f4_4048_82f1_a2bf5b40c08f
ELIN-958862-2017 | EL-496885-2017 | 11/17/2017 12:59:16 PM | ASSESS: EL: Final | png | #asFound | EL325 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3 | 3 | #Improper_and_unapproved_neutral_termination1.png,Improper_and_unapproved_neutral_termination2.png,Improper_and_unapproved_neutral_termination3.png,Improper_and_unapproved_neutral_termination4.png Termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a house being upgraded and renovated had a 100A sub-panel feeder cable neutral conductor termination that was not approved for use with the panel that it was installed in. The termination lug was a solderless lug that was not approved for installation on the neutral bus within the particular panel that it was installed in. This may cause a poor connection that can not be installed and tightened adequately. Left uncorrected this is a fire hazard if the conductor termination becomes over he | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Improper_and_unapproved_neutral_termination4.png | file://x:/photopub/docs/0000000698/554ff28c-8c42-43e9-a160-b3ab6e331ec4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a4af276_db8d_4c59_bde6_31e0f62d6da7
ELIN-958862-2017 | EL-496885-2017 | 11/17/2017 12:59:16 PM | ASSESS: EL: Final | png | #asFound | EL325 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3 | 3 | #Improper_and_unapproved_neutral_termination1.png,Improper_and_unapproved_neutral_termination2.png,Improper_and_unapproved_neutral_termination3.png,Improper_and_unapproved_neutral_termination4.png Termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a house being upgraded and renovated had a 100A sub-panel feeder cable neutral conductor termination that was not approved for use with the panel that it was installed in. The termination lug was a solderless lug that was not approved for installation on the neutral bus within the particular panel that it was installed in. This may cause a poor connection that can not be installed and tightened adequately. Left uncorrected this is a fire hazard if the conductor termination becomes over he | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Improper_and_unapproved_neutral_termination3.png | file://x:/photopub/docs/0000000698/c70a5848-d486-400a-9f1d-25a7dcb89174.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a4af276_db8d_4c59_bde6_31e0f62d6da7
ELIN-958862-2017 | EL-496885-2017 | 11/17/2017 12:59:16 PM | ASSESS: EL: Final | png | #asFound | EL325 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 3 | 3 | #Improper_and_unapproved_neutral_termination1.png,Improper_and_unapproved_neutral_termination2.png,Improper_and_unapproved_neutral_termination3.png,Improper_and_unapproved_neutral_termination4.png Termination lugs or connection devices are required to be approved for the use and properly installed onto electrical equipment prior to terminating conductors. This is required to ensure a solid low impedance connection that will not over heat and fail over time under varying load and temperature conditions. This installation at a house being upgraded and renovated had a 100A sub-panel feeder cable neutral conductor termination that was not approved for use with the panel that it was installed in. The termination lug was a solderless lug that was not approved for installation on the neutral bus within the particular panel that it was installed in. This may cause a poor connection that can not be installed and tightened adequately. Left uncorrected this is a fire hazard if the conductor termination becomes over he | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Improper_and_unapproved_neutral_termination2.png | file://x:/photopub/docs/0000000698/d50e161a-99d7-43d6-b71d-36c768c35d1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a4af276_db8d_4c59_bde6_31e0f62d6da7
ELIN-961691-2017 | EL-491139-2017 | 11/17/2017 3:07:02 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | #Wire_and_heating_ducts_need_insulation_or_air_between_them.png This assessment found that wire in close proximity to heating ducts, creating a fire hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Wire_and_heating_ducts_need_insulation_or_air_between_them.png | file://x:/photopub/docs/0000000698/676d8755-c84f-4a27-840d-482c3e0efde9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b05b3a96_46f9_4d0f_b9ea_223b92283896
ELOP-954117-2017 | 4888092 | 11/16/2017 7:39:04 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #SOW_cable1.png,SOW_cable2.png,SOW_cable3.png,SOW_cable4.png,SOW_cable5.png Flexible cord has been used to feed 15 amp 208 volt equipment but is in locations subject to mechanical damage and is also being walked on. This poses a shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | SOW_cable5.png | file://x:/photopub/docs/0000000699/af0b2154-73b2-49cf-9974-dab9127fff6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5550d01c_c76e_41ca_9a6c_3ba024d5766d
ELOP-954117-2017 | 4888092 | 11/16/2017 7:39:04 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #SOW_cable1.png,SOW_cable2.png,SOW_cable3.png,SOW_cable4.png,SOW_cable5.png Flexible cord has been used to feed 15 amp 208 volt equipment but is in locations subject to mechanical damage and is also being walked on. This poses a shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | SOW_cable2.png | file://x:/photopub/docs/0000000699/90a21148-3f6c-49dd-92cd-38d263f8ac19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5550d01c_c76e_41ca_9a6c_3ba024d5766d
ELOP-954117-2017 | 4888092 | 11/16/2017 7:39:04 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #SOW_cable1.png,SOW_cable2.png,SOW_cable3.png,SOW_cable4.png,SOW_cable5.png Flexible cord has been used to feed 15 amp 208 volt equipment but is in locations subject to mechanical damage and is also being walked on. This poses a shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | SOW_cable4.png | file://x:/photopub/docs/0000000699/fb7f32d3-b871-4e77-85f8-a04ad8c7700f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5550d01c_c76e_41ca_9a6c_3ba024d5766d
ELOP-954117-2017 | 4888092 | 11/16/2017 7:39:04 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #SOW_cable1.png,SOW_cable2.png,SOW_cable3.png,SOW_cable4.png,SOW_cable5.png Flexible cord has been used to feed 15 amp 208 volt equipment but is in locations subject to mechanical damage and is also being walked on. This poses a shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | SOW_cable3.png | file://x:/photopub/docs/0000000699/22edcd9d-5583-4965-bd2a-ec771361d3ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5550d01c_c76e_41ca_9a6c_3ba024d5766d
ELOP-954117-2017 | 4888092 | 11/16/2017 7:39:04 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #SOW_cable1.png,SOW_cable2.png,SOW_cable3.png,SOW_cable4.png,SOW_cable5.png Flexible cord has been used to feed 15 amp 208 volt equipment but is in locations subject to mechanical damage and is also being walked on. This poses a shock hazard to persons and potential mechanical damage to the electrical components. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | SOW_cable1.png | file://x:/photopub/docs/0000000699/c624e2c5-f8cc-4e39-92f5-6ffa000668d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5550d01c_c76e_41ca_9a6c_3ba024d5766d
ELHE-964897-2017 | HE-543663-2017 | 11/17/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Exterior_receptacle_on_dwelling_unit.png Exterior 120 volt 15 amp receptacles for dwelling units are not ground fault circuit interrupt protected (G.F.C.I.) increasing the likelihood of sustained electrical shock in the event that a fault to ground may occur during use. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_receptacle_on_dwelling_unit.png | file://x:/photopub/docs/0000000699/56c3d510-98ef-4c39-8b95-5f1cc1b985d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cfc12a4_8b39_4066_aac6_21289c8ceeb9
ELIN-957024-2017 | EL-590324-2017 | 11/14/2017 1:11:52 PM | ASSESS: EL: Final | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | #BB_heater_cable_and_dishwasher_cable_are_exposed_and_energized.png Energized cables for the dishwasher and BB Heater in kitchen are energized. The ends of the Cale are exposed and the conductors are protected with only a wire nut to prevent accidental,contact | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | BB_heater_cable_and_dishwasher_cable_are_exposed_and_energized.png | file://x:/photopub/docs/0000000696/194c46e1-5351-4120-82ef-57cdfbb39137.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__398547da_0140_4959_b00d_c0b35250b3d3
ELIN-955686-2017 | EL-548585-2017 | 11/14/2017 | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #NS_cable1.png,NS_cable2.png,NS_cable3.png,NS_cable4.png Neutral support cable is not spliced with proper connectors. This could eventually become a hazard due to the splices not meeting minimum requirements. The current splicing connectors could eventually overheat and cause a fire. | 3 | General Equipment is not approved for the specific use | NS_cable3.png | file://x:/photopub/docs/0000000696/0767c220-3190-4c31-bbc9-6ec17a05d583.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b47b9fb3_3776_4084_94ad_72fa70f8822a
ELIN-955686-2017 | EL-548585-2017 | 11/14/2017 | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #NS_cable1.png,NS_cable2.png,NS_cable3.png,NS_cable4.png Neutral support cable is not spliced with proper connectors. This could eventually become a hazard due to the splices not meeting minimum requirements. The current splicing connectors could eventually overheat and cause a fire. | 3 | General Equipment is not approved for the specific use | NS_cable4.png | file://x:/photopub/docs/0000000696/2f6cefa2-3d43-40b6-8db3-8daa341f6033.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b47b9fb3_3776_4084_94ad_72fa70f8822a
ELIN-955686-2017 | EL-548585-2017 | 11/14/2017 | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #NS_cable1.png,NS_cable2.png,NS_cable3.png,NS_cable4.png Neutral support cable is not spliced with proper connectors. This could eventually become a hazard due to the splices not meeting minimum requirements. The current splicing connectors could eventually overheat and cause a fire. | 3 | General Equipment is not approved for the specific use | NS_cable1.png | file://x:/photopub/docs/0000000696/0c3e0bdf-28ec-4397-8392-89f496d0d055.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b47b9fb3_3776_4084_94ad_72fa70f8822a
ELIN-955686-2017 | EL-548585-2017 | 11/14/2017 | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | #NS_cable1.png,NS_cable2.png,NS_cable3.png,NS_cable4.png Neutral support cable is not spliced with proper connectors. This could eventually become a hazard due to the splices not meeting minimum requirements. The current splicing connectors could eventually overheat and cause a fire. | 3 | General Equipment is not approved for the specific use | NS_cable2.png | file://x:/photopub/docs/0000000696/5a8d1a66-df5b-4ac9-a5f4-c1bb1eee51ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b47b9fb3_3776_4084_94ad_72fa70f8822a
ELIN-967445-2017 | EL-618010-2017 | 11/23/2017 11:53:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL301 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Service_conductors1.png,Service_conductors2.png In the existing 100 amp 120/240 volt Main Electrical Panel, the service conductors have been damaged, this poses a shock hazard to persons and potential mechanical damage to the electrical equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | Service_conductors1.png | file://x:/photopub/docs/0000000702/438a0606-8bad-4a38-884c-d3a214197151.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce701e3a_958f_4844_9a18_1c89ea7e753c
BPVIN-943706-2017 | UW-581475-2017 | 11/21/2017 | ASSESS: BPV IN: Final (First Certification) REF/PV | pdf | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of 24 Pressure vessels it was found that 2 oil coolers wth MAWP of 300 psig had the PRDâ€™s overdue as per CSA B-51. This can contribute to the failure of the PRDâ€™s in case of vessel overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Refrigeration Units PRD Infomation 2017-10-26.pdf | file://x:/photopub/docs/0000000700/ac72ac70-8a76-4b29-93f0-697163c01bd2.pdf | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c5d44d4_77c4_4290_a7cb_b0953aebbe08
ELIN-967890-2017 | EL-618241-2017 | 11/23/2017 9:47:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 3 | 3 | #No_ground_conductor.png In a single family dwelling service upgrade a ground conductor was not present in main distribution at time of assessment. This could result in a thermal effect condition. Picture attached. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_ground_conductor.png | file://x:/photopub/docs/0000000702/3491b1db-69dd-4131-b966-f3d8a56591cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ea15de7_4e51_4d0a_9836_1080af02ea1d
ELIN-960501-2017 | EL-541169-2017 | 11/22/2017 7:26:02 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Hazard1.png,Hazard1.png GFCI protection was not provided within 1.5M of sink this may be a shock hazard to personal using electrical equipment in the kitchen, GFCIâ€™s add protection when using electrical equipment around sinks. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Hazard1.png | file://x:/photopub/docs/0000000701/826f4b5c-808a-4215-b2e8-022d2914d850.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce25a650_2c3e_4a5a_ba8c_9809a1c62f58
ELIN-967445-2017 | EL-618010-2017 | 11/23/2017 11:53:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL301 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | 3 | 3 | #Service_conductors1.png,Service_conductors2.png In the existing 100 amp 120/240 volt Main Electrical Panel, the service conductors have been damaged, this poses a shock hazard to persons and potential mechanical damage to the electrical equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Low voltage service equipment has been damaged and is now compromised, repairs are necessary. | Service_conductors2.png | file://x:/photopub/docs/0000000702/7c7ddf0a-e19d-468c-886b-c03196dbd35f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce701e3a_958f_4844_9a18_1c89ea7e753c
GAIN-962240-2017 | GA-559578-2017 | 11/21/2017 8:33:09 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Overview_return_air.png | 3 | Appliance not installed according to installation instructions | Overview_return_air.png | file://x:/photopub/docs/0000000700/42a8389f-32ee-4be4-8cd2-d8bfabf297ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59349684_0339_4f24_999f_a8d21fda8011
PROP-871019-2017 | PR-480015-2016 | 11/23/2017 4:09:39 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | #Conveyor_skirting1.png,Conveyor_skirting2.png,Conveyor_skirting3.png,Conveyor_skirting4.png Conveyor requires rigid skirting at all times during operation, skirting could become compromised with snow load , allowing areas of turning machinery to be open to the public, if skirting is not inspected and maintained daily. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Conveyor_skirting1.png | file://x:/photopub/docs/0000000702/3a7b96f8-0b62-43c7-9f00-5fea53d6182c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7D2FF9B7_DD94_40EE_983F_828CB43B967D
PROP-871019-2017 | PR-480015-2016 | 11/23/2017 4:09:39 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | #Conveyor_skirting1.png,Conveyor_skirting2.png,Conveyor_skirting3.png,Conveyor_skirting4.png Conveyor requires rigid skirting at all times during operation, skirting could become compromised with snow load , allowing areas of turning machinery to be open to the public, if skirting is not inspected and maintained daily. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Conveyor_skirting2.png | file://x:/photopub/docs/0000000702/f86ef350-c5b0-47a2-9be7-779661eab59b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7D2FF9B7_DD94_40EE_983F_828CB43B967D
PROP-871019-2017 | PR-480015-2016 | 11/23/2017 4:09:39 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | #Conveyor_skirting1.png,Conveyor_skirting2.png,Conveyor_skirting3.png,Conveyor_skirting4.png Conveyor requires rigid skirting at all times during operation, skirting could become compromised with snow load , allowing areas of turning machinery to be open to the public, if skirting is not inspected and maintained daily. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Conveyor_skirting3.png | file://x:/photopub/docs/0000000702/9d3f8648-58c1-4272-ac74-dc269f15b656.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7D2FF9B7_DD94_40EE_983F_828CB43B967D
ELIN-966139-2017 | EL-617271-2017 | 11/23/2017 6:50:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL295 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #B.png A 200 Amp distribution panel installed outside on a pole does not have a panel cover installed. This poses a serious risk of personal injury (shock) and property damage (thermal event) resulting from failure of system protection measures. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | B.png | file://x:/photopub/docs/0000000702/9ec37866-05a3-44c0-ba52-66f75dc824fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__351ff3b1_f5a0_48c2_b40b_1c958ef9866a
ELIN-956035-2017 | EL-565192-2017 | 11/21/2017 7:51:27 AM | ASSESS: EL: Final | png | #asFound | EL110 | Conductors Conductors are not suitably identified. | 3 | 3 | #All_locations_meter_panels__sub_psnels.png The main system and sub feed neutral conductor's for a 400 amp 240 volt distribution system have not been properly identified. This can lead to confusion during servicing with a potential for injury to persons | 3 | Conductors Conductors are not suitably identified. | All_locations_meter_panels__sub_psnels.png | file://x:/photopub/docs/0000000700/9d941bdd-2c82-4755-b2d3-b068b673071c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c7cd0cb_df63_4cf2_a69e_f7d2086c7ef6
GAIN-937606-2017 | GA-578614-2017 | 11/22/2017 5:12:49 PM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Range_and_piping1.png,Range_and_piping2.png The as-found condition is that the gas pressure connected to two ranges in a commercial kitchen is higher than the appliances are rated for. The potential hazard is that the ranges will overfire, resulting in a fire hazard and damage to equipment | 4 | Appliance regulator not installed, incorrect delivery pressure | Range_and_piping1.png | file://x:/photopub/docs/0000000701/6e172bb3-1bfd-483a-bfec-844ad4eb869f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a42b47f3_ef50_4ac2_b21a_9ce4936b2178
GAIN-937606-2017 | GA-578614-2017 | 11/22/2017 5:12:49 PM | ASSESS: GA: Final | png | #asFound | GA167 | Appliance regulator not installed, incorrect delivery pressure | 4 | 4 | #Range_and_piping1.png,Range_and_piping2.png The as-found condition is that the gas pressure connected to two ranges in a commercial kitchen is higher than the appliances are rated for. The potential hazard is that the ranges will overfire, resulting in a fire hazard and damage to equipment | 4 | Appliance regulator not installed, incorrect delivery pressure | Range_and_piping2.png | file://x:/photopub/docs/0000000701/b93bd715-0311-4fd1-87aa-84ca320eee46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a42b47f3_ef50_4ac2_b21a_9ce4936b2178
ELOP-956287-2017 | 2166994 | 11/21/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | #Hazard.png Box cover removed from energized outlet box leaving exposed electrical conductors and a potential fire hazard as any fault or overload may not be contained within the box by a cover as intended | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Hazard.png | file://x:/photopub/docs/0000000701/ad72bd72-83eb-4e50-b2e3-0d31d59bfcfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2f8e8ff_ef90_4590_8b8f_605bbc54cab2
ELIN-965282-2017 | EL-614051-2017 | 11/20/2017 3:43:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL291 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | #Energized_buss.png This assessment found the service panel cover off exposing energized buss. This presents a shock hazard | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_buss.png | file://x:/photopub/docs/0000000700/31b6b0ba-f12f-4ddf-9736-eb094a8084cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45899535_b35e_4a24_9366_574f687d1ec1
BPOP-936299-2017 | BPV-472431-2015 | 11/22/2017 3:24:31 PM | ASSESS: Propane PV: Periodic | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Rv_date11.png Pressure relief valve exceeds to maximum service interval. This may compromise the relief valves functionality. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Rv_date11.png | file://x:/photopub/docs/0000000701/0f9496fa-916b-4d6a-afe5-331d98875ddd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbcc7064_f174_4174_bbe2_7fb06cc6f1a3
GAUP-962973-2017 | UW-615562-2017 | 11/17/2017 3:09:52 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA069 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | 3 | 3 | #Gas_line.png Gas lines are undersized for the appliances. This could lead to incomplete combustion and the production of carbon monoxide. | 3 | Improperly sized gas piping or tubing according to delivery pressure for multiple appliances | Gas_line.png | file://x:/photopub/docs/0000000701/1162be98-2a33-4d28-a482-8888e8cd69f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d389a7c1_fa89_4033_8001_92a7489275a9
ELIN-965313-2017 | EL-400926-2016 | 11/21/2017 7:01:00 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL310 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | 3 | 3 | #Subpanel_.png In the energized 100 amp 120/240 volt electrical panel, unused opening in the panel cover have not been filled or effectively covered/guarded to prevent persons from contacting the energized components inside the panel. This could result in a shock hazard to persons and potential damage to the electrical equipment. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | Subpanel_.png | file://x:/photopub/docs/0000000700/acbfd559-60d3-4f68-a236-8798c579b1d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7a9aa1b_c140_4783_bdee_d69f5c48ebbb
GAIN-964138-2017 | GA-572724-2017 | 11/20/2017 12:37:26 PM | ASSESS: GA: Rough-In | png | #asFound | GA136 | Uncertified appliance connected to gas supply but not in service | 3 | 3 | #Water_heater_3.png Water heater not certified to a recognized standard. Safety controls and construction methods may pose a hazard due to not being constructed to a minimum standard. Possible fire risk. | 3 | Uncertified appliance connected to gas supply but not in service | Water_heater_3.png | file://x:/photopub/docs/0000000700/ff90a323-959a-4950-8d58-36e2e86db3fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4d4375c_be53_4d24_8b58_cd913dc0784a
GAHE-969547-2017 | HE-618998-2017 | 11/24/2017 9:50:23 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA001 | Paint/coating required on tank/cylinder | 1 | 1 | #Paint_required1.png,Paint_required2.png | 1 | Paint/coating required on tank/cylinder | Paint_required2.png | file://x:/photopub/docs/0000000702/17a802bd-ebb4-4ed2-8363-25bb169ff010.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b899b37_a555_46f2_8ee4_071f6b06aead
GAHE-969547-2017 | HE-618998-2017 | 11/24/2017 9:50:23 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA001 | Paint/coating required on tank/cylinder | 1 | 1 | #Paint_required1.png,Paint_required2.png | 1 | Paint/coating required on tank/cylinder | Paint_required1.png | file://x:/photopub/docs/0000000702/b6e52c1d-974a-48e6-a250-2e810ce09d57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b899b37_a555_46f2_8ee4_071f6b06aead
GAIN-969719-2017 | GA-609662-2017 | 11/24/2017 3:39:20 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | #Rating_plate.png | 3 | Appliance not installed according to installation instructions | Rating_plate.png | file://x:/photopub/docs/0000000702/44a89cc3-d409-476f-9a34-689caeba20f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf9d444b_00b3_4a82_8602_fb85378ff402
ELHE-966330-2017 | HE-617465-2017 | 11/21/2017 3:09:04 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL314 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | 4 | 4 | #Deteriorated_breakers_in_panel.png In a commercial facility a 100 amp 120/240 volt sub panel was found to be deteriorated. This is an equipment damage condition. Picture attached. | 4 | Improper installation or location of equipment, conductors, cables or raceways High voltage equipment has been damaged and is now compromised, repairs are necessary; Low voltage equipment has been compromised, continued use is not authorized | Deteriorated_breakers_in_panel.png | file://x:/photopub/docs/0000000701/8f82bd0a-93eb-486d-8c67-e1e434e01380.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3f64889_afe4_47b6_ade8_57aa135fb272
ELIN-968792-2017 | EL-605561-2017 | 11/23/2017 2:25:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #No_receptacle_cover_plate.png A 15 amp 120 volt double duplex receptacle installed on the interior wall of the service shed is missing the coverplate, Service is not energized however once the service becomes energized this will become a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | No_receptacle_cover_plate.png | file://x:/photopub/docs/0000000702/0c184c29-7de0-461f-8637-23cc0fa17cbf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01b77517_0a63_4bee_87a4_8a01599b16ea
ELIN-964435-2017 | EL-613082-2017 | 11/22/2017 2:54:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Hazard1.png Panelboards without the protective barriers and covers expose energized parts this may cause a shock hazard to people. The covers also help contain any electrical fault and without the barriers and covers this may cause a fire hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Hazard1.png | file://x:/photopub/docs/0000000701/1f482892-db7a-4e37-a0d3-1f69d7481bc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5fa0d835_3eb9_4297_8a96_54f99f7fb5ff
BPVOP-964574-2017 | 3063947 | 11/20/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_and_nameplate_for_vessel_age_1.png,Pressure_relief_and_nameplate_for_vessel_age_2.png Pressure Relief device has no records or maintenance of testing or replacement. Pressure Relief Device must comply with Safety Order SO-B6 050421 1 | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_and_nameplate_for_vessel_age_2.png | file://x:/photopub/docs/0000000700/db55c72f-7720-4a6f-90a0-a95623611b35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__309fab04_bf1c_41a2_99a2_4043f4cdecfa
BPVOP-964574-2017 | 3063947 | 11/20/2017 | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Pressure_relief_and_nameplate_for_vessel_age_1.png,Pressure_relief_and_nameplate_for_vessel_age_2.png Pressure Relief device has no records or maintenance of testing or replacement. Pressure Relief Device must comply with Safety Order SO-B6 050421 1 | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_and_nameplate_for_vessel_age_1.png | file://x:/photopub/docs/0000000700/9ddbcd28-9731-47ef-b924-6c04b4180add.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__309fab04_bf1c_41a2_99a2_4043f4cdecfa
ELIN-966240-2017 | EL-564144-2017 | 11/21/2017 1:17:31 PM | ASSESS: EL: Final | png | #asFound | EL326 | Conductors Equipment is subject to mechanical damage such as directly exposed, not protected or not buried to an acceptable depth | 4 | 4 | #Exposed_non-metallic_sheathed_cable.png Exposed, energized nonmetallic sheathed cable, at a height of less than 1.5m above floor, must be protected from mechanical damage in order to prevent damage to cable, minimizing the risk associated with accidental electrical shock in the event that a cable is damaged and an energized conductor is exposed to accidental contact | 4 | Conductors Equipment is subject to mechanical damage such as directly exposed, not protected or not buried to an acceptable depth | Exposed_non-metallic_sheathed_cable.png | file://x:/photopub/docs/0000000700/61647005-7cf0-4505-a782-36f084aec489.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72a4c6c8_1589_472f_8b52_5673ae400185
ELIN-961714-2017 | EL-528638-2017 | 11/17/2017 | ASSESS: EL: Final | png | #asFound - NMD 90 cable | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Pic_1.png -Unit #1020-2 approx. 1m of NMD 90 2/#14 cable and its conductors located in basement boiler closet was left hanging and unprotected which may lead to accidental contact or damage. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Pic_1.png | file://x:/photopub/docs/0000000700/b6e42867-96da-478f-aea8-7817ee6998bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4329449_4564_4eca_bd64_0a40b57b0540
ELIN-957968-2017 | EL-518871-2017 | 11/23/2017 8:50:25 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | #Extension_cord__extension_cord_wiring_to_permanent_heat_exchanger.png Flexible cord operating at 120 volts and 15 amps was found being used as a substitute if he power to a permanent heat exchanger. Flexible cord when used in this way can deteriorate over time energizing metal structures or causing arc fault damage to combustible surfaces and can result in injury to persons or damage to structures. | 4 | Conductors, Misuse of flexible cords. | Extension_cord__extension_cord_wiring_to_permanent_heat_exchanger.png | file://x:/photopub/docs/0000000701/1e6cdd3a-a98e-4e8b-92ec-def349ec69db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64556c3e_3cba_4cdb_92ed_9eb1f71dde07
ELIN-957928-2017 | EL-305792-2015 | 11/22/2017 8:55:12 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Open_lamp_fixture_closet.png A light fixture with an open lamp has been installed above a shelf in a residential closet. The open lamp can be damaged and then ignite surrounding combustibles damaging property or injuring persons, or both | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Open_lamp_fixture_closet.png | file://x:/photopub/docs/0000000701/de7eeadb-7d2f-4e09-8622-ad1f9695247f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fc0552e_73aa_455f_8e38_7074f7f9bcb6
ELIN-939535-2017 | EL-586678-2017 | 11/21/2017 1:10:20 PM | ASSESS: EL: Final | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 3 | #Hot_water_tank1.png,Hot_water_tank2.png The wiring of a 3000 watt 240 volt hot water tank is fed from a 30 amp 240 volt circuit c/w #10cu cable can allow an overload to occur without de-energizing of the circuit, this can lead to an equipment damage and thermal hazard issue | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | Hot_water_tank2.png | file://x:/photopub/docs/0000000700/dd440836-08bc-48d5-9260-b7af19ca5aab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc5e757_cebd_4ef4_a8bb_afacc3c4035a
PROP-871019-2017 | PR-480015-2016 | 11/23/2017 4:09:39 PM | ASSESS: PR OP: RAP | png | #asFound | PR018 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | #Conveyor_skirting1.png,Conveyor_skirting2.png,Conveyor_skirting3.png,Conveyor_skirting4.png Conveyor requires rigid skirting at all times during operation, skirting could become compromised with snow load , allowing areas of turning machinery to be open to the public, if skirting is not inspected and maintained daily. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Conveyor_skirting4.png | file://x:/photopub/docs/0000000702/313712e6-2c97-4e4f-8b1b-92cb1ccd3715.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7D2FF9B7_DD94_40EE_983F_828CB43B967D
ELIN-959986-2017 | EL-433866-2016 | 11/24/2017 10:39:32 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_Energized_Outlet_Boxes1.png,Open_Energized_Outlet_Boxes2.png,Open_Energized_Outlet_Boxes3.png 120 volt 15 amp outlet boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to persons. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_Energized_Outlet_Boxes1.png | file://x:/photopub/docs/0000000702/130e39bc-4efc-406c-b476-35ec850e619e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2cec38d_f585_490b_8569_ff09c8b090ae
ELIN-959986-2017 | EL-433866-2016 | 11/24/2017 10:39:32 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_Energized_Outlet_Boxes1.png,Open_Energized_Outlet_Boxes2.png,Open_Energized_Outlet_Boxes3.png 120 volt 15 amp outlet boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to persons. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_Energized_Outlet_Boxes3.png | file://x:/photopub/docs/0000000702/539a95bb-403b-407a-be34-d6d5aedb7e28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2cec38d_f585_490b_8569_ff09c8b090ae
ELIN-959986-2017 | EL-433866-2016 | 11/24/2017 10:39:32 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | #Open_Energized_Outlet_Boxes1.png,Open_Energized_Outlet_Boxes2.png,Open_Energized_Outlet_Boxes3.png 120 volt 15 amp outlet boxes are open and have not been provided with cover plates in areas where the wiring and connections are accessible to persons. This poses a shock hazard to persons and potential mechanical and electrical damage to the wiring. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_Energized_Outlet_Boxes2.png | file://x:/photopub/docs/0000000702/5a4cf1c2-81d2-49db-a2f8-df82b0b57d3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2cec38d_f585_490b_8569_ff09c8b090ae
GAIN-957656-2017 | GA-607785-2017 | 11/21/2017 10:58:07 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | #Tank2.png Vent terminal located within the regulator minimum clearance zone. Failure of the regular would allow high pressure gas to be released. Risk of fuel entering into appliance vent opening. Fire and or upset condition. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Tank2.png | file://x:/photopub/docs/0000000700/e1757bc3-80a4-441f-b6c1-69869d45847a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2db924f7_6efb_4e76_a5fa_cde841ddee40
ELIN-965209-2017 | EL-600982-2017 | 11/21/2017 10:23:10 AM | ASSESS: EL: Final | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | #Branch_circuit_through_main_compartment_of_panel.png In a single family dwelling, a 20 amp 120/240 volt branch circuit conductor passed through the consumer service compartment of the panel. This could result in an equipment damage condition. Picture attached. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Branch_circuit_through_main_compartment_of_panel.png | file://x:/photopub/docs/0000000700/74a97356-0cb4-4cc0-88cd-f7af9cd7b894.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42b86c43_3bce_4ac3_89e9_462bdcc70851
GAIN-944789-2017 | GA-544529-2017 | 11/21/2017 9:51:00 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | #Vent.png The as-found condition is that a portion of single wall vent is in close proximity to combustible material. The potential hazard is that the high heat of the vent will cause the combustible material to ignite, creating a fire hazard in an occupied space | 3 | Non compliant Type C Vent clearance | Vent.png | file://x:/photopub/docs/0000000700/ad71055f-fb63-4fc2-882a-140614f32ff6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f7456b1_a077_43ee_9f40_432bf0d99ae3
BPVIN-968478-2017 | BPV-617585-2017 | 11/22/2017 | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | #No_remote_emergency_shutdown.png A disconnect means capable of being locked in the open position shall be installed at an accessible location so the boiler can be disconnected in event of an emergency. There was no remote shutdown switch installed on the hot water boiler. Potential exists for an incident due to missing remote emergency control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_remote_emergency_shutdown.png | file://x:/photopub/docs/0000000702/a5bebd25-4759-4c1d-9cd2-3046c6c1dc81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a31ace46_e7e6_46e2_a35b_aa2a72c896d6
ELIN-969524-2017 | UW-618981-2017 | 11/22/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #outside_fixtures1.png,outside_fixtures2.png Electrical equipment used on the exterior of building must be rated for outdoor locations. This to protect from moisture entering the equipment and causing damage. During an assessment for unpermitted work at a duplex, the safety officer found NMD 90 cable strapped to the exterior of the building for outside lights. This cable is rated for damp locations and will breakdown when exposed to UV lighting. This cable entered surface mount, non-metallic boxes that are rated for dry locations only. This installation for the exterior light fixtures could allow moisture to to enter the junction boxes which could cause equipment damage to the fixtures. A potential shock hazard also exists for a person that comes in contact with the fixtures. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | outside_fixtures2.png | file://x:/photopub/docs/0000000702/d10dee5a-e26d-4779-bc6c-de096155c870.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6dc76aa_ae0a_444b_8c73_319909d53747
ELIN-969524-2017 | UW-618981-2017 | 11/22/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #outside_fixtures1.png,outside_fixtures2.png Electrical equipment used on the exterior of building must be rated for outdoor locations. This to protect from moisture entering the equipment and causing damage. During an assessment for unpermitted work at a duplex, the safety officer found NMD 90 cable strapped to the exterior of the building for outside lights. This cable is rated for damp locations and will breakdown when exposed to UV lighting. This cable entered surface mount, non-metallic boxes that are rated for dry locations only. This installation for the exterior light fixtures could allow moisture to to enter the junction boxes which could cause equipment damage to the fixtures. A potential shock hazard also exists for a person that comes in contact with the fixtures. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | outside_fixtures1.png | file://x:/photopub/docs/0000000702/fd62b0cd-62bb-491c-a683-1de40f9c3d98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6dc76aa_ae0a_444b_8c73_319909d53747
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet7.png | file://x:/photopub/docs/0000000702/a847a654-09c1-452d-8574-62c8aa8dabb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
ELIN-967152-2017 | EL-556651-2017 | 11/23/2017 5:21:00 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #Hot_tub_breaker_installed_closer_than_3M1.png,Hot_tub_breaker_installed_closer_than_3M2.png Ground Fault Circuit Interrupter (GFCI) breakers are required to be installed a minimum of 3M from a hot tub. This is required to prevent the occupant of the hot tub from contacting the GFCI device. This installation at an existing house has a new hot tub installed that has the GFCI breaker installed 2M from the hot tub. This is a potential shock hazard if the hot tub occupant contacts the device. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Hot_tub_breaker_installed_closer_than_3M2.png | file://x:/photopub/docs/0000000702/90cded6d-47cc-4f03-9f56-42bc25617a30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__146aa697_0d96_4a2b_b7eb_8e78a793c2cd
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet4.png | file://x:/photopub/docs/0000000702/9432c39e-f42d-44de-98c0-8318113c6b96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
ELIN-967152-2017 | EL-556651-2017 | 11/23/2017 5:21:00 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | #Hot_tub_breaker_installed_closer_than_3M1.png,Hot_tub_breaker_installed_closer_than_3M2.png Ground Fault Circuit Interrupter (GFCI) breakers are required to be installed a minimum of 3M from a hot tub. This is required to prevent the occupant of the hot tub from contacting the GFCI device. This installation at an existing house has a new hot tub installed that has the GFCI breaker installed 2M from the hot tub. This is a potential shock hazard if the hot tub occupant contacts the device. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Hot_tub_breaker_installed_closer_than_3M1.png | file://x:/photopub/docs/0000000702/e3142741-81b8-4dca-bac3-d9e08013e3cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__146aa697_0d96_4a2b_b7eb_8e78a793c2cd
EDIN-966517-2017 | ED-420434-2016 | 11/22/2017 5:39:26 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | #Lighting.png Dimly or lack of lighting at landings will cause tripping hazards | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Lighting.png | file://x:/photopub/docs/0000000701/69bcf01b-b0ac-4af2-a670-34f03fa09919.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f13e995_f74d_439a_ad67_e9b50b10646c
ELIN-966146-2017 | EL-617303-2017 | 11/23/2017 12:13:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL293 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | #Panel_as_found.png The 100amp 120/240 volt temporary service installation is intended to be energized and utilizes electrical tape for various breaker filler plates, this tape is not approved as filler plates, is weathered and peeling off. This will expose access to energized panel buss and can become a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_as_found.png | file://x:/photopub/docs/0000000702/04e32a8e-812c-49d4-b67a-cc67725b206a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2cf5498e_fc49_478a_8df3_3c5af76d98c3
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet6.png | file://x:/photopub/docs/0000000702/eaa7b3f0-fb58-49c6-bbc7-b7dc84016fa1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet2.png | file://x:/photopub/docs/0000000702/c1251d65-09f5-4970-8831-dfc3f0d5f553.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet1.png | file://x:/photopub/docs/0000000702/e4a27012-15cf-48e7-b1ec-c6ba2eed46d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet5.png | file://x:/photopub/docs/0000000702/2b951c52-c44c-4f72-836e-8bf42a2333c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
ELIN-963533-2017 | EL-521447-2017 | 11/22/2017 | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | #Bare_lamp_fixtures_installed_in_clothes_closet1.png,Bare_lamp_fixtures_installed_in_clothes_closet2.png,Bare_lamp_fixtures_installed_in_clothes_closet3.png,Bare_lamp_fixtures_installed_in_clothes_closet4.png,Bare_lamp_fixtures_installed_in_clothes_closet5.png,Bare_lamp_fixtures_installed_in_clothes_closet6.png,Bare_lamp_fixtures_installed_in_clothes_closet7.png Light fixtures install in clothes closets are not permitted to be of the bare lamp type. This is intended to prevent combustible material (ie: boxes, clothes, material, etc) from coming into contact with the heat producing bulbs. It is also intended to contain hot lamp particles if the bare lamp should rupture. This installation in a new house has recessed fixtures with bare lamps installed in clothes closets. This is a fire hazard if combustible materials contact hot bulbs or if bulbs rupture and hot bare lamp parts contact combustible materials. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Bare_lamp_fixtures_installed_in_clothes_closet3.png | file://x:/photopub/docs/0000000702/ee7fdbf9-ab7c-40b3-b013-881a30a13caf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74907a0f_9677_4a72_9728_e8637608155b
EDIN-967567-2017 | ED-532661-2017 | 11/22/2017 4:34:20 PM | ASSESS: ED IN: Acceptance | png | #asFound Drain pipe is run across floor 3 feet in front of door to equipment room causing a trip hazard to any personnel needing to access elevator machine room (top right of picture is elevator machine room) | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | #Drain_pipe_causing_trip_hazard.png Drain pipe is run across floor 3 feet in front of door to equipment room causing a trip hazard to any personnel needing to access elevator machine room (top right of picture is elevator machine room) | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Drain_pipe_causing_trip_hazard.png | file://x:/photopub/docs/0000000701/25d8f50e-3f4f-43f6-9fa9-693a02b9bb47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc0955a1_078e_44d9_bb9c_0245cdc5ee1a
ELIN-966602-2017 | EL-612073-2017 | 11/23/2017 2:42:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_located_within_1m_of_window1.png,Service_located_within_1m_of_window2.png Exposed service conductors are located within 1 meter of window. This could be a shock hazard if a person was to grab the service conductors from the window. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_located_within_1m_of_window2.png | file://x:/photopub/docs/0000000702/3fc9bbdf-11c5-430a-a729-edd22d47659c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7ff50f_6f76_42e0_9dac_5cad3e2bd51e
ELIN-966602-2017 | EL-612073-2017 | 11/23/2017 2:42:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | #Service_located_within_1m_of_window1.png,Service_located_within_1m_of_window2.png Exposed service conductors are located within 1 meter of window. This could be a shock hazard if a person was to grab the service conductors from the window. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_located_within_1m_of_window1.png | file://x:/photopub/docs/0000000702/9efe3251-2208-4a61-af4d-10059022d678.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7ff50f_6f76_42e0_9dac_5cad3e2bd51e
ELIN-966368-2017 | UW-617496-2017 | 11/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL349 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | #Hazard.png Energized armoured cable (BX) with no box cover or connectors were the conductors issue from the armour creating a potential shock or fire hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Hazard.png | file://x:/photopub/docs/0000000702/701ccb9e-a532-45a6-8eba-bb048a1738d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10b5ec40_92bc_4035_84f6_cb2baf62e4ea
ELHE-965114-2017 | HE-616700-2017 | 11/20/2017 | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL351 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | #Pic1.png Un-approved equipment has a higher risk of fire and shock because it has not been tested to a standard recognized in Canada. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Pic1.png | file://x:/photopub/docs/0000000701/390394b2-bde7-4e59-bf70-6d365b49c36a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f87d78f_be93_4e4b_afda_45598426a435
ELIN-960501-2017 | EL-541169-2017 | 11/22/2017 7:26:02 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | #Hazard1.png,Hazard1.png GFCI protection was not provided within 1.5M of sink this may be a shock hazard to personal using electrical equipment in the kitchen, GFCIâ€™s add protection when using electrical equipment around sinks. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Hazard1.png | file://x:/photopub/docs/0000000701/c45052c9-fbf7-4eec-b2b5-27b1f4a46638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce25a650_2c3e_4a5a_ba8c_9809a1c62f58
GAIN-953191-2017 | GA-610443-2017 | 11/23/2017 9:45:38 AM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | #LP_LOW_Switch.png -furnace missing mandatory safety controls. The low pressure gas safety switch has not been wired as per the propane conversion kit supplied by manufacturer. If the propane pressure were to get to low it could cause incomplete combustion and malfunctioning of the furnace. | 4 | Missing mandatory safety controls | LP_LOW_Switch.png | file://x:/photopub/docs/0000000701/c15b77d3-ff6a-4e12-bf8c-89c200bb6fb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f52b8759_82af_489d_b6c2_c76cb3c07e0f
ELOP-966314-2017 | 5281983 | 11/21/2017 | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | #Hazard.png Armoured cable (bx) without box, connector or cover creating a potential shock or fire hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Hazard.png | file://x:/photopub/docs/0000000702/c39cb5c0-b834-4859-8b29-eaea7437d3af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0810553b_b5d3_4e3d_86a2_46c59a23484d
ELIN-966333-2017 | UW-617470-2017 | 11/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL310 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | 3 | 3 | #Hazard1.png,Hazard2.png Panel breaker space open on energized panel leaving exposed electrical parts and a potential shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | Hazard1.png | file://x:/photopub/docs/0000000702/58726797-49a2-46c3-82be-075aa28ca187.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6747bd4_7844_49df_8979_508480f95e4b
ELIN-966333-2017 | UW-617470-2017 | 11/21/2017 | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL310 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | 3 | 3 | #Hazard1.png,Hazard2.png Panel breaker space open on energized panel leaving exposed electrical parts and a potential shock hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed | Hazard2.png | file://x:/photopub/docs/0000000702/cd0f0735-dedb-494f-9416-1b4648e32f3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6747bd4_7844_49df_8979_508480f95e4b
ELIN-968808-2017 | EL-553791-2017 | 11/23/2017 4:23:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | #PVC_Service_Conduit.png In a new 200 amp 120/240 volt underground electrical service the 3â€ PVC conduit that comes up from the underground trench to the Meterbase has not been provided with an expansion fitting. This could result in the conduit pulling out of the Meterbase due to settling of the ground or temperature changes. This poses a shock hazard to persons and potential mechanical damage to the electrical equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_Service_Conduit.png | file://x:/photopub/docs/0000000702/c0ccbc0f-cb62-4f44-b395-769bb3671ccb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11bddaec_ec1c_4315_a61b_72221b54dbca