## Select iminspection
INSPECTIONNUMBER | PERMITNUMBER | INSPECTIONDATE | INSPECTIONTYPE | FILETYPE | ATTACHMENTNOTES | HAZARDMAPCELLREFERENCE | HAZARDMAP | HAZARDRATINGBYMAP | HAZARDRATINGBYSO | HAZARDDESC | HAZARDMAPRATING | HAZARDMAPDESCRIPTION | FILENAME | PHOTOLINK | INSPECTIONLINK
ELIN-417696-2015 | EL-263557-2015 | 8/5/2015 1:44:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | Water has infiltrated the service entrance portion of the temporary weatherproof panel and could result in shorting of the service conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Water_at_neutral_bus.png | file://x:/photopub/docs/0000000312/6243bd66-8759-4561-85d9-06b5dab8b565.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__823b26b0_0536_4b22_a412_321a2682ed4b
ELIN-417696-2015 | EL-263557-2015 | 8/5/2015 1:44:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | Water has infiltrated the service entrance portion of the temporary weatherproof panel and could result in shorting of the service conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Water_on_breaker.png | file://x:/photopub/docs/0000000312/6770ae35-4e9b-4ac8-bc86-cf6a18cd1c4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__823b26b0_0536_4b22_a412_321a2682ed4b
ELIN-417386-2015 | EL-272867-2015 | 8/6/2015 2:23:20 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | NMD90 cable installed in an unapproved location, subject to effects of weather and mechanical damage. This could lead to degradation of the cabling resulting in a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_feeders.png | file://x:/photopub/docs/0000000312/35f67c1c-037d-43c1-90d9-990f0d9b8930.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44cb066a_d19a_4544_8470_56462f7bf039
ELIN-414172-2015 | EL-263155-2015 | 8/6/2015 2:23:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Inappropriate cable type for installed location. NMD90 cabling installed below grade in a wet location. This could lead to cable degradation resulting in a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Detail02_feeder.png | file://x:/photopub/docs/0000000312/89e67619-082e-4d33-81c3-bc55c3482f4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab3100a8_03a0_4bf5_b5a6_e0a0888c65eb
ELIN-417386-2015 | EL-272867-2015 | 8/6/2015 2:23:20 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | NMD90 cable installed in an unapproved location, subject to effects of weather and mechanical damage. This could lead to degradation of the cabling resulting in a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Detail02_feeders.png | file://x:/photopub/docs/0000000312/793f41b5-e595-40c5-b8fc-0df39be7c287.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44cb066a_d19a_4544_8470_56462f7bf039
ELIN-414172-2015 | EL-263155-2015 | 8/6/2015 2:23:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Inappropriate cable type for installed location. NMD90 cabling installed below grade in a wet location. This could lead to cable degradation resulting in a potential shock or fire hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_main_distribution.png | file://x:/photopub/docs/0000000312/f58c640c-3d55-411a-a1b7-e5be486c2ac0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab3100a8_03a0_4bf5_b5a6_e0a0888c65eb
ELIN-419995-2015 | EL-196022-2014 | 8/11/2015 6:27:58 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 2 | Exterior receptacle cover plate not installed allowing access to side mounted terminal screws while device is energized. This could result in potential shock and fire hazards leading to property damage and personal injury. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Detail01_exterior_receptacle.png | file://x:/photopub/docs/0000000314/21d8c385-4afd-40a3-a7ea-230c9b410d02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92cf1abf_106a_4a68_bf3c_109e08e45d88
ELIN-414713-2015 | EL-196635-2014 | 8/5/2015 7:34:04 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 2 | Service conductors are too low for the commercial location. They have been hit a number of times. The new attachment point is high enough but not substantial enough for the size of service. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Attachment01.png | file://x:/photopub/docs/0000000312/a94ee249-cc6e-4888-9ea0-f54e20458f15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1076be52_d2d0_414a_9147_d8f502d7afc9
ELIN-420667-2015 | EL-271005-2015 | 8/12/2015 10:42:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 3 | Work is incomplete or client is simply unaware. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Pole_installed_with_no_guy-assembly.png | file://x:/photopub/docs/0000000314/a5541c36-fd96-4c30-985d-f30910435533.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91ee7c7b_3420_4f50_bf02_c601c6ffdc60
ELIN-420667-2015 | EL-271005-2015 | 8/12/2015 10:42:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 3 | Work is incomplete or client is simply unaware. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Weather_Head_height.png | file://x:/photopub/docs/0000000314/c3b7e5ba-92db-4a5b-9e9b-c3acca4cbcf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91ee7c7b_3420_4f50_bf02_c601c6ffdc60
ELIN-411621-2015 | EL-249238-2015 | 8/4/2015 5:48:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Adequate secure footing to meet minimum requirements for working space around electrical equipment not provided at main disconnect. This could create unsafe conditions when operating main disconnect resulting in potential shock hazard. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | View01_service.png | file://x:/photopub/docs/0000000312/1e787715-a7bf-439c-9a80-8d519e989ab8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__257b5acf_7d78_4d80_a9b7_55c0f4d48ea6
ELIN-415225-2015 | EL-271256-2015 | 7/31/2015 8:22:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Temporary construction service equipment not adequately protected against weather. This could lead to deterioration of service equipment resulting in personal injury or damage to property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | View01_service_equipment.png | file://x:/photopub/docs/0000000312/61381c30-91a6-4fdf-88d0-8e52b1c12a39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658c7e33_ac96_443c_a721_b2e7b050c497
ELIN-415225-2015 | EL-271256-2015 | 7/31/2015 8:22:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Temporary construction service equipment not adequately protected against weather. This could lead to deterioration of service equipment resulting in personal injury or damage to property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Detail02_meter_base.png | file://x:/photopub/docs/0000000312/48afcba2-5a4c-44a7-9ab3-a9c0c31d83c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658c7e33_ac96_443c_a721_b2e7b050c497
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corroded_pressure_vessel_.png | file://x:/photopub/docs/0000000311/0bf026de-1091-4c5a-b92b-426ff1ce9820.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Moist_insulation.png | file://x:/photopub/docs/0000000311/780f6859-dfe3-45e1-a4c4-8dd612645c20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Outside_piping_corrosion_2.png | file://x:/photopub/docs/0000000311/fd096991-001d-4bca-8a4a-e571b559dd16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corroded_structural_steel.png | file://x:/photopub/docs/0000000311/473dba07-9b1a-4a82-92e3-88d3ae2d519f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corroded_pressure_vessel_2.png | file://x:/photopub/docs/0000000311/1432f974-65fa-4f8b-8054-f90886bb5092.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Outside_piping_corrosion.png | file://x:/photopub/docs/0000000311/084b1c3b-e90c-4a94-87fb-650919fb67e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corroded_supports.png | file://x:/photopub/docs/0000000311/e3d563da-e7b2-4b06-b90b-aae12fefc332.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
BPVOP-353542-2015 | 2250684 | 8/5/2015 8:34:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Corroded_supports_1.png | file://x:/photopub/docs/0000000311/3de1ad67-4b92-4a93-8509-ba9ac00c33a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__705a5a7b_3740_44df_b7d8_270e367843b0
GAIN-418891-2015 | GA-196775-2014 | 8/7/2015 12:50:51 PM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | Plastic hose connected to energize gas system | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | __test_gauge.png | file://x:/photopub/docs/0000000312/54513c0b-e617-4972-b9e8-e02866616014.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b98c586_5544_4858_838b_43b1111907b4
GAUP-417999-2015 | UW-273377-2015 | 8/7/2015 3:51:49 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was multiple pieces of uncertified or approved equipment that had been damaged over years of operation in use at a festival. The damage included rusted out burners and bypassed safety controls. This hazard was created due to a lack of maintenance or attention from any qualified individuals. | 4 | Missing mandatory safety controls | removed_temp_safety.png | file://x:/photopub/docs/0000000312/62eba9c8-21c7-45ce-afc5-13f4e6b9a39e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64031cb7_9c8d_4f6c_ac57_5521d8d0df0d
GAUP-417999-2015 | UW-273377-2015 | 8/7/2015 3:51:49 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was multiple pieces of uncertified or approved equipment that had been damaged over years of operation in use at a festival. The damage included rusted out burners and bypassed safety controls. This hazard was created due to a lack of maintenance or attention from any qualified individuals. | 4 | Missing mandatory safety controls | Carbon_build_up.png | file://x:/photopub/docs/0000000312/c48b3091-c352-4e82-9183-e65a24c30fd6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64031cb7_9c8d_4f6c_ac57_5521d8d0df0d
GAUP-417999-2015 | UW-273377-2015 | 8/7/2015 3:51:49 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was multiple pieces of uncertified or approved equipment that had been damaged over years of operation in use at a festival. The damage included rusted out burners and bypassed safety controls. This hazard was created due to a lack of maintenance or attention from any qualified individuals. | 4 | Missing mandatory safety controls | Deep_Fryer_with_bypassed_piolt_and_temp_control.png | file://x:/photopub/docs/0000000312/0b7256bf-acf9-44a6-a332-8bcfddc3a5c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64031cb7_9c8d_4f6c_ac57_5521d8d0df0d
GAUP-417999-2015 | UW-273377-2015 | 8/7/2015 3:51:49 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was multiple pieces of uncertified or approved equipment that had been damaged over years of operation in use at a festival. The damage included rusted out burners and bypassed safety controls. This hazard was created due to a lack of maintenance or attention from any qualified individuals. | 4 | Missing mandatory safety controls | piping.png | file://x:/photopub/docs/0000000312/7c1856c1-b0cd-427b-96fc-5d531895f41b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64031cb7_9c8d_4f6c_ac57_5521d8d0df0d
ELIN-418607-2015 | UW-273866-2015 | 8/6/2015 11:38:48 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL171 | Conductor sizing Loads exceed branch circuit conductor ampacity. | 3 | 3 | Overloaded circuit on the secondary side of a 350VA transformer for extra low voltage lighting 12v. | 3 | Conductor sizing Loads exceed branch circuit conductor ampacity. | 2.png | file://x:/photopub/docs/0000000312/cd9d9b0b-2984-4ec7-a674-b3bad18694ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea963e56_fa29_40c0_a209_9faa34b01ef0
ELIN-423805-2015 | EL-272344-2015 | 8/25/2015 7:18:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Plastic bushings prevent potential arcing and conductor damage where conductors issue from armor. No plastic bushings were provided for this installation connector used had very sharp edges | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | No_bushing_cable_termination_meter_base.png | file://x:/photopub/docs/0000000319/0fec6d30-ff65-4139-8d91-ee28f0b0c9e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4109550_ce1a_45fe_a0c7_99bad8190c3b
ELIN-423412-2015 | EL-262702-2015 | 8/18/2015 9:54:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | It is important to to ground the service with a grounding conductor run from service grounding electrode in earth to service system conductors. Observed there was no grounding conductor installed into main service switch and no grounding conductor was terminated at all on service neutral bar. The service system was not grounded. By not grounding the service system and if there is an electrical short circuit or fault in the electrical system, then an electrical fault could cause an electrical fire or shock hazard to persons or property. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Fused_disconnect_service_outdoor_has_no_grounded_conductor_installed_at_all.png | file://x:/photopub/docs/0000000316/1dc30e48-99e1-4083-a931-a123b9b0004d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8b9562_e3a1_4321_892b_75996af11d5e
ELIN-423412-2015 | EL-262702-2015 | 8/18/2015 9:54:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | It is important to to ground the service with a grounding conductor run from service grounding electrode in earth to service system conductors. Observed there was no grounding conductor installed into main service switch and no grounding conductor was terminated at all on service neutral bar. The service system was not grounded. By not grounding the service system and if there is an electrical short circuit or fault in the electrical system, then an electrical fault could cause an electrical fire or shock hazard to persons or property. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | No_grounding_conductor_installed_or_terminated_onto_service_neutral_bar_terminal.png | file://x:/photopub/docs/0000000316/5ad9c27b-487a-408f-ab42-795ad61ce936.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8b9562_e3a1_4321_892b_75996af11d5e
ELIN-423412-2015 | EL-262702-2015 | 8/18/2015 9:54:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | It is important to to ground the service with a grounding conductor run from service grounding electrode in earth to service system conductors. Observed there was no grounding conductor installed into main service switch and no grounding conductor was terminated at all on service neutral bar. The service system was not grounded. By not grounding the service system and if there is an electrical short circuit or fault in the electrical system, then an electrical fault could cause an electrical fire or shock hazard to persons or property. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | No_grounding_conductor_from_electrode_terminated_onto_service_neutral_bar.png | file://x:/photopub/docs/0000000316/174f03ab-d9eb-4d39-bc80-1fa14c94ff02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8b9562_e3a1_4321_892b_75996af11d5e
ELIN-416651-2015 | EL-208031-2015 | 8/14/2015 3:20:34 PM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 4 | It is important for electrical contractor and FSR that declares all permit work is complete, that the FSR actually physically examines and ensures that all electrical work and equipment on site is safe and compliant and all work is completed as required by code and regulations. Found two kitchen exhaust fans and several devices for switches and receptacles installation not fully completed and there was live exposed conductors khanging mid air without junction boxes and covers installed to contain llive exposed conductors in a box with covers. Devices are required to be fully supported in place in outlet boxes with covers on and ends of conductors for exhaust fans require junction boxes with covers which are fully supported in place. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_conductors_for_kitchen_exhaust_fan_with_no_junction_box_on_end.png | file://x:/photopub/docs/0000000316/2e5b6d35-ffb9-48eb-8723-37d406136d6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31248b36_a1a9_4f7b_98f5_3397906b837d
ELIN-416651-2015 | EL-208031-2015 | 8/14/2015 3:20:34 PM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 4 | It is important for electrical contractor and FSR that declares all permit work is complete, that the FSR actually physically examines and ensures that all electrical work and equipment on site is safe and compliant and all work is completed as required by code and regulations. Found two kitchen exhaust fans and several devices for switches and receptacles installation not fully completed and there was live exposed conductors khanging mid air without junction boxes and covers installed to contain llive exposed conductors in a box with covers. Devices are required to be fully supported in place in outlet boxes with covers on and ends of conductors for exhaust fans require junction boxes with covers which are fully supported in place. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_conductors_for_kitchen_exhaust_fan_with_no_junction_box_on_end_2nd_kitchen.png | file://x:/photopub/docs/0000000316/485bea37-7fe0-421b-9844-c163983a8708.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31248b36_a1a9_4f7b_98f5_3397906b837d
ELIN-416651-2015 | EL-208031-2015 | 8/14/2015 3:20:34 PM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 4 | It is important for electrical contractor and FSR that declares all permit work is complete, that the FSR actually physically examines and ensures that all electrical work and equipment on site is safe and compliant and all work is completed as required by code and regulations. Found two kitchen exhaust fans and several devices for switches and receptacles installation not fully completed and there was live exposed conductors khanging mid air without junction boxes and covers installed to contain llive exposed conductors in a box with covers. Devices are required to be fully supported in place in outlet boxes with covers on and ends of conductors for exhaust fans require junction boxes with covers which are fully supported in place. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Devices_not_completed_for_job_final_with_live_exposed_conductors.png | file://x:/photopub/docs/0000000316/aab18a91-df4b-45b3-8845-59039631b167.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31248b36_a1a9_4f7b_98f5_3397906b837d
ELIN-416651-2015 | EL-208031-2015 | 8/14/2015 3:20:34 PM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 4 | It is important for electrical contractor and FSR that declares all permit work is complete, that the FSR actually physically examines and ensures that all electrical work and equipment on site is safe and compliant and all work is completed as required by code and regulations. Found two kitchen exhaust fans and several devices for switches and receptacles installation not fully completed and there was live exposed conductors khanging mid air without junction boxes and covers installed to contain llive exposed conductors in a box with covers. Devices are required to be fully supported in place in outlet boxes with covers on and ends of conductors for exhaust fans require junction boxes with covers which are fully supported in place. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Devices_not_completed_for_job_final_with_live_exposed_conductors_2.png | file://x:/photopub/docs/0000000316/c4d51587-c157-46b8-af42-fb5f53f559bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31248b36_a1a9_4f7b_98f5_3397906b837d
ELIN-416651-2015 | EL-208031-2015 | 8/14/2015 3:20:34 PM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 4 | It is important for electrical contractor and FSR that declares all permit work is complete, that the FSR actually physically examines and ensures that all electrical work and equipment on site is safe and compliant and all work is completed as required by code and regulations. Found two kitchen exhaust fans and several devices for switches and receptacles installation not fully completed and there was live exposed conductors khanging mid air without junction boxes and covers installed to contain llive exposed conductors in a box with covers. Devices are required to be fully supported in place in outlet boxes with covers on and ends of conductors for exhaust fans require junction boxes with covers which are fully supported in place. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_conductor_ends_for_final_of_of_job.png | file://x:/photopub/docs/0000000316/68fcc48f-418d-463a-b35a-e32f63b40195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31248b36_a1a9_4f7b_98f5_3397906b837d
ELIN-423150-2015 | EL-275751-2015 | 8/18/2015 9:53:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_approved_for_the_use_or_correct_size_for_cables_installed_4.png | file://x:/photopub/docs/0000000316/d2b3ce62-e84e-49d8-b007-5dccceff3b28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__746e64b9_9907_4fdb_bd0b_40de0921544f
ELIN-423150-2015 | EL-275751-2015 | 8/18/2015 9:53:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_approved_for_the_use_or_correct_size_for_cables_installed_1.png | file://x:/photopub/docs/0000000316/e4300bff-696f-4220-aefe-0c3ab4487d6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__746e64b9_9907_4fdb_bd0b_40de0921544f
ELIN-423150-2015 | EL-275751-2015 | 8/18/2015 9:53:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_approved_for_the_use_or_correct_size_for_cables_installed_6.png | file://x:/photopub/docs/0000000316/2a62650b-5dfa-46da-b3f2-c6a3297264bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__746e64b9_9907_4fdb_bd0b_40de0921544f
ELIN-423150-2015 | EL-275751-2015 | 8/18/2015 9:53:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_approved_for_the_use_or_correct_size_for_cables_installed_5.png | file://x:/photopub/docs/0000000316/65662268-ab6d-4222-b5d0-b21edb9b0641.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__746e64b9_9907_4fdb_bd0b_40de0921544f
ELIN-423150-2015 | EL-275751-2015 | 8/18/2015 9:53:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_approved_for_the_use_or_correct_size_for_cables_installed_3.png | file://x:/photopub/docs/0000000316/37f5f106-2a0b-464e-8dd1-4c1ab08d0c24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__746e64b9_9907_4fdb_bd0b_40de0921544f
ELIN-423150-2015 | EL-275751-2015 | 8/18/2015 9:53:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_approved_for_the_use_or_correct_size_for_cables_installed_2.png | file://x:/photopub/docs/0000000316/40d33ab2-a0e2-4e2e-87f8-ece50b50721b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__746e64b9_9907_4fdb_bd0b_40de0921544f
ELIN-423163-2015 | EL-275079-2015 | 8/18/2015 9:54:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | It is important that electrical equipment that may produce electrical arcing is located more than one meter away from gas meter relief valves. Observed that this installation had electrical meterbase, and its meter which is a possible arcing device, to be located less than one meter away from outdoor gas vent. This is a possible electrical fire hazard in the event there is gas coming out of the gas vent and the meter is pulled or disconnected from meterbase. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Electric_meter_less_than_one_meter_from_gas_vent_3.png | file://x:/photopub/docs/0000000316/009986cb-17e4-45d9-ad05-7a75bf6a8705.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceaf8979_71cc_4f80_b2a5_13e956ce7a8a
ELIN-423163-2015 | EL-275079-2015 | 8/18/2015 9:54:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | It is important that electrical equipment that may produce electrical arcing is located more than one meter away from gas meter relief valves. Observed that this installation had electrical meterbase, and its meter which is a possible arcing device, to be located less than one meter away from outdoor gas vent. This is a possible electrical fire hazard in the event there is gas coming out of the gas vent and the meter is pulled or disconnected from meterbase. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Electric_meter_less_than_one_meter_from_gas_vent_4.png | file://x:/photopub/docs/0000000316/d418dcfc-a6c0-496a-8879-7ca08a25d358.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceaf8979_71cc_4f80_b2a5_13e956ce7a8a
ELIN-423163-2015 | EL-275079-2015 | 8/18/2015 9:54:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | It is important that electrical equipment that may produce electrical arcing is located more than one meter away from gas meter relief valves. Observed that this installation had electrical meterbase, and its meter which is a possible arcing device, to be located less than one meter away from outdoor gas vent. This is a possible electrical fire hazard in the event there is gas coming out of the gas vent and the meter is pulled or disconnected from meterbase. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Electric_meter_less_than_one_meter_from_gas_vent_2.png | file://x:/photopub/docs/0000000316/f8202bd5-404f-40c5-87cd-1af2a2f63e5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceaf8979_71cc_4f80_b2a5_13e956ce7a8a
ELIN-423163-2015 | EL-275079-2015 | 8/18/2015 9:54:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | It is important that electrical equipment that may produce electrical arcing is located more than one meter away from gas meter relief valves. Observed that this installation had electrical meterbase, and its meter which is a possible arcing device, to be located less than one meter away from outdoor gas vent. This is a possible electrical fire hazard in the event there is gas coming out of the gas vent and the meter is pulled or disconnected from meterbase. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Electric_meter_less_than_one_meter_from__gas_vent_1.png | file://x:/photopub/docs/0000000316/fbb9e751-c4dd-4c33-8310-1b0febbfebce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceaf8979_71cc_4f80_b2a5_13e956ce7a8a
ELIN-427915-2015 | EL-243326-2015 | 8/24/2015 4:20:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Unprotected service conductors are run in contact with combustible material. BC Hydro protection is not adequate for the conductor size and they can cause a fire if exposed to combustible material. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Service_conductors.png | file://x:/photopub/docs/0000000318/6e1fb2ee-87e0-4c8f-8d92-b72f34e2a015.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af70f7b7_58a5_408d_b390_933e122c50f9
BPVOP-427485-2015 | 2266775 | 8/21/2015 11:52:20 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During assessment of machine mounted air receiver l found that relief valve exceeded 3yr interval for servicing or replacement. In the event of failure of operating control to shut down compressor at set operating pressure, vessel will be subjected to pressure beyond maximum allowable working pressure of 200psig if relief valve fails to operate, resulting in permanent damage or rupture of vessel with likelihood of severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE_FOR_AIR_RECEIVER.png | file://x:/photopub/docs/0000000318/7ccda2a5-295b-41b3-94df-3d1bc13d4229.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e13d8f0e_e392_48fb_a063_048d0292491b
ELIN-423570-2015 | EL-275751-2015 | 8/18/2015 9:49:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | It is important that hydro meters located outdoors be located more than one meter from gas meter vent as required by code. Found this installation that hydro meters located outdoors are not located more than one meter from gas meter vent as required by code. This is a possible electrical fire hazard to persons and property in the event that there is an arcing device too close to gas vent and may cause a gas fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 4_meter_too_close_to_gas_vent.png | file://x:/photopub/docs/0000000317/21a73b21-eecb-4b9b-b7f8-79f473d36516.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ebded74_b3d6_457f_bd31_947ee75c12ad
ELIN-423570-2015 | EL-275751-2015 | 8/18/2015 9:49:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | It is important that hydro meters located outdoors be located more than one meter from gas meter vent as required by code. Found this installation that hydro meters located outdoors are not located more than one meter from gas meter vent as required by code. This is a possible electrical fire hazard to persons and property in the event that there is an arcing device too close to gas vent and may cause a gas fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3_meter_too_close_to_gas_vent.png | file://x:/photopub/docs/0000000317/9d4871fc-3aea-43f8-ac92-0341eb40eaf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ebded74_b3d6_457f_bd31_947ee75c12ad
ELIN-423570-2015 | EL-275751-2015 | 8/18/2015 9:49:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | It is important that hydro meters located outdoors be located more than one meter from gas meter vent as required by code. Found this installation that hydro meters located outdoors are not located more than one meter from gas meter vent as required by code. This is a possible electrical fire hazard to persons and property in the event that there is an arcing device too close to gas vent and may cause a gas fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 2_meter_too_close_to_gas_vent.png | file://x:/photopub/docs/0000000317/7541a74f-aa08-4aa8-beb9-d43ebdb96332.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ebded74_b3d6_457f_bd31_947ee75c12ad
ELIN-423570-2015 | EL-275751-2015 | 8/18/2015 9:49:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | It is important that hydro meters located outdoors be located more than one meter from gas meter vent as required by code. Found this installation that hydro meters located outdoors are not located more than one meter from gas meter vent as required by code. This is a possible electrical fire hazard to persons and property in the event that there is an arcing device too close to gas vent and may cause a gas fire. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 1_meter_too_close_to_gas_vent.png | file://x:/photopub/docs/0000000317/efdb9bea-3433-46ab-8e8a-bd58941563c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ebded74_b3d6_457f_bd31_947ee75c12ad
BPVOP-337310-2015 | 2250760 | 8/27/2015 2:01:36 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Pressure_vessel_insulation_.png | file://x:/photopub/docs/0000000319/88e53a9b-9617-4f1c-8f7c-0021c561a8b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a7a5e28_f4b4_47ad_9fc3_ff7850e31421
BPVOP-337310-2015 | 2250760 | 8/27/2015 2:01:36 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Ammonia_piping_not_insulated.png | file://x:/photopub/docs/0000000319/03f4a0c8-1c41-4ae2-af94-cdefb0a9bb0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a7a5e28_f4b4_47ad_9fc3_ff7850e31421
ELIN-423588-2015 | EL-276173-2015 | 8/19/2015 11:35:47 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | It is important for homeowner to ensure all electrical equipment which is connected to power supply system is safe and compliant and an approved wiring method with live conductors entered and contained in a junction box with cover on and must be inspected and authorized by a safety officer for before connection is made. Found live exposed splice of branch circuit conductors without a junction box and cover and without inspection and authorization by safety officer for connection of installed/altered equipment. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_unsafe_circuit_without_junction_box4.png | file://x:/photopub/docs/0000000317/74933064-86e5-447d-a5bc-9612b7152f99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__561056ef_cc1f_4190_8958_a1329068b52e
ELIN-423588-2015 | EL-276173-2015 | 8/19/2015 11:35:47 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | It is important for homeowner to ensure all electrical equipment which is connected to power supply system is safe and compliant and an approved wiring method with live conductors entered and contained in a junction box with cover on and must be inspected and authorized by a safety officer for before connection is made. Found live exposed splice of branch circuit conductors without a junction box and cover and without inspection and authorization by safety officer for connection of installed/altered equipment. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_unsafe_circuit_without_junction_box1.png | file://x:/photopub/docs/0000000317/a0d18aa3-b244-4b33-8d5d-6369ada74369.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__561056ef_cc1f_4190_8958_a1329068b52e
ELIN-423588-2015 | EL-276173-2015 | 8/19/2015 11:35:47 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | It is important for homeowner to ensure all electrical equipment which is connected to power supply system is safe and compliant and an approved wiring method with live conductors entered and contained in a junction box with cover on and must be inspected and authorized by a safety officer for before connection is made. Found live exposed splice of branch circuit conductors without a junction box and cover and without inspection and authorization by safety officer for connection of installed/altered equipment. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_unsafe_circuit_without_junction_box3.png | file://x:/photopub/docs/0000000317/e3b4898b-ce43-42e8-a40b-a58d25717dda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__561056ef_cc1f_4190_8958_a1329068b52e
ELIN-423588-2015 | EL-276173-2015 | 8/19/2015 11:35:47 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | It is important for homeowner to ensure all electrical equipment which is connected to power supply system is safe and compliant and an approved wiring method with live conductors entered and contained in a junction box with cover on and must be inspected and authorized by a safety officer for before connection is made. Found live exposed splice of branch circuit conductors without a junction box and cover and without inspection and authorization by safety officer for connection of installed/altered equipment. This is in order to protect persons and property from electrical fire or shock hazards to persons and property. | 3 | Protection and control Low voltage protection damaged or not provided. | Live_exposed_unsafe_circuit_without_junction_box2.png | file://x:/photopub/docs/0000000317/007dd19d-9e97-4078-ad2c-66be4a26e792.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__561056ef_cc1f_4190_8958_a1329068b52e
BPVOP-428316-2015 | 5219801 | 8/24/2015 6:21:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During assessment of 160psig coil type domestic hot water boiler operating with 250*Fahrenheit Maximum Allowable Temperature I found that safety relief valve exceeded 6yr interval for servicing or replacement. In the event of failure of controls to shut down boiler, boiler will be subjected to pressure beyond maximum allowable working pressure if safety relief valve fails to operate, resulting in permanent damage or rupture of boiler with likelihood of severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000318/ddb903c5-f7a6-4b60-9cf0-3220bf30382a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58f50d04_ad02_4ec0_a26d_0e63d066ddb1
ELIN-424693-2015 | EL-277931-2015 | 8/20/2015 8:26:40 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 2 | -secondary suite combination panel is located on outside of suite. -secondary suite panel is not independently supplied. No access to the overcurrent device. Suite Panel could be disconnected without access to the occupant. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Secondary_suite_panel.png | file://x:/photopub/docs/0000000317/a8a074f8-9e72-4e28-8300-6348df8c232a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d413abef_661e_4145_bf3b_9b79b762caa5
BPVOP-337310-2015 | 2250760 | 8/27/2015 2:01:36 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Pressure vessels must be structurally sound in order to retain pressure. I found that some sections of ammonia piping/low pressure receivers are affected by corrosion. Pressure vessel rupture may occur should pressure rise to a level high enough to cause remaining metal weakness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Piping_insulation_moist.png | file://x:/photopub/docs/0000000319/318f6a06-b8c7-4460-9d2c-90b9faf96329.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a7a5e28_f4b4_47ad_9fc3_ff7850e31421
ELIN-426174-2015 | EL-271256-2015 | 8/21/2015 4:25:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding conductor is terminated incorrectly on the load side of the main service disconnecting means. This poses a hazard resulting in potential injury to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Detail02__system_grounding_conductor.png | file://x:/photopub/docs/0000000317/671d328f-f386-4241-a4f4-7dc53c3aa959.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0b9e9a7_bf01_481a_a93c_14658c1a3e19
ELIN-426174-2015 | EL-271256-2015 | 8/21/2015 4:25:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding conductor is terminated incorrectly on the load side of the main service disconnecting means. This poses a hazard resulting in potential injury to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Detail03__system_grounding_conductor.png | file://x:/photopub/docs/0000000317/92e2c084-33b3-4bb8-ac3b-b0aad0911d0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0b9e9a7_bf01_481a_a93c_14658c1a3e19
ELIN-426174-2015 | EL-271256-2015 | 8/21/2015 4:25:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding conductor is terminated incorrectly on the load side of the main service disconnecting means. This poses a hazard resulting in potential injury to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | View01__service.png | file://x:/photopub/docs/0000000317/4b745099-4e71-4137-935e-10036270e8fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0b9e9a7_bf01_481a_a93c_14658c1a3e19
ELIN-426174-2015 | EL-271256-2015 | 8/21/2015 4:25:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding conductor is terminated incorrectly on the load side of the main service disconnecting means. This poses a hazard resulting in potential injury to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Detail04__system_grounding_conductor.png | file://x:/photopub/docs/0000000317/37bd65e6-c4d7-46e0-81f6-5f035a9bd503.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0b9e9a7_bf01_481a_a93c_14658c1a3e19
BPVOP-366523-2015 | 2288348 | 8/13/2015 8:57:10 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves require periodic servicing and replacement. I found that safety valve was installed in 1992, and was never replaced since. An incident may occur due to an old safety valve not functioning properly, which has never been checked or serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_1992.png | file://x:/photopub/docs/0000000315/41c6949b-c6b4-4522-a4bd-45f5e01890f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1803215_beee_4469_b08a_2a18c25e1975
BPVOP-366523-2015 | 2288348 | 8/13/2015 8:57:10 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety valves require periodic servicing and replacement. I found that safety valve was installed in 1992, and was never replaced since. An incident may occur due to an old safety valve not functioning properly, which has never been checked or serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | New_safety_valve_installed_on_expansion_line.png | file://x:/photopub/docs/0000000315/e231f360-9e18-4715-8b88-9ed18ec655e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1803215_beee_4469_b08a_2a18c25e1975
ELIN-427849-2015 | EL-271037-2015 | 8/26/2015 11:56:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding conductor terminated on housing of main distribution. This could lead to the service ground being inadvertently disconnected. This creates the potential for risk of personal injury or property damage due to failure of disconnecting means to operate properly in a fault condition | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Detail01_system_ground_conductor.png | file://x:/photopub/docs/0000000319/e1d39a18-f915-4e8a-8f1e-f6364752dfb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5296b10e_f3bf_4729_83b9_148a0221e4d6
ELIN-431534-2015 | EL-280269-2015 | 9/2/2015 1:13:47 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound |  |  |  | 3 | Ground conductor not terminated at neutral point |  |  | G.png | file://x:/photopub/docs/0000000322/e644e14a-101c-45d2-a5ff-1b27a32072bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45d0749f_76fb_413d_96e6_6a14142a307d
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 7.png | file://x:/photopub/docs/0000000322/d47c4eda-b4da-4c6d-8d22-8e4b9a4458c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 13.png | file://x:/photopub/docs/0000000322/3e91ee77-2515-46f4-b885-ffd7e8a0d0ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000322/5e2892db-4b98-43d2-aee1-63c00091579d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 6.png | file://x:/photopub/docs/0000000322/69285bf0-5526-4f02-ba2e-5b5b08c96331.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000322/dd788a49-7f43-4535-82e1-fcd0ea261958.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 9.png | file://x:/photopub/docs/0000000322/211d6155-4705-4449-8909-ff489e40f2e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 10.png | file://x:/photopub/docs/0000000322/1e5d99b2-74d3-4ae0-8a1a-6a5eb83acfbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 8.png | file://x:/photopub/docs/0000000322/80fbb044-bbd2-46c1-add6-6dfe882aeaef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000322/6388096b-2179-4138-ba0e-d2e85aecbf17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 12.png | file://x:/photopub/docs/0000000322/75be71ed-325f-41a5-8e8b-48f6add57492.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 11.png | file://x:/photopub/docs/0000000322/6bdb3dbb-191f-4661-bddc-38aaa7cb86cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-428455-2015 | EL-279913-2015 | 9/1/2015 6:02:12 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord was fed from an outside use receptacle with flexible cord passing through the skirting of the mobile home. Flexible cord was run in the crawlspace under the living area in the home, in lieu of permanent fixed wiring. Flexible cord is existing and is showing uv and rain damage which is most notable where flexible cord passes through skirting of trailer where occupants would normally connect outside yard equipment for use outdoors. Connections between 120 volt heat trace and flexible cord was corroded. The damage found on the existing flexible extension cord wiring is consistent with other installations where property damage due to fire in the wiring, and adjacent combustible materials has been caused by faults in flexible cord and the cord and cord cap connection method feeding permanent equipment. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_from_outside_plug_to_crawl_.png | file://x:/photopub/docs/0000000321/cf3357ed-18fe-4a47-9cee-a80d047ad018.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ffadef7_6b4b_4631_95d1_418af8549306
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 5.png | file://x:/photopub/docs/0000000322/944e643c-572a-4009-a0f5-4588009debe0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-434018-2015 | EL-283642-2015 | 9/2/2015 3:41:49 PM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead consumer's service equipment was reconnected to utility supply system while service head and its service head conductors were damaged and strained and pulled from existing meter-base due to tree falling and damaging service equipment. This consumer's service and its distribution equipment was not checked, tested, corrected and made safe and compliant and was not authorized for connection before supply authority made service connection. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000322/76b2c001-e85b-406c-8fda-03503e5abce5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1682a5d_f05b_4664_aec3_29018daee461
ELIN-437235-2015 | UW-285701-2015 | 9/8/2015 5:06:55 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel covers are required to be in place at all times when electrical panels are connected to an electrical supply. This installation has the main service panel and a sub-panel that do not have covers installed. The main breaker of the service panel is currently turned off but could easily be turned on creating a shock hazard should a person come in contact with the equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Water_entering_the_service_panel.png | file://x:/photopub/docs/0000000324/9881c62a-c570-4f06-b861-b9e1419df884.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e007591d_d2a8_4c0f_a753_690cefcfcff8
ELIN-423011-2015 | 5237042 | 8/31/2015 1:38:02 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Electrical components which are or could be energized must be guarded to avoid accidental contact. Contact could result in electric shock, and unintentional contact could result in arc flash. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Generator_connection.png | file://x:/photopub/docs/0000000323/695a4b80-326a-4135-9f15-a48a34985ac4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4e05117_11d1_40d8_9cc2_6efaf9750031
ELIN-423011-2015 | 5237042 | 8/31/2015 1:38:02 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Electrical components which are or could be energized must be guarded to avoid accidental contact. Contact could result in electric shock, and unintentional contact could result in arc flash. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Dry_room_panel.png | file://x:/photopub/docs/0000000323/91622591-90c3-48ca-a06d-6a8bdac688ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4e05117_11d1_40d8_9cc2_6efaf9750031
ELIN-423011-2015 | 5237042 | 8/31/2015 1:38:02 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Electrical components which are or could be energized must be guarded to avoid accidental contact. Contact could result in electric shock, and unintentional contact could result in arc flash. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Well_pump_connection.png | file://x:/photopub/docs/0000000323/8cb2018a-debd-446e-a5e4-74c2a51f6eee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4e05117_11d1_40d8_9cc2_6efaf9750031
ELIN-436680-2015 | EL-276550-2015 | 9/8/2015 7:05:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL106 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | 2 | 2 | The exterior outer thermoplastic jacket has been damaged and therefore exposing metal armor casing too wet weather. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | Consumer_service_cable_damaged_jacket_.png | file://x:/photopub/docs/0000000324/561ead77-1539-4c82-a28b-c14d3f78bf86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d59a20c_f120_45b1_9009_f21a82332ac6
ELIN-434431-2015 | EL-275911-2015 | 9/8/2015 7:14:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | A raceway emerges from grade and connects to a hub in an enclosure with no expansion joint provided. The raceway could settle and damage equipment on pole | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | No_expansion_joint_communication_conduit.png | file://x:/photopub/docs/0000000324/4bc77779-e68a-4bea-bae9-4cf5b2da0b9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0a40e52_b7b1_4e2d_8ddf_717aa1f38e22
ELIN-423604-2015 | 5308783 | 9/1/2015 5:31:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service conductors may not be located within 1 m of opening windows. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_too_close_to_window.png | file://x:/photopub/docs/0000000321/3d38ab5c-9a2d-4fe6-9232-f13510ad3f4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be98b506_f39a_4a94_8b75_84ad047348ce
ELIN-394395-2015 | 5142952 | 8/31/2015 9:21:24 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Panel boards may not be left without protective covers when energized. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_panel.png | file://x:/photopub/docs/0000000321/bd16d262-0646-4b51-96d2-d13069db2c54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7b149ffc_337f_4d4a_a644_a9ee43ceb7f6
ELOP-226526-2014 | 5393753 | 8/31/2015 9:22:11 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Service conductors and raceways must be kept in safe condition. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Big_house.png | file://x:/photopub/docs/0000000321/ff4147f6-3d0b-46a4-bab4-4aeb11be3d7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e82c4a5c_3fdd_4792_86cd_e9c7f7898c22
ELIN-437235-2015 | UW-285701-2015 | 9/8/2015 5:06:55 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel covers are required to be in place at all times when electrical panels are connected to an electrical supply. This installation has the main service panel and a sub-panel that do not have covers installed. The main breaker of the service panel is currently turned off but could easily be turned on creating a shock hazard should a person come in contact with the equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_missing_from_service_panel_.png | file://x:/photopub/docs/0000000324/6d4ea1e5-87a0-47b9-8533-7086b85d4248.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e007591d_d2a8_4c0f_a753_690cefcfcff8
ELIN-436287-2015 | EL-283238-2015 | 9/8/2015 9:03:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | The service nipple from the meter to the panel has no bond bushing. A short circuit between the meter base and the panel would create a fire if not correctly bonded. There has to be a low enough resistance to the bonded service neutral to open the fuses or other protective devices. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_bond_bushing_missing.png | file://x:/photopub/docs/0000000324/b32645b0-c2fd-4ac2-8c81-f0f1c7007709.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b6a1cf_c7a1_455a_a1b4_c66806a9adb4
ELIN-436287-2015 | EL-283238-2015 | 9/8/2015 9:03:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | The service nipple from the meter to the panel has no bond bushing. A short circuit between the meter base and the panel would create a fire if not correctly bonded. There has to be a low enough resistance to the bonded service neutral to open the fuses or other protective devices. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Meter_base_bushing.png | file://x:/photopub/docs/0000000324/2840cdc3-1d14-4627-bf70-08de9864a883.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b6a1cf_c7a1_455a_a1b4_c66806a9adb4
ELIN-431590-2015 | UW-281658-2015 | 8/27/2015 9:02:40 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMD 90 run on surface of wall and below 5'. This type of wire requires mechanical protection when installed in this manner as it only has a plastic jacket. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000319/64220d9e-5bb3-49ab-9023-5076aa4bf56e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a50d9f1_a0d6_49ae_9db9_35811364f2f0
ELIN-431590-2015 | UW-281658-2015 | 8/27/2015 9:02:40 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMD 90 run on surface of wall and below 5'. This type of wire requires mechanical protection when installed in this manner as it only has a plastic jacket. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000319/65f0c115-f7ae-4eb0-be5c-afeba91155d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a50d9f1_a0d6_49ae_9db9_35811364f2f0
ELIN-423288-2015 | EL-277042-2015 | 9/4/2015 7:33:45 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Three light junction boxes were not covered. This could result in accidental contact with a live conductor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Hall_light_junction_box.png | file://x:/photopub/docs/0000000323/2628f15e-c3d4-464e-b39e-f72a902f14f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71a17eb0_5f1d_4885_914d_c1f06ce1cb1e
ELIN-432576-2015 | EL-280656-2015 | 8/31/2015 3:03:29 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | No hazard. No FSR inspection. Work not ready for assessment. | 0 | No Created Hazard Identified | Work_not_ready.png | file://x:/photopub/docs/0000000320/57ba3d23-6aee-4acc-b641-f80ddb997a66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff4c4432_5846_4754_ac70_2eb709ddbf91
ELIN-314370-2015 | 5142952 | 8/31/2015 9:21:37 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Energized terminals must be contained within approved device boxes and protected by approved plates. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_conductors.png | file://x:/photopub/docs/0000000321/792e84fd-7e89-4d6d-a29e-a3e866ee0c0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d20d1ce_ccb1_4c6b_9d71_41c7927eded0
ELOP-226526-2014 | 5393753 | 8/31/2015 9:22:11 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Service conductors and raceways must be kept in safe condition. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Lucy_s_house.png | file://x:/photopub/docs/0000000321/42bc4423-e997-4a43-92a4-9220c1dd1de2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e82c4a5c_3fdd_4792_86cd_e9c7f7898c22
GAIN-435739-2015 | GA-282752-2015 | 9/8/2015 11:13:52 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Poly gas piping above grade is subject to damage which could cause a leak and possible fire | 3 | Non-compliant material/fittings installed | Poly_piping.png | file://x:/photopub/docs/0000000324/b86843a3-467b-46c0-a5ba-0c1495f3de57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__822a8dc2_b19b_4c38_a94e_a170f65ab197
ELIN-428326-2015 | EL-274800-2015 | 8/27/2015 3:19:58 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Gas line, cable/tel demarcation boxes not bonded, NMWU installed in walls, bonding to all outlet boxes not installed to manufactures specifications, LVT was going to be installed on concrete. Also, improper straps were used on TECK 90 sub feeder. | 3 | Continuity Bonding; method for equipment is not adequate. | NMWU_installed_in_walls.png | file://x:/photopub/docs/0000000319/04ad7995-9c17-48fb-8d31-6063d5628d0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__959f6cf4_a849_4907_a859_f7b095b5e968
ELIN-428327-2015 | EL-274800-2015 | 8/27/2015 3:20:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | No rough wire partials submitted for U/G raceways and improperly sized straps. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Improper_sized_straps__.png | file://x:/photopub/docs/0000000319/fe39d438-e87a-43d9-a59a-e93c95ecde0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f3825f4_cd01_4e38_a5c9_19c91d362506
ELIN-428326-2015 | EL-274800-2015 | 8/27/2015 3:19:58 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Gas line, cable/tel demarcation boxes not bonded, NMWU installed in walls, bonding to all outlet boxes not installed to manufactures specifications, LVT was going to be installed on concrete. Also, improper straps were used on TECK 90 sub feeder. | 3 | Continuity Bonding; method for equipment is not adequate. | Incorrect_method_of_installing_bond_wires.png | file://x:/photopub/docs/0000000319/0056776a-2524-4a94-b395-a17571c16ba1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__959f6cf4_a849_4907_a859_f7b095b5e968
ELIN-428326-2015 | EL-274800-2015 | 8/27/2015 3:19:58 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Gas line, cable/tel demarcation boxes not bonded, NMWU installed in walls, bonding to all outlet boxes not installed to manufactures specifications, LVT was going to be installed on concrete. Also, improper straps were used on TECK 90 sub feeder. | 3 | Continuity Bonding; method for equipment is not adequate. | No_bond_wire_for_demarcation__boxes_.png | file://x:/photopub/docs/0000000319/b964d31b-1db9-4e98-b96d-c47deee7687c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__959f6cf4_a849_4907_a859_f7b095b5e968
ELOP-434964-2015 | 5103152 | 6/30/2015 6:48:47 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL187 | General Construction Outdoor: inadequate clearances. | 3 | 3 | Vegetation other present inside transformer fence enclosures impacting on required clearances around equipment. This could result in a thermal event causing property damage. | 3 | General Construction Outdoor: inadequate clearances. | View01_kiln_transformer.png | file://x:/photopub/docs/0000000324/20406b28-cb14-4898-b42e-1abcf210e50f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a38a64fb_09dd_4efb_82e7_973ac45685bc
ELOP-434964-2015 | 5103152 | 6/30/2015 6:48:47 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL187 | General Construction Outdoor: inadequate clearances. | 3 | 3 | Vegetation other present inside transformer fence enclosures impacting on required clearances around equipment. This could result in a thermal event causing property damage. | 3 | General Construction Outdoor: inadequate clearances. | View02_south_side_transformer.png | file://x:/photopub/docs/0000000324/1c513f5d-39b7-44bc-9913-b35935e1ffc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a38a64fb_09dd_4efb_82e7_973ac45685bc
ELOP-434958-2015 | 4697749 | 6/30/2015 6:48:59 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords used in place of permanent wiring means. This use of regulated product in a manner it was not designed for could result in potential shock or fire hazard. | 4 | Conductors, Misuse of flexible cords. | Detail01_flexible_cords.png | file://x:/photopub/docs/0000000324/a2ac43d7-05eb-4930-9863-571ab7797fff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b68b23a_61c3_4094_add8_4f89f3d7ad18
ELIN-431544-2015 | EL-233501-2015 | 9/2/2015 5:55:30 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Neutral conductor has been connected to a lug not approved by the manufacturer in the subfeed to the suite panel. The lug provided is susceptible to loosening which could contribute to appliance failure or overheating of electrical equipment with potential for fire. | 3 | General Equipment is not approved for the specific use | Lug_not_approved.png | file://x:/photopub/docs/0000000322/f25a6397-069e-4a25-8b50-657acdb8cff8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0d581f3_69ee_49e0_9917_c1933ab375f8
ELIN-432200-2015 | EL-281516-2015 | 8/27/2015 10:41:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Main distribution was not installed in a weatherproof lockable enclosure. At time of assessment building had no roof installed on it. Main distribution is exposed to environmental elements and unauthorized personal. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_installed_without_enclosure.png | file://x:/photopub/docs/0000000320/8490a580-c097-495a-b49f-88cfc66644d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53a38909_f763_46aa_abc9_2a6c29d0917f
ELIN-434320-2015 | EL-279478-2015 | 9/2/2015 6:58:01 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Cable not buried. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000322/3ebca21e-e63d-4705-bb9e-7de6330a7f4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__519434c8_e862_4ee8_81e8_6f9d61c6a73b
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 5.png | file://x:/photopub/docs/0000000322/af1a3f8e-7c67-4c0b-985b-cb3b7c3302ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000322/7bee27cb-0a1b-482a-b5a0-1597a5064f2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 10.png | file://x:/photopub/docs/0000000322/64e39108-3c57-4738-aa7d-cd07a5c65fc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 8.png | file://x:/photopub/docs/0000000322/37e30d2e-564a-4a28-a7b6-df442902c66f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000322/b838d2f7-12fa-478a-ae2b-25653cb2a7d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 7.png | file://x:/photopub/docs/0000000322/5bfac894-eba5-460d-ac38-a4a959c66c46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 9.png | file://x:/photopub/docs/0000000322/eee68ddf-dd5d-4223-ade9-39fbbddf3db2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000322/40728452-4fe1-465c-9da4-fb7e3e811cda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000322/9b7175c7-818f-42c5-acc4-01d2f2166fb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-434852-2015 | UW-284182-2015 | 9/1/2015 4:16:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found service head and its service conductors were damaged and were not corrected and made safe and compliant before service was connected. The unsafe damaged overhead service equipment that was connected without authorization for connection is an electrical fire or shock hazard to persons and property while service is connected. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 6.png | file://x:/photopub/docs/0000000322/374d3d75-4d69-40c0-baff-98ed4962735a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be27496_48be_456a_bfc3_d681b30a1e61
ELIN-432684-2015 | EL-276062-2015 | 9/1/2015 5:04:46 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 3 | Weather proof covers are required to be installed on exterior receptacles and switches to prevent accidental contact with energized terminals on the devices, and to protect them from mechanical, and environment damage. This house has an exterior box with a 15 amp, 120 volt rated switch, and receptacle located near the front entrance. The devices are energized and do not have a cover plate on them. The circuit is ground fault circuit interrupter (GFCI) protected from a receptacle inside the house. The terminals on the devices are exposed to accidental contact which may create a shock hazard if the GFCI device fails. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exterior_switch_and_receptacle_with_no_cover_.png | file://x:/photopub/docs/0000000321/f8294506-4930-4c05-b4eb-df8a1cbaeae5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28891934_2247_4952_baf0_a24d38fbaec8
ELIN-434637-2015 | EL-273647-2015 | 9/1/2015 9:59:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | The service entrance conduit between the meter base and the main electrical panel was not adequately bonded to ground. In the event of a fault to the enclosure, there may not be sufficient electrical conductivity to return the fault to the source and trip the protective device. This could result in significant damage to the equipment and surroundings. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_grounding_bushing_installed_on_service_entrance_conduit_.png | file://x:/photopub/docs/0000000322/55cbfd5e-fd26-41a3-b934-ca2016b71212.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14ff216d_b44e_4d99_adda_401536f18046
ELIN-433373-2015 | EL-283165-2015 | 9/3/2015 3:23:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Service_conduit_.png | file://x:/photopub/docs/0000000322/6a604fb5-0063-4487-bd53-3e7b0fb884c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__874acae3_d40b_4915_90c8_1f6ace395f62
BPVOP-433680-2015 | 4393854 | 9/3/2015 1:21:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP054 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | 2 | 2 | Lack of lighting and housekeeping in both boiler rooms. | 2 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | PACIFIC_VALLEY_1.png | file://x:/photopub/docs/0000000322/973d99f2-5c4c-4f55-ae1f-2e8a670fc09d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcbadfa4_1aa8_48f3_a73b_3064ce318ef2
BPVOP-433680-2015 | 4393854 | 9/3/2015 1:21:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP054 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | 2 | 2 | Lack of lighting and housekeeping in both boiler rooms. | 2 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | PACIFIC_VALLEY_2.png | file://x:/photopub/docs/0000000322/e4023d21-44ac-4b3d-b932-3ac5eba0284d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcbadfa4_1aa8_48f3_a73b_3064ce318ef2
ELIN-434690-2015 | EL-186034-2014 | 9/4/2015 6:55:25 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet boxes with energized conductors need to be covered to prevent accidental contact with energized conductors. This installation has a 15 amp 120 volt garburator outlet box that has an open, energized, bare conductor exposed to contact in the cabinet under the kitchen sink. This is a shock and fire hazard should someone or something come into contact with the energized conductor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_energized_wiring_for_garburator_outlet.png | file://x:/photopub/docs/0000000323/8260bbc4-ca1e-45e9-be30-08fb514d0389.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__313eb533_db70_4660_a268_66b322159392
ELIN-436531-2015 | EL-282471-2015 | 9/4/2015 6:55:33 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | A 15 amp split, or 20 amp receptacle is required for the kitchen counter work surface of a peninsula. This is required to provide for use of portable kitchen appliances on the island. The required receptacle for this kitchen renovation installation has not provided a circuit or outlet box for this receptacle. Without a receptacle located on the peninsula occupants may use extension cords, or power bars as a permanent wiring method to provide power for portable appliances. This can create a shock and fire hazard if the cord or power bar gets damaged. Also receptacles that are not intended to supply power to portable appliances may become over loaded creating a fire hazard. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | New_kitchen_peninsula__counter_without_a_receptacle_roughed_in_.png | file://x:/photopub/docs/0000000323/74f4ca26-086e-4da8-9bf4-a07a5c6b394d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65c396f9_8db9_4232_a5aa_5cbaadf945ab
ELOP-414524-2015 | 5118258 | 7/29/2015 1:34:32 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL077 | Effective grounding, high voltage Fence is damaged. | 3 | 3 | Portions of transformer fence enclosure missing required attachment to station grounding electrode. This could present a shock hazard resulting in potential risk of personal injury or property damage due to energization of transformer fence enclosure under fault conditions. | 3 | Effective grounding, high voltage Fence is damaged. | Detail01_transformer_fence_enclosure_.png | file://x:/photopub/docs/0000000322/e9e229e7-c33c-46a8-9618-edb5e112e4dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4847925_8d97_43a2_ae08_222ecdc85cbd
ELOP-414537-2015 | 3722722 | 7/30/2015 1:35:01 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL077 | Effective grounding, high voltage Fence is damaged. | 3 | 3 | Portions of transformer fence enclosure missing required attachment to station grounding electrode. This could present a shock hazard resulting in potential risk of personal injury or property damage due to energization of transformer fence enclosure under fault conditions | 3 | Effective grounding, high voltage Fence is damaged. | View02_load_break_switch_.png | file://x:/photopub/docs/0000000322/0005f1a8-1d10-4312-9cbe-05b3c17d076f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2f626b0_ee49_480f_b1b7_ec8cfafbdb3e
ELOP-415138-2015 | 5172927 | 7/29/2015 1:35:40 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Outlet box cover missing, creating potential for mechanical damage to live conductors contained within. This could result in risk of a shock hazard causing personal injury or property damage. | 0 | No Created Hazard Identified | Detail01_outlet_box.png | file://x:/photopub/docs/0000000322/10e15948-e51e-4ec0-973f-db7f13678ccf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8585db80_4ad3_4efa_b77f_ada5d26dce6a
ELOP-414537-2015 | 3722722 | 7/30/2015 1:35:01 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL077 | Effective grounding, high voltage Fence is damaged. | 3 | 3 | Portions of transformer fence enclosure missing required attachment to station grounding electrode. This could present a shock hazard resulting in potential risk of personal injury or property damage due to energization of transformer fence enclosure under fault conditions | 3 | Effective grounding, high voltage Fence is damaged. | Detail01_transformer_fence_enclosure_grounding.png | file://x:/photopub/docs/0000000322/c7dcf14e-d2bc-475c-8de6-917624010be6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2f626b0_ee49_480f_b1b7_ec8cfafbdb3e
ELOP-414654-2015 | 3248 | 7/30/2015 1:34:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL077 | Effective grounding, high voltage Fence is damaged. | 3 | 3 | Portions of transformer fence enclosure missing required attachment to station grounding electrode. This could present a shock hazard resulting in potential risk of personal injury or property damage due to energization of transformer fence enclosure under fault conditions | 3 | Effective grounding, high voltage Fence is damaged. | View01_transformer_fence_enclosure_.png | file://x:/photopub/docs/0000000322/83c95ad1-ed4b-4109-a1e6-e9a613f5f9a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c204ae35_6717_44d3_9b94_bdb05824189c
ELOP-418304-2015 | 5172927 | 7/29/2015 1:35:33 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet box cover missing, creating potential for mechanical damage to live conductors contained within. This could result in risk of a shock hazard causing personal injury or property damage. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Detail01_outlet_box_branch_circuit.png | file://x:/photopub/docs/0000000322/aa3230b4-a2f1-436f-a66e-6320528e901c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c102fc47_9aa4_4cf7_a0a0_685883c506ac
BPVOP-434497-2015 | 2279230 | 9/3/2015 9:42:10 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During assessment of domestic hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 210*Fahrenheit, I found that safety relief valve exceeded 6yr interval for servicing or replacement(Regular testing and servicing ensures proper operation of safety relief valve). In the event of failure of controls to shut down boiler, boiler will be subjected to pressure beyond maximum allowable working pressure if safety relief valve fails to operate, resulting in permanent damage or rupture of boiler with likelihood of severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_WITHOUT_INSTALLATION_OR_SERVICING_DATE_TAG.png | file://x:/photopub/docs/0000000322/1a1f410f-25f6-4026-9b54-95765825ce76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7481edc9_883c_4451_aad6_080607dca829
ELIN-424846-2015 | 4097716 | 8/31/2015 10:17:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | Panel cover was not installed at time of inspection, with the solar power pack placed in front of panel with open wiring connections. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Open_panel.png | file://x:/photopub/docs/0000000321/d793f278-86b4-4937-890a-effd03938d77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b494e264_05e0_4b4d_8380_fec05bfc7e6a
ELIN-424846-2015 | 4097716 | 8/31/2015 10:17:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | Panel cover was not installed at time of inspection, with the solar power pack placed in front of panel with open wiring connections. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Panel_clearance.png | file://x:/photopub/docs/0000000321/a81afc34-da60-4d86-aa20-9cab29c82bc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b494e264_05e0_4b4d_8380_fec05bfc7e6a
ELIN-424846-2015 | 4097716 | 8/31/2015 10:17:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | Panel cover was not installed at time of inspection, with the solar power pack placed in front of panel with open wiring connections. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Splices.png | file://x:/photopub/docs/0000000321/d648b195-d906-4894-8dbd-69b8ce14b8af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b494e264_05e0_4b4d_8380_fec05bfc7e6a
ELIN-424846-2015 | 4097716 | 8/31/2015 10:17:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | Panel cover was not installed at time of inspection, with the solar power pack placed in front of panel with open wiring connections. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Not_terminated.png | file://x:/photopub/docs/0000000321/a71dcb66-2fe8-4adc-8940-a6d53758a5da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b494e264_05e0_4b4d_8380_fec05bfc7e6a
ELIN-383279-2015 | EL-243351-2015 | 7/14/2015 6:53:37 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Large, angular aggregate material present in trench with feeder conductors of 600V step up/step down system. This could lead to mechanical damage of energized conductors resulting in risk of personal injury or property damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View02_feeder.png | file://x:/photopub/docs/0000000321/97e9186c-498a-428a-b1e7-d99aa865703d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e66deaa9_d6fe_4ce0_b46e_877b35ba84a7
ELIN-383279-2015 | EL-243351-2015 | 7/14/2015 6:53:37 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Large, angular aggregate material present in trench with feeder conductors of 600V step up/step down system. This could lead to mechanical damage of energized conductors resulting in risk of personal injury or property damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_feeder.png | file://x:/photopub/docs/0000000321/4ba951e2-65ba-49ee-b16a-24e3451bcc4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e66deaa9_d6fe_4ce0_b46e_877b35ba84a7
ELIN-409920-2015 | EL-267319-2015 | 9/8/2015 3:19:33 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | 20 amp breaker protecting conductors rated at 15 amp protection by rule 14-104 | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Branch_circuit_protection.png | file://x:/photopub/docs/0000000323/0a368ed3-c300-4263-b663-616b895c3d76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1dea07c9_b015_4dad_a5d2_d10210abbc12
ELIN-437452-2015 | UW-285962-2015 | 9/8/2015 2:50:59 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles supplying temporary construction power are subject to stresses not normally associated with permanent wiring methods. As such, there are specific requirements for temporary construction power to ensue safe use and operation. During an inspection, energized residential style wiring and device boxes were found outdoors laying on a sidewalk to provide temporary power to several building sites. Note, there were children in the area. The wiring, device boxes, and covers were not approved for location. In addition, the receptacles were not GFCI protected. Should an individual come in contact with this wet device a shock could occur. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_Power_Satellite_Receptacles_.png | file://x:/photopub/docs/0000000323/228518e1-ff53-480c-a43d-d4464c042bc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91241cab_d992_43ea_a2d9_94f23e15e5e5
ELIN-432593-2015 | EL-282662-2015 | 8/31/2015 7:22:45 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Receptacles installed below 2 meters in a dwelling unit not tamper resistant. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Receptacles_not_tamper_resistant.png | file://x:/photopub/docs/0000000321/29172873-a772-431a-ad02-f5574b6a3c1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a7d2c5c_c3e9_43d6_9294_ca4c51328850
ELIN-437053-2015 | EL-236453-2015 | 9/8/2015 1:26:18 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 2 | Isolated work surfaces (islands) in kitchens require at least one receptacle. This is to eliminate the use of extension cords to power counter top appliances. During a final inspection, it was determined that the kitchen island did not have a receptacle. The lack of an receptacle would require an occupant to use an extension cord to power future appliances located on island. An extension cord would be a trip hazard in this location resulting in possible equipment damage. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_Island_.png | file://x:/photopub/docs/0000000323/3eb8b33b-d399-4317-8675-92e04e202b9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1dc65ea6_3d47_438f_a300_461dfdc3dc9f
ELIN-307495-2015 | EL-089447-2014 | 8/31/2015 2:18:43 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Unused openings in electrical cabinets and enclosures must be filled to prevent accidental contact. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_bottom.png | file://x:/photopub/docs/0000000322/5b6f31e6-a674-4b5b-ba2f-1ae7a9bd61c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b32b120d_6423_4745_9bd4_faa0c0ec7bd0
ELIN-317387-2015 | EL-157822-2014 | 8/31/2015 5:39:23 PM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Overhead service conductors must be removed and terminations made safe when buildings are disconnected. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Coiled_conductor.png | file://x:/photopub/docs/0000000321/16da3133-a88b-4245-ac26-220cc979b065.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de110462_3e71_4e62_a008_520f9d0fe38a
ELIN-435550-2015 | EL-283658-2015 | 9/8/2015 6:33:28 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Service conductors must be sized to accommodate the calculated load. This must be reviewed when additional loads such as electric furnaces are added to existing services. Failure to size service conductors appropriately may result in overheating or fire. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Added_60_amp_furnace_breaker.png | file://x:/photopub/docs/0000000324/b3897c92-e72a-45fe-8ed5-91b8fb89df40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__150bf527_d7b8_42da_b285_6f1688397b45
ELIN-435858-2015 | EL-284858-2015 | 9/8/2015 6:34:14 PM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | A service neutral may only be bonded to ground at one point in the service - normally at the first disconnecting means. Failure to follow this procedure may allow a parallel path of current to exist on the service neutral and service grounded conductor. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Distribution_at_trailer.png | file://x:/photopub/docs/0000000324/503132ef-6825-4262-a2a6-e765f6181da9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__967cd0ac_7cea_4227_9d41_43e1a1b52c52
ELIN-431356-2015 | EL-272783-2015 | 8/28/2015 5:56:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Ground electrode not buried. This is a hazard as voltage spikes caused from lightening could cause a fire or shock because it has no path to ground. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A.png | file://x:/photopub/docs/0000000320/745af495-b9ec-4f39-9d67-2c182c4ae1a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd4beea6_c97a_4399_9e61_40b8e348dbea
ELIN-431356-2015 | EL-272783-2015 | 8/28/2015 5:56:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Ground electrode not buried. This is a hazard as voltage spikes caused from lightening could cause a fire or shock because it has no path to ground. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | B.png | file://x:/photopub/docs/0000000320/64ac63ab-5af5-4f41-938b-e97ba689eea8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd4beea6_c97a_4399_9e61_40b8e348dbea
ELIN-419031-2015 | EL-265091-2015 | 9/3/2015 1:26:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Main service work is in complete. Main service mast and feeder conductors are not installed. Should the Supply authority connect, there would be nothing to connect to, thus leaving live exposed conductors at the top of the power pole. This could result in a line to line touch and short circuit condition. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Shop_service_with_no_mast.png | file://x:/photopub/docs/0000000322/85ba1acf-c8f4-44b3-b163-a3ad84c35c9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3603be6_7e63_45f4_8150_1643548ab969
ELIN-436045-2015 | EL-252159-2015 | 9/8/2015 6:49:43 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | No ground wire was installed to the identified conductor at the main distribution panel. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_ground_conductor_installed.png | file://x:/photopub/docs/0000000324/f49e4eac-1e20-4497-ba0f-4cca2c2a866d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79415964_dce4_4739_8291_f60391ee2519
ELIN-432535-2015 | EL-259479-2015 | 8/31/2015 4:04:15 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | One of the energized conductors | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Energized_conductors.png | file://x:/photopub/docs/0000000320/6c51d515-968f-4899-93bb-4f9eecbb8b3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f685fa1_4477_4e15_9b0e_08da8fe3582e
ELIN-410322-2015 | EL-141383-2014 | 9/2/2015 5:56:03 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Receptacles have not been provided on kitchen counter in 2 locations which could lead to use of extension cords by occupants | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Spacing_exceeded.png | file://x:/photopub/docs/0000000323/25704827-3270-41a3-acd1-be9428deeccd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7178e189_1258_4925_8c8e_eee9571c60eb
ELIN-410322-2015 | EL-141383-2014 | 9/2/2015 5:56:03 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Receptacles have not been provided on kitchen counter in 2 locations which could lead to use of extension cords by occupants | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 150_cm_to_first_receptacle_right_side_walloven.png | file://x:/photopub/docs/0000000323/b5e6de69-8728-4d6c-9bf0-73a1bae66f45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7178e189_1258_4925_8c8e_eee9571c60eb
ELIN-430839-2015 | EL-229601-2015 | 9/3/2015 9:04:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding system electrode cannot be verified as to minimum requirements. Potential safety issues present where electrode not to minimum requirements for safety of persons and property | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Electrode_not__electrode_not_visible_for_inspection.png | file://x:/photopub/docs/0000000323/a040a1e8-ed80-4124-9351-cd102139e95c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3e51813_fcdd_4d46_bf31_5fc06b8b1924
ELIN-435190-2015 | EL-074037-2013 | 9/3/2015 5:35:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 2 | Arc-fault protection is required for bedroom receptacle circuits. This is required to protect occupants by tripping circuit breakers where series and parallel arcing is caused by damaged electrical equipment or circuit conductors. This installation has 15 amp, 120 volt bedroom circuits energized that are not arc-fault protected. The bedrooms are not currently used for sleeping while construction is in progress so the hazard is minimal at this time. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_arc-fault_breakers_installed_for_basement_bedroom_circuits.png | file://x:/photopub/docs/0000000322/a3cbf231-9bd7-4a6f-93f9-2463e86fe527.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65c1c827_e8bb_4a0b_b74f_b41d1948b979
ELIN-434593-2015 | EL-258297-2015 | 9/3/2015 6:53:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Ground electrode was laying in an open trench. This is a shock and fire hazard. If the pole were to get hit by lightening there is not a low resistance path to ground. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A.png | file://x:/photopub/docs/0000000322/52ed345e-0c3f-4e00-9737-2bbf1a53d094.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__405a72b3_3d2c_4a78_8620_8851cf562f73
ELIN-433536-2015 | EL-278497-2015 | 9/3/2015 6:53:10 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Panel supplying a patient care area is bonded with aluminum. Code requires a copper bond wire. The bond wire installation is required to have a voltage drop of less than 0.3%. This is necessary for the proper operation of the medical instruments and the protection of patients in the event of an electrical fault on the system. | 0 | No Created Hazard Identified | B.png | file://x:/photopub/docs/0000000322/93e5a9d8-b7e5-43d5-aded-55933839d9e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cb7a25a_91fe_46cd_85ba_8580924d0e37
ELIN-430952-2015 | EL-279757-2015 | 8/28/2015 5:43:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 | System ground not terminated on supply side of main service. #6 AWG insulated Cu for Tel/Cable bond not insulated. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | No_neutral_ground.png | file://x:/photopub/docs/0000000320/f47b1de2-5c39-43e8-bec4-2e18e4cabf7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd96d1df_462b_42ae_811b_602fc6033eff
ELIN-430952-2015 | EL-279757-2015 | 8/28/2015 5:43:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 | System ground not terminated on supply side of main service. #6 AWG insulated Cu for Tel/Cable bond not insulated. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Cable_tel_bond_is_bare_Cu.png | file://x:/photopub/docs/0000000320/0e82fa14-0249-4563-bd56-7a5566252441.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd96d1df_462b_42ae_811b_602fc6033eff
ELIN-421660-2015 | EL-202931-2015 | 8/26/2015 9:39:00 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | Outdoor installed circuit breakers supplying indoor circuits may not function in cold weather. | 3 | Conductors Equipment is not approved for the specific use. | Exterior_mounted_service_panel.png | file://x:/photopub/docs/0000000320/e11fdff5-4f1b-4435-809b-b2e1e8cde272.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52bcb1e4_4a81_429a_8add_5f5c49250f4f
ELIN-425124-2015 | EL-243146-2015 | 8/28/2015 4:49:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Unprotected service conductors have no mechanical protection emerging from the ground on the pole to the meter base. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | No_mechanical_protection_on_service_conductors.png | file://x:/photopub/docs/0000000320/7cd6009a-e627-4c0a-8f07-9cca4b070009.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcecef91_4716_4705_8d65_6dd47a6f3918
ELIN-432844-2015 | EL-225403-2015 | 9/3/2015 6:23:48 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Service conductors must be mechanically protected when the exit the ground and must be cemented where minimum burial depths cannot be obtained. Consumer service conductors may not exceed 1.5 m in length under or within a building. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Open_service_conductors.png | file://x:/photopub/docs/0000000322/a6f67658-b7ea-4b5f-8edf-b36bb244fa4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54c6a25b_ee12_4aeb_a947_02bf28693c00
ELIN-420866-2015 | EL-225403-2015 | 9/3/2015 6:23:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Mechanical protection must be provided where cables emerge from the ground. Concrete encasement is required when minimum burial depths cannot be obtained and where consumer service conductor length inside and under buildings exceeds 1.5 m. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_conductors_under_building_exceed_maximum.png | file://x:/photopub/docs/0000000322/6a4f6757-6aa2-460f-93ea-25e95c894cba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a625d9ab_b393_4042_8888_63b6a62be800
ELIN-423594-2015 | 4854326 | 9/3/2015 6:23:32 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings in electrical equipment must be closed with approved fillers. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Filler_missing_receptacle_not_approved.png | file://x:/photopub/docs/0000000322/8100d9bb-446a-4826-b140-5cc02ffe8756.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b0dc406_3dc7_44c9_a94b_5330c11c085e
ELIN-420874-2015 | EL-231372-2015 | 9/3/2015 6:24:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | A single rigid mast is not acceptable for a 400 amp service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Single_rigid_mast.png | file://x:/photopub/docs/0000000322/6bb301eb-3c0a-40c8-b4a0-453dfb084ad6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edb6d6c1_d765_4b8f_8f58_6481c5a493af
ELIN-420866-2015 | EL-225403-2015 | 9/3/2015 6:23:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Mechanical protection must be provided where cables emerge from the ground. Concrete encasement is required when minimum burial depths cannot be obtained and where consumer service conductor length inside and under buildings exceeds 1.5 m. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_conductors_unprotected.png | file://x:/photopub/docs/0000000322/84986b9a-27ba-4879-b658-10d1b23f2d65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a625d9ab_b393_4042_8888_63b6a62be800
ELIN-431884-2015 | EL-197643-2015 | 8/28/2015 12:33:54 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized Electrical panel and cover missing. Panels are energized. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | North_lab_area.png | file://x:/photopub/docs/0000000320/c15b6a16-8bf3-4b36-b6ee-010c37463264.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2c25e_347e_4eeb_bdb9_876aea2f91ea
ELIN-431884-2015 | EL-197643-2015 | 8/28/2015 12:33:54 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized Electrical panel and cover missing. Panels are energized. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Electrical_room.png | file://x:/photopub/docs/0000000320/9e28373d-03af-4d12-ba65-da899368d3a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2c25e_347e_4eeb_bdb9_876aea2f91ea
ELIN-270563-2014 | EL-137483-2014 | 8/28/2015 11:44:57 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 240 volt conductors must be contained in approved raceways or enclosures. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_not_contained_in_raceway.png | file://x:/photopub/docs/0000000320/87dc415f-27ae-440d-818e-370779ef36f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15c2f365_e495_46fc_87b4_273ca4d123a9
ELOP-223113-2014 | EL-123876-2014 | 8/27/2015 11:44:07 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | Cable splice made midway to connector. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Cable_splice.png | file://x:/photopub/docs/0000000320/3eed4505-cb4d-4a69-9b6e-a4e1aae82207.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76e5a7f3_e060_4219_a883_3422b753b5a1
ELIN-174502-2014 | EL-112079-2014 | 8/27/2015 11:44:35 AM | ASSESS: EL: Final | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | Transformer capacity exceeded. | 3 | Protection and control Loading of distribution equipment exceeded. | To_meter.png | file://x:/photopub/docs/0000000320/eb6525fb-694c-47cd-96c8-221e60e3a234.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521d92ce_0a74_4a09_a452_6c122f0098b0
ELOP-278316-2014 | EL-171216-2014 | 8/28/2015 11:44:33 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Bonding bushings are required when metal sheathed cable is used in conjunction with nonmetallic boxes. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | No_bonding_bushings.png | file://x:/photopub/docs/0000000320/5106b267-17c9-498c-8662-a68785f4b43a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff630792_ce9f_4d7a_bc54_68ef482529e5
ELIN-432046-2015 | EL-274586-2015 | 8/27/2015 8:09:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Found overhead service conductors were installed too close to communication cables and overhead service conductors attachment device was too high and was not located properly as required to be between 150 to 300 mm below service head. Service conductors could contact communication lines and water could enter service head and cause electrical fir or shock hazards to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Overhead_lines_and_support_attachment_location_1.png | file://x:/photopub/docs/0000000320/35a0bc12-5410-4b77-bf46-b09f86e44b7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cd0c495_cc5d_4cef_a202_c07785ea467e
ELIN-432046-2015 | EL-274586-2015 | 8/27/2015 8:09:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Found overhead service conductors were installed too close to communication cables and overhead service conductors attachment device was too high and was not located properly as required to be between 150 to 300 mm below service head. Service conductors could contact communication lines and water could enter service head and cause electrical fir or shock hazards to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Overhead_lines_and_support_attachment_location_4.png | file://x:/photopub/docs/0000000320/19e39fe4-ff41-4649-bef5-ce0d7638bea3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cd0c495_cc5d_4cef_a202_c07785ea467e
ELIN-432046-2015 | EL-274586-2015 | 8/27/2015 8:09:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Found overhead service conductors were installed too close to communication cables and overhead service conductors attachment device was too high and was not located properly as required to be between 150 to 300 mm below service head. Service conductors could contact communication lines and water could enter service head and cause electrical fir or shock hazards to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Overhead_lines_and_support_attachment_location_3.png | file://x:/photopub/docs/0000000320/c4926ed5-f7ca-4efb-ab9b-925f816b73d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cd0c495_cc5d_4cef_a202_c07785ea467e
ELIN-432046-2015 | EL-274586-2015 | 8/27/2015 8:09:46 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Found overhead service conductors were installed too close to communication cables and overhead service conductors attachment device was too high and was not located properly as required to be between 150 to 300 mm below service head. Service conductors could contact communication lines and water could enter service head and cause electrical fir or shock hazards to people and property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Overhead_lines_and_support_attachment_location2.png | file://x:/photopub/docs/0000000320/2b3213a2-69fa-43be-a54f-7b067819f8f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cd0c495_cc5d_4cef_a202_c07785ea467e
ELIN-432887-2015 | EL-282968-2015 | 8/31/2015 11:03:08 AM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found empty breaker spaces without filler plates leaving possibility that people may come in contact with live conductors or bus bars once service is connected. Electrical equipment is required to be fully contained in approved enclosures with all knockouts or empty spaces closed off to prevent electrical fire or shock hazards to persons and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Filler_plates_or_covers_missing_on_empty_breaker_spaces.png | file://x:/photopub/docs/0000000321/f8a9e34c-e8ed-46a5-b0a6-acfb5385aeea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9dc6941_4e88_4680_851c_cc1a1e95f447
GAIN-435111-2015 | GA-244225-2015 | 9/3/2015 1:22:35 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Continuous movement of appliances will prematurely where out gas connector because restraint is too long | 2 | Physical protection of piping and tubing absent. | 22644_dewdney.png | file://x:/photopub/docs/0000000322/958d268c-b954-4e61-8aa2-14c2ba43b1fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d88febb4_2453_493f_85f1_e784ea40a6aa
GAIN-434946-2015 | GA-277109-2015 | 9/3/2015 1:22:35 PM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | The gas piping in the boiler room had numerous bushings installed that were only one pipe size change | 3 | Non-compliant material/fittings installed | 22644_240th_str_boiler_room.png | file://x:/photopub/docs/0000000322/8336e67b-327b-43ba-8f6b-8a740452932c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8ceee8c_eddf_49ea_a619_52b65efd677a
ELIN-432887-2015 | EL-282968-2015 | 8/31/2015 11:03:08 AM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found empty breaker spaces without filler plates leaving possibility that people may come in contact with live conductors or bus bars once service is connected. Electrical equipment is required to be fully contained in approved enclosures with all knockouts or empty spaces closed off to prevent electrical fire or shock hazards to persons and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Panel_cover_with_missing_filler_plates.png | file://x:/photopub/docs/0000000321/dc1a140b-12c6-46db-99bb-5f39bbd03bed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9dc6941_4e88_4680_851c_cc1a1e95f447
ELIN-425393-2015 | EL-029644-2013 | 8/28/2015 7:11:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 2 | Branch circuit wiring incomplete | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Branch_circuits_not_connected.png | file://x:/photopub/docs/0000000320/924927a8-33d4-4063-9ead-16a21db03e39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9874338e_c0a7_49a9_be0f_37dfc1ce7814
ELIN-442240-2015 | EL-276677-2015 | 9/16/2015 6:28:24 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240V electrical panels are not rated for outdoor environments. Panels should be installed in a weather proof lockable enclosure. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Sub_distribution_1.png | file://x:/photopub/docs/0000000327/1c6934aa-adc1-43da-b548-30389483e805.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbe7e279_ab98_4b74_9b9f_22df3e5985d2
GAIN-437763-2015 | GA-214659-2015 | 9/10/2015 8:46:29 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Boiler intake too close to regulator relief. Release of gas could be drawn into boiler intake causing an over fired condition and possible fire | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Boiler_termination1.png | file://x:/photopub/docs/0000000326/a6119b40-89bf-406e-808c-08aa332a8509.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f30258d2_3daf_4db4_9a29_0a7b074a2ad4
ELIN-434549-2015 | EL-253999-2015 | 9/9/2015 7:32:50 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The main system ground is not connected to the neutral busbar, additionally the bond between the panel enclosure and the neutral has been removed leaving it ungrounded. Overcurrent devices may not react predictably when grounding is not correctly installed | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Main_ground_not_connected_correctly__neutral_bar_isolated.png | file://x:/photopub/docs/0000000324/d5502f97-19ce-46e1-97f7-6e46eb0f371c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc972089_b7ab_4a69_86a5_63faed21d72c
ELIN-439658-2015 | EL-284117-2015 | 9/15/2015 6:12:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound |  |  |  |  | Unprotected Non Metalic Sheeth cables installed closer than 32 mm to stud surface may get injured with screws etc. causing fire. |  |  | NMD-1.png | file://x:/photopub/docs/0000000327/42f050e1-ddc9-4ac3-8a73-cd0b48fb6488.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7cdc932e_8858_499a_9793_09fca0cb24ed
ELIN-437444-2015 | EL-215192-2015 | 9/10/2015 9:16:25 AM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Appliance that requires dedicated branch circuit (microwave oven) being supplied from portion of split kitchen counter receptacle branch circuit. This could potentially result in a fire posing risk of personal injury and property damage. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Detail01_microwave_branch_circuit.png | file://x:/photopub/docs/0000000325/5d1eb9ec-2c21-4a9b-a52b-b733c2e4f718.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38636353_1c17_4330_ae10_110dc6218f1d
ELIN-437354-2015 | EL-258712-2015 | 9/9/2015 3:56:09 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | A junction box containing electrical conductors was found with no cover. This could expose a person to electrical shock if they should become energized. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | JB_cover_missing.png | file://x:/photopub/docs/0000000324/c01d02c8-02ef-4366-8d21-739e7b73dd79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ffaca10_e2c1_4b4d_a409_264746e51f84
ELIN-442123-2015 | EL-258071-2015 | 9/19/2015 4:34:49 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 |  | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | Nmd90_in_contact_with_metal_heating_duct.png | file://x:/photopub/docs/0000000328/36af5ad3-e631-4a83-9ffc-204d092d5d82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29f7adae_587e_4045_9eb3_58aab6dd53ca
ELIN-442119-2015 | EL-258071-2015 | 9/19/2015 4:34:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 2 | Expansion fittings are required to be installed where under ground conduits exit the under ground location to terminate into electrical equipment. This is required to allow for settlement of the ground to prevent damage to conduits, conductors, or electrical equipment that the conduit is terminated at. This installation has an underground service conduit that terminates into a meter base at a service pole without the required expansion fitting. Left uncorrected this is a potential fire or arc-flash hazard should the conduit settle, pull out of the metal meter base enclosure and damage conductor insulation. Contact between the damaged conductors and the metal enclosure could case an arc-fault condition. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Under_ground_raceway_no_expansion_joint_for_settling_at_pole.png | file://x:/photopub/docs/0000000328/77c1e9d5-aa27-44c0-b724-fef2b0b41908.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__828cb4e1_aa19_46d2_8340_e244eb189757
ELIN-441053-2015 | UW-289134-2015 | 9/14/2015 9:51:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 4 | NMWU installed below 5', buried 2" deep with no connector where it enters the box. This is a fire and a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000327/2c2c91ff-ffee-4f77-ac33-322d65c630f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af36f7d4_ae77_4749_b2b8_ff8e2a24b575
ELIN-441053-2015 | UW-289134-2015 | 9/14/2015 9:51:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 4 | NMWU installed below 5', buried 2" deep with no connector where it enters the box. This is a fire and a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | C.png | file://x:/photopub/docs/0000000327/13c395f2-ee50-4bcd-9489-d86228502e93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af36f7d4_ae77_4749_b2b8_ff8e2a24b575
ELIN-441053-2015 | UW-289134-2015 | 9/14/2015 9:51:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 4 | NMWU installed below 5', buried 2" deep with no connector where it enters the box. This is a fire and a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000327/e0ea92b8-80d2-4be4-8d31-22fb55da98eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af36f7d4_ae77_4749_b2b8_ff8e2a24b575
ELIN-436360-2015 | EL-151178-2014 | 9/10/2015 8:08:17 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | 120/240 volt 200 amp panel does not have panel cover installed. Live buss bars are exposed, and contacted could be made by persons. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_cover_not_installed.png | file://x:/photopub/docs/0000000326/79ebb1ff-7cfe-41d1-b14a-8125ecc30eb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de9aa7e6_ec9d_4ff4_b084_3e892d76b659
ELIN-439082-2015 | EL-249971-2015 | 9/11/2015 8:08:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Receptacle spacing along floor line exceeds 1.8m from receptacles. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Spacing_of_receptacles.png | file://x:/photopub/docs/0000000326/b6216a16-f705-4592-b769-eefb6e6180c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d40d43b7_3d3f_40ba_8884_64d39ce09044
ELIN-435121-2015 | EL-284400-2015 | 9/10/2015 4:22:45 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Take-1.png | file://x:/photopub/docs/0000000325/c82adcf2-5890-428b-b284-a596f1cb50a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2e52506_1e88_4f14_b06b_dbc8f3142bb2
ELIN-439653-2015 | EL-260526-2015 | 9/16/2015 11:15:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Some one has threaded potable water pipe and entered directly into threaded metal conduit entry. Pipe is not equivalent to rigid pipe required for mechanical protection and pipe has been damaged by the threading process | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Threaded_potable_water_pipe.png | file://x:/photopub/docs/0000000327/09a4f2b6-29e7-4862-b9e1-66a678181501.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a945cea_389e_4deb_93ed_81cdd707c840
ELIN-437146-2015 | EL-264796-2015 | 9/9/2015 10:38:11 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Electrical panels are required to have openings covered to prevent accidental contact with energized components, and to prevent equipment from damage. During an inspection, I discovered a 600 volt, 200amp panel board with three open breaker positions (missing panel fillers). This panel was located in a room which was accessible to unqualified individuals. The panel cover was not locked in the closed position and the energized buss was exposed. This presents a shock hazard should an individual come in contact with the energized buss. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Missing_Panel_Fillers_.png | file://x:/photopub/docs/0000000324/cff44146-193e-475e-8797-9bd1d87bc352.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dae0a8b_4148_4c7c_8a19_c502a3ecf710
ELIN-439720-2015 | EL-283817-2015 | 9/15/2015 7:17:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240V 200A type 1 rated panel installed in exterior environmental elements. Panel type is not rated to be installed outdoors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_install.png | file://x:/photopub/docs/0000000327/1c9c53d3-7f72-4eaa-a7d7-5878f40ed0bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59ccd1d8_0197_4900_8b90_83f99a2674fe
ELIN-433387-2015 | EL-273896-2015 | 9/17/2015 12:18:19 PM | ASSESS: EL: Final | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Panel board safe working space is obstructed by shed, panel is mounted to pole with 1/2 inch plywood | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Shed_within_450_mm_of_panel__plywood_used_to_mount_equipment.png | file://x:/photopub/docs/0000000327/dc52b14a-a410-4475-91a2-499c9b625028.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70ba3e81_8a48_43d6_9427_c6c2fb39a49b
ELIN-443607-2015 | EL-287563-2015 | 9/17/2015 12:18:20 PM | ASSESS: EL: Final | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | The Nova or Westinghouse Circuit breakers provided in the Seimens panel board are not approved for use in this particular panel board and do not fit the panel correctly. When circuit breakers have not been tested and approved in a panel board they may not be compatible with the panel. and can overheat damaging electrical equipment and conductors with a potential for fire in surrounding combustible materials. | 3 | Category 1 Equipment is not approved for the specific use or location. | Nova_and_ge_breakers_in_Seimens_panel.png | file://x:/photopub/docs/0000000327/f53917de-4623-4bdc-b7a1-b7e438ae802e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__422a6db8_4c29_45ea_a3d4_a6f2770fbcf4
ELIN-440086-2015 | EL-287556-2015 | 9/17/2015 12:18:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Improper installation of overhead service conductors. Heat shrink in place of weather head has been oriented straight up and could allow water to follow conductors into electrical equipment which would lead to corrosion and potential for loss of power to dwelling and damage to electrical equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_conductors_from_heat_shrink_straight_up.png | file://x:/photopub/docs/0000000327/de513e8e-bfba-4e55-a6f4-1773340545dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f2cd155_d306_4c64_a356_996ef3fe7fd2
ELIN-441845-2015 | UW-289509-2015 | 9/15/2015 3:15:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Water inside of panel | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_inside_panel.png | file://x:/photopub/docs/0000000326/c749ea1f-24f1-46c5-95d8-c9c6506c1311.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e38f433_f7e2_4bb2_a470_02dbb100db06
ELIN-441845-2015 | UW-289509-2015 | 9/15/2015 3:15:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Water inside of panel | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Outdoor_service.png | file://x:/photopub/docs/0000000326/06db6e80-a44a-427e-a802-86fec4493dd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e38f433_f7e2_4bb2_a470_02dbb100db06
ELIN-441845-2015 | UW-289509-2015 | 9/15/2015 3:15:06 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Water inside of panel | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_inside_panel_2.png | file://x:/photopub/docs/0000000326/2eeeab46-39e4-4096-84d9-a7f73fbf2e7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e38f433_f7e2_4bb2_a470_02dbb100db06
ELIN-429453-2015 | UW-280571-2015 | 9/10/2015 5:20:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | High voltage switch gear ground in missing | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Missing_ground.png | file://x:/photopub/docs/0000000325/5630cc75-b565-40a9-b656-0b4dfb37f32f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6477d87a_d4c8_4d42_9e15_465294238ee2
ELIN-429453-2015 | UW-280571-2015 | 9/10/2015 5:20:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | High voltage switch gear ground in missing | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 155_Skinner_HV_switchgear.png | file://x:/photopub/docs/0000000325/459a8502-0f6c-4083-9311-b38610df5268.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6477d87a_d4c8_4d42_9e15_465294238ee2
ELIN-429453-2015 | UW-280571-2015 | 9/10/2015 5:20:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | High voltage switch gear ground in missing | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Name_plate_not_ledgible2.png | file://x:/photopub/docs/0000000325/eff88c9d-e200-49d7-b7ce-f4df1129fecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6477d87a_d4c8_4d42_9e15_465294238ee2
ELIN-424978-2015 | EL-214871-2015 | 9/9/2015 8:43:03 AM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | A joint is required to allow movement of the service conduit due to settling or conduit lift. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | The_picture_is_looking_up_the_guard__over_the_service_conduit__there_is_no_settling_joint_installed_.png | file://x:/photopub/docs/0000000324/ab121ebe-8f25-4af9-9c7d-299d474e2ecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d79cdad_b562_4d32_aea0_f83ee000238d
ELIN-442240-2015 | EL-276677-2015 | 9/16/2015 6:28:24 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240V electrical panels are not rated for outdoor environments. Panels should be installed in a weather proof lockable enclosure. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Connection_of_identified_conductor_to_grounding_electrode.png | file://x:/photopub/docs/0000000327/850f8737-1b5b-43e8-af07-7ccf01f9019e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbe7e279_ab98_4b74_9b9f_22df3e5985d2
ELIN-431592-2015 | EL-261436-2015 | 9/16/2015 1:27:50 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Distribution equipment located inside a poultry barn where corrosive vapours are present. This leads to the deterioration of electrical equipment and failure of safety measures inherent to the equipment, resulting in risk of personal injury and property damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View_01_main_distribution.png | file://x:/photopub/docs/0000000327/724116bd-e6a6-4017-abfa-2567cdaca58f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3f5622c_1f10_4b4e_86dd_c65ccb6fbf2a
ELIN-427787-2015 | EL-279418-2015 | 9/3/2015 8:10:26 AM | ASSESS: EL: Final | png | #asFound | EL050 | Protection and control Loading of distribution equipment exceeded. | 3 | 3 | The breaker supplying the load is undersized which could lead to overheating of the service equipment resulting in thermal damage to the equipment or surrounding structure. | 3 | Protection and control Loading of distribution equipment exceeded. | Main_service_panel_with_sub_feed_breaker_in_HWT_space.png | file://x:/photopub/docs/0000000325/05fa9dc2-27af-4aa4-a16c-d7dfd6ca1f85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5e6d05b_2769_49fb_bbe6_8550ce9d7e50
GAIN-434366-2015 | GA-284014-2015 | 9/16/2015 2:10:47 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | Regulator relief too close to source of ignition. If regulator relieves, gas could be ignited by generator | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Generator.png | file://x:/photopub/docs/0000000328/80fea470-b9ad-45e2-866d-9d49ad1b60b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30758aa5_f247_4155_9f85_d864307f2539
ELOP-445410-2015 | 5363392 | 9/18/2015 11:36:35 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL008 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. | 4 | 4 | Electrical equipment enclosures are required to be closed and fitted properly to prevent contact with energized parts, damage to equipment from contact and and the environment, and to contain the effects of thermal heating should the equipment fail. Multiple pieces or electrical equipment at this mill site do not have the proper equipment enclosures or the enclosures are not properly affixed the equipment. One of the electric motor connection boxes is covered with a cedar shingle taped to the motor connection box. This has created a shock and fire hazard should the equipment fail without the proper covered in place. | 4 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. | Switch_door_for_hog_motor_disconnect_not_closed_properly.png | file://x:/photopub/docs/0000000329/c37340c0-5076-4171-af84-a3d7bd12a47e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb0ae682_e281_46a3_8821_967c9c770724
ELOP-445410-2015 | 5363392 | 9/18/2015 11:36:35 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL008 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. | 4 | 4 | Electrical equipment enclosures are required to be closed and fitted properly to prevent contact with energized parts, damage to equipment from contact and and the environment, and to contain the effects of thermal heating should the equipment fail. Multiple pieces or electrical equipment at this mill site do not have the proper equipment enclosures or the enclosures are not properly affixed the equipment. One of the electric motor connection boxes is covered with a cedar shingle taped to the motor connection box. This has created a shock and fire hazard should the equipment fail without the proper covered in place. | 4 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. | Profiler_enclosure_not_covered_properly.png | file://x:/photopub/docs/0000000329/bfb45cb6-0e57-456b-8138-c2fd08293079.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb0ae682_e281_46a3_8821_967c9c770724
ELOP-445410-2015 | 5363392 | 9/18/2015 11:36:35 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL008 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. | 4 | 4 | Electrical equipment enclosures are required to be closed and fitted properly to prevent contact with energized parts, damage to equipment from contact and and the environment, and to contain the effects of thermal heating should the equipment fail. Multiple pieces or electrical equipment at this mill site do not have the proper equipment enclosures or the enclosures are not properly affixed the equipment. One of the electric motor connection boxes is covered with a cedar shingle taped to the motor connection box. This has created a shock and fire hazard should the equipment fail without the proper covered in place. | 4 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. | Cedar_shingle_used_as_motor_connection_box.png | file://x:/photopub/docs/0000000329/af373aed-0696-4a91-9576-15fa79614a37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb0ae682_e281_46a3_8821_967c9c770724
ELIN-443675-2015 | EL-289989-2015 | 9/21/2015 12:51:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Neutral lug in meter base is not properly secured. This could lead to a potential shock hazard as the meter base is normally bonded by the neutral lug. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | B.png | file://x:/photopub/docs/0000000329/92748717-6026-4afd-8bfd-a23ab501b055.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f34f23_bfa4_4bcc_8b84_51143ba4b4b5
ELIN-443675-2015 | EL-289989-2015 | 9/21/2015 12:51:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Neutral lug in meter base is not properly secured. This could lead to a potential shock hazard as the meter base is normally bonded by the neutral lug. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | A.png | file://x:/photopub/docs/0000000329/a671076a-af8f-4336-893f-7d79f42e8426.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f34f23_bfa4_4bcc_8b84_51143ba4b4b5
BPVOP-440022-2015 | 3276012 | 9/12/2015 1:55:28 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP220 | 5.1.2 Validation: work performed - No records of original equipment specifications such as manufacturer's data report, drawings, calculations, material or code of construction | 3 | 3 | New Canadian Registration Number, Serial # and date of manufacture entered on 2015-09-12 due to a re-tubing of the boiler in 2013. New data plate and H-3 (Repair Data Sheet) were found loose on the boiler. No repair report is on record for the re-tubing repair. | 3 | 5.1.2 Validation: work performed - No records of original equipment specifications such as manufacturer's data report, drawings, calculations, material or code of construction | H-3_AND_DATA_PLATE.png | file://x:/photopub/docs/0000000325/12adb6ad-2cac-48ad-bb4d-740c2b466033.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4c713ea_7f7d_4f36_86ab_83834803b4c4
BPVIN-409167-2015 | UW-228979-2015 | 9/11/2015 11:30:00 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Found flow switch was not installed on boiler outlet piping for a boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit. If there is no flow switch installed on boiler outlet piping, there would be no way to detect minimum flow as required to prevent overheating of coil or fin-tube and consequently failure of coil or fin-tube may result. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | NON_COMPLIANT_TO_CSA_B52-2014_6_3_2_3.png | file://x:/photopub/docs/0000000325/78eab8b0-b85f-43a6-9359-42138ad98ae1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a4e67dc_a075_4c61_8e0f_a15ebdfca24a
ELIN-439058-2015 | EL-287035-2015 | 9/14/2015 3:39:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrician has not install the required grounding bushing at service location thus not completing the bonding path. This can result in human body to complete path to ground upon touching equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_bushing.png | file://x:/photopub/docs/0000000326/8150c87e-f7aa-495b-bcd2-a7bd1fe69870.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c6b7cd3_4836_41eb_9892_243e7bc81d4e
ELIN-439449-2015 | EL-274944-2015 | 9/14/2015 7:05:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240V 200A Main distribution panel not installed in a lockable enclosure to provide unqualified personal from access to it. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_installation.png | file://x:/photopub/docs/0000000326/f15d7ea8-5e53-4a43-a1be-b2968f7ff3ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71d4613f_287a_419b_a566_5410f47b2b5d
ELIN-440133-2015 | EL-243345-2015 | 9/14/2015 7:05:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240volt, 200amp Sub distribution panels are installed with no lockable and weather proof enclosure and can be accessed from unqualified persons and exterior weather elements. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Sub_distribution_panel_.png | file://x:/photopub/docs/0000000326/bb16ff68-bfb8-417c-a5dc-8c3662e4275f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9e054cb_bdab_48e3_9d8d_d482a19dc967
ELIN-436985-2015 | EL-285541-2015 | 9/10/2015 8:43:44 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | The location of cables is not acceptable. Contractor buried cable, not to minimum depth both ends of cable install, angles up at both ends of run, no allowance for settling could result in cable and conductor damage after installation or damage after construction when owner or others do gardening or interfere with soil in back yard of home. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Only_200_mm_deep__no_caution_tape.png | file://x:/photopub/docs/0000000325/f211b1ba-ffe1-43bf-98bd-14d5b6b06bf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__abaca49d_2f24_46aa_8292_b2b6e96c2b7c
ELIN-437673-2015 | EL-275573-2015 | 9/10/2015 8:43:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | 2/0 copper conductors on parallel provided to 400 amp non residential service to school portable. Mast installed was not sufficient for the weight of the utility service conductors and was rated for a maximum service of 200 amps. Structural failure of mast or building was possible with mast installation and overheating of conductors and equipment can occur when conductors are not sized correctly to the temperature rating of the equipment | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 2_0_conductors_175_amp_max_on_400_amp_oc.png | file://x:/photopub/docs/0000000325/524a7ff1-e797-40c1-94bb-087601911841.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c02cc70_ba25_4720_850b_1675786cf6af
ELIN-438884-2015 | UW-287197-2015 | 9/10/2015 8:43:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Owner has installed 4 circuits in building without a permit and this was confirmed in phone conversation with CONTRACTOR FSR at approximately 12:30 pm while questioning contractor as to extent of work done under installation permit authorized as all work complete at the same address. Unpermitted work is not to be connected to electrical supply due to unknown potential hazards in system that can lead to unpredictable failure of wiring system | 0 | No Created Hazard Identified | One_of_outlets_identified_as_installed_no_permit.png | file://x:/photopub/docs/0000000325/06e7958c-6b3b-4717-80db-76340b8c4932.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28d62c4f_4c7a_4d8b_9d4f_ea18b9e141c1
BPVOP-437502-2015 | 4454204 | 9/9/2015 11:40:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | Scale and deposits. | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scaling.png | file://x:/photopub/docs/0000000324/3588da38-c8e5-4792-837e-c05b04567497.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8352bdd_714c_442a_8320_e34ed58a57e0
BPVOP-437502-2015 | 4454204 | 9/9/2015 11:40:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | Scale and deposits. | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Mud_drum_scale_.png | file://x:/photopub/docs/0000000324/5389472b-590c-46ff-9cd5-2793bbffc34d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8352bdd_714c_442a_8320_e34ed58a57e0
BPVOP-437502-2015 | 4454204 | 9/9/2015 11:40:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 | Scale and deposits. | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Mud_drum_scale.png | file://x:/photopub/docs/0000000324/2f7fdb8f-9d2a-4c27-b94e-ab6455584d6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8352bdd_714c_442a_8320_e34ed58a57e0
ELIN-436973-2015 | EL-272449-2015 | 9/16/2015 5:54:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Dry location cable connectors used to terminate armoured cables where exposed to wet location, could allow water to enter meter enclosures or cables and cause damage to equipment or cables in the form of corrosion and could promote deterioration to point of power failure. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Dry_location_connectors_outdoor_cable_terminations.png | file://x:/photopub/docs/0000000327/b646e79b-fa78-4c63-8132-fefa8b583c67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f9c804f_16c8_4846_9827_519fcd46db0b
ELIN-443930-2015 | EL-290389-2015 | 9/18/2015 6:45:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Temp_post_not_supported_.png | file://x:/photopub/docs/0000000328/4f9080fe-7532-41c4-9be1-0d43fae4fb7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce721be5_c11b_4643_bf58_4fe76a701c40
ELIN-440364-2015 | EL-286391-2015 | 9/18/2015 6:50:53 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Non IC rated fixtures, in contact with combustible material. This is a fire hazard as these types of fixtures can become very hot, there needs to bea minimum 13mm gap between the fixture and combustible material on all sides, except for the point of attachment. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | A.png | file://x:/photopub/docs/0000000328/2531e4ae-c16e-492f-9a0e-58aafa572549.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aeea27b3_7d19_4a1c_9d5c_09c48a9c52ef
ELIN-434247-2015 | EL-283959-2015 | 9/16/2015 5:54:37 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 20 amp wire has been connected to a 30 amp circuit breaker feeding a 30 amp receptacle which could cause conductor overheating and damage when load imposed | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 12_copper_on_30_amp_breaker_identified_conductor_used_line_voltage.png | file://x:/photopub/docs/0000000327/5e1878af-683b-417d-9d23-0b257f07c66b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9701a2c1_3fc0_4801_bd02_80c9d77cce66
ELIN-438465-2015 | EL-262323-2015 | 9/18/2015 3:30:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exterior receptacles must be installed flush mounted to finished surfaces with approved covers. Failure to properly protect persons from accidental contact with live conductors or parts could result in a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_receptacle.png | file://x:/photopub/docs/0000000328/9c1f623f-90f0-4431-9e0e-92ebb6f6c3a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__396edb04_554a_43c1_924f_bcf96b6612d2
ELIN-443816-2015 | EL-290312-2015 | 9/17/2015 10:01:23 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Extension cord has been used in damp crawlspace to feed to permanent heat trace and is subject to corrosion or unpredictable failure | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_to_permanent_heat_trace_.png | file://x:/photopub/docs/0000000328/d177fb39-cac9-475f-a42a-6aa9082971a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82fcb897_3701_4fb0_bfdb_66f1b74d3654
ELIN-438165-2015 | EL-160739-2014 | 9/11/2015 9:08:08 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Single conductor cables spaced between 25% and 100% are required to be derated as per table 5D. This is necessary so cables are not subject heating effects from adjacent cables, which can result in overheating and may cause a fire and or arc flash. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Cables_spacing.png | file://x:/photopub/docs/0000000325/353916cb-c2d5-4864-bbaf-5c49abe2bdd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0a93d04_5cbe_4400_9803_78a6434a7d00
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 6.png | file://x:/photopub/docs/0000000328/c345135c-d7ae-42e1-88ad-3ef54d56a29c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 7.png | file://x:/photopub/docs/0000000328/4a1e0612-63b9-48cd-8aa1-589177c444f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5.png | file://x:/photopub/docs/0000000328/7936147c-d95d-4e8b-a27f-fda0c60d26e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000328/1f20e179-e631-4538-80b3-b949b8b210c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000328/647a05ee-b7ba-43db-b497-0268a33d8b67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000328/b3b6e8c0-32dc-4333-b68b-3f4c0df15787.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-436020-2015 | EL-274360-2015 | 9/15/2015 5:58:40 AM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found energized exposed bus bars and conductors on an energized main service panel board which had missing cover and electrical equipment was damaged and there were burn marks on the electrical equipment. Energized exposed bus bars and conductors in a panel with cover missing is a possible electrical fire or shock hazard to people and property because people could inadvertently come in contact with the energized conductors. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000328/c7472b9b-ee27-4df4-9774-94f202a5bd85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72bbe418_cfb7_4178_9300_f69cdf3e1526
ELIN-428104-2015 | EL-262201-2015 | 9/10/2015 6:41:32 AM | ASSESS: EL: Final | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 15A receptacles installed on a 30A over current device. 15A receptacle installed on a 40A over current device. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Over_current_device_exceeds_receptacle_rating.png | file://x:/photopub/docs/0000000325/90663fa9-0b98-44ac-8193-e101e8fea46e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__660d8654_3509_4a74_be16_d844532fa08e
ELIN-441126-2015 | EL-277852-2015 | 9/15/2015 7:46:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Contractor has installed temporary wiring on a 60 amp breaker. At the end of the cable which is exposed to mechanical damage, open splices not contained in a junction box have been done, with number 10 copper flexible cord x 3 cables connected to extension cables to construction heaters. Ineffective protection and open splices could contribute to property damage or injury to workers | 4 | Conductors, Misuse of flexible cords. | 60_amp_breaker_protecting_10_copper_conductors.png | file://x:/photopub/docs/0000000327/eb3ba0c1-b2ab-4f37-859d-73a866cdeb6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fcef13b_770c_4a6c_9aa2_ac5f09bd9729
ELIN-441126-2015 | EL-277852-2015 | 9/15/2015 7:46:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Contractor has installed temporary wiring on a 60 amp breaker. At the end of the cable which is exposed to mechanical damage, open splices not contained in a junction box have been done, with number 10 copper flexible cord x 3 cables connected to extension cables to construction heaters. Ineffective protection and open splices could contribute to property damage or injury to workers | 4 | Conductors, Misuse of flexible cords. | Open_splices_on_60_amp_overcurrent_device.png | file://x:/photopub/docs/0000000327/07e41dc3-464e-4701-b174-d5d0711c8441.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fcef13b_770c_4a6c_9aa2_ac5f09bd9729
ELIN-437456-2015 | EL-285186-2015 | 9/15/2015 7:46:42 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The main system ground bare number 6 is not protected from mechanical damage and could leave system ungrounded at residence if damaged either during or after construction. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Main_ground_outside_building_exposed_to_damage.png | file://x:/photopub/docs/0000000327/edd0d4fc-8c81-4f4f-b4e7-2f4f2990f895.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7905722_a52b_4c25_a359_70a8a36733e5
ELOP-190493-2014 | 5363392 | 9/15/2015 5:19:12 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Proper motor connection box covers are required to be in place to prevent contact with or damage to motor connections and to contain sparks, arcs, or thermally damaged equipment from causing fires. This installation has a cedar shingle used as a motor connection box cover. This has created a fire hazard due to the flammable shingle being in contact or close proximity to the energized conductors and connections. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Shingle_used_as_motor_connection_box_cover.png | file://x:/photopub/docs/0000000326/97a0baa6-f304-45ce-85a6-8b52012320a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5815655_efa9_421b_b80d_c8a77c018eaf
ELIN-438719-2015 | EL-265091-2015 | 9/10/2015 5:14:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL110 | Conductors Conductors are not suitably identified. | 3 | 4 | The supposed neutral conductor (black leg) is not identified at top of pole, but is connected to the neutral lug in the meter base. This could result in the Supply authority making connection to the wrong feeder conductor, which in turn would result in a short circuit situation upon energizing. | 3 | Conductors Conductors are not suitably identified. | Meterbase_connection_.png | file://x:/photopub/docs/0000000325/1c08e3fa-1be5-4c48-a87f-6162780581d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa797356_36a9_4cff_8ace_2777d12a9bff
ELIN-438719-2015 | EL-265091-2015 | 9/10/2015 5:14:19 PM | ASSESS: EL: Service Connection | png | #asFound | EL110 | Conductors Conductors are not suitably identified. | 3 | 4 | The supposed neutral conductor (black leg) is not identified at top of pole, but is connected to the neutral lug in the meter base. This could result in the Supply authority making connection to the wrong feeder conductor, which in turn would result in a short circuit situation upon energizing. | 3 | Conductors Conductors are not suitably identified. | Overhead_line_.png | file://x:/photopub/docs/0000000325/2457e59a-7fa6-46fa-b08e-e567d11c5ceb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa797356_36a9_4cff_8ace_2777d12a9bff
ELIN-441744-2015 | EL-282503-2015 | 9/16/2015 2:23:37 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Exposed wiring. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Exposed_switch_and_live_wires_.png | file://x:/photopub/docs/0000000327/1444bb26-4596-48df-9220-b5db55c25a96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8e167cf_8b08_4990_9115_5316df9b6b20
ELIN-441744-2015 | EL-282503-2015 | 9/16/2015 2:23:37 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Exposed wiring. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Exposed_pump_wiring_.png | file://x:/photopub/docs/0000000327/0f70fc00-d35d-4f19-bcb4-dfec2f4d0ccd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8e167cf_8b08_4990_9115_5316df9b6b20
ELIN-441744-2015 | EL-282503-2015 | 9/16/2015 2:23:37 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Exposed wiring. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Missing_cover_plates_.png | file://x:/photopub/docs/0000000327/1dd32c03-a014-4657-96b4-a7660d64843b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8e167cf_8b08_4990_9115_5316df9b6b20
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Areas_requiring_special_attention.png | file://x:/photopub/docs/0000000324/83807bbe-dd49-43fc-8bd2-11539712920c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-349667-2015 | 5691 | 9/9/2015 3:32:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Due to environmental conditions, wood dust observed due to the manufacture of wooden beams | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Locations_of__locations_of_class_to_class_two_division_one.png | file://x:/photopub/docs/0000000324/aae5b40c-828a-4e64-9570-4f0901d9e2b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f9794d0_1a83_40cd_8b53_e6a11db61d87
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Dust_accumulation_in_bag_house__clasified_class2_div1_location.png | file://x:/photopub/docs/0000000324/4e1edfbd-656c-4713-8c3a-af387649a6ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-349667-2015 | 5691 | 9/9/2015 3:32:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Due to environmental conditions, wood dust observed due to the manufacture of wooden beams | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Wood_dust_accumulating_on_cable_tray_and_electrical_cables.png | file://x:/photopub/docs/0000000324/0e333282-001c-4b63-a9ca-f8a4f257fbf1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f9794d0_1a83_40cd_8b53_e6a11db61d87
ELOP-349667-2015 | 5691 | 9/9/2015 3:32:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Due to environmental conditions, wood dust observed due to the manufacture of wooden beams | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Wood_dust_accumulatio_on_wax_tank.png | file://x:/photopub/docs/0000000324/1eebdd71-605e-47bc-a208-86f91451b258.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f9794d0_1a83_40cd_8b53_e6a11db61d87
ELOP-349667-2015 | 5691 | 9/9/2015 3:32:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Due to environmental conditions, wood dust observed due to the manufacture of wooden beams | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Accumulation_of_wood_dust_in_non_hazardous_classified_location.png | file://x:/photopub/docs/0000000324/120c029d-d1cf-43a3-ab98-8bba7815f5ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f9794d0_1a83_40cd_8b53_e6a11db61d87
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Dust_thicker_than_a_dime.png | file://x:/photopub/docs/0000000324/b6986d20-1927-4ddf-ac2c-51aaa07c2eb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Dust_accumulation_on_cales_and_cable_tray.png | file://x:/photopub/docs/0000000324/735e39f4-b6b2-4081-9fae-855a99e71aaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Dust_accumulation_on_i_beam_in_class2__div1_location.png | file://x:/photopub/docs/0000000324/9afb6070-262d-4b22-b4f0-3d392c989d83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Dust_hazard_locations.png | file://x:/photopub/docs/0000000324/a588e6c0-e7e6-4ea7-8c79-561d56701071.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-349667-2015 | 5691 | 9/9/2015 3:32:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Due to environmental conditions, wood dust observed due to the manufacture of wooden beams | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Would_dust__Wood_dust_thicker_than_the_size_of_a_dime.png | file://x:/photopub/docs/0000000324/72bdd3b9-932f-4ab9-b2fa-d61f59739cd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f9794d0_1a83_40cd_8b53_e6a11db61d87
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Weekly_dust__Weekly_dust_checklist_performed_by_management_and_ohs.png | file://x:/photopub/docs/0000000324/254ca10e-8dbb-4ba4-9cc7-6b2207e5dafe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELOP-349667-2015 | 5691 | 9/9/2015 3:32:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 | Due to environmental conditions, wood dust observed due to the manufacture of wooden beams | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Weekly_checklist.png | file://x:/photopub/docs/0000000324/f4cac98c-d7d7-4bf7-b63c-88bf91027299.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f9794d0_1a83_40cd_8b53_e6a11db61d87
ELOP-436526-2015 | 5691 | 9/9/2015 3:32:38 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Fipi_information_provided_to_permit_holder.png | file://x:/photopub/docs/0000000324/426acce1-3dc1-446a-aace-1f497d59e748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7f8a6c6_a5c3_4f88_91f3_6cc8e195d005
ELIN-437624-2015 | EL-282559-2015 | 9/9/2015 7:35:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas lines are required to be bonded. This mitigates damage from lightening strikes and also protects from shock should the gas line become accidentally energized. | 3 | Equipment Gas line, cast or water pipe has not been bonded | A.png | file://x:/photopub/docs/0000000324/c29d7454-f976-4ca3-abd9-480268a7899b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e044b419_3604_409b_9563_2973b7b4ef57
ELIN-442718-2015 | EL-215192-2015 | 9/16/2015 1:29:48 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Exterior receptacles installed within 2.5m of finished grade not GFCI protected. This results in the risk of personal injury or property damage. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Microwave_receptacle.png | file://x:/photopub/docs/0000000327/3ee6806d-48e5-4559-916f-d8ca778b07b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c5f4fd7_c5e5_413b_bb0f_ede3c5745ccb
ELIN-449131-2015 | EL-274360-2015 | 9/17/2015 11:41:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found electrical outlet boxes are not installed properly so that edges of outlet boxes are flush with finished walls/ceilings surfaces in a combustible type of building. When outlet boxes edges are not flush with finished walls/ceilings surfaces, then energized conductors inside outlet boxes could come in contact with combustible building structure and any possible electrical fault or short circuit would not be fully contained within an electrical box as required to prevent possible electrical fire or shock hazards to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 1.png | file://x:/photopub/docs/0000000331/609a5863-c7a1-43f5-b0b9-6e20cee195c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ab477ba_57a7_4df0_be43_29ff10546140
ELIN-449131-2015 | EL-274360-2015 | 9/17/2015 11:41:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found electrical outlet boxes are not installed properly so that edges of outlet boxes are flush with finished walls/ceilings surfaces in a combustible type of building. When outlet boxes edges are not flush with finished walls/ceilings surfaces, then energized conductors inside outlet boxes could come in contact with combustible building structure and any possible electrical fault or short circuit would not be fully contained within an electrical box as required to prevent possible electrical fire or shock hazards to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 3.png | file://x:/photopub/docs/0000000331/9b3ec2ff-b07e-4286-8094-078f51d7ad74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ab477ba_57a7_4df0_be43_29ff10546140
ELIN-449131-2015 | EL-274360-2015 | 9/17/2015 11:41:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found electrical outlet boxes are not installed properly so that edges of outlet boxes are flush with finished walls/ceilings surfaces in a combustible type of building. When outlet boxes edges are not flush with finished walls/ceilings surfaces, then energized conductors inside outlet boxes could come in contact with combustible building structure and any possible electrical fault or short circuit would not be fully contained within an electrical box as required to prevent possible electrical fire or shock hazards to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 2.png | file://x:/photopub/docs/0000000331/5cd50200-c11e-42b0-a5e5-e42117519363.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ab477ba_57a7_4df0_be43_29ff10546140
ELIN-445742-2015 | EL-286391-2015 | 9/22/2015 4:22:07 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Exposed consumer service conductor pose a hazard as the utility over current devices are over sized. This could cause a large arc flash if the cable were to become damaged. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000329/975074ac-1405-403e-a67f-6d2d34a3f7e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af52f4bf_1eed_4996_89c9_9b217bbc4743
ELIN-447399-2015 | EL-274360-2015 | 9/23/2015 7:43:23 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | Found outlet boxes installed in finished drywall of house which do not have the outlet boxes edges flush with finished wall surface as required by code for combustible buildings. When the outlet boxes edges are installed too deep into wall, the conductors (when energized) could short out or be exposed and could cause an electrical fault to combustible building structure and could cause an electrical fire or shock hazard to persons and property if covers become broken or covers are removed when painting etc. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | boxes_to_deep_in_wall_of_combustible_building_1.png | file://x:/photopub/docs/0000000330/0b327ad9-497b-4cb1-bd45-42d3cd82c685.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fda3df6_0e97_49f0_8d0a_109dd08ed8a4
ELIN-447399-2015 | EL-274360-2015 | 9/23/2015 7:43:23 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | Found outlet boxes installed in finished drywall of house which do not have the outlet boxes edges flush with finished wall surface as required by code for combustible buildings. When the outlet boxes edges are installed too deep into wall, the conductors (when energized) could short out or be exposed and could cause an electrical fault to combustible building structure and could cause an electrical fire or shock hazard to persons and property if covers become broken or covers are removed when painting etc. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | boxes_to_deep_in_wall_of_combustible_building_2.png | file://x:/photopub/docs/0000000330/1c10a9bc-1b33-4f4c-81b8-6274c2426cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fda3df6_0e97_49f0_8d0a_109dd08ed8a4
ELIN-438086-2015 | EL-284532-2015 | 9/17/2015 10:58:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Existing sub-panel on bottom floor was found to have filler cover plates missing in empty breaker spaces and has live exposed conductors or bus bars. Leaving empty breaker spaces on the front of an energized panel-board with energized conductors and bus bars exposed may result in accidental contact or electrical fault condition with energized conductors and which may result in possible electrical fire or shock hazard to persons and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 2.png | file://x:/photopub/docs/0000000331/23c8db01-2f65-4284-b04b-690011fbfc7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70ad78e6_b747_43ad_96af_75d3a923fb71
ELIN-438086-2015 | EL-284532-2015 | 9/17/2015 10:58:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Existing sub-panel on bottom floor was found to have filler cover plates missing in empty breaker spaces and has live exposed conductors or bus bars. Leaving empty breaker spaces on the front of an energized panel-board with energized conductors and bus bars exposed may result in accidental contact or electrical fault condition with energized conductors and which may result in possible electrical fire or shock hazard to persons and property. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 1.png | file://x:/photopub/docs/0000000331/adf4e0d9-65d6-4979-bee3-d15a7df63a53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70ad78e6_b747_43ad_96af_75d3a923fb71
ELIN-449410-2015 | EL-293366-2015 | 9/28/2015 8:39:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Raceway connections in damp locations must adequately prevent the entrance of moisture into electrical equipment. Water in the meter base is a shock hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | A.png | file://x:/photopub/docs/0000000332/89326a17-d852-4f7a-a24a-440d5ab9e325.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53005db1_d209_4ae2_934c_e2cf28a31fca
ELIN-449410-2015 | EL-293366-2015 | 9/28/2015 8:39:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | Raceway connections in damp locations must adequately prevent the entrance of moisture into electrical equipment. Water in the meter base is a shock hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | B.png | file://x:/photopub/docs/0000000332/bd5f05f0-7191-4df0-badd-43a3f280bc54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53005db1_d209_4ae2_934c_e2cf28a31fca
ELIN-445936-2015 | EL-212426-2015 | 9/23/2015 12:39:52 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exterior receptacle energized without cover plate installed. This is accessible to the general public and presents a serious risk of personal injury or property damage. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_receptacle.png | file://x:/photopub/docs/0000000330/cf6c0a3a-1571-4c6d-a644-a5862ec313b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac5ab25f_1df1_4d72_a952_99590efc86ec
ELIN-449200-2015 | EL-293112-2015 | 9/28/2015 3:43:11 PM | ASSESS: EL: Final | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Panel cover missing, owner says it is offsite to find space fillers and will be replaced. Power currently disconnected. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Suite_panel.png | file://x:/photopub/docs/0000000331/936774d7-eff4-42ad-ba5a-4ceb83051e80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__228b406a_a280_4e08_b461_eed23854a76f
ELIN-448858-2015 | EL-292520-2015 | 9/28/2015 4:42:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service conductor length inside buildings is limited by Directive to 1.5 m. Failure to limit this length exposes the installation to potential overheating of the cable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Cable_in_crawl.png | file://x:/photopub/docs/0000000331/058dd6a7-ed56-4e11-8f4f-fac2f61eade5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f86f88c_4046_4cb3_a86f_fd8539cfce86
ELIN-449698-2015 | EL-229113-2015 | 9/28/2015 5:29:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Service mast is not supported as per code. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Service-2.png | file://x:/photopub/docs/0000000331/a2f96fa4-24b8-40cc-8cff-80a8b1b818db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e97ce03_4116_4735_ad8c_a89e4292bc4a
ELIN-449698-2015 | EL-229113-2015 | 9/28/2015 5:29:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Service mast is not supported as per code. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Service-1.png | file://x:/photopub/docs/0000000331/72ecf091-adef-46a6-9bb5-8fcfa79571d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e97ce03_4116_4735_ad8c_a89e4292bc4a
ELIN-445506-2015 | EL-279637-2015 | 9/28/2015 6:26:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Ground terminated to meter base. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | View_rd_powell_river.png | file://x:/photopub/docs/0000000331/74f5138f-8242-473d-99c3-009c32a03eed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d45d20e2_2ff9_4db3_91d9_ff4627a21d1c
BPVOP-445759-2015 | 2252974 | 9/22/2015 1:37:14 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | Pressure relief devices are required in order to protect regulated equipment from over pressure. I found that there was no pressure relief device installed on a pressure vessel. Potential exists for an incident due to a possible overpressurization. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | No_pressure_relief_line.png | file://x:/photopub/docs/0000000329/40d894c3-8d78-47cf-a09d-23cc6f3b4fe4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ab4e8c8_46cc_40c6_a8c7_7bcf87e3d3cc
ELIN-431253-2015 | EL-279551-2015 | 9/29/2015 10:05:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Cables emerging from an outdoor construction service panel are not protected from weather entry into panel, and are also lacking strain relief at base of pole where cables feed above grade to sub panels. Cables are not protected from damage and cables were found driven over by vehicles and cable has been pulled from one dry location connector at temporary service panel. Damage to cables where driven over or where subject to undue strain and damage at temporary panel could result in injury to persons or damage to property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Car_has_driven_over_acwu_cables.png | file://x:/photopub/docs/0000000332/a031784d-ee88-4374-8a02-b7ba245cef39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b022ae57_d75f_473a_a157_3880bc581f41
ELIN-431253-2015 | EL-279551-2015 | 9/29/2015 10:05:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Cables emerging from an outdoor construction service panel are not protected from weather entry into panel, and are also lacking strain relief at base of pole where cables feed above grade to sub panels. Cables are not protected from damage and cables were found driven over by vehicles and cable has been pulled from one dry location connector at temporary service panel. Damage to cables where driven over or where subject to undue strain and damage at temporary panel could result in injury to persons or damage to property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Dry_location_connectors_no_support_at_pole_or_strapping__panel_bottom_damaged_by_strain.png | file://x:/photopub/docs/0000000332/5651a516-e7b9-4e24-bdeb-8ec08c733a32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b022ae57_d75f_473a_a157_3880bc581f41
ELIN-443988-2015 | EL-288209-2015 | 9/21/2015 9:14:40 AM | ASSESS: EL: Final | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Main system ground exposed to mechanical damage on exterior of wall where lawn is planted | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Main_ground_not_mech_protected_exterior_of_building__lawn_area.png | file://x:/photopub/docs/0000000329/36a2722f-2367-4152-ac9a-c8e8d09b421d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__358ba7c4_259d_4fb7_a1db_f311adfab65c
ELIN-447417-2015 | EL-292383-2015 | 9/23/2015 4:10:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service conductors are too close to the roof. This could pose a risk to roofers also the conductors might rub on the roof. Minimum 600mm clearance required from roof to bottom of drip loops. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | A.png | file://x:/photopub/docs/0000000330/357d6484-f607-4370-bbbb-ed5555f6b7ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89d6de58_1f1e_4fa1_b317_f75c42e0f94c
ELIN-446659-2015 | EL-291516-2015 | 9/23/2015 4:10:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 3 | Screw in style lag type Emily knob used as point of attachment. This is a known fire hazard. There have been instances where the lag type Emily knob is pulled out placing strain on service conductors caused a fire. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | B.png | file://x:/photopub/docs/0000000330/10a2075a-8548-4560-af68-1836bcf34ce0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2268f74_0580_4614_ab2f_5c4588f26eb1
ELIN-444921-2015 | EL-281341-2015 | 9/21/2015 8:51:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling in excess of 1.5m inside of building is not provided with suitable means of mechanical protection. This could lead to mechanical damage to consumer service cabling resulting in risk of personal injury or property damage due to thermal event. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_consumer_service_cabling.png | file://x:/photopub/docs/0000000330/ca50e2b5-abd0-4c4b-80e5-58c9a7662737.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55ac54e8_cc76_4b01_ba38_3b0f73aa371c
ELIN-440633-2015 | UW-288913-2015 | 9/25/2015 12:02:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Required covers for energized sub-distribution equipment accessible to general public are not in place. This presents a serious risk to personal safety due to contact with energized equipment or property damage due to thermal event. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | View01_sub-distribution.png | file://x:/photopub/docs/0000000330/b2ee91bb-ae85-4812-83fe-7cf62c3a7f41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9b02a0e_8c74_4a3f_a7c2_66c5baacef14
ELIN-440633-2015 | UW-288913-2015 | 9/25/2015 12:02:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Required covers for energized sub-distribution equipment accessible to general public are not in place. This presents a serious risk to personal safety due to contact with energized equipment or property damage due to thermal event. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Detail02_sub_distribution.png | file://x:/photopub/docs/0000000330/f5ad9c8e-0db8-41cf-8107-5ff2095285ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9b02a0e_8c74_4a3f_a7c2_66c5baacef14
ELIN-440633-2015 | UW-288913-2015 | 9/25/2015 12:02:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Required covers for energized sub-distribution equipment accessible to general public are not in place. This presents a serious risk to personal safety due to contact with energized equipment or property damage due to thermal event. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | View03_sub_distribution.png | file://x:/photopub/docs/0000000330/f121f606-8d0c-456c-a49e-11aa5f0fed30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9b02a0e_8c74_4a3f_a7c2_66c5baacef14
ELIN-447462-2015 | EL-258429-2015 | 9/24/2015 4:15:11 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Cables that could become energized must be terminated in approved junction boxes or locked out with approved devices. Failure to do so can result in a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | NMS_not_terminated.png | file://x:/photopub/docs/0000000330/73f5c26f-e747-4182-a58f-b6c86e7e8c2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e2aaae4_1d53_4516_8943_f23fdf4b30c7
ELIN-451282-2015 | EL-260816-2015 | 9/30/2015 8:58:28 AM | ASSESS: EL: Final | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | Only one circuit & receptacle provided for kitchen counter. | 3 | Protection and control Low voltage protection damaged or not provided. | Cooke_comox_.png | file://x:/photopub/docs/0000000333/930abcc1-a0f8-4416-8c68-33e833cccac1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14938ed1_2ad6_4849_bac3_c1bee90a7e94
ELIN-447316-2015 | EL-252551-2015 | 9/25/2015 8:31:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | This is rated as a level 2; no description required. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | View01_system_bonding.png | file://x:/photopub/docs/0000000331/4267c380-51b9-443e-9376-fbb02ef06578.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40ccc7a3_ed76_4f2a_8045_5f3c1b211f0f
ELIN-447124-2015 | EL-292099-2015 | 9/25/2015 8:31:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuitry not suitable for exposure to the effects of weather located in an unprotected exterior location. Water in and around branch circuitry and utilization devices accessible to general public presents a serious risk of personal injury due to electric shock. The is also a risk of property damage as a result of thermal event due to deterioration and increased oxidization of electrical connections and equipment. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Detail02_branch_circuit_.png | file://x:/photopub/docs/0000000331/5cd60909-ae48-443d-9780-58132a6fd318.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3316ad9_75bd_4781_ac7d_2d6ccd46acee
ELIN-447124-2015 | EL-292099-2015 | 9/25/2015 8:31:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuitry not suitable for exposure to the effects of weather located in an unprotected exterior location. Water in and around branch circuitry and utilization devices accessible to general public presents a serious risk of personal injury due to electric shock. The is also a risk of property damage as a result of thermal event due to deterioration and increased oxidization of electrical connections and equipment. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | View01_branch_circuits.png | file://x:/photopub/docs/0000000331/b2f51382-d474-4e4a-8e4c-d5ca2972c6ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3316ad9_75bd_4781_ac7d_2d6ccd46acee
ELIN-439594-2015 | EL-231370-2015 | 9/22/2015 8:34:56 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings in electrical enclosures must be suitably closed. Failure to do so could result in electric shock or the enclosure could be unable to contain a blast in the event of a fault resulting in an arc-flash condition. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Open_bus_in_sub.png | file://x:/photopub/docs/0000000329/bdaf0a83-a0f5-4b60-937b-b380b7b1613f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aad1a336_0a8d_40e1_9a53_b43cb0ac3abc
ELIN-419872-2015 | EL-250645-2015 | 9/22/2015 8:34:36 PM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | Armoured cables must be bonded where they enter nonmetallic enclosures. Failure to do so could result in the metallic sheath becoming energized in a fault situation. This could present a shock hazard. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | TECK_to_PVC_no_bond.png | file://x:/photopub/docs/0000000329/f9a6fd9c-8078-4be7-9191-2c531408d409.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75cfcfee_19dc_42bd_9fe8_5fad135da24b
ELIN-440487-2015 | 3850456 | 9/22/2015 8:34:15 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables exiting generators must be contained in an approved connector. Failure to do so could result in live conductors becoming exposed to the touch, possibly resulting in electric shock hazards. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Connection_at_genset.png | file://x:/photopub/docs/0000000329/c1c77ca4-7fa6-4fb6-9072-fac68242c59a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f17a7b_8520_4af1_9b70_a2e020b206f4
ELIN-436889-2015 | EL-215345-2015 | 9/22/2015 8:35:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Communication systems must be grounded. Failure to do so could result in poor system operation or failure during lightning strike or other fault resulting in equipment damage or shock. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | No_bond_at_demark.png | file://x:/photopub/docs/0000000329/d5e6aa29-8575-42a2-b42d-c83748a9d607.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce54d748_74e1_4a37_82a8_28f3d5e95aa9
ELOP-447152-2015 | EL-044430-2013 | 9/23/2015 5:40:57 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Unapproved electrical found on site in many various locations and the electrical equipment extension cords were bundled together and could cause overheating or possible electrical fire as found installed. When unapproved electrical equipment is installed and used the equipment has not been tested and proven and rated for the type and use the electrical equipment is specifically approved for and is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | Unapproved_electrical_equipment_ballasts_approval_evidence_not_found_2.png | file://x:/photopub/docs/0000000331/697f3619-d896-4162-9341-cb25f12ba33d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4d0a159_a903_4ff2_a468_4e448d948e3c
ELOP-447152-2015 | EL-044430-2013 | 9/23/2015 5:40:57 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Unapproved electrical found on site in many various locations and the electrical equipment extension cords were bundled together and could cause overheating or possible electrical fire as found installed. When unapproved electrical equipment is installed and used the equipment has not been tested and proven and rated for the type and use the electrical equipment is specifically approved for and is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | Unapproved_electrical_equipment_ballasts_approval_evidence_not_found_1.png | file://x:/photopub/docs/0000000331/0499a492-a3c1-41bf-8bce-d9a531b2d3dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4d0a159_a903_4ff2_a468_4e448d948e3c
ELIN-449246-2015 | EL-284441-2015 | 9/25/2015 5:05:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | Installation of trench work was by general contractor and FSR was trying to cover the installation. There is inadequate Product used for conduit covering as well there is no caution tape used within trench. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Trench_works_without_caution_tape.png | file://x:/photopub/docs/0000000331/1af1d522-bc00-4200-bc12-506b284b3a27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1893d79_4f05_48e0_b18a_77e20d70f272
ELIN-444611-2015 | EL-291053-2015 | 9/21/2015 7:14:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240 volt 125 amp main distribution panel installed to outdoor exterior elements. For panels installed for construction use, panels should be installed in weatherproof, lockable enclosures. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Installation_of_panel_exposed_to_outdoor_elements.png | file://x:/photopub/docs/0000000329/2147f5a3-25ad-4c2d-b15a-e3dabaaa6836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2594e38a_2652_448d_8d9f_0fcb39d68123
BPVOP-449689-2015 | 2263086 | 9/28/2015 3:16:29 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Vessel.png | file://x:/photopub/docs/0000000331/8542f7eb-8b2a-4b44-8c62-1d0b40f0ec0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f8355c0_a450_487f_979c_4f064454192d
BPVOP-449692-2015 | 2263097 | 9/28/2015 2:59:15 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP071 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | CUI.png | file://x:/photopub/docs/0000000331/22bd6e8f-9a4a-4daf-bdb7-c5f3ceafbd65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d54eea8e_81ca_4789_b518_d136ba4b69b7
BPVOP-449680-2015 | 2295436 | 9/28/2015 2:59:48 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP071 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | CUI_.png | file://x:/photopub/docs/0000000331/968688eb-853a-49e5-97ce-81622db3902a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c2b0a4d_7206_410e_b350_bec83d7706c9
BPVOP-418508-2015 | 2295418 | 9/28/2015 2:58:29 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | CUI_1.png | file://x:/photopub/docs/0000000331/534d7f37-ca1d-4e67-bc38-3bcd24a9cc7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eac47226_c46c_4191_af35_4ac562da0795
ELOP-191700-2014 | 5241350 | 9/25/2015 6:25:07 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables connected to motors or any electrical equipment must be installed in such away that they do not get damaged so that the integrity of the cables conductors does not become compromised. This installation has several 600V, 3 phase motors that have the cables that are connected to them pulled out of the connectors or the armour on the cable damaged. This can create a shock or fire hazard if the cable conductors insulation gets damaged and faults to the cable armour, of to other conductive material. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Damaged_cable_at_motor_connection.png | file://x:/photopub/docs/0000000331/2ec0a37b-d828-4b8d-9c09-2c16c49b1176.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__386977cd_96de_4a93_9f98_4fba22cb63ab
ELIN-448781-2015 | EL-286848-2015 | 9/30/2015 5:23:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Cables are required to be mechanically protected where they rise from underground installations to terminate at electrical equipment. This installation has two service cables that are not mechanically protected where they rise from the underground installation to terminate at the meter base on the service pole. This can create a shock or fire hazard of the cable becomes damaged and a fault occurs. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cables_at_pole_are_not_mechancially_protected_where_they_exit_the_underground_run_to_terminate_at_the_meter_base.png | file://x:/photopub/docs/0000000333/d47051cd-e17f-4efe-a502-f721d667d4ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11789b84_ca2f_47af_ba95_79e59352ae04
GAWP-450239-2015 | GA-282478-2015 | 9/28/2015 6:00:14 PM | ASSESS: GA Work In Progress | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was unapproved piping had been used on the venting system. This is a hazard because the piping was never designed to convey flue gasses which could lead to venting failure. | 3 | Unapproved venting material | furnace.png | file://x:/photopub/docs/0000000332/e66b2149-69a8-4313-8363-2a48ede3f697.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2839dc7e_2735_4ca4_bbd7_f6a827cf0e4e
GAWP-450239-2015 | GA-282478-2015 | 9/28/2015 6:00:14 PM | ASSESS: GA Work In Progress | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | The as found hazard was unapproved piping had been used on the venting system. This is a hazard because the piping was never designed to convey flue gasses which could lead to venting failure. | 3 | Unapproved venting material | potable_PVC.png | file://x:/photopub/docs/0000000332/23804f1a-1525-4206-a1ea-187fe32c3d67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2839dc7e_2735_4ca4_bbd7_f6a827cf0e4e
ELIN-444755-2015 | EL-229614-2015 | 9/25/2015 7:08:53 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15A- 120V branch circuit supplying a bedroom is not protected by a arc fault circuit interrupter. Bedroom circuits required to have arc fault circuit interrupter installed. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Breakers_installed_in_main_distrubution.png | file://x:/photopub/docs/0000000331/29078537-2317-4d45-bc48-47b89640d816.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f102a3c5_f1db_4806_9788_84accf3b90cd
ELIN-444492-2015 | EL-214858-2015 | 9/30/2015 2:45:01 PM | ASSESS: EL: Final | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Receptacle spacing is not to minimum requirements and could lead to use of extension cord wiring to permanent electrical equipment. Extension cord wiring to permanent electrical equipment is known to be a potential for shock or fire hazard. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Inadequate_number_receptacles_bedroom.png | file://x:/photopub/docs/0000000333/e4200532-efcc-47af-b4bf-7018f7e056b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79fa768a_a75b_4ce8_9bea_0fd4a3e3cdef
ELIN-448223-2015 | EL-293023-2015 | 9/25/2015 6:59:22 PM | ASSESS: EL: Service Connection | png | #asFound |  |  |  |  | The Main Panel is not protected from the weather, Suite disconnect switch is not service entrance rated and main ground is not terminated at the main neutral buss. If the Main panel is open to rain (wet) conditions, the energized panel could create a potential for a shock hazard to any persons in contact with the panel due to water being a conductor of electricity. |  |  | Electrical_equipmen__electrical_equipment_exposed_to_the_weather.png | file://x:/photopub/docs/0000000331/e6518cec-6f00-4081-8a8b-4e4bce0eda46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d506f7d0_5974_4c25_ac71_f0a5592d9c6e
ELIN-448223-2015 | EL-293023-2015 | 9/25/2015 6:59:22 PM | ASSESS: EL: Service Connection | png | #asFound |  |  |  |  | The Main Panel is not protected from the weather, Suite disconnect switch is not service entrance rated and main ground is not terminated at the main neutral buss. If the Main panel is open to rain (wet) conditions, the energized panel could create a potential for a shock hazard to any persons in contact with the panel due to water being a conductor of electricity. |  |  | Main_service__main_service_neutral_not_grounded.png | file://x:/photopub/docs/0000000331/3aa87876-e8d0-48ec-804d-bb1c37a2c339.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d506f7d0_5974_4c25_ac71_f0a5592d9c6e
ELIN-448223-2015 | EL-293023-2015 | 9/25/2015 6:59:22 PM | ASSESS: EL: Service Connection | png | #asFound |  |  |  |  | The Main Panel is not protected from the weather, Suite disconnect switch is not service entrance rated and main ground is not terminated at the main neutral buss. If the Main panel is open to rain (wet) conditions, the energized panel could create a potential for a shock hazard to any persons in contact with the panel due to water being a conductor of electricity. |  |  | Disconnect_switch_is__disconnect_switch_is_not_service_rated.png | file://x:/photopub/docs/0000000331/48736815-7a32-4b16-9e4f-1b5fc440fa87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d506f7d0_5974_4c25_ac71_f0a5592d9c6e
ELIN-448223-2015 | EL-293023-2015 | 9/25/2015 6:59:22 PM | ASSESS: EL: Service Connection | png | #asFound |  |  |  |  | The Main Panel is not protected from the weather, Suite disconnect switch is not service entrance rated and main ground is not terminated at the main neutral buss. If the Main panel is open to rain (wet) conditions, the energized panel could create a potential for a shock hazard to any persons in contact with the panel due to water being a conductor of electricity. |  |  | No_ground__no_ground_fault_protection.png | file://x:/photopub/docs/0000000331/444e7ebe-02a1-44a9-a0f3-416b7c882afc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d506f7d0_5974_4c25_ac71_f0a5592d9c6e
ELIN-448223-2015 | EL-293023-2015 | 9/25/2015 6:59:22 PM | ASSESS: EL: Service Connection | png | #asFound |  |  |  |  | The Main Panel is not protected from the weather, Suite disconnect switch is not service entrance rated and main ground is not terminated at the main neutral buss. If the Main panel is open to rain (wet) conditions, the energized panel could create a potential for a shock hazard to any persons in contact with the panel due to water being a conductor of electricity. |  |  | Main_panel__main_panel_bonding_screw_left_installed.png | file://x:/photopub/docs/0000000331/951d0e5f-2acd-4580-bae4-b9509570e325.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d506f7d0_5974_4c25_ac71_f0a5592d9c6e
ELIN-451053-2015 | EL-282747-2015 | 9/30/2015 2:09:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | Found a non-metallic sheathed cable (12/2 NMWU) installed directly buried and in contact with concrete floor. This cable could possibly become damaged from the concrete causing a possible electrical fire or shock hazard to people or property.” | 3 | Conductors Equipment is not approved for the specific use. | Nmwu_coming_up_throug_slab.png | file://x:/photopub/docs/0000000333/e6f35106-5cef-4465-bb8f-70bc9de97984.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8362f48d_cdff_4237_a467_640d5afed374
ELIN-423788-2015 | UW-277458-2015 | 9/24/2015 9:37:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A windstorm brought a tree down across a power line at an occupied RV park. The line is energized and only partially supported on a fence. A shock hazard exists. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Photo_4.png | file://x:/photopub/docs/0000000330/49e94953-9d1d-48a1-a86e-102438b2026f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30372108_28e9_4638_9a6e_f20fa4c59fe4
ELIN-423788-2015 | UW-277458-2015 | 9/24/2015 9:37:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A windstorm brought a tree down across a power line at an occupied RV park. The line is energized and only partially supported on a fence. A shock hazard exists. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Photo_2.png | file://x:/photopub/docs/0000000330/d530d77e-36c6-40b4-adf0-a4152d8be0e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30372108_28e9_4638_9a6e_f20fa4c59fe4
ELIN-423788-2015 | UW-277458-2015 | 9/24/2015 9:37:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A windstorm brought a tree down across a power line at an occupied RV park. The line is energized and only partially supported on a fence. A shock hazard exists. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Photo_1.png | file://x:/photopub/docs/0000000330/5dfc18c7-c6b5-4009-a6e8-0df19afcecb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30372108_28e9_4638_9a6e_f20fa4c59fe4
ELIN-423788-2015 | UW-277458-2015 | 9/24/2015 9:37:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A windstorm brought a tree down across a power line at an occupied RV park. The line is energized and only partially supported on a fence. A shock hazard exists. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Photo_5.png | file://x:/photopub/docs/0000000330/74cd3704-39d1-4a42-8c08-5067fe69c94c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30372108_28e9_4638_9a6e_f20fa4c59fe4
ELIN-439108-2015 | EL-186361-2014 | 9/30/2015 5:22:51 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Receptacles for dwelling units are required to be tamper resistant to prevent accidental contact with the energized openings receptacles. This installation has an exterior receptacle that is not tamper resistant. This is a potential shock hazard if left uncorrected. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non-tamper_resistant_exterior_receptacle.png | file://x:/photopub/docs/0000000333/6144fb49-05ea-4301-84bb-b88824c0c515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d628245_3e15_4d1d_af51_c305d7d005d7
ELIN-447616-2015 | EL-292229-2015 | 9/24/2015 2:18:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 2 | System grounding conductor is not adequately supported at point of entry into main distribution equipment that is accessible to general public. This could result in mechanical damage occurring to the point of attachment leading to failure of the system grounding. This poses a serious risk of personal injury (shock) and property damage (thermal event) due to failure of the system protection mechanisms to operate properly under fault conditions. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | View02_system_grounding_conductor.png | file://x:/photopub/docs/0000000330/1abf605c-a145-4ecb-a0d1-7b644e5a57ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__318f744e_37fa_4ed0_8e38_87f8e1f50509
ELIN-363454-2015 | EL-224780-2015 | 9/28/2015 1:30:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pic1.png | file://x:/photopub/docs/0000000331/cdd1a2e2-8df5-4398-b394-ba5e97693b2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f2e06d5_10aa_4486_ab18_d2a792684e89
ELIN-363454-2015 | EL-224780-2015 | 9/28/2015 1:30:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Tpic3.png | file://x:/photopub/docs/0000000331/c9a95ca2-df54-4283-832e-bc6abfaaa508.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f2e06d5_10aa_4486_ab18_d2a792684e89
ELIN-363454-2015 | EL-224780-2015 | 9/28/2015 1:30:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pic2.png | file://x:/photopub/docs/0000000331/ddcab596-f2f4-4b9f-9b48-7071687ea5c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f2e06d5_10aa_4486_ab18_d2a792684e89
ELIN-363454-2015 | EL-224780-2015 | 9/28/2015 1:30:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pic4.png | file://x:/photopub/docs/0000000331/52418eab-af31-4397-9361-d68b2bed16db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f2e06d5_10aa_4486_ab18_d2a792684e89
ELIN-447414-2015 | EL-261107-2015 | 9/22/2015 9:04:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Conductor termination lugs are marked with a minimum and maximum cable size. These are the cable sizes that the lug is approved for. Conductors larger or smaller terminated to these lugs may cause connection problems resulting in over heating of the terminations. This can cause damage to the conductor, conductor insulation, or the lugs and equipment the lugs are connected to. This installation has service conductors terminated at a panel and meter base that are larger than the manufacturer permits for the lug size. Left uncorrected there is a potential for the termination to fail and become overheated causing thermal damage to the electrical equipment and a possible fire hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Label_on_panel_cover_with_max_conductor_sizes.png | file://x:/photopub/docs/0000000329/816fde1e-f081-41ae-98c2-0eb8ab90f638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d8f2fb5_b87f_4d2a_89ca_f3ec40bff395
ELIN-447414-2015 | EL-261107-2015 | 9/22/2015 9:04:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Conductor termination lugs are marked with a minimum and maximum cable size. These are the cable sizes that the lug is approved for. Conductors larger or smaller terminated to these lugs may cause connection problems resulting in over heating of the terminations. This can cause damage to the conductor, conductor insulation, or the lugs and equipment the lugs are connected to. This installation has service conductors terminated at a panel and meter base that are larger than the manufacturer permits for the lug size. Left uncorrected there is a potential for the termination to fail and become overheated causing thermal damage to the electrical equipment and a possible fire hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Shop_panel_terminations_350_kcmil_conductors_in_250_kcmil_lugs.png | file://x:/photopub/docs/0000000329/0e19fde2-c086-4d25-9fcd-e3ed34e9c0e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d8f2fb5_b87f_4d2a_89ca_f3ec40bff395
ELIN-445717-2015 | EL-143688-2014 | 9/21/2015 6:58:32 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found bonding conductor connected to one box and that all sections of multiple ganged sectional outlet boxes are not bonded together as required for bonding all electrical equipment together. Incomplete or improper bonding does not provide a proper bonding path to ground for tripping over current devices during an electrical fault condition. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | sectional_boxes_are_not_bonded_together.png | file://x:/photopub/docs/0000000329/9119cf3f-d6af-427d-9ba2-b0d3e7e89e79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98d2b0be_36a3_411a_9e52_c83f75c29f81
ELIN-447870-2015 | EL-180392-2014 | 9/29/2015 9:39:49 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | NMD wiring is in contact with heating duct and this will cause temperatures that will exceed the insulation rating over a period of time causing the insulation of the NMD to fail. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD_Heating_duct.png | file://x:/photopub/docs/0000000332/88239b9c-d9a8-4842-b23f-34804c1265dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f56269a7_31c5_45c7_ae56_e4a7da5cfeb4
ELIN-448893-2015 | EL-290272-2015 | 9/25/2015 7:35:57 AM | ASSESS: EL: Final | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor does not connect directly to the neutral bar in the panel. It is connected in a way which requires several screws and straps to remain in place. Should the ground neutral connection be broken it could lead to a shock condition to anyone Who touched the metal of the panel as the ground fault would not clear to the transformer neutral. | 4 | Installation Grounding; conductor is not continuous. | Ground_to_panel_not_neutral.png | file://x:/photopub/docs/0000000331/5c1b43bd-add5-437e-aae4-071170d57743.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7be5d12d_11ac_44bf_a8f6_a82a7bc15ba9
ELIN-448893-2015 | EL-290272-2015 | 9/25/2015 7:35:57 AM | ASSESS: EL: Final | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor does not connect directly to the neutral bar in the panel. It is connected in a way which requires several screws and straps to remain in place. Should the ground neutral connection be broken it could lead to a shock condition to anyone Who touched the metal of the panel as the ground fault would not clear to the transformer neutral. | 4 | Installation Grounding; conductor is not continuous. | Overhead_connection.png | file://x:/photopub/docs/0000000331/f9a8b267-f5b4-451f-8800-e995cb8f2e5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7be5d12d_11ac_44bf_a8f6_a82a7bc15ba9
ELIN-448893-2015 | EL-290272-2015 | 9/25/2015 7:35:57 AM | ASSESS: EL: Final | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The ground conductor does not connect directly to the neutral bar in the panel. It is connected in a way which requires several screws and straps to remain in place. Should the ground neutral connection be broken it could lead to a shock condition to anyone Who touched the metal of the panel as the ground fault would not clear to the transformer neutral. | 4 | Installation Grounding; conductor is not continuous. | Minimal_antioxidant.png | file://x:/photopub/docs/0000000331/9f0bd4e3-17cd-449b-baff-305ab84abafd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7be5d12d_11ac_44bf_a8f6_a82a7bc15ba9
ELIN-454810-2015 | EL-285850-2015 | 10/6/2015 6:59:36 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | 120/240 bond wires in place but not terminated in pool panel. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bond_wire_not_terminated_to_pool_panel_.png | file://x:/photopub/docs/0000000336/dba1459b-4b58-4ff0-a9fb-e3ec77d0269c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__213761c5_7785_465d_b775_e5d6d0198d77
ELIN-453497-2015 | EL-295852-2015 | 10/8/2015 3:50:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | Non-metallic sheathed cable (NMD90 14/2) is in contact with metal heating duct. This could cause deteriation of the cable insulation, resulting in possible overheating and/or arc fault condition. This would have the possibility of becoming a fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 1.png | file://x:/photopub/docs/0000000337/9f5a9166-e76a-4928-af42-ae20951e2ce9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a947810_d5b6_47f1_865f_1cc41a0586b7
ELIN-443340-2015 | EL-287238-2015 | 10/1/2015 2:06:47 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | A triplex cable was hanging on the ground, and the electrical work was incomplete. The triplex cable has not been attached to structure or connected to sub-panel feeder cable. The work to be performed on the sub-panel and sub-distribution installation is also incomplete. Should this become energized it could lead to a dead short line to line or line to ground. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Triplex_uninstalled.png | file://x:/photopub/docs/0000000333/1cf17bb6-7cb8-42da-bf44-8fc2a2339323.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30c17023_e987_4875_ad49_8c795e0d2dea
ELIN-442756-2015 | EL-287238-2015 | 10/1/2015 2:07:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | The 100amp 120/240 volt secondary pole service assembly is incomplete. Power pole assembly is not completed. The Contractor has not built this system to comply with the requirements in the Overhead Lines Guidelines. This could result in property damage and possibly human injuries. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Power_pole_in_relation_to_hydro_pole.png | file://x:/photopub/docs/0000000333/d5116586-5a38-4001-92b7-fd2eaaa78931.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__327ff371_59a3_4f4f_b3c4_14916a3c35ee
ELIN-455930-2015 | EL-107720-2014 | 10/6/2015 5:29:05 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Electrical_room_location.png | file://x:/photopub/docs/0000000335/452a92ca-dcbb-4dcf-a8ba-3baec5ce348e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c23f5b1_9ac9_4311_bfcb_4f34af57bc88
ELIN-455930-2015 | EL-107720-2014 | 10/6/2015 5:29:05 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Front_of_the_building.png | file://x:/photopub/docs/0000000335/6b46168c-802b-4b32-b2b4-8845694b5532.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c23f5b1_9ac9_4311_bfcb_4f34af57bc88
ELIN-455930-2015 | EL-107720-2014 | 10/6/2015 5:29:05 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Meter_stack_.png | file://x:/photopub/docs/0000000335/7a257d43-795f-48e7-b015-a23f22b23129.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c23f5b1_9ac9_4311_bfcb_4f34af57bc88
ELIN-455933-2015 | EL-107716-2014 | 10/6/2015 5:29:57 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Jumpered_out_meters_with__10_awg_wire.png | file://x:/photopub/docs/0000000335/86d58ed6-de35-4556-adae-b2945060c495.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c2767e1_2156_4bb3_9a98_a80bb5288eb0
ELIN-455933-2015 | EL-107716-2014 | 10/6/2015 5:29:57 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Location_of_electrical_room.png | file://x:/photopub/docs/0000000335/4706fab0-c45b-48cf-a3fc-b14a60e4bfed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c2767e1_2156_4bb3_9a98_a80bb5288eb0
ELIN-455933-2015 | EL-107716-2014 | 10/6/2015 5:29:57 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Row_housing_complex_where_meters_were_jumpered_out.png | file://x:/photopub/docs/0000000335/7246b38e-a3ae-43c3-8d59-e0b0e9ad9023.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c2767e1_2156_4bb3_9a98_a80bb5288eb0
ELIN-455930-2015 | EL-107720-2014 | 10/6/2015 5:29:05 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | Meter bases are normally fitted with BC Hydro's meters. This installation has 10 occupied units of a new row housing complex that have the meters jumpered out in the meter stack with #10 awg copper conductors. The units have 100 amp, and 125 amp rated sub-services to provide power to the units. This has created a thermal hazard because the #10 awg conductors can not safely carry the rated current of the sub-services. Also the conductors are not approved for installation as jumpers in meter bases. This could cause thermal damage to the meter base and electrical equipment. The hazard was created by the electrical contractor. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Jumpered_meters.png | file://x:/photopub/docs/0000000335/afc2697a-3c41-4f5f-a36f-c4b46dfacb52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c23f5b1_9ac9_4311_bfcb_4f34af57bc88
GAIN-456700-2015 | GA-295191-2015 | 10/8/2015 1:57:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Incorrect_vent__incorrect_vent_termination.png | file://x:/photopub/docs/0000000337/ffd7bb64-33fd-4253-9d59-997e4a8c560f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52451acf_19a9_4d98_904b_cfdb4e6b5883
ELIN-449319-2015 | EL-247813-2015 | 10/1/2015 2:19:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | Proper identification not done on service neutral. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Neutral_idetification.png | file://x:/photopub/docs/0000000333/6d1e7ea7-a888-4205-adac-db981ac5f2bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d11cad9d_fc9a_4dd7_bc23_9696e1ff5463
GAIN-453909-2015 | GA-077053-2013 | 10/5/2015 11:30:11 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | Gas odor (although minor) should not be present and indicates a gas leak. Leak determined to originate from faulty gas pressure switch on boiler valve train. Pressure switches are part of safety components protecting boiler from unsafe operating condition or nuisance shutdowns. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | CA_duct.png | file://x:/photopub/docs/0000000335/e3482f29-3e23-458a-987f-dfb867ef0a02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47cd94fa_b423_48b8_8d05_de2cee7cf38e
GAIN-453909-2015 | GA-077053-2013 | 10/5/2015 11:30:11 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | Gas odor (although minor) should not be present and indicates a gas leak. Leak determined to originate from faulty gas pressure switch on boiler valve train. Pressure switches are part of safety components protecting boiler from unsafe operating condition or nuisance shutdowns. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Termination.png | file://x:/photopub/docs/0000000335/7db17bc8-6b8f-4a2f-8a33-444a643b2bfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47cd94fa_b423_48b8_8d05_de2cee7cf38e
ELIN-457976-2015 | UW-269301-2015 | 10/9/2015 3:01:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Open unused breaker spaces in circuit breaker panels are required to closed to prevent accidental contact with energized parts of the panel. This installation has multiple open breaker spaces in a warehouse location where employees could accidentally contact live parts of the panel. This is a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_with_open_breaker_spaces.png | file://x:/photopub/docs/0000000337/20710baa-91bc-449a-9659-741d62945cef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adc961f8_dfda_4d09_922b_b0f01ffb3cc4
ELIN-457976-2015 | UW-269301-2015 | 10/9/2015 3:01:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Open unused breaker spaces in circuit breaker panels are required to closed to prevent accidental contact with energized parts of the panel. This installation has multiple open breaker spaces in a warehouse location where employees could accidentally contact live parts of the panel. This is a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_breaker_spaces_in_load_center.png | file://x:/photopub/docs/0000000337/9981af67-f8db-4a4c-9426-85c5cade1e3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adc961f8_dfda_4d09_922b_b0f01ffb3cc4
ELIN-457976-2015 | UW-269301-2015 | 10/9/2015 3:01:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Open unused breaker spaces in circuit breaker panels are required to closed to prevent accidental contact with energized parts of the panel. This installation has multiple open breaker spaces in a warehouse location where employees could accidentally contact live parts of the panel. This is a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Sub-distribution_where_panel_with_open_breaker_spaces_is_located.png | file://x:/photopub/docs/0000000337/7eef0df0-920b-4159-876b-d77ee1223161.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adc961f8_dfda_4d09_922b_b0f01ffb3cc4
GAIN-447862-2015 | GA-292800-2015 | 10/7/2015 8:25:20 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | 1.Gas range installed to close to a combustible wall 2.When cooking open flame is too close to combustible wall and could cause a fire | 3 | Clearance to combustible not met | Range_to_close_to_wall.png | file://x:/photopub/docs/0000000336/26564eda-18fe-466c-ba8a-77a73e6f1284.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0f1649f_1045_4c6b_8ae1_8b47d5b6e378
ELIN-450243-2015 | EL-285243-2015 | 10/1/2015 3:01:26 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Receptacles are required to be properly rated for the branch circuits they are connected to. This is required to prevent the receptacles from getting thermally damaged if they are not properly protected by the branch circuit. This installation has a 15 amp, 120 volt rated receptacle installed on a 20 amp, 120 volt rated branch circuit. This is a potential fire hazard if the receptacle becomes overloaded and is thermally damaged. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 20A_breaker_and_branch_circuit_installed_for_a_15A_receptacle.png | file://x:/photopub/docs/0000000333/ad9e4ed5-5e0d-4328-877a-43882d2d71c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aaa8b844_2758_4d53_bea9_c1d84f416ed8
ELIN-450243-2015 | EL-285243-2015 | 10/1/2015 3:01:26 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Receptacles are required to be properly rated for the branch circuits they are connected to. This is required to prevent the receptacles from getting thermally damaged if they are not properly protected by the branch circuit. This installation has a 15 amp, 120 volt rated receptacle installed on a 20 amp, 120 volt rated branch circuit. This is a potential fire hazard if the receptacle becomes overloaded and is thermally damaged. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 15A_receptacle_installed_on_a_20A_circuit.png | file://x:/photopub/docs/0000000333/03bfc91b-0581-413c-a6f7-a63f3ee535b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aaa8b844_2758_4d53_bea9_c1d84f416ed8
ELIN-452612-2015 | EL-293203-2015 | 10/9/2015 7:05:31 AM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Sub panel neutral is re- bonded to enclosure allowing possible thermal overheating of cable bonding conductor | 3 | Continuity Bonding; method for equipment is not adequate. | Sub_panel_in_out_building.png | file://x:/photopub/docs/0000000338/89e938da-1082-4e3d-b38b-44abf7f7cb11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3412a80a_04b4_43f8_b682_1d90571e7618
ELIN-453524-2015 | EL-281574-2015 | 10/2/2015 11:33:49 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Non-metallic cables must be mechanically protected where they are exposed to injury and where they are less than 1.5 m above the floor. Failure to do so could result in the cable being damaged and possibly creating a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | NMS_is_too_low.png | file://x:/photopub/docs/0000000334/b4ba7a84-d964-4b5a-ac80-b634a730d892.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdabb8db_865c_4ef1_ae71_0cf63cbd98d8
ELIN-445600-2015 | EL-189484-2014 | 10/6/2015 8:54:59 AM | ASSESS: EL: Final | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Armor of cables has not been extended and attached to equipment leaving conductors exposed to sharp edges of armor of two cables enclosed in a plastic raceway. A potential arc fault to the armour of the cable will not cause overcurrent device to react due to isolation and could cause fire | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | No_neutral_id__boning_incomplete__exposed_sharp_edges_conductor_armor.png | file://x:/photopub/docs/0000000336/edeecbcf-57a3-468b-9c06-e6a902ca175e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d359096_0ae8_4348_b383_c8b8625b9ba6
ELIN-441862-2015 | EL-269288-2015 | 10/6/2015 8:54:22 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | A new mobile home with 100 amp breaker has been fed with a 60 amp overcurrent device from an existing 100 amp 120/240 volt sub service with existing loads. Conductors are not sized for their intended use. This creates a thermal risk. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Breaker_feeding_mobile_home_marked_welder_to_100_amp_init.png | file://x:/photopub/docs/0000000336/c0c9314c-696e-4d82-85b5-7f3d3f50b650.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c9337cf_60f1_43a4_94b2_49401b9e2d9a
BPVIN-453368-2015 | BPV-293339-2015 | 10/7/2015 11:26:54 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Flow_sensing_device_inlet.png | file://x:/photopub/docs/0000000336/5ded3aca-521e-43cc-8a76-2228777ff175.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98dc8b18_0b92_42f7_a251_a0e844a4c625
ELIN-455485-2015 | EL-294834-2015 | 10/7/2015 8:14:53 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | No bond bushing installed. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_bushing.png | file://x:/photopub/docs/0000000336/0c49eacc-7534-4575-9fea-11476c87e13b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98c596a0_7aa1_4580_948f_4898e85a9367
ELIN-452087-2015 | EL-295719-2015 | 10/5/2015 2:12:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | 100 amp service is not compression connected to 200 amp service. | 4 | Installation Grounding; conductor is not continuous. | Not_connected.png | file://x:/photopub/docs/0000000335/b90a2220-25cf-47c2-96c4-d7546cba54f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42c84f3c_b14c_4fda_9bee_ce9153733cb7
ELIN-451488-2015 | EL-294649-2015 | 10/2/2015 7:16:16 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 120/240V 50 amp Ground fault circuit interrupter for hot tub installed within 3 meters of hot tub. Shock risk present for persons in hot tub if they were to attempt to reset breaker. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Hot_tub_GFCI_installed_within_1m_of_hot_tub.png | file://x:/photopub/docs/0000000335/bb2cb856-f0e1-4ca7-be9f-e70c4d70c9ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e66591a_88d2_4dd0_bed3_9eefc6a61772
ELIN-453305-2015 | EL-284132-2015 | 10/2/2015 7:15:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | 120/240 volt, 100 amp overhead pole service. The service conductors attachment point installed above service head. This could cause the migration of water to run down service conductors and into the meter base resulting in equipment failure.. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_conductor_attachment.png | file://x:/photopub/docs/0000000335/2561a8aa-07c2-48a4-a1a1-1f60892e671b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6df5e4d_d235_4c76_ac47_ab1bc9adb930
BPVOP-451041-2015 | 4814039 | 10/5/2015 12:13:02 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | PRD_horizontal.png | file://x:/photopub/docs/0000000335/8a879712-ab14-4509-ba81-e28d0e7fdd0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__377fac8c_6dff_42eb_af9b_b98f14d65efc
ELIN-447371-2015 | EL-291844-2015 | 9/29/2015 7:21:00 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Service conduit (mast) for overhead consumer service on a single family dwelling is not adequately supported. The failure of the attachment system will lead to serious mechanical damage of the consumer service conductors resulting in property damage (thermal event). | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Detail01_service_conduit.png | file://x:/photopub/docs/0000000338/6605aff4-571c-4700-aeef-f9d55f8f0613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a85851_43d2_4eab_84f6_5a57984f60cc
ELIN-359745-2015 | EL-167896-2014 | 9/29/2015 7:20:24 AM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Energized main distribution equipment and devices for temporary construction service accessible to general public are inadequately mounted to service pole. Deterioration due to the effects of weather or mechanical damage (eg. vehicular impact) will result in energized equipment becoming separated from pole resulting in personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | View01_main_distribution.png | file://x:/photopub/docs/0000000338/52520bbb-e2f6-4fdb-8880-7fbf2d693947.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4947fd1b_7204_4091_b72e_9eca28c5fa3a
ELIN-450768-2015 | EL-294741-2015 | 10/1/2015 7:20:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Proper cover plates have not been installed on receptacles accessible to general public. This allows for contact with exposed, energized terminals resulting in personal injury (shock) or property damage (thermal event). | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | View01_receptacles.png | file://x:/photopub/docs/0000000338/b3b18670-e728-42fc-b9a9-9fea570f9dc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6504f01_4ad0_4fb7_a1fd_5734075ff7c0
ELIN-451873-2015 | EL-282661-2015 | 10/1/2015 6:56:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 20A- 120V receptacles missing cover plates. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Covers_missing_on_receptacles_.png | file://x:/photopub/docs/0000000334/f8edb7d6-c5e6-453d-90d4-1c07510980fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__097c618e_ded9_4b09_95cd_621d875d65b1
ELIN-443918-2015 | EL-276633-2015 | 9/28/2015 1:13:15 PM | ASSESS: EL: Final | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 20 amp- 208 volt over current device exceeds the ampacity of motor conductor feeder. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Over_current_devices_installed.png | file://x:/photopub/docs/0000000334/7c3aa140-5ba5-40ad-9995-0c0c33388cd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08680f49_145e_440b_8909_3bb2c890d1c8
AMIN-453790-2015 | AM-295570-2015 | 10/6/2015 11:38:47 AM | ASSESS: AM IN: Acceptance | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | The padding around the entrance/exit of the device does not extend sufficiently to provide adequate protection to a participant that may trip and fall as they exit the device. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Missing_section_of_padding_observers_right_side_.png | file://x:/photopub/docs/0000000335/5a447ccd-a999-46d1-9b4f-4ab834ce1038.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e57d585_d20a_4f6d_8f93_6cc45a6b700c
ELIN-454705-2015 | EL-294103-2015 | 10/6/2015 4:30:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Outside consumer service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_-1.png | file://x:/photopub/docs/0000000335/5dfeafc8-3fe6-4d79-bba5-6036bff89891.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4415032b_f9cb_47dd_93a6_6313a87ca10f
ELIN-454705-2015 | EL-294103-2015 | 10/6/2015 4:30:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Outside consumer service. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service-2.png | file://x:/photopub/docs/0000000335/bd113248-4ddc-4028-b2b2-4506a6862353.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4415032b_f9cb_47dd_93a6_6313a87ca10f
ELIN-431069-2015 | EL-269788-2015 | 10/2/2015 2:27:26 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | To avoid potential shock a power receptacle accessible from the ground of a dwelling or on a dock, is required to be "ground fault protected" | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Dock_receptacle.png | file://x:/photopub/docs/0000000335/8d91cea0-56ac-47d1-96b4-a8585b4ffdd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8c6c8f3_6aee_4cfe_9eb9_869d1993b5dc
ELIN-453847-2015 | EL-295356-2015 | 10/5/2015 7:15:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | The main neutral conductor was not clearly identified, this could pose a potential shock or equipment damage as it has not been marked differently from the main power supply conductors. There is the chance of mixing up these conductors if they are not identified. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Neutral.png | file://x:/photopub/docs/0000000335/93c8ad21-c421-4a5b-8df2-e4ad7c393354.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77284464_b924_46a0_890b_271fcd5cbee8
ELIN-451648-2015 | EL-159843-2014 | 10/5/2015 7:15:56 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Wrong type of fitting has been used, it is not designed to work with the flexible conduit used and will allow moisture and water through the connector resulting in possible equipment damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Dry_fittings.png | file://x:/photopub/docs/0000000335/12a4d355-5455-4db4-8ea4-eaf227453afb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34fd3d12_6132_4662_bb53_67b91acf4a4b
ELIN-456435-2015 | EL-291409-2015 | 10/8/2015 5:35:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be as short as practicable and not over 1.5 meters long inside of buildings before terminating at the service equipment over current device. This is required because the service cable may lack effective over current protection at BC Hydro's transformer. If the cable is damaged (ie: by a nail, screw, or other damage) this can create a fire hazard because there may not be over current devices that can effectively prevent a high heat thermal condition caused by a fault on the damaged cable. This installation has approximately 10 meters of service cable inside the building before it terminates at the main breaker in the service panel. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_over_1_5M_inside_house_before_terminating_at_service_equipment.png | file://x:/photopub/docs/0000000337/6425125f-8cfb-443e-b90b-6444d2d463ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60babea4_6896_4d0b_b368_98a498c82a04
ELIN-450413-2015 | EL-275349-2015 | 10/8/2015 5:36:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Underground conduits are required to be installed to the proper burial depth to prevent conduit and wiring from getting mechanically damaged after the installation. This installation has conduits that are installed just below the surface of the ground. They have also been installed without the use of a suitable marker (warning tape). This is a potential shock hazard should the conduits and conducts inside them be accidentally damaged during future excavation of the ground. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Exposed_conduit.png | file://x:/photopub/docs/0000000337/20f28b5e-668f-43d9-9ae8-ffeff4e28d96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__226bc865_fef1_4814_9906_ff8b996dc0af
ELIN-456252-2015 | EL-208862-2015 | 10/8/2015 7:50:45 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 120 volt 20 amp receptacle installed within 1.5 meters of sink not ground fault protected. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_not_GFCI_protected.png | file://x:/photopub/docs/0000000337/b9b94142-15e2-40fd-95d2-8410dbb550e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcf35031_01f1_47cf_a6f3_12f69b1e5c67
ELIN-450413-2015 | EL-275349-2015 | 10/8/2015 5:36:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Underground conduits are required to be installed to the proper burial depth to prevent conduit and wiring from getting mechanically damaged after the installation. This installation has conduits that are installed just below the surface of the ground. They have also been installed without the use of a suitable marker (warning tape). This is a potential shock hazard should the conduits and conducts inside them be accidentally damaged during future excavation of the ground. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Exposed_conduit_.png | file://x:/photopub/docs/0000000337/75edcb31-73a0-4d61-bf3a-6f2b980027f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__226bc865_fef1_4814_9906_ff8b996dc0af
ELIN-456435-2015 | EL-291409-2015 | 10/8/2015 5:35:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be as short as practicable and not over 1.5 meters long inside of buildings before terminating at the service equipment over current device. This is required because the service cable may lack effective over current protection at BC Hydro's transformer. If the cable is damaged (ie: by a nail, screw, or other damage) this can create a fire hazard because there may not be over current devices that can effectively prevent a high heat thermal condition caused by a fault on the damaged cable. This installation has approximately 10 meters of service cable inside the building before it terminates at the main breaker in the service panel. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_over_1_5M_inside_wall.png | file://x:/photopub/docs/0000000337/0fff26b1-6142-4129-9f4f-2a88d3d73899.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60babea4_6896_4d0b_b368_98a498c82a04
ELIN-451589-2015 | EL-159850-2014 | 10/7/2015 9:12:04 PM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Energized wire is not protected by accidentally contact which could result in a shock or possible fatality. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_wire.png | file://x:/photopub/docs/0000000336/1c9ea3e3-5e1a-4990-b6d1-5fa943fd70a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18fd5c3a_2cfd_405b_8d95_4634cc4112ba
ELIN-456435-2015 | EL-291409-2015 | 10/8/2015 5:35:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service cables are required to be as short as practicable and not over 1.5 meters long inside of buildings before terminating at the service equipment over current device. This is required because the service cable may lack effective over current protection at BC Hydro's transformer. If the cable is damaged (ie: by a nail, screw, or other damage) this can create a fire hazard because there may not be over current devices that can effectively prevent a high heat thermal condition caused by a fault on the damaged cable. This installation has approximately 10 meters of service cable inside the building before it terminates at the main breaker in the service panel. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_over_1_5M_inside_house.png | file://x:/photopub/docs/0000000337/9702e929-5b16-4be7-a04c-fcabc7fefb7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60babea4_6896_4d0b_b368_98a498c82a04
ELIN-455931-2015 | EL-288918-2015 | 10/7/2015 7:01:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 120 volt 15A switches installed within 1 meter of bath tub. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Outlet_installed_within_1m_of_bath_tub.png | file://x:/photopub/docs/0000000336/8f00a9a2-b96e-4ca1-9411-f7894a670bce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7f6f541_3e7b_4ca6_95ba_ace4bcfafb84
EDMA-451987-2015 | ED-169076-2014 | 10/2/2015 5:42:18 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED042 | Wear/Defects resulting in the brake to stop car/step unsafely. Likely to progress additional means of deceleration are functional. Risk Reg ED-02 | 3 | 3 | Speed governors which detect elevator over speed conditions are allowed to be located inside the hoistway. When a governor is located inside the hoistway it needs to be reset from outside the hoistway, because it is hazardous for an elevator mechanic to step on top of a car that went into over speed to reset the governor. During an acceptance test the governor was tripped by over-speeding the elevator (rated speed is 150 fpm , the governor could not be remotely reset. The elevator contractor had ordered the incorrect hand of the governor and changed the handing in the field but reassembled it incorrectly. The rated speed of the elevator is 150 fpm. This 5 stop basement traction elevator is located in an office building (Richmond School Board). | 3 | Wear/Defects resulting in the brake to stop car/step unsafely. Likely to progress additional means of deceleration are functional. Risk Reg ED-02 | Governor.png | file://x:/photopub/docs/0000000334/10342354-8499-4837-97c5-360c609978dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d8d8973_2116_4380_bc15_39e556742d8b
BPVOP-454149-2015 | 2292319 | 10/8/2015 5:30:51 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP107 | 3.0.1 Safeties will not function - Pressure Relief Device No drain hole provided in the device body or discharge piping to allow drainage of liquids | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device No drain hole provided in the device body or discharge piping to allow drainage of liquids | PRD_inlet.png | file://x:/photopub/docs/0000000337/b086a4be-3b71-4db7-999d-41bbcabca52f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69d2a096_27e1_4f75_9f75_79eb80f06e7e
BPVOP-454143-2015 | 2253876 | 10/8/2015 5:30:49 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety relief valves must be regularly serviced, tested or replaced. I found no records of service or replacement for safety valves. Potential exists for an incident due to a safety valve not functioning due to inadequate servicing or testing. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Old_PRD.png | file://x:/photopub/docs/0000000337/4aa63ca1-0fea-4285-bb10-6e35c6bc3d75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff3af903_adb2_47ac_95b0_7d7bf86b45e8
BPVOP-454147-2015 | 2292320 | 10/8/2015 5:30:36 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | PRD_on_inlet.png | file://x:/photopub/docs/0000000337/d03ad05b-748c-4b1a-9f3c-92d8291617e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94a67a24_aa87_4589_927c_5d25515b233f
BPVIN-454141-2015 | UW-296560-2015 | 10/2/2015 5:57:59 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Required_capacity.png | file://x:/photopub/docs/0000000334/9553b74e-fc1b-4d99-acb3-a0a244ff0c23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98af4879_779a_4194_8e84_2818a79a1de0
BPVOP-453815-2015 | 2302544 | 10/2/2015 5:57:20 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Required_capacity__.png | file://x:/photopub/docs/0000000334/74418b30-87e9-498e-a7a2-f66cd3b2a83b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18ce934a_4941_4dca_85af_a08d5a09f83d
BPVOP-453815-2015 | 2302544 | 10/2/2015 5:57:20 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Valve.png | file://x:/photopub/docs/0000000334/52370e89-9785-455d-813e-3c3246810425.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18ce934a_4941_4dca_85af_a08d5a09f83d
BPVIN-454141-2015 | UW-296560-2015 | 10/2/2015 5:57:59 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | PRD_.png | file://x:/photopub/docs/0000000334/48648644-b4a5-4c17-a048-302a1cecfb0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98af4879_779a_4194_8e84_2818a79a1de0
ELIN-450222-2015 | EL-275911-2015 | 10/5/2015 7:01:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Sharing a microwave circuit with a gas range and under counter lighting can result in an overloaded circuit, leaving all 3 electrical systems without power. Damage to conductors can occur or nuisance tripping of circuit breaker feeding microwave can also be a result. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Microwave_fed_through_to_counter_lighting_and_gas_range_outlet_.png | file://x:/photopub/docs/0000000335/c8b1ecf6-fafc-4aa7-aad0-61f24dbc778b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c220b007_575d_41a2_a5a3_cbeef03a112d
ELIN-451474-2015 | EL-218131-2015 | 10/5/2015 7:01:57 AM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | 120/240 volt 60 amp overcurrent device installed to protect 3 conductor 6 aluminum branch circuit wiring only rated for 50 amps. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Overcurrent_device_installed_in_main_distribution__.png | file://x:/photopub/docs/0000000335/2357c50f-2b69-468c-a3d9-76c1ec507c76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e47498d9_0f71_4a02_b902_685a5947beee
ELIN-446103-2015 | EL-153208-2014 | 10/14/2015 12:54:51 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Garage_sub-panel_.png | file://x:/photopub/docs/0000000339/57d38768-a86c-4fce-a138-bccc2c1811c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da08fb97_2ea7_40c5_b373_da1da45d53a4
ELIN-446103-2015 | EL-153208-2014 | 10/14/2015 12:54:51 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Main_panel_cover.png | file://x:/photopub/docs/0000000339/e07dad40-9a2f-4ab5-acf5-e265c8a246b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da08fb97_2ea7_40c5_b373_da1da45d53a4
GAIN-459712-2015 | GA-299655-2015 | 10/19/2015 11:00:29 AM | ASSESS: GA: Rough-In | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 1 | Compromised wall thickness of black iron pipe caused by poor threading process. | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | Damaged_pipe_2.png | file://x:/photopub/docs/0000000340/9189f708-82e4-4673-af4c-42c65dade3e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa558a56_8758_4342_951f_a1161166c5b3
GAIN-459712-2015 | GA-299655-2015 | 10/19/2015 11:00:29 AM | ASSESS: GA: Rough-In | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 1 | Compromised wall thickness of black iron pipe caused by poor threading process. | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | Damaged_pipe_1.png | file://x:/photopub/docs/0000000340/fbf65a84-e28c-42b6-8044-da8a348ee36c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa558a56_8758_4342_951f_a1161166c5b3
BPVOP-453289-2015 | 2284501 | 10/20/2015 1:02:54 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_1997.png | file://x:/photopub/docs/0000000341/f881ab63-120f-453c-a422-acbf56f76fd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5956bd0b_d441_4041_ad97_e92a17d59ba5
BPVOP-453287-2015 | 2284492 | 10/20/2015 1:02:21 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found that safety valve was overdue for replacement for 4 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_prd.png | file://x:/photopub/docs/0000000341/95480f7f-1b52-4251-a32a-76556b9c426f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__487a03ac_4d1b_41eb_886f_1f7281cc7a8f
ELIN-460860-2015 | EL-247575-2015 | 10/16/2015 7:47:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | General purpose convenience outlets120 volt, 15 amp, receptacles have spacing greater the 12 feet. This could lead to the use of extension cords, which is a thermal hazard. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacle_are_not_properly_spaced.png | file://x:/photopub/docs/0000000340/17e69ed4-fb25-40c2-ad69-e3f90b3e08d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a83ca0f_b9ff_40d6_88f3_70cfb78eafa4
GAIN-462635-2015 | GA-241866-2015 | 10/20/2015 11:42:42 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Concentric vent too close to grade(must be 24") Supply air may become blocked by snow | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | vent_term.png | file://x:/photopub/docs/0000000342/58886ddd-b9e4-4f59-ab7f-e2296cece73f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92934df7_7cf8_4062_bd55_c32ec06f138d
GAIN-462635-2015 | GA-241866-2015 | 10/20/2015 11:42:42 AM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Concentric vent too close to grade(must be 24") Supply air may become blocked by snow | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_Gasket.png | file://x:/photopub/docs/0000000342/5be30d95-5d6a-4a85-b909-fd4436e6fd0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92934df7_7cf8_4062_bd55_c32ec06f138d
BPVOP-240173-2014 | 2258678 | 10/13/2015 1:04:23 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 3 | The discharge from safety relief valves are required to exhaust the contents of the working fluid to an area that will protect the public and environment. During Inspection I found that the termination point from the safety relief valve was within 25ft of an air intake system. This could lead to the contents being discharged and pulled into the facility's HVAC system. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | safety_valve_discharge_rooftop.png | file://x:/photopub/docs/0000000339/6da0d4fa-3193-4fd3-8448-e29b7708d1b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__681566E4_1DE8_4D6E_95D7_CDD547814A63
BPVOP-240173-2014 | 2258678 | 10/13/2015 1:04:23 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 3 | The discharge from safety relief valves are required to exhaust the contents of the working fluid to an area that will protect the public and environment. During Inspection I found that the termination point from the safety relief valve was within 25ft of an air intake system. This could lead to the contents being discharged and pulled into the facility's HVAC system. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | safety_valve_discahrge_with_air_intake_system.png | file://x:/photopub/docs/0000000339/cf030d58-68f5-4ed3-b7d0-77902cc52a29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__681566E4_1DE8_4D6E_95D7_CDD547814A63
ELIN-459365-2015 | EL-298587-2015 | 10/14/2015 5:07:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 2 | A dry-type connector is being used outdoors. This could result in cable deterioration. | 3 | Category 1 Equipment is not approved for the specific use or location. | Dry_type_connector_below_meterbase.png | file://x:/photopub/docs/0000000339/4b3bcc81-7520-4647-a83e-f015ee1a4de3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59856b60_0c3b_4096_8121_549d7fbe0710
GAIN-447130-2015 | GA-179694-2014 | 10/13/2015 11:21:58 AM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | tank_piping.png | file://x:/photopub/docs/0000000339/01eb0344-fa23-4cc4-82b4-7a2db9c6f7e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75d190bc_1720_4c02_a34c_9d6cdd9c1f78
ELIN-463891-2015 | EL-296959-2015 | 10/22/2015 5:59:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding electrode has not yet been installed by the electrical contractor | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_ground__no_ground_electrode_installed_at_the_time_of_assessment.png | file://x:/photopub/docs/0000000342/d80efc36-adfb-4984-b170-b8578f7a4dfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23c7a70d_1c00_46f2_8215_0a12c32522ab
BPVIN-463343-2015 | UW-302509-2015 | 10/20/2015 12:00:00 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP205 | 5.1.0 In service proc/process - Housekeeping of boiler or machinery rooms not compliant personal safety, and general safety etc. | 2 | 2 | Clearances are to be sufficient enough to have access to equipment for maintenance and inspection. I found that the clearances for the expansion tank to be minimal. this may lead to tripping hazards and/or difficulty for maintenance projects. | 2 | 5.1.0 In service proc/process - Housekeeping of boiler or machinery rooms not compliant personal safety, and general safety etc. | expansion_tank_clearances.png | file://x:/photopub/docs/0000000341/8c408a06-ad24-4cf3-a5b3-d259e88ed657.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f38631e8_e7dc_4de8_ad5a_d3de222c20a2
ELIN-458862-2015 | EL-299045-2015 | 10/14/2015 5:15:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | 120/240 volt 200 amp service conductors exceed 1.5 meters within a building. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_conductors_exceed_maximum_length.png | file://x:/photopub/docs/0000000339/14485a69-0d20-46c6-84bd-c69342cf7088.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c7fa0e1_64ef_4ae2_8104_4727619ddd37
ELIN-458925-2015 | EL-300015-2015 | 10/14/2015 5:16:00 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240 volt 200 amp main distribution panel has no lockable cover. Unauthorized personal can access panel during construction. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | No_lockable_cover_on_main_distrubution.png | file://x:/photopub/docs/0000000339/536f14c6-9c9b-4d0b-8df2-936d61c386a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238ea609_0313_483b_964c_2b92bec1f69d
ELIN-450660-2015 | EL-292318-2015 | 10/19/2015 6:59:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 3 | Non weather proof fasteners, no bracket on bottom of meter base | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 1836_preston.png | file://x:/photopub/docs/0000000341/d2906843-05fb-40ef-92f1-ad3d68ca0f99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e0427cc_4c6d_4fc0_9094_86ccb7dd44d6
ELIN-459335-2015 | EL-290403-2015 | 10/19/2015 6:58:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | Panel not protected from the rain. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 8390_fannybay.png | file://x:/photopub/docs/0000000341/179f8abd-5e11-407e-bd74-8b337d55769b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4627150a_40c3_4975_9c58_de4d0dbebf37
ELIN-458299-2015 | EL-290463-2015 | 10/13/2015 5:48:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Terminations of stranded aluminum conductors are required to be made using a joint compound to prevent oxide film on the terminations. This installation has aluminum service conductor terminations that have been made without the required joint compound on a 200 amp, 120/240 volt service cable at the meter base and service panel. This is a potential thermal hazard if the terminations become oxidized and create a high resistance connection. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | No_anti-oxidant_compound_used_at_aluminum_meter_base_terminations.png | file://x:/photopub/docs/0000000338/e8e4e368-e34b-41f9-90c7-5c297c601e6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70e48c0b_65e0_4b73_a103_d4f84bc27cac
ELIN-458299-2015 | EL-290463-2015 | 10/13/2015 5:48:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Terminations of stranded aluminum conductors are required to be made using a joint compound to prevent oxide film on the terminations. This installation has aluminum service conductor terminations that have been made without the required joint compound on a 200 amp, 120/240 volt service cable at the meter base and service panel. This is a potential thermal hazard if the terminations become oxidized and create a high resistance connection. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Aluminum_service_cable_terminations_have_been_made_without_the_use_of_anti-oxidant_compound.png | file://x:/photopub/docs/0000000338/6c8c14bc-a9c0-4a82-b232-39931e25d9de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70e48c0b_65e0_4b73_a103_d4f84bc27cac
BPVOP-463650-2015 | 2250693 | 10/21/2015 3:06:55 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion_.png | file://x:/photopub/docs/0000000342/27f8d5ae-b3ad-445b-a3a3-476614a52c5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acb91cc8_918f_4d31_9807_8d57ef119569
ELIN-463382-2015 | EL-159854-2014 | 10/22/2015 10:46:31 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | #2 AWG aluminum identified conductor from the transfer switch feeder cable has been split at the end and pushed under two terminal screws on the neutral bar at the 200 amp 120/240 volt main distribution panel. Improper terminations can cause thermal effects. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Neutral.png | file://x:/photopub/docs/0000000343/9a15cbe3-50c3-4edd-a393-ce064b7932b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95dc3c92_d476_4f63_91d6_2c9d89d50686
ELIN-460648-2015 | EL-251087-2015 | 10/21/2015 10:46:00 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding has been done at the meter base instead of the main panel. The grounding of the neutral is required at the neutral point connection to allow the proper function of the breakers in a fault condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Meterbase_ground.png | file://x:/photopub/docs/0000000343/955e5d1a-a1ad-4a28-b313-9f38344f5425.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2780f4d_879b_49a7_bc04_b00bd008aaae
BPVOP-419476-2015 | 2250684 | 10/8/2015 3:45:03 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP045 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | 4 | 4 | Liquid ammonia pressure containers must be fit for service and maintain minimal required shell thickness in order to contain maximum rated working pressure. I found that some pressure vessels may not be fit for service because of an active general corrosion, which supposedly exceeds the allowable amount. Potential exists for an incident due to deteriorating condition of pressure retaining vessels. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | Pressure_vessel.png | file://x:/photopub/docs/0000000342/3664a74a-aa1e-45a2-8bf3-7cfdea65d87e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1228d0c6_6eb3_4b3c_9cc2_107532b75225
GAIN-457512-2015 | GA-271948-2015 | 10/19/2015 9:29:47 AM | ASSESS: GA: Rough-In | png | #asFound | GA049 | Piping union installed in a concealed area | 2 | 2 | Ceiling will be dropped and Union concealed unless builder modifies design of hallway. Unions are a potential gas leak source and the ceiling cavity presents a large contained cavity for gas to accumulate. | 2 | Piping union installed in a concealed area | Concealed_union_2.png | file://x:/photopub/docs/0000000341/b197e6bd-7968-4ee3-92fd-4246a46118ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1761edc9_47ee_4815_aab9_b5b84adac120
GAIN-457512-2015 | GA-271948-2015 | 10/19/2015 9:29:47 AM | ASSESS: GA: Rough-In | png | #asFound | GA049 | Piping union installed in a concealed area | 2 | 2 | Ceiling will be dropped and Union concealed unless builder modifies design of hallway. Unions are a potential gas leak source and the ceiling cavity presents a large contained cavity for gas to accumulate. | 2 | Piping union installed in a concealed area | Concealed_union_3.png | file://x:/photopub/docs/0000000341/01aded3a-5b1e-4cbe-8d25-4e3fa15e9cce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1761edc9_47ee_4815_aab9_b5b84adac120
GAIN-457512-2015 | GA-271948-2015 | 10/19/2015 9:29:47 AM | ASSESS: GA: Rough-In | png | #asFound | GA049 | Piping union installed in a concealed area | 2 | 2 | Ceiling will be dropped and Union concealed unless builder modifies design of hallway. Unions are a potential gas leak source and the ceiling cavity presents a large contained cavity for gas to accumulate. | 2 | Piping union installed in a concealed area | Concealed_union_1.png | file://x:/photopub/docs/0000000341/f735f7d6-1d81-4fe9-8b6d-faf9ab2c7cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1761edc9_47ee_4815_aab9_b5b84adac120
EDOP-461482-2015 | 2050556 | 10/14/2015 10:03:08 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If a car is stopped/stuck outside of a landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside the unlocking zone (landing) is restricted to 4". It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. Note: The picture is just being used for reference and it is not an actual site photo. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000341/99410753-f49a-4860-a2a9-338972327417.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb946e79_cafb_4dcc_8835_ed6dc6061a8f
ELIN-459087-2015 | EL-294309-2015 | 10/21/2015 3:27:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Outdoor RV service main panel located in a enclosure that is not approved for the weather. Equipment could be subject to weather and cause a fault/shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | enclosure_not_approved.png | file://x:/photopub/docs/0000000342/0404904b-fabc-40f0-8a44-34cb065aed0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b45392fa_418d_4221_ae7e_6057961441f0
ELIN-456334-2015 | EL-285954-2015 | 10/21/2015 3:27:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | The distribution panel has been installed in a small shed that does not provide for secure footing of 1 meter, nor does the shed provide minimum vertical clearance for panel board. Workers could be injured working on electrical equipment when minimum footing and headroom not provided. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Headroom_not_provided_in_shed.png | file://x:/photopub/docs/0000000342/d921ea62-3f20-4ab1-ae44-7d2e9630dcac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea6d1ca0_aeab_4470_8ab9_3b48c2375cd7
ELIN-456334-2015 | EL-285954-2015 | 10/21/2015 3:27:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | The distribution panel has been installed in a small shed that does not provide for secure footing of 1 meter, nor does the shed provide minimum vertical clearance for panel board. Workers could be injured working on electrical equipment when minimum footing and headroom not provided. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Minimum_working_space_not_provided.png | file://x:/photopub/docs/0000000342/78205a61-f6c3-43bd-aa01-f61dcf4a130b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea6d1ca0_aeab_4470_8ab9_3b48c2375cd7
ELIN-456334-2015 | EL-285954-2015 | 10/21/2015 3:27:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | The distribution panel has been installed in a small shed that does not provide for secure footing of 1 meter, nor does the shed provide minimum vertical clearance for panel board. Workers could be injured working on electrical equipment when minimum footing and headroom not provided. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Main_service_switch_screwed_to_pole.png | file://x:/photopub/docs/0000000342/7cfedee2-41e9-4943-8854-383a31a31046.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea6d1ca0_aeab_4470_8ab9_3b48c2375cd7
ELIN-460364-2015 | EL-299194-2015 | 10/21/2015 3:52:58 PM | ASSESS: EL: Final | png | #asFound | EL251 | Category 1 Area classification required | 2 | 2 |  | 2 | Category 1 Area classification required | 1.png | file://x:/photopub/docs/0000000342/2b72b853-9d00-4271-8b20-61b0d75d1e1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8750dcd3_5a31_4d89_86f7_b93a8dd1b64c
GAIN-453015-2015 | 5035821 | 10/16/2015 6:50:33 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Scott_Road_Headly.png | file://x:/photopub/docs/0000000340/5dbad147-b03e-4042-a656-11b413dc6af1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5A0715B1_284F_4515_9B20_D4E0B9FDFEBB
ELIN-459001-2015 | EL-292306-2015 | 10/19/2015 11:47:11 AM | ASSESS: EL: Final | png | #asFound | EL034 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not located as close as practicable to point of conductor entry into building | 3 | 3 | The point of connection to an overhead service must not be higher than the point of entry into the building. Failure to do so could result in condensation accumulating in the service conductor and equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not located as close as practicable to point of conductor entry into building | Connection_above_entrance.png | file://x:/photopub/docs/0000000340/d016489d-c39c-4e59-85c7-0718dbf82bf5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4eb6271_7ca9_494e_986a_12ec0e9f465d
ELIN-454703-2015 | EL-294103-2015 | 10/22/2015 2:17:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Neutral not complete, ground at wrong location. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Taylor-1.png | file://x:/photopub/docs/0000000342/32ea1046-4248-47dc-bc7a-6b6cb7699e72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a5ac960_2c30_437e_b1ac_efddf73f371c
EDOP-461473-2015 | 2050555 | 10/14/2015 3:08:55 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If a car is stopped/stuck outside of a landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside the unlocking zone (landing) is restricted to 4". It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. Note: The picture is just being used for reference and it is not an actual site photo. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000341/603b4708-0df6-4e4c-9195-9ff5a6c5d64f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__380e7b8a_87fe_40b1_b6a3_e261221f16f3
ELOP-440706-2015 | EL-044446-2013 | 10/19/2015 3:12:39 PM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL231 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | 3 | 3 | Combustible dust is accumulating in this Motor control center. The motor control centre contains arcing and sparking equipment such as disconnects and motor starters. Sparks may escape from confines of starters and switches and cause a fire in the equipment. | 3 | Class II, wood dust Accumulations of combustible dust or explosive dust clouds are observed. Wood dust mitigation and fire plan are in place however, they are not being followed. | Up_to_1_2_inch_dust_in_mcc__no_longer_sealed_due_to_age.png | file://x:/photopub/docs/0000000341/75cfd5e3-3f93-44b0-b930-5aab0e653313.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae58bb4a_bc71_476b_b548_97b2e3dfbf8b
ELIN-464814-2015 | EL-303094-2015 | 10/22/2015 2:09:48 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Raceways_in_trench.png | file://x:/photopub/docs/0000000342/da524dcd-9262-4f8c-a083-494e7d02d158.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1dd66bbe_7e32_4d7a_b6f6_f65ab0349dab
ELOP-226701-2014 | 4020748 | 10/15/2015 5:46:20 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL074 | Effective grounding, high voltage Fence is not installed. | 4 | 4 | High voltage equipment must be enclosed in an approved fence. Failure to do so could result in unauthorized access and potential shock and arc flash hazards. | 4 | Effective grounding, high voltage Fence is not installed. | No_fence.png | file://x:/photopub/docs/0000000340/d068c9dd-8f16-411b-a47f-8db46d83c081.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70d56008_f9c0_4254_bd48_c9a39840b2b8
ELOP-195853-2014 | 1204 | 10/15/2015 5:46:03 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL074 | Effective grounding, high voltage Fence is not installed. | 4 | 4 | High voltage equipment must be contained within a fence which is bonded to the same system electrode as the equipment itself. Failure to do so could result in a touch potential between the fence and equipment. This is especially concerning as the equipment voltage is 25,000 volts. | 4 | Effective grounding, high voltage Fence is not installed. | Fence_not_bonded.png | file://x:/photopub/docs/0000000340/d8180db2-8523-4932-9b94-94a49ba7d472.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0d04503_b00b_4d07_a086_541a75ded43b
ELOP-195716-2014 | 1224 | 10/16/2015 6:32:04 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords cannot be used as a replacement for permanent wiring. Failure to do so can result in a potential overheating situation. | 4 | Conductors, Misuse of flexible cords. | Flexible_cords.png | file://x:/photopub/docs/0000000340/9f013851-1c33-4fd8-8a93-976ca2636349.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__383586c7_13f5_4976_bc67_4097fc46ebb4
ELOP-196173-2014 | 1206 | 10/16/2015 6:32:04 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Service conductor raceways must be maintained in good condition. Failure to do so could result in loss of power to the system supplied. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Broken_weatherhead_1.png | file://x:/photopub/docs/0000000340/2645ffed-7947-4332-acb9-d50e644b5c27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bccaee7_8a11_4fe3_b80b_d33e24396391
ELOP-226696-2014 | 4020691 | 10/16/2015 6:32:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Approved connectors are required where conductors enter electrical enclosures. Failure to do so could result in cable damage and a resulting shock or arc flash hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Flex_cord.png | file://x:/photopub/docs/0000000340/690aedf7-5c2c-4947-bda7-ced254d62382.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9716765b_8382_4d4a_aa1f_6f992d82b5b8
ELOP-226727-2014 | 4020464 | 10/16/2015 6:31:33 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Baseboard heaters cannot be blocked. If they are an overheating situation could be created. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Baseboard_covered.png | file://x:/photopub/docs/0000000340/d6e03fb1-af5e-4d56-bad1-af4b55db0358.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98a72777_912c_4743_a50c_9df5af4a012a
GAIN-459684-2015 | GA-292800-2015 | 10/14/2015 10:18:48 AM | ASSESS: GA: Final | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Gas_range__gas_range_installation_with_correct_clearances.png | file://x:/photopub/docs/0000000339/6069cb2b-9902-4b44-9153-c109bddb3761.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d1347dd_9e0e_46bd_a0e9_3392b25d23a4
ELIN-456515-2015 | EL-247900-2015 | 10/14/2015 9:17:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Aluminum bonding conductor has been wrapped around the bonding screw but good connection has not been made and two dissimilar metals are in contact. This could result in the bonding failing at the metal box allowing a possible short or shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Range.png | file://x:/photopub/docs/0000000339/757e5b26-8a4c-4888-ba1d-70f02f3ffd7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5752935_e866_45ec_8261_523e61d06ad4
ELIN-458595-2015 | EL-260499-2015 | 10/14/2015 9:17:19 PM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | Armour on the ACWU is not properly bonded. This could prevent proper protection of the cable. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | ACWU_connector.png | file://x:/photopub/docs/0000000339/86af3eab-f197-480f-935b-8bba33bc25fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71d923e5_62d9_4a3f_886e_84c420417b82
ELIN-458597-2015 | EL-260495-2015 | 10/14/2015 9:17:44 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Grounding bushing has not been used on the conduit from the Meterbase. This is required to maintain continuity and ensure proper protection of persons and equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Ground_bushing.png | file://x:/photopub/docs/0000000339/dbbb5ad1-05a3-40a2-a45d-1b751ff61e16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b86da061_9ece_4c8d_8648_28610a3fcf7f
ELIN-458594-2015 | EL-260500-2015 | 10/14/2015 9:17:50 PM | ASSESS: EL: Final | png | #asFound | EL109 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 |  | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Neutral.png | file://x:/photopub/docs/0000000339/c2a82600-b8de-47ed-9c3a-2175733e1924.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b27b9f8_808b_452a_9072_290b284c8976
BPVIN-458694-2015 | UW-299852-2015 | 10/13/2015 9:12:45 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment it is determined that expansion tank is a Non-ASME vessel. Non-ASME vessel may not be appropriate for the intended service and may fail in service. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Non-ASME_EXPANSION_TANK.png | file://x:/photopub/docs/0000000338/086afe58-8c07-4982-99f9-c04c3466b46a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a105ff4_a66d_47c8_aab5_d30b97c73fae
BPVIN-458691-2015 | BPV-153368-2014 | 10/13/2015 9:13:31 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment it is determined that expansion tank is a Non-ASME vessel. Non-ASME vessel may not be appropriate for the intended service and pressure boundary may fail in service. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | NON-AMME_EXPANSION_TANK.png | file://x:/photopub/docs/0000000338/1546182d-bd8e-444d-8456-bcd7a7d9dc2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38aa6720_c45d_4be6_be97_0d66a3816c06
ELIN-463776-2015 | EL-286660-2015 | 10/20/2015 11:30:00 AM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | There are live connections that are exposed to anyone, should they come into contact with the receptacle from within the vanity cabinet. This could result in a shock to the human touch or even a fire should combustible products come into contact with the live terminals and a grounded source. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | GFCI_and_wiring_.png | file://x:/photopub/docs/0000000342/992a9a88-2578-45aa-b2d9-7a992da936b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e691019b_7586_4861_8f1d_9626bdf3c858
GAIN-459636-2015 | GA-278918-2015 | 10/15/2015 3:48:28 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | 1.Gas regulator has been installed in the location that is too close to the appliance combustion air inlet and mechanical air inlet into building 2. If the regulator was to release gas through the relief opening the gas would migrate into the combustion chamber and could cause a explosion when the appliance tries to ignite the burner | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | regulator_vent.png | file://x:/photopub/docs/0000000339/20dac6e4-74af-41f1-a911-008fad198597.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__433f0cc7_612e_47cf_a05e_9db5e2c97d59
GAIN-459636-2015 | GA-278918-2015 | 10/15/2015 3:48:28 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | 1.Gas regulator has been installed in the location that is too close to the appliance combustion air inlet and mechanical air inlet into building 2. If the regulator was to release gas through the relief opening the gas would migrate into the combustion chamber and could cause a explosion when the appliance tries to ignite the burner | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Vent_Clearance_and_dirt_pocket.png | file://x:/photopub/docs/0000000339/390a1966-d47f-44dd-80c9-303dca37fb01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__433f0cc7_612e_47cf_a05e_9db5e2c97d59
GAIN-459844-2015 | GA-288501-2015 | 10/15/2015 3:48:30 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Generator_venting.png | file://x:/photopub/docs/0000000339/a0fd1930-9c4f-4c48-9652-3169bf08e649.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ccd9d13_b27a_4091_b7ce_c6d9c9f0b46e
ELIN-451463-2015 | EL-276176-2015 | 10/22/2015 12:13:27 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Panel_directory_not_completed.png | file://x:/photopub/docs/0000000342/557e2f55-2586-47f4-9ef9-5b9a5f7eac9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70d68f2c_e227_43d1_bb85_4acb4c1d09ce
GAIN-452120-2015 | GA-016254-2013 | 10/20/2015 8:52:40 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 2 | Bonding wire wrapped around piping, not making use of proper bonding clamp to ensure electrical continuity. | 3 | Non-compliant material/fittings installed | Glen_view-_bonding_not_properly_secured_.png | file://x:/photopub/docs/0000000341/5d5f1161-a6ad-40ec-8401-839c04b93264.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__B20C4791_6CF5_44CE_A2C7_1DD59E5DE9B2
GAIN-452121-2015 | GA-016261-2013 | 10/20/2015 9:52:08 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Final termination of venting not glue together. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 1074_fleetwood_unglued_joints_.png | file://x:/photopub/docs/0000000341/91337754-b141-4e00-b579-a67b10e8cc4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7A138CE2_19BC_4D68_8DF6_63800DB1D3E7
ELIN-457909-2015 | EL-269066-2015 | 10/13/2015 9:46:39 PM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Electrical continuity has not been maintained by terminating the cable armour in a fitting to the electrical panel. The armour could come in contact with the energized conductors but not operate the overcurrent protection which may result in fire or mechanical damage. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | ACWU_Feeder.png | file://x:/photopub/docs/0000000338/512b19dc-6163-4998-bbd0-fec44a28c88f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97aaccb1_d4a6_49d1_8d07_13f0b43f8820
ELIN-458613-2015 | EL-268742-2015 | 10/13/2015 9:46:39 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 2 | Outside covering of wire has been damaged which could mean further damage has been done to the conductors. Result could be failure of equipment or controls. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Thermostat_wire.png | file://x:/photopub/docs/0000000338/f7996396-fed4-4245-b599-15c39b4dcc8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ac54479_e3e3_4e1e_8471_3874b659b5e6
ELIN-455098-2015 | EL-293783-2015 | 10/16/2015 3:44:56 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Accessible outlet within 1.5 m of sink must be G .F.C.I. protected. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Washer_outlet_near_sink.png | file://x:/photopub/docs/0000000340/293cd714-d2e8-4e78-a220-f76b716e0e02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63fb41a9_d4df_42f0_a92c_9c7a3703c775
BPVIN-462313-2015 | UW-302216-2015 | 10/9/2015 2:53:47 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP205 | 5.1.0 In service proc/process - Housekeeping of boiler or machinery rooms not compliant personal safety, and general safety etc. | 2 | 2 | Clearances are to be sufficient enough to have access to equipment for maintenance and inspection. I found that the clearances for the expansion tank to be minimal. This may lead to tripping hazards and/or difficulty for maintenance projects. | 2 | 5.1.0 In service proc/process - Housekeeping of boiler or machinery rooms not compliant personal safety, and general safety etc. | expansion_tank_minimal_clearance.png | file://x:/photopub/docs/0000000341/12e26890-2526-4e13-8cba-5caaf1bf38e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee605744_b8f0_47ef_a2cd_1f69e68031f9
ELIN-455528-2015 | EL-294502-2015 | 10/15/2015 7:25:55 AM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | 120/240 volt 200 amp fuses installed in fused disconnect switch. Ampacity of fuses exceed maximum ampacity of conductor. This could cause overloading of conductor , which could cause a thermal effect. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Fuses_installed_in_trailer_disconnect.png | file://x:/photopub/docs/0000000340/f60606d8-2dad-424f-865d-ef4416c7aefa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__689a97b5_69df_4667_ae30_379c487a8e38
BPVOP-463648-2015 | 2250694 | 10/21/2015 1:03:27 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP045 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | 4 | 4 | Pressure retaining components must be fit for service and maintain minimal required shell thickness in order to retain maximum rated working pressure. I found that this pressure retaining component may not be fit for service because of an active general corrosion, which supposedly exceeds the allowable amount. Potential exists for an incident due to deteriorated condition of pressure retaining parts. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | Local_wasted_area.png | file://x:/photopub/docs/0000000342/33379eec-3c86-435b-84ee-5b963589f668.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4523983c_4374_4c57_8a7b_28e78f081a41
BPVOP-463643-2015 | 2250686 | 10/21/2015 12:51:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP045 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | 4 | 4 | Pressure retaining components must be fit for service and maintain minimal required shell thickness in order to retain maximum rated working pressure. I found that this pressure retaining component may not be fit for service because of an active general corrosion, which supposedly exceeds the allowable amount. Potential exists for an incident due to deteriorated condition of pressure retaining parts. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | External_condition.png | file://x:/photopub/docs/0000000342/fb4e9a8d-d762-49a8-b4a5-9de4169cd4b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94058096_ae1e_448a_b110_8e0ee3748eab
ELIN-464173-2015 | UW-303647-2015 | 10/21/2015 7:03:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | A panel board and service conductor along with other extensive electrical renovations have been done without a permit. The service cable which is of a type without mechanical protection is aluminum and has been entered into an older S type meter base with copper only lugs. S type meter bases have a very low cubic inch air capacity and are not approved for use with aluminum. The service cable lacks effective protection in the wall as is required for service conductors. A real potential for overheating of conductor terminations inside the meter could occur or damage to unprotected service conductors in wall could also occur. Either of these two items could result in property damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | NMD_90_service_cable.png | file://x:/photopub/docs/0000000342/749254fe-00d5-4624-bca2-b0beeedd25a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__717809d5_c684_4aa8_be92_14cb6ac5a84b
ELIN-464173-2015 | UW-303647-2015 | 10/21/2015 7:03:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | A panel board and service conductor along with other extensive electrical renovations have been done without a permit. The service cable which is of a type without mechanical protection is aluminum and has been entered into an older S type meter base with copper only lugs. S type meter bases have a very low cubic inch air capacity and are not approved for use with aluminum. The service cable lacks effective protection in the wall as is required for service conductors. A real potential for overheating of conductor terminations inside the meter could occur or damage to unprotected service conductors in wall could also occur. Either of these two items could result in property damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Aluminum_cable_enters_copper_only_m_base.png | file://x:/photopub/docs/0000000342/919998d7-24da-4e3f-bec6-ff047b1678af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__717809d5_c684_4aa8_be92_14cb6ac5a84b
EDOP-461470-2015 | 2050554 | 10/14/2015 2:22:06 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If a car is stopped/stuck outside of a landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside the unlocking zone (landing) is restricted to 4". It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000341/fbdf4ebe-8e87-4f51-8a91-5fecdea2aec1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adbe06f2_24e4_4e4d_8dba_1f1ffbda3841
ELIN-462856-2015 | EL-178832-2014 | 10/22/2015 3:14:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 4 | This installation is a BCH work with. New meter shows Conductors going through wall into a live panel ,cover for panel had been removed to accommodate new conductors. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | River_rd-1.png | file://x:/photopub/docs/0000000342/8bdecdfa-8275-4759-8584-0512ae501ada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__577df521_fa21_4132_8f08_7b389e5f5522
ELOP-361312-2015 | 5300882 | 10/15/2015 7:08:53 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Large lumber equipment such as loaders have made contact with customer owned high voltage switch. Coupled with erosion of switch operator standing area and no gradient grounding mat this service is unsafe to operate in it's current condition. In the event of an emergency, overall power to the site can not be disconnected, and could lead to unpredictable property or personnel damages | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Damaged_switch_handle_assembly.png | file://x:/photopub/docs/0000000340/9fa30f25-01d6-40b9-a930-d482a2538f36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf5ebbc2_787d_4b60_90f2_d00d8c76560a
ELOP-361312-2015 | 5300882 | 10/15/2015 7:08:53 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Large lumber equipment such as loaders have made contact with customer owned high voltage switch. Coupled with erosion of switch operator standing area and no gradient grounding mat this service is unsafe to operate in it's current condition. In the event of an emergency, overall power to the site can not be disconnected, and could lead to unpredictable property or personnel damages | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Safe_operator_arra_eroded__gradient_mat_hanging_in_ditch.png | file://x:/photopub/docs/0000000340/f1535936-251b-4c25-b06e-82dac96b8486.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf5ebbc2_787d_4b60_90f2_d00d8c76560a
ELOP-361312-2015 | 5300882 | 10/15/2015 7:08:53 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Large lumber equipment such as loaders have made contact with customer owned high voltage switch. Coupled with erosion of switch operator standing area and no gradient grounding mat this service is unsafe to operate in it's current condition. In the event of an emergency, overall power to the site can not be disconnected, and could lead to unpredictable property or personnel damages | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Station_ground_dug_up.png | file://x:/photopub/docs/0000000340/650bb59b-892f-4565-8ec9-3ee6ac3a3fde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf5ebbc2_787d_4b60_90f2_d00d8c76560a
ELOP-361312-2015 | 5300882 | 10/15/2015 7:08:53 AM | ASSESS: EL OP: Dust Assessment | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Large lumber equipment such as loaders have made contact with customer owned high voltage switch. Coupled with erosion of switch operator standing area and no gradient grounding mat this service is unsafe to operate in it's current condition. In the event of an emergency, overall power to the site can not be disconnected, and could lead to unpredictable property or personnel damages | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Remains_of_station_ground.png | file://x:/photopub/docs/0000000340/b807befb-8649-4fc2-be71-284285915bfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf5ebbc2_787d_4b60_90f2_d00d8c76560a
ELOP-446057-2015 | 4997978 | 9/29/2015 12:35:34 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a saw mill site motor control center located outdoors in a wood dust hazardous location which was not protected from dust and had energized exposed conductors (400amp 480 volt 3 phase). The doors on motor control center enclosure did not close-off and contain the internal energized electrical components from dust and did not have all the individual doors bolted or screwed shut. The enclosure in several locations had doors missing screws and latching devices and doors were swinging freely open leaving energized exposed conductors to possible shock contact or short circuit fault condition. This is an electrical fire or shock hazard because the energized electrical equipment could short out and fault and cause a severe wood dust fire or cause an electrical shock to persons on site. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Doors_not_latching_shut_or_closed_for_MCC_in_dust_location_4.png | file://x:/photopub/docs/0000000340/4d30859a-9dba-478f-b3bd-23c093df823b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37462e6e_b342_4a8c_b2ba_4519be7215c6
ELOP-446057-2015 | 4997978 | 9/29/2015 12:35:34 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a saw mill site motor control center located outdoors in a wood dust hazardous location which was not protected from dust and had energized exposed conductors (400amp 480 volt 3 phase). The doors on motor control center enclosure did not close-off and contain the internal energized electrical components from dust and did not have all the individual doors bolted or screwed shut. The enclosure in several locations had doors missing screws and latching devices and doors were swinging freely open leaving energized exposed conductors to possible shock contact or short circuit fault condition. This is an electrical fire or shock hazard because the energized electrical equipment could short out and fault and cause a severe wood dust fire or cause an electrical shock to persons on site. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Doors_not_latching_shut_or_closed_for_MCC_in_dust_location_3.png | file://x:/photopub/docs/0000000340/9c77fe88-b810-4780-8b1a-d4cfc8cd7956.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37462e6e_b342_4a8c_b2ba_4519be7215c6
ELOP-446057-2015 | 4997978 | 9/29/2015 12:35:34 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a saw mill site motor control center located outdoors in a wood dust hazardous location which was not protected from dust and had energized exposed conductors (400amp 480 volt 3 phase). The doors on motor control center enclosure did not close-off and contain the internal energized electrical components from dust and did not have all the individual doors bolted or screwed shut. The enclosure in several locations had doors missing screws and latching devices and doors were swinging freely open leaving energized exposed conductors to possible shock contact or short circuit fault condition. This is an electrical fire or shock hazard because the energized electrical equipment could short out and fault and cause a severe wood dust fire or cause an electrical shock to persons on site. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Doors_not_latching_shut_or_closed_for_MCC_in_dust_location_2.png | file://x:/photopub/docs/0000000340/420ee194-5480-4449-90fb-6b4c01d04a1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37462e6e_b342_4a8c_b2ba_4519be7215c6
ELOP-446057-2015 | 4997978 | 9/29/2015 12:35:34 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a saw mill site motor control center located outdoors in a wood dust hazardous location which was not protected from dust and had energized exposed conductors (400amp 480 volt 3 phase). The doors on motor control center enclosure did not close-off and contain the internal energized electrical components from dust and did not have all the individual doors bolted or screwed shut. The enclosure in several locations had doors missing screws and latching devices and doors were swinging freely open leaving energized exposed conductors to possible shock contact or short circuit fault condition. This is an electrical fire or shock hazard because the energized electrical equipment could short out and fault and cause a severe wood dust fire or cause an electrical shock to persons on site. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Doors_not_latching_shut_or_closed_for_MCC_in_dust_location_1.png | file://x:/photopub/docs/0000000340/2edf2751-a23d-419a-8749-cb06609903a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37462e6e_b342_4a8c_b2ba_4519be7215c6
GAIN-460179-2015 | GA-289301-2015 | 10/20/2015 9:07:06 AM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | Water can enter regulator vent and chase pressure fluctuations. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Reg_vent_2.png | file://x:/photopub/docs/0000000341/43bc991f-2ba9-433a-bb61-20a3866e85f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd070102_1aa2_44c5_a667_8da86928deab
GAIN-460179-2015 | GA-289301-2015 | 10/20/2015 9:07:06 AM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | Water can enter regulator vent and chase pressure fluctuations. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Reg_vent_1.png | file://x:/photopub/docs/0000000341/154a10cb-b571-46a6-96b2-31714a4ac489.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd070102_1aa2_44c5_a667_8da86928deab
BPVOP-464930-2015 | 2275056 | 10/27/2015 8:22:03 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve on this hot water boiler for the last 7 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV.png | file://x:/photopub/docs/0000000344/94a72f59-464a-4d42-84b3-11eb7311b48c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__563bd985_076b_4848_80b8_3caedca8de6c
BPVOP-464933-2015 | 2284737 | 10/27/2015 8:31:20 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve for the last 7 years on this air receiver. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | safety_valve.png | file://x:/photopub/docs/0000000344/2a756cfe-f157-4159-bf88-7724487f89bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__583e7ace_ccdd_4f5c_9d8b_edf0f29ba8ef
ELIN-439711-2015 | EL-260583-2015 | 10/23/2015 5:01:42 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Two ground wires to the neutral, one to an electrode the other to the meter, but energized at time of inspection undetermined termination point. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Dolmage-1.png | file://x:/photopub/docs/0000000343/44f71c6f-5cae-4857-871d-ff3a3d2b5d7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62be10fa_5653_4117_8dcd_6b578e2c70a2
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_3.png | file://x:/photopub/docs/0000000345/96ce2c05-5c7a-44cd-ab76-147da80ca0df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_9.png | file://x:/photopub/docs/0000000345/3a330a32-3017-4299-a75c-6ca653805642.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_10.png | file://x:/photopub/docs/0000000345/39352e7f-f1d5-4d33-a9c7-44835f9f6b57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_6.png | file://x:/photopub/docs/0000000345/f7fcf63e-0483-4bfe-a093-d04e9eacf1fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_5.png | file://x:/photopub/docs/0000000345/32c818ab-4c80-49c4-9be6-3d1bff8da7e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_8.png | file://x:/photopub/docs/0000000345/d3403aa1-fa1c-41bb-8822-bf770f73f28d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_7.png | file://x:/photopub/docs/0000000345/93d31620-f0af-4f76-82c3-5e5bc8daf700.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_4.png | file://x:/photopub/docs/0000000345/39571834-7ba0-48c0-b16e-9a33c4b1576b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_1.png | file://x:/photopub/docs/0000000345/18378d6c-ce4a-49a9-8122-43ce6f6a1119.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_11.png | file://x:/photopub/docs/0000000345/c36b8f65-fffe-4d48-955c-fff4b6131cb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462751-2015 | UW-302596-2015 | 10/30/2015 4:26:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found an existing installation of privately owned high-voltage overhead consumer's service equipment (consumer's service switch, poles and overhead line conductors) has been affected and has been altered from original installation and has become an electrical hazard because of the addition of earth landfill in and around the overhead line electrical equipment. This is an electrical shock hazard to people because the overhead line conductors and its electrical equipment is now too low above earth grade and people or equipment may come too close or in contact with high-voltage electrical equipment which may cause a severe or catastrophic electrical fire or shock hazard. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Privately_owned_High_voltage_consumers_service_too_low_not_safe_2.png | file://x:/photopub/docs/0000000345/82f517ef-d958-4e56-b5dc-c475decee089.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e9b0db_779e_4737_b632_d253642f42d7
ELIN-462282-2015 | UW-302182-2015 | 10/22/2015 5:10:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found existing meterbase located outdoors on pole has meter removed and has 2 sets of #10AWG sized copper single conductors energized and installed temporarily jumpering out the line side of lugs to load side terminals of meter-base. This conductor was used to feed power supply to an adjacent service panel on a pole. The energized conductors and meter-base bus bars are exposed and are an electrical fire or shock hazard to persons and property when meter and cover are removed. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Existing_meter_with_energized_exposed_conductors_on_meter_3.png | file://x:/photopub/docs/0000000345/c6d5343b-a93d-4e92-af39-59328b390442.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260f408d_3716_468e_a6bd_c80f21e06828
ELIN-462282-2015 | UW-302182-2015 | 10/22/2015 5:10:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found existing meterbase located outdoors on pole has meter removed and has 2 sets of #10AWG sized copper single conductors energized and installed temporarily jumpering out the line side of lugs to load side terminals of meter-base. This conductor was used to feed power supply to an adjacent service panel on a pole. The energized conductors and meter-base bus bars are exposed and are an electrical fire or shock hazard to persons and property when meter and cover are removed. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Existing_meter_with_energized_exposed_conductors_on_meter_1.png | file://x:/photopub/docs/0000000345/e6797094-e3f2-49b1-a710-300d78ee4fb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260f408d_3716_468e_a6bd_c80f21e06828
ELIN-466714-2015 | EL-299744-2015 | 10/27/2015 6:00:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 3 | Boxes used to mount pendant ceiling fans are required to be approved for supporting a ceiling fan and so marked. This installation has a box installed in a location intended to have a ceiling fan installed. The box is not rated for fan support. This is a potential hazard if the fan is not supported properly and calls from the ceiling and/or damages wiring. | 4 | Installation of electrical equipment Fixtures without suitable support. | Ceiling_fan_rated_box_is_not_installed_in_a_location_intended_for_a_ceiling_fan.png | file://x:/photopub/docs/0000000344/28a997df-48f1-460e-a77a-a6048d4a0061.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed966b49_ec1e_4874_8bd6_e9f34658d301
ELIN-467036-2015 | EL-293717-2015 | 10/27/2015 6:01:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Service panels for buildings under construction are required to be protected from the weather to prevent equipment from getting wet. This installation has a service panel installed in a wooden enclosure for use during construction of a new house. The panel enclosure is open on the top which may allow the panel to get wet when it rains. This may potentially cause circuit breakers to be damaged and in some circumstances may create a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_enclosure_open_on_top.png | file://x:/photopub/docs/0000000344/36e7b3e9-a956-43a9-b793-14fb0184ee1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e9b4063_81c4_46b6_ad86_84b36d26ed83
ELIN-467036-2015 | EL-293717-2015 | 10/27/2015 6:01:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Service panels for buildings under construction are required to be protected from the weather to prevent equipment from getting wet. This installation has a service panel installed in a wooden enclosure for use during construction of a new house. The panel enclosure is open on the top which may allow the panel to get wet when it rains. This may potentially cause circuit breakers to be damaged and in some circumstances may create a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_enclosure_open_on_top_.png | file://x:/photopub/docs/0000000344/e0753040-851f-4af8-818e-37c8304808b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e9b4063_81c4_46b6_ad86_84b36d26ed83
ELIN-463564-2015 | EL-282839-2015 | 10/27/2015 6:00:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metal sheathed cables are required to have a minimum clearance of 25mm from metal heating ducts or must have thermal insulation installed between the cables and the ducting. This is required to protect the cables from mechanical damage due to thermal damage to the jacket and insulation on the cable and conductors. This electrical installation for wiring of a new house has multiple cables in contact with metal heating ducts. This is a potential shock and fire hazard if the cables become damaged from the heating ducts. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_ducts_______.png | file://x:/photopub/docs/0000000344/e7cd7706-f49f-49d6-b77b-0cb9ef337d63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5557065b_479e_429d_9d73_40018ded2e45
ELIN-464223-2015 | EL-279048-2015 | 10/29/2015 7:42:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Found service compartment of main service panel has knockout holes open and ready for entry of branch circuit cables into consumer's service compartment which is not approved for the use or safe to do so. By entering the branch circuit cables into service compartment, a worker would have to work on energized equipment because the line side of main breaker would still be energized even when the main breaker is in OFF position and could be an electrical shock hazard to people working on these branch circuits passing through service compartment of panelboard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3.png | file://x:/photopub/docs/0000000345/2bb186c2-f546-465c-8197-cee0e0af2803.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0698a287_dfcb_48cb_b7dd_2c6fb956b5e6
ELIN-464223-2015 | EL-279048-2015 | 10/29/2015 7:42:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Found service compartment of main service panel has knockout holes open and ready for entry of branch circuit cables into consumer's service compartment which is not approved for the use or safe to do so. By entering the branch circuit cables into service compartment, a worker would have to work on energized equipment because the line side of main breaker would still be energized even when the main breaker is in OFF position and could be an electrical shock hazard to people working on these branch circuits passing through service compartment of panelboard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 1.png | file://x:/photopub/docs/0000000345/a6750b6d-3b57-4710-b03c-4def12744bad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0698a287_dfcb_48cb_b7dd_2c6fb956b5e6
ELIN-464223-2015 | EL-279048-2015 | 10/29/2015 7:42:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Found service compartment of main service panel has knockout holes open and ready for entry of branch circuit cables into consumer's service compartment which is not approved for the use or safe to do so. By entering the branch circuit cables into service compartment, a worker would have to work on energized equipment because the line side of main breaker would still be energized even when the main breaker is in OFF position and could be an electrical shock hazard to people working on these branch circuits passing through service compartment of panelboard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 2.png | file://x:/photopub/docs/0000000345/c2f7b95e-2184-4e42-92b8-651c6a4380db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0698a287_dfcb_48cb_b7dd_2c6fb956b5e6
ELIN-464223-2015 | EL-279048-2015 | 10/29/2015 7:42:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Found service compartment of main service panel has knockout holes open and ready for entry of branch circuit cables into consumer's service compartment which is not approved for the use or safe to do so. By entering the branch circuit cables into service compartment, a worker would have to work on energized equipment because the line side of main breaker would still be energized even when the main breaker is in OFF position and could be an electrical shock hazard to people working on these branch circuits passing through service compartment of panelboard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 4.png | file://x:/photopub/docs/0000000345/34cd73c0-9132-4e4e-9a0b-87eb8583a16e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0698a287_dfcb_48cb_b7dd_2c6fb956b5e6
ELIN-463564-2015 | EL-282839-2015 | 10/27/2015 6:00:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non metal sheathed cables are required to have a minimum clearance of 25mm from metal heating ducts or must have thermal insulation installed between the cables and the ducting. This is required to protect the cables from mechanical damage due to thermal damage to the jacket and insulation on the cable and conductors. This electrical installation for wiring of a new house has multiple cables in contact with metal heating ducts. This is a potential shock and fire hazard if the cables become damaged from the heating ducts. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_heating_ducts_.png | file://x:/photopub/docs/0000000344/9bb1ca36-46ad-44b2-8cd9-31e6e9af6482.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5557065b_479e_429d_9d73_40018ded2e45
ELIN-466099-2015 | EL-181135-2014 | 10/26/2015 2:11:37 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | The blue phase conductor is actually a neutral conductor. There is a possibility that someone will mistakenly identified this wire as a ungrounded conductor. If the splice is opened incorrectly it would cause the neutral "grounded point" to shift in relationship to the load and would likely damage all 120 volt electrical equipment. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Blue_phase_conductor_to_be_re_identified_white.png | file://x:/photopub/docs/0000000343/1d6191a9-3015-45ac-947b-200695572a9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdf02d84_dbff_4167_8dd5_9781d94375af
ELIN-460302-2015 | EL-232993-2015 | 10/26/2015 8:32:07 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Exposed plastic boxes to weather. Not approved for specific use. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Located_at_entry_of_car_port_with_no_doors.png | file://x:/photopub/docs/0000000344/271fe27d-6854-493c-a8f3-e477b5cd4bad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f79184eb_b0e6_4c79_950b_3236f505c6c8
ELOP-460974-2015 | 5239499 | 10/30/2015 8:01:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Conductor terminations inside of electrical equipment need to be checked periodically to ensure that connections remain tight and in good operating condition. This is particularly necessary in areas of high vibration such as a mill. This inspection has identified two 30A 480V switches that have connections that have become loose. This has created a high resistance connection and resulted in overheating of the terminations and conductors. The result is thermal damage to the conductor insulation which can lead to excessive conductor overheating or a fault condition and a resulting arc flash. The equipment is located in a shingle mill which left undetected and uncorrected could have resulted in a fire. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Fused_disconnect_switch.png | file://x:/photopub/docs/0000000346/f79914bb-b908-4eb2-9052-12fc39b13661.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930f864c_29e0_4d5c_b265_0f85a64730ee
ELOP-460974-2015 | 5239499 | 10/30/2015 8:01:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Conductor terminations inside of electrical equipment need to be checked periodically to ensure that connections remain tight and in good operating condition. This is particularly necessary in areas of high vibration such as a mill. This inspection has identified two 30A 480V switches that have connections that have become loose. This has created a high resistance connection and resulted in overheating of the terminations and conductors. The result is thermal damage to the conductor insulation which can lead to excessive conductor overheating or a fault condition and a resulting arc flash. The equipment is located in a shingle mill which left undetected and uncorrected could have resulted in a fire. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Melted_conductor_insulation_inside_fuse_disconnect_switch_for_conveyor_motor.png | file://x:/photopub/docs/0000000346/ad7fdbea-98d2-4414-bfa4-1efa01e4acd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930f864c_29e0_4d5c_b265_0f85a64730ee
ELOP-460974-2015 | 5239499 | 10/30/2015 8:01:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Conductor terminations inside of electrical equipment need to be checked periodically to ensure that connections remain tight and in good operating condition. This is particularly necessary in areas of high vibration such as a mill. This inspection has identified two 30A 480V switches that have connections that have become loose. This has created a high resistance connection and resulted in overheating of the terminations and conductors. The result is thermal damage to the conductor insulation which can lead to excessive conductor overheating or a fault condition and a resulting arc flash. The equipment is located in a shingle mill which left undetected and uncorrected could have resulted in a fire. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Shingle_mill_distribution.png | file://x:/photopub/docs/0000000346/6a008b70-d48b-40f5-a62a-254bf502c3ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930f864c_29e0_4d5c_b265_0f85a64730ee
ELOP-460974-2015 | 5239499 | 10/30/2015 8:01:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Conductor terminations inside of electrical equipment need to be checked periodically to ensure that connections remain tight and in good operating condition. This is particularly necessary in areas of high vibration such as a mill. This inspection has identified two 30A 480V switches that have connections that have become loose. This has created a high resistance connection and resulted in overheating of the terminations and conductors. The result is thermal damage to the conductor insulation which can lead to excessive conductor overheating or a fault condition and a resulting arc flash. The equipment is located in a shingle mill which left undetected and uncorrected could have resulted in a fire. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Disconnect_switch_for_shingle_machine.png | file://x:/photopub/docs/0000000346/749cd04a-e5f0-4511-8ef9-b171eb5ebf37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930f864c_29e0_4d5c_b265_0f85a64730ee
ELOP-460974-2015 | 5239499 | 10/30/2015 8:01:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Conductor terminations inside of electrical equipment need to be checked periodically to ensure that connections remain tight and in good operating condition. This is particularly necessary in areas of high vibration such as a mill. This inspection has identified two 30A 480V switches that have connections that have become loose. This has created a high resistance connection and resulted in overheating of the terminations and conductors. The result is thermal damage to the conductor insulation which can lead to excessive conductor overheating or a fault condition and a resulting arc flash. The equipment is located in a shingle mill which left undetected and uncorrected could have resulted in a fire. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Melted_conductor_insulation_inside_disconnect_switch_or_shingle_machine.png | file://x:/photopub/docs/0000000346/1994d11d-2cfc-44c9-872f-a5e71fddd6a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930f864c_29e0_4d5c_b265_0f85a64730ee
ELIN-468102-2015 | EL-306101-2015 | 10/29/2015 3:01:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | No system grounding conductor installed on service. No system ground. Shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_conductor_hanging_loose__no_electrode.png | file://x:/photopub/docs/0000000345/b995b102-5c53-412c-a517-a605a871739f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2276d38a_e258_466c_ae46_4f659d49b94d
ELIN-468373-2015 | EL-207825-2015 | 10/29/2015 3:01:36 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Service conduit nipple is not bonded. Shock hazard | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_grounding_bushing.png | file://x:/photopub/docs/0000000345/9d4708b1-ca80-4b75-a556-141144f79f01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e448533_1f76_46d3_8d53_f7bbbb0a26dd
ELIN-468373-2015 | EL-207825-2015 | 10/29/2015 3:01:36 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | Service conduit nipple is not bonded. Shock hazard | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Locally_manufactured_buss_bar.png | file://x:/photopub/docs/0000000345/e607c6e4-d4e3-4f80-812d-81dc9b65a74e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e448533_1f76_46d3_8d53_f7bbbb0a26dd
ELIN-466601-2015 | EL-291962-2015 | 10/30/2015 6:52:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 120/240 volt 200 amp rated residential branch circuit cable has exposed conductors accessible to persons. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors_to_persons.png | file://x:/photopub/docs/0000000347/f8fcad3d-b08a-4c7f-b496-0cffdfda666d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce6b8d9b_f030_414b_a1a1_77a3986fafbf
ELIN-465710-2015 | EL-235987-2015 | 10/29/2015 7:05:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 120/240 volt 100 amp Siemens sub distribution panel has Eaton branch circuit over current devices installed that are not approved for application. | 3 | General Equipment is not approved for the specific use | Over_current_devices_not_approved_for_sub_distribution_panel.png | file://x:/photopub/docs/0000000345/611bc079-3d21-442b-bc4f-f7fe1b580bb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07b4d20f_bf14_4189_bd88_5f1e23172c4b
ELIN-467475-2015 | EL-295349-2015 | 10/29/2015 7:05:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | 120/240 volt 125 amp main distribution panel not bonded to grounded system conductor. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_screw_or_strap_installed_in_panel.png | file://x:/photopub/docs/0000000345/9e9c4b34-4384-4c19-8dc1-6a4c0d81ecaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6796457f_5bd3_4465_be06_2c29ea4d62f3
BPVOP-453290-2015 | 3336290 | 10/27/2015 8:14:08 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | scale.png | file://x:/photopub/docs/0000000344/738f6dee-ac56-4b59-96ab-ed8cdf31d88a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63c8b7f7_d201_4692_a40a_04f025fbc69e
GAIN-462801-2015 | GA-301020-2015 | 10/21/2015 9:04:54 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Venting.png | file://x:/photopub/docs/0000000343/de22dbe8-5199-4c21-a9a4-1f682f2edab6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba65280_9be7_41a7_8d51_b6a8fd25681c
ELIN-466984-2015 | EL-210066-2015 | 10/28/2015 4:06:46 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Contractor is trying to use the BC amendment on a commercial installation. 4/0 aluminum conductors do not have adequate ampacity for a 200A commercial service. They are allowed to be installed on 200A single family dwellings only. 200A commercial service require 250mcm aluminum conductors. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | A.png | file://x:/photopub/docs/0000000345/4130b6df-e423-491e-8f32-da264bbd6dc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a341d112_ab09_4b76_b17a_a06a9062bbff
ELIN-465207-2015 | EL-302857-2015 | 10/23/2015 11:28:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | -the service cable which is unfused from hydro has been installed within the residential dwelling. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Pic_1.png | file://x:/photopub/docs/0000000343/3adc4dfc-05f3-467a-a7bb-3a9c760c6e61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a9f0f77_f7c8_4865_8e7e_7cdff78a7982
ELIN-467612-2015 | UW-305837-2015 | 10/27/2015 2:36:55 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 4 | Not able to access site | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Photo_from_nanaimo_building_inspection.png | file://x:/photopub/docs/0000000344/2d9b7241-981a-495d-b471-e1b5966dc9ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e517698b_df22_455a_8aab_a004f7480a9f
ELIN-462823-2015 | EL-296923-2015 | 10/26/2015 7:27:49 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | 15 amp 120 volt circuit has extension cord used to supply heating cable under trailer. Extension cords are not to be used as fixed wiring methods, and be run through walls. Extension cords could become overloaded and may cause a fire to occur. | 4 | Conductors, Misuse of flexible cords. | Extension_cord_used_for_fixed_wiring.png | file://x:/photopub/docs/0000000344/d02157a1-8c08-42cd-8c67-888941ec19cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62ccfedb_92a9_42a5_839c_e5463d3ce3d6
ELIN-469808-2015 | EL-185008-2014 | 11/2/2015 7:06:28 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | # 10 AWG, 240 volt dryer branch circuit non metallic sheathed cable installed in rigid conduit without a connector installed on non metallic sheathed cable as it enters the conduit. This could cause damage to the conductor insulation. | 3 | Conductors Equipment is not approved for the specific use. | NMD90_installed_with_no_connector.png | file://x:/photopub/docs/0000000347/bc8d223e-f21c-4de1-84d5-768c443a09dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f962a50_95cc_4a4e_807b_8b801401b222
ELIN-469804-2015 | EL-187610-2014 | 11/2/2015 7:07:36 AM | ASSESS: EL: Final | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | 120/208 volt 100 amp sub distribution panel has bond screw still installed on the grounded conductor. This provides the possibility of multiple pathes to ground. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Bonding_screw_installed_in_sub_distribution_panel.png | file://x:/photopub/docs/0000000347/750bbfee-8aa4-41c1-8472-1f60a8d499e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8eb954a4_f708_409f_b453_53775b20c46b
ELIN-469649-2015 | EL-302687-2015 | 11/2/2015 7:06:10 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 15 amp, 120 volt, lighting switches installed within proximity of bathtub. This is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Switches_by_tub.png | file://x:/photopub/docs/0000000347/e4bdd142-1e04-4ccc-8dcf-1c5c4d15d5f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85ca7889_ac18_434b_b988_548d62d63ffa
GAIN-452102-2015 | GA-007617-2013 | 10/29/2015 4:51:26 PM | ASSESS: GA: Final | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | GA104 leaking or failing special vent system. Unglued connection in system 636 pvc vent on outside of house has come apart. Vent termination clearance no longer met. | 3 | Power vent not installed according to installation instruction. | Unapproved_vent_termination_.png | file://x:/photopub/docs/0000000345/dd4b66e9-8b2e-444f-9197-aa5d158334a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__367F1AC0_47B4_4647_9B1A_867C6BD10A42
GAIN-452102-2015 | GA-007617-2013 | 10/29/2015 4:51:26 PM | ASSESS: GA: Final | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | GA104 leaking or failing special vent system. Unglued connection in system 636 pvc vent on outside of house has come apart. Vent termination clearance no longer met. | 3 | Power vent not installed according to installation instruction. | Unglued_pvc_venting.png | file://x:/photopub/docs/0000000345/0555d988-6b42-4fb3-a42f-9e21db52d8a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__367F1AC0_47B4_4647_9B1A_867C6BD10A42
ELIN-447491-2015 | EL-285541-2015 | 11/2/2015 7:35:20 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Weatherproof cover provided allows water to enter receptacle when a cord is connected and it is raining. Corrosion can occur and create a risk for persons or property when the correct weatherproof cover is not in place. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | In_use_weatherproof_cover_not_provided.png | file://x:/photopub/docs/0000000347/d53b9cce-bac9-43d9-af00-1e8b42c30b44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__108b6cae_d5fb_459c_8085_ada1663f3993
ELIN-463414-2015 | EL-290222-2015 | 10/26/2015 4:57:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Terminations of cables to panel neutral busses must be made using the provided termination provisions or by adding an approved termination lug to the bus for a proper connection. This installation has a lug terminated to the neutral bus using a wire termination screw on the bus. The lug is being used to terminate a #1 aluminum neutral conductor for the sub-panel. This is a potential fire hazard as the lug is not approved for this use or installed properly and may become loose creating a high resistance connection. | 3 | General Equipment is not approved for the specific use | Unproved_termination_lug_and_method_for_this_panel.png | file://x:/photopub/docs/0000000343/7a657548-b79a-4826-a2ea-44723bac09c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4cbb311_ff3c_4955_901e_5a467406e6ef
ELIN-463590-2015 | EL-303208-2015 | 10/26/2015 4:58:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary service panel enclosures for construction must be properly sealed to prevent the panel from getting wet. This installation for a new house under construction has a temporary service enclosure that is not sealed on the top. When it rains the equipment may get wet. This may cause water damage to the panel and circuit breakers and under some circumstances can create a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Top_of_service_enclosure_is_not_sealed_to_prevent_the_equipment_from_getting_wet.png | file://x:/photopub/docs/0000000343/baa71b4b-7757-4cf7-8a58-24b7edd9ebd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26b2073d_6c74_448c_b6d9_f74de1bc9ca7
ELIN-464262-2015 | UW-303696-2015 | 10/21/2015 4:58:05 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Communications wiring installed in under ground conduit must be approved for a wet location. The cabling installed at this site is only approved for a dry location. Over time cables may become damaged and no work properly is exposed to water. | 0 | No Created Hazard Identified | Cat5e_cable_installed_in_underground_conduit_sytem_for_new_gas_station.png | file://x:/photopub/docs/0000000343/4eaa9c3e-b00b-4186-afa3-d3a52afc72ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15cdff2a_d6df_47cc_aa1d_d493af3b1f78
ELOP-465734-2015 | EL-298722-2015 | 10/29/2015 9:20:00 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Motor starters with energized terminals are required to have covers in place to prevent accidental contact with live terminals, mechanical or environmental damage to equipment, and to contain heat or arcs from escaping from the equipment in the event of equipment failure. This installation has a 480 volt motor starter that is missing it's cover. The equipment is energized and in an area where workers frequently have access to and work around. This is a shock and fire hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Shingle_press_machine.png | file://x:/photopub/docs/0000000345/6595406a-f252-4074-b932-b96c2809f493.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c09f9eb_2f43_44d3_af6c_70c333d4daa7
ELOP-465734-2015 | EL-298722-2015 | 10/29/2015 9:20:00 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Motor starters with energized terminals are required to have covers in place to prevent accidental contact with live terminals, mechanical or environmental damage to equipment, and to contain heat or arcs from escaping from the equipment in the event of equipment failure. This installation has a 480 volt motor starter that is missing it's cover. The equipment is energized and in an area where workers frequently have access to and work around. This is a shock and fire hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Shingle_press_machine_hydraulic_pump_motor_starter.png | file://x:/photopub/docs/0000000345/1f2277a7-8ab7-4934-a2c4-3fc6aad23113.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c09f9eb_2f43_44d3_af6c_70c333d4daa7
ELOP-465734-2015 | EL-298722-2015 | 10/29/2015 9:20:00 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Motor starters with energized terminals are required to have covers in place to prevent accidental contact with live terminals, mechanical or environmental damage to equipment, and to contain heat or arcs from escaping from the equipment in the event of equipment failure. This installation has a 480 volt motor starter that is missing it's cover. The equipment is energized and in an area where workers frequently have access to and work around. This is a shock and fire hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Motor_starter_cover_missing.png | file://x:/photopub/docs/0000000345/18e3d4f0-87f1-416a-bc5c-598a211b42d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c09f9eb_2f43_44d3_af6c_70c333d4daa7
ELOP-465734-2015 | EL-298722-2015 | 10/29/2015 9:20:00 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Motor starters with energized terminals are required to have covers in place to prevent accidental contact with live terminals, mechanical or environmental damage to equipment, and to contain heat or arcs from escaping from the equipment in the event of equipment failure. This installation has a 480 volt motor starter that is missing it's cover. The equipment is energized and in an area where workers frequently have access to and work around. This is a shock and fire hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Shingle_press_machine_.png | file://x:/photopub/docs/0000000345/561ee1e9-f2f3-49e8-9e17-5a2b42724cfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c09f9eb_2f43_44d3_af6c_70c333d4daa7
BPVOP-468119-2015 | 2252773 | 10/28/2015 10:44:47 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Minor_scale.png | file://x:/photopub/docs/0000000344/fe154e7d-14d2-4a2c-9e2b-634efaf82012.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fc2a37a_6530_4705_bde9_a13e906929a4
GAIN-457322-2015 | GA-295224-2015 | 10/27/2015 5:07:51 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Replacement furnace installed in an enclosure without outdoor combustion air supplied to room. The furnace was drawing its combustion air from the enclosure it was installed in. Without supplying outdoor combustion air to the enclosure the furnace could create a negative pressure environment causing other gas equipment to spill products of combustion into the living space possibly causing CO poisoning. | 4 | Combustion air supply missing | Furnace_combustion_air.png | file://x:/photopub/docs/0000000344/76b24f4f-3941-4499-a62c-bda22cae1837.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__268a7cba_3448_404b_b0c7_ae39a9a42a9d
GAIN-469303-2015 | GA-263250-2015 | 11/2/2015 4:18:05 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was a boiler (for heat and domestic hot water) which had been installed without the required pressure relief device on the domestic hot water side of the system. This is a hazard because in the event of an over pressure condition the system would be potentially subjected to pressures above their maximum allowable limits. | 4 | Missing mandatory safety controls | HTP_boiler.png | file://x:/photopub/docs/0000000347/ceb56329-84db-4c55-9a14-40539467570b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d676b55c_8145_4913_9c00_41664eab8ac4
GAIN-469313-2015 | GA-263252-2015 | 11/2/2015 4:18:16 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was a boiler (for heat and domestic hot water) which had been installed without the required pressure relief device on the domestic hot water side of the system. This is a hazard because in the event of an over pressure condition the system would be potentially subjected to pressures above their maximum allowable limits. | 4 | Missing mandatory safety controls | HTP_boiler_info.png | file://x:/photopub/docs/0000000347/e0d10b08-adb1-4e6d-9b52-c91488ff914a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3944499b_d6f7_40e8_bd97_da5d202ccfb7
ELIN-469671-2015 | UW-307257-2015 | 10/30/2015 8:51:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | Lighting equipment has been provided by two separate manufacturers and installed on a pair of sign support pylons . The sign is fed with a 100 amp 208 volt single phase tap from a 3 phase service on the property. None of the 5 separate signs bear evidence of approval. Electrical equipment that has not been evaluated for safe use and that is accessible to general public can present a safety risk to persons or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Dry_location_components_with_opening_to_sky_on_top_of_equipment.png | file://x:/photopub/docs/0000000347/596e1b2d-8c73-4b7e-8671-175ff4d92eaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1f836ae_b9da_43d3_ad48_7f1208ff6acf
ELIN-469722-2015 | UW-307305-2015 | 11/2/2015 8:51:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Factory mounting holes were not used to mount this weatherproof equipment. The main service switch rated 400 amps 240 volts, single phase is not splash proof and is mounted at grade. These installation errors can allow water to enter enclosures and promote unpredictable failure of equipment | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Holes_drilled_in_weatherproof_equipment_to_line_up_with_home_made_support_structure.png | file://x:/photopub/docs/0000000347/b15f7972-b150-4054-870f-24a4506153c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__453147d2_e338_4a48_bace_ffc7fef2dd23
ELIN-469671-2015 | UW-307257-2015 | 10/30/2015 8:51:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | Lighting equipment has been provided by two separate manufacturers and installed on a pair of sign support pylons . The sign is fed with a 100 amp 208 volt single phase tap from a 3 phase service on the property. None of the 5 separate signs bear evidence of approval. Electrical equipment that has not been evaluated for safe use and that is accessible to general public can present a safety risk to persons or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Extensive_communication_and_line_voltage_cabling_.png | file://x:/photopub/docs/0000000347/7af17127-4848-450a-965f-96a1c8252023.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1f836ae_b9da_43d3_ad48_7f1208ff6acf
ELIN-455765-2015 | EL-187375-2014 | 10/8/2015 7:55:18 AM | ASSESS: EL: Final | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Misuse of flexible cords, unused openings in energized equipment allowing access to connections, inappropriate access to equipment control panels and disconnecting means. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Openings_in_energized_lighting_fixtures__less_than_5feet_aff.png | file://x:/photopub/docs/0000000347/4f04ec30-098e-421a-91b8-25c63defa88c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87c2d2ec_9a28_4b8b_b7bb_a6dd5fd946a6
ELIN-455765-2015 | EL-187375-2014 | 10/8/2015 7:55:18 AM | ASSESS: EL: Final | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Misuse of flexible cords, unused openings in energized equipment allowing access to connections, inappropriate access to equipment control panels and disconnecting means. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Loose_cords_1.png | file://x:/photopub/docs/0000000347/3d6209fd-2fbb-4e19-a5be-e2bccc5619d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87c2d2ec_9a28_4b8b_b7bb_a6dd5fd946a6
ELIN-465307-2015 | EL-304323-2015 | 11/2/2015 9:39:48 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Service equipment is installed exposed to weather and not compliant as per section 76 requirements | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Non_weatherproof__service_equipment_exposed.png | file://x:/photopub/docs/0000000347/3ab8cfb2-88bd-4ffc-8ce4-03148a3d5dcb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a666bad5_c9d3_4173_a6a6_51362e837a17
ELIN-455765-2015 | EL-187375-2014 | 10/8/2015 7:55:18 AM | ASSESS: EL: Final | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | Misuse of flexible cords, unused openings in energized equipment allowing access to connections, inappropriate access to equipment control panels and disconnecting means. | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Misuse_of_cords1.png | file://x:/photopub/docs/0000000347/de83c011-c043-4754-bdc4-a1889c81b285.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87c2d2ec_9a28_4b8b_b7bb_a6dd5fd946a6
GAIN-466071-2015 | GA-196932-2014 | 10/26/2015 8:26:26 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Vent termination has not been installed correctly, too close to the soffit and combustion air inlet | 2 | Side wall vent termination not compliant with installation instructions | Vent_termination_.png | file://x:/photopub/docs/0000000344/14a2839f-9e5c-430d-bd18-82d3af787fc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8defb2_7703_4188_9c2a_5e2581b77042
GAIN-466070-2015 | GA-196930-2014 | 10/26/2015 8:26:34 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Boiler vent termination has been installed too close to soffit and combustion air inlet | 2 | Side wall vent termination not compliant with installation instructions | The_termination.png | file://x:/photopub/docs/0000000344/5ce76b18-8f46-423f-89e2-a84f56d8ea5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5fc4113_c12a_424d_9fbb_f0ab0c209dd2
BPVOP-464886-2015 | 2297090 | 10/26/2015 10:43:46 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found no safety device (Low Water Cutoff Device on a boiler) installed. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | SRV.png | file://x:/photopub/docs/0000000343/1fe7d35c-d647-4cd4-b619-368cc447d2e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15a1a779_f82a_4d15_b840_05b9d41056a7
ELIN-462282-2015 | UW-302182-2015 | 10/22/2015 5:10:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found existing meterbase located outdoors on pole has meter removed and has 2 sets of #10AWG sized copper single conductors energized and installed temporarily jumpering out the line side of lugs to load side terminals of meter-base. This conductor was used to feed power supply to an adjacent service panel on a pole. The energized conductors and meter-base bus bars are exposed and are an electrical fire or shock hazard to persons and property when meter and cover are removed. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Existing_meter_with_energized_exposed_conductors_on_meter_2.png | file://x:/photopub/docs/0000000345/985b507d-1add-415c-b67f-f30d6780b839.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260f408d_3716_468e_a6bd_c80f21e06828
ELIN-462282-2015 | UW-302182-2015 | 10/22/2015 5:10:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found existing meterbase located outdoors on pole has meter removed and has 2 sets of #10AWG sized copper single conductors energized and installed temporarily jumpering out the line side of lugs to load side terminals of meter-base. This conductor was used to feed power supply to an adjacent service panel on a pole. The energized conductors and meter-base bus bars are exposed and are an electrical fire or shock hazard to persons and property when meter and cover are removed. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Existing_meter_with_energized_exposed_conductors_on_meter_4.png | file://x:/photopub/docs/0000000345/5db5cb12-db2f-408a-a818-70604756a48c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260f408d_3716_468e_a6bd_c80f21e06828
ELIN-462282-2015 | UW-302182-2015 | 10/22/2015 5:10:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found existing meterbase located outdoors on pole has meter removed and has 2 sets of #10AWG sized copper single conductors energized and installed temporarily jumpering out the line side of lugs to load side terminals of meter-base. This conductor was used to feed power supply to an adjacent service panel on a pole. The energized conductors and meter-base bus bars are exposed and are an electrical fire or shock hazard to persons and property when meter and cover are removed. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Existing_meter_with_energized_exposed_conductors_on_meter_5.png | file://x:/photopub/docs/0000000345/63082695-8a75-4167-be3a-d688587ae56e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260f408d_3716_468e_a6bd_c80f21e06828
ELIN-468287-2015 | EL-306238-2015 | 10/29/2015 10:21:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary construction service equipment installed in unbraced wall not capable of being locked to prevent use by unauthorized persons. This results in a serious risk of personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Detail02_main_distribution_.png | file://x:/photopub/docs/0000000345/fd29aa17-cb3f-45b5-b8e0-5450c347a7f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4775c8e2_8172_4375_88da_52dd7a3cf025
BPVOP-463638-2015 | 2301173 | 11/2/2015 1:58:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Corrosion_.png | file://x:/photopub/docs/0000000347/bfb556bc-2337-4046-9cd5-8be993a4500a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4ebbf4a_f717_4d37_abda_290d8b0b8e55
BPVOP-463638-2015 | 2301173 | 11/2/2015 1:58:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Corrosion_1.png | file://x:/photopub/docs/0000000347/5621d2c2-7a73-4a3e-a3e2-4ce15fc6dfef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4ebbf4a_f717_4d37_abda_290d8b0b8e55
ELIN-468287-2015 | EL-306238-2015 | 10/29/2015 10:21:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary construction service equipment installed in unbraced wall not capable of being locked to prevent use by unauthorized persons. This results in a serious risk of personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_main_distribution.png | file://x:/photopub/docs/0000000345/825c5fa7-82e9-4e92-8c34-1b3d49c075b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4775c8e2_8172_4375_88da_52dd7a3cf025
ELIN-468439-2015 | EL-303963-2015 | 10/30/2015 3:31:43 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The installation of an 100 amp underground service without the required expansion joint could lead to settlement causing damage on the main service conductors | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 100_amp__underground_service.png | file://x:/photopub/docs/0000000346/92ad3fd9-c42b-4d62-9598-57dfad120c3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3af5897e_a3c0_4b12_88c9_df6aa4d4d302
ELIN-418336-2015 | EL-156583-2014 | 8/21/2015 11:40:22 AM | ASSESS: EL: Final | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Paint spray booth equipment and controls not installed to comply with the requirement for handouts locations creating a severe danger of explosion, fire, and physical injuries. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Air_solenoid_and_supply_piping_next_to_open_front_door.png | file://x:/photopub/docs/0000000346/b1d25ea8-d4a4-4bdb-b528-ec5d65164121.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aedcee7a_42e3_483f_ae14_42552e514693
ELIN-418336-2015 | EL-156583-2014 | 8/21/2015 11:40:22 AM | ASSESS: EL: Final | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Paint spray booth equipment and controls not installed to comply with the requirement for handouts locations creating a severe danger of explosion, fire, and physical injuries. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Paint_storage_mixing_room_lighting.png | file://x:/photopub/docs/0000000346/a9e9dee6-a7ce-4a60-85c9-9fe746c41b68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aedcee7a_42e3_483f_ae14_42552e514693
ELIN-418336-2015 | EL-156583-2014 | 8/21/2015 11:40:22 AM | ASSESS: EL: Final | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Paint spray booth equipment and controls not installed to comply with the requirement for handouts locations creating a severe danger of explosion, fire, and physical injuries. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Front_face_of_spray_booth.png | file://x:/photopub/docs/0000000346/05cde40b-a05d-49a1-af8c-2519ad40cea5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aedcee7a_42e3_483f_ae14_42552e514693
ELIN-418336-2015 | EL-156583-2014 | 8/21/2015 11:40:22 AM | ASSESS: EL: Final | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Paint spray booth equipment and controls not installed to comply with the requirement for handouts locations creating a severe danger of explosion, fire, and physical injuries. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | Field_wiring_of_controls_and_fan_operations_.png | file://x:/photopub/docs/0000000346/3167c429-0b42-41f7-9d5b-839d99c29b00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aedcee7a_42e3_483f_ae14_42552e514693
ELIN-470712-2015 | EL-181425-2014 | 11/2/2015 2:47:16 PM | ASSESS: EL: Final | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found termination of feeder conductors in a junction box appeared to have inadequate amount of insulation tape applied to termination splicing of feeder conductors. Electrician on site showed how the conductor had shorted out and arc-faulted to junction box metal and caused an arc flash. When conductor termination splicing connections are made and are not fully insulated to properly cover the conductors to the equivalent insulation of conductors being terminated, an arc flash can occur and cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | JB_SPLICE_NOT_INSULATED_PROPERLY_1.png | file://x:/photopub/docs/0000000347/420bb0b9-1d79-4629-b1de-52fe9ca2f6ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1052ad50_4945_4747_bc4d_a9c65758fa11
ELIN-470712-2015 | EL-181425-2014 | 11/2/2015 2:47:16 PM | ASSESS: EL: Final | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found termination of feeder conductors in a junction box appeared to have inadequate amount of insulation tape applied to termination splicing of feeder conductors. Electrician on site showed how the conductor had shorted out and arc-faulted to junction box metal and caused an arc flash. When conductor termination splicing connections are made and are not fully insulated to properly cover the conductors to the equivalent insulation of conductors being terminated, an arc flash can occur and cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | JB_SPLICE_NOT_INSULATED_PROPERLY_3.png | file://x:/photopub/docs/0000000347/85cb52e7-7abc-4112-a74a-413d9193fb0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1052ad50_4945_4747_bc4d_a9c65758fa11
ELIN-470712-2015 | EL-181425-2014 | 11/2/2015 2:47:16 PM | ASSESS: EL: Final | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found termination of feeder conductors in a junction box appeared to have inadequate amount of insulation tape applied to termination splicing of feeder conductors. Electrician on site showed how the conductor had shorted out and arc-faulted to junction box metal and caused an arc flash. When conductor termination splicing connections are made and are not fully insulated to properly cover the conductors to the equivalent insulation of conductors being terminated, an arc flash can occur and cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | JB_SPLICE_NOT_INSULATED_PROPERLY_5.png | file://x:/photopub/docs/0000000347/c993867f-dd39-4023-8b15-819ff3c5ee2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1052ad50_4945_4747_bc4d_a9c65758fa11
ELIN-470712-2015 | EL-181425-2014 | 11/2/2015 2:47:16 PM | ASSESS: EL: Final | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found termination of feeder conductors in a junction box appeared to have inadequate amount of insulation tape applied to termination splicing of feeder conductors. Electrician on site showed how the conductor had shorted out and arc-faulted to junction box metal and caused an arc flash. When conductor termination splicing connections are made and are not fully insulated to properly cover the conductors to the equivalent insulation of conductors being terminated, an arc flash can occur and cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | JB_SPLICE_NOT_INSULATED_PROPERLY_6.png | file://x:/photopub/docs/0000000347/e54ead1f-8785-48ad-95e7-53d6e40c24f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1052ad50_4945_4747_bc4d_a9c65758fa11
ELIN-470712-2015 | EL-181425-2014 | 11/2/2015 2:47:16 PM | ASSESS: EL: Final | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found termination of feeder conductors in a junction box appeared to have inadequate amount of insulation tape applied to termination splicing of feeder conductors. Electrician on site showed how the conductor had shorted out and arc-faulted to junction box metal and caused an arc flash. When conductor termination splicing connections are made and are not fully insulated to properly cover the conductors to the equivalent insulation of conductors being terminated, an arc flash can occur and cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | JB_SPLICE_NOT_INSULATED_PROPERLY_2.png | file://x:/photopub/docs/0000000347/4cb2364b-e11e-484f-b974-1d5613f27fde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1052ad50_4945_4747_bc4d_a9c65758fa11
ELIN-470712-2015 | EL-181425-2014 | 11/2/2015 2:47:16 PM | ASSESS: EL: Final | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found termination of feeder conductors in a junction box appeared to have inadequate amount of insulation tape applied to termination splicing of feeder conductors. Electrician on site showed how the conductor had shorted out and arc-faulted to junction box metal and caused an arc flash. When conductor termination splicing connections are made and are not fully insulated to properly cover the conductors to the equivalent insulation of conductors being terminated, an arc flash can occur and cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | JB_SPLICE_NOT_INSULATED_PROPERLY_4.png | file://x:/photopub/docs/0000000347/22f1dcbd-8f4e-45ae-b166-a4397d9e3111.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1052ad50_4945_4747_bc4d_a9c65758fa11
BPVOP-469475-2015 | UW-307117-2015 | 10/29/2015 5:24:41 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Owner of regulated equipment are required to comply with Safey Orders. I found that this air receiver was in service since 1982 and never had an NDE performed, which is a requirement of the Safety Order. Potential exists for an incident due to a questionable condition of this air receiver. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Plate.png | file://x:/photopub/docs/0000000345/6f2f9411-c7bf-4f6d-b0c2-1900b4d9d4ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6900174c_3dcf_4224_8405_42af10a078ca
GAIN-452170-2015 | GA-047963-2013 | 10/26/2015 6:29:05 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | 6" b vent is oversized for single water heater input. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Oversized_chimney_.png | file://x:/photopub/docs/0000000343/298fd3d9-5494-40a1-bad3-8a60f04a9db7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7CB35797_5EF6_4ACB_BEA3_946A26FBDC94
GAIN-452161-2015 | GA-028755-2013 | 10/26/2015 6:29:17 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Reverse_grade_on_poorly_supported_piping_.png | file://x:/photopub/docs/0000000343/24b58975-34aa-4a05-881b-946248cc8883.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__EC04F584_3AD4_400B_9848_316C5B0EAC64
ELIN-468580-2015 | EL-168961-2014 | 10/29/2015 4:25:17 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 18m_span.png | file://x:/photopub/docs/0000000345/717c11e6-42a2-45ce-81c3-8baad9f65734.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__475bee55_6fc2_4195_95e8_97f4ea0d9d85
ELIN-468580-2015 | EL-168961-2014 | 10/29/2015 4:25:17 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Existing_building_attachment.png | file://x:/photopub/docs/0000000345/8633d61a-6cb8-445b-843b-aaf624167f9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__475bee55_6fc2_4195_95e8_97f4ea0d9d85
ELIN-468580-2015 | EL-168961-2014 | 10/29/2015 4:25:17 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Unsupported_cable.png | file://x:/photopub/docs/0000000345/edcca2aa-8abb-42f0-a51e-3cd3fc2420e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__475bee55_6fc2_4195_95e8_97f4ea0d9d85
ELIN-465119-2015 | EL-303226-2015 | 10/23/2015 8:23:23 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | -ground conductor terminated onto enclosure of service entrance equipment. The ungrounded conductor does not have a direct unimpeded path back to ground. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Pic_1.png | file://x:/photopub/docs/0000000343/904858a6-3829-4cb3-8d01-9429a424e5f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35cddd80_7f84_4bd4_bd15_7e2ab5f9b22b
BPVOP-468712-2015 | 4252384 | 10/23/2015 4:41:13 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve for the last 6 years on this air receiver. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_receiver_mounted_with_machine.png | file://x:/photopub/docs/0000000345/adda9e79-c13b-4adf-ba84-97d0989cc979.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ce1530f_6cfe_4c7c_acd8_523c9d5d0082
GAIN-462665-2015 | GA-297497-2015 | 10/27/2015 5:49:11 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Corrugated appliance connector used on commercial range installation. | 2 | Certified appliance connector installed but not approved for application | Appliance_connector_not_certified_for_commercial.png | file://x:/photopub/docs/0000000344/7e58bff6-17fc-409a-939a-a2973ba63e8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f19ed7c5_32d2_46c0_b284_2d7214d11901
GAIN-433532-2015 | GA-193469-2014 | 10/27/2015 5:48:52 AM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 | Vent terminations on natural venting appliances must extend 2 ft above any obstruction with in 10 ft. | 2 | Non compliant Type B Vent Clearance | Vent_terminations.png | file://x:/photopub/docs/0000000344/92c2c066-fcdd-4fb8-9033-2ec4cc93b999.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17385611_3cab_46f9_859c_dc177c38f3c7
ELIN-468580-2015 | EL-168961-2014 | 10/29/2015 4:25:17 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Daycare_side_attachment.png | file://x:/photopub/docs/0000000345/2a17e14f-e01f-4163-b6d9-c860107ecb41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__475bee55_6fc2_4195_95e8_97f4ea0d9d85
ELIN-450900-2015 | EL-157425-2014 | 10/27/2015 9:05:40 AM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 4 | Raceways enter a dwelling below grade. The raceways are not drained properly and can permit water to enter dwelling causing damage to property | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | DB2_at_pole_end_above_grade_and_10-20_meters_altitude_higher_than_basement_of_dwelling.png | file://x:/photopub/docs/0000000344/7f0bbcac-692d-4c20-b59c-b43c1ad7470f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de9a0b83_6551_4af2_85f7_da280bc7d61b
ELIN-450900-2015 | EL-157425-2014 | 10/27/2015 9:05:40 AM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 4 | Raceways enter a dwelling below grade. The raceways are not drained properly and can permit water to enter dwelling causing damage to property | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | DB_2_and_other_raceways_enter_basement_of_dwelling_with_elevation_loss_of_up_to_20_meterd.png | file://x:/photopub/docs/0000000344/7b237be0-6405-4e57-9c02-ceee3f547483.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de9a0b83_6551_4af2_85f7_da280bc7d61b
ELOP-468722-2015 | 5234898 | 10/28/2015 7:13:23 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables are required to be installed into connectors and properly supported to prevent damage to the cable and conductor insulation. This installation has multiple 480V, 3 phase armoured cables that have been pulled out of connectors. This is a potential shock and fire hazard if the insulation on the conductors is damaged and causes the conductors to fault on the metal connectors and boxes. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Cable_pulled_from_connector_.png | file://x:/photopub/docs/0000000345/6cfe77a9-01c8-467b-8f45-ca605f7212a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1e4290_76fb_4968_a755_c39611eeed85
ELOP-468722-2015 | 5234898 | 10/28/2015 7:13:23 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables are required to be installed into connectors and properly supported to prevent damage to the cable and conductor insulation. This installation has multiple 480V, 3 phase armoured cables that have been pulled out of connectors. This is a potential shock and fire hazard if the insulation on the conductors is damaged and causes the conductors to fault on the metal connectors and boxes. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 480V_3phase_teck_canle_pulled_from_connector.png | file://x:/photopub/docs/0000000345/55ef79cf-84ad-4e40-972d-aca05e4b9869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1e4290_76fb_4968_a755_c39611eeed85
ELOP-468722-2015 | 5234898 | 10/28/2015 7:13:23 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables are required to be installed into connectors and properly supported to prevent damage to the cable and conductor insulation. This installation has multiple 480V, 3 phase armoured cables that have been pulled out of connectors. This is a potential shock and fire hazard if the insulation on the conductors is damaged and causes the conductors to fault on the metal connectors and boxes. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Cable_pulled_from_connector.png | file://x:/photopub/docs/0000000345/20d44cdd-3832-4233-8395-69aed2e4f9b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc1e4290_76fb_4968_a755_c39611eeed85
ELIN-462204-2015 | EL-193519-2014 | 11/2/2015 6:09:32 PM | ASSESS: EL: Final | png | #asFound | EL220 | All Classes, All Zones Area is classified: equipment is not suitable for the area classification. | 4 | 4 | Equipment installed within a hazardous area must be approved for that location. Failure to do so could result in equipment failing to contain a blast as required resulting in a fire. | 4 | All Classes, All Zones Area is classified: equipment is not suitable for the area classification. | PVC_in_hazardous_area.png | file://x:/photopub/docs/0000000347/f4693133-26fb-40f4-acd9-8b234d3fff81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb97e7f2_c3d5_4cc9_948c_59f6003c3be7
ELIN-466265-2015 | EL-223917-2015 | 11/2/2015 6:09:16 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Junction box covers must be installed when circuits are energized. Failure to do so could result in inadvertent contact with live conductors and result in electric shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | NMS_below_1_5_m.png | file://x:/photopub/docs/0000000347/6a5a720f-913b-4622-8ec4-731a2e0e3425.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03aec0ce_08f2_4a8c_9fdd_8aef68a05be2
ELIN-466265-2015 | EL-223917-2015 | 11/2/2015 6:09:16 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Junction box covers must be installed when circuits are energized. Failure to do so could result in inadvertent contact with live conductors and result in electric shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Cable_under_trailer.png | file://x:/photopub/docs/0000000347/37d9a7ca-ea63-4df2-af09-311bb49f82a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03aec0ce_08f2_4a8c_9fdd_8aef68a05be2
ELIN-469245-2015 | 3342466 | 11/2/2015 6:08:59 PM | ASSESS: EL: Final | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Supply authority metering equipment must be accessible. Failure to provide access will frustrate attempts to read consumption meters. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Service_and_outbuilding.png | file://x:/photopub/docs/0000000347/5454f9c0-c3c2-4e40-b817-bbe10026c57d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20aba9c3_d901_444b_9dd5_c2b1292b9d35
ELIN-466265-2015 | EL-223917-2015 | 11/2/2015 6:09:16 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Junction box covers must be installed when circuits are energized. Failure to do so could result in inadvertent contact with live conductors and result in electric shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_junction_boxes.png | file://x:/photopub/docs/0000000347/4975dc40-4923-471f-90cc-5630091a1712.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03aec0ce_08f2_4a8c_9fdd_8aef68a05be2
ELIN-469696-2015 | EL-288674-2015 | 11/5/2015 8:02:24 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Where grounding-type receptacles are used in existing installations to replace the ungrounded type the grounding terminal shall be effectively bonded to ground or the branch circuit feeding the receptacles must be ground fault circuit interrupter protected. This is required to prevent a shock hazard in the event that a portable appliance or fixture has a fault that causes the metal parts to become energized. This installation has two receptacles in the eating area of a house that do not have their grounding terminals bonded to ground. Left uncorrected this is a potential shock hazard. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Unbonded_circuit_and_receptacle.png | file://x:/photopub/docs/0000000349/192bbc97-dda2-4f13-b827-f489478b5871.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e15d9ec_50f7_4bf2_afcd_51c8e13eef00
GAIN-473974-2015 | GA-194425-2014 | 11/5/2015 5:14:40 PM | ASSESS: GA: Rough-In | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system which had been installed without the use of appropriate fittings to transition between two different sizes of vent piping. Tape had been used to attempt to seal up the large gaps between the two vent pipes. This was a hazard because the tape is not meant for this application and had warped and come off allowing flue products to escape through the openings in the venting system into the mechanical room. High potential risk of carbon monoxide poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Vent_pic2.png | file://x:/photopub/docs/0000000349/40dabfde-e88e-4365-b087-535c21600df7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c8dad67_3e5b_457b_9225_82cfc993bec2
GAIN-473974-2015 | GA-194425-2014 | 11/5/2015 5:14:40 PM | ASSESS: GA: Rough-In | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system which had been installed without the use of appropriate fittings to transition between two different sizes of vent piping. Tape had been used to attempt to seal up the large gaps between the two vent pipes. This was a hazard because the tape is not meant for this application and had warped and come off allowing flue products to escape through the openings in the venting system into the mechanical room. High potential risk of carbon monoxide poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Boiler1.png | file://x:/photopub/docs/0000000349/9a39691a-3624-41f7-bd6a-8dbf93e9c25e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c8dad67_3e5b_457b_9225_82cfc993bec2
GAIN-473974-2015 | GA-194425-2014 | 11/5/2015 5:14:40 PM | ASSESS: GA: Rough-In | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system which had been installed without the use of appropriate fittings to transition between two different sizes of vent piping. Tape had been used to attempt to seal up the large gaps between the two vent pipes. This was a hazard because the tape is not meant for this application and had warped and come off allowing flue products to escape through the openings in the venting system into the mechanical room. High potential risk of carbon monoxide poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Boiler_Pic2.png | file://x:/photopub/docs/0000000349/130af5cb-c731-495a-9468-506ba8ce919f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c8dad67_3e5b_457b_9225_82cfc993bec2
GAIN-473974-2015 | GA-194425-2014 | 11/5/2015 5:14:40 PM | ASSESS: GA: Rough-In | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The as found hazard was a venting system which had been installed without the use of appropriate fittings to transition between two different sizes of vent piping. Tape had been used to attempt to seal up the large gaps between the two vent pipes. This was a hazard because the tape is not meant for this application and had warped and come off allowing flue products to escape through the openings in the venting system into the mechanical room. High potential risk of carbon monoxide poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Vent_pic.png | file://x:/photopub/docs/0000000349/c79c6b33-4218-4a42-87cc-ad0cb9c9a5db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c8dad67_3e5b_457b_9225_82cfc993bec2
ELIN-474712-2015 | EL-250995-2015 | 11/9/2015 3:37:02 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Holes in live panels are required to be filled because this is a shock hazard. People could come into contact with the live parts of the panel if the holes are not closed properly. This is also a fire hazard. Short circuits (faults) can cause extreme heat that ionizes the air creates a condition called an Arc Flash. Temperatures of Arc Flashes can be as hot as the sun and vaporize copper. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | C.png | file://x:/photopub/docs/0000000350/554e5d7c-596e-40f9-8490-d94192cef061.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff1c994a_16ca_4da2_9bcd_f7f09cbd664b
ELIN-473845-2015 | UW-306337-2015 | 11/5/2015 3:36:36 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 3 | Hydro pole appears to have shifted or lean. This has pulled the point of attachment off of the service mast. This is a fire hazard as the splices may become stressed causing hot spots. The pole is a class 2 LPP, Installed 1995. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | A.png | file://x:/photopub/docs/0000000350/84990e3d-df74-49b2-9075-4bd8d589fadc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d671f76_3403_4085_b4b0_50f3ff56ab4a
ELIN-474562-2015 | EL-309974-2015 | 11/9/2015 3:37:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Armoured cable not properly terminated. The locknut on the tech connector should be tight and in good contact with the enclosure. This is a fire hazard, if a fault occurs a poor connection at the meter base could cause a hotspot. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | B.png | file://x:/photopub/docs/0000000350/10ddd51d-59e1-4940-875e-54d64b3953a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc17a4c1_e41b_469e_b931_283a456f2de6
ELIN-466257-2015 | EL-244142-2015 | 11/7/2015 6:33:46 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Circuits must not be loaded such than the capacity of conductors is exceeded. Failure to do so could result in an overheating situation on the cable. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Panel_directory_loads_combined.png | file://x:/photopub/docs/0000000350/4259283f-e00b-4e4a-8d67-2869e25eea9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4a79348_f90f_4c73_a9bd_6842cfe049e1
ELIN-474829-2015 | UW-136403-2014 | 11/9/2015 4:18:38 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | A system ground conductor must be continuous. Unapproved joints could result in an inadvertent open circuit on that conductor resulting in unintended voltages on the service or a possible inability of the system to react to a short circuit. | 4 | Installation Grounding; conductor is not continuous. | Joint_in_ground_conductor.png | file://x:/photopub/docs/0000000350/c67be27d-53a6-4296-862b-ffc95004d4c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20f69212_9e82_4490_9c43_7554d12a5cb1
ELIN-423790-2015 | UW-277460-2015 | 11/7/2015 4:18:38 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | A system ground conductor must be continuous. Failure to do so could result in accidental failure of unapproved joints or splices resulting in inadvertent undesirable voltages on the system or an inability by the system to detect and defend against a short circuit. | 4 | Installation Grounding; conductor is not continuous. | Ground_joint.png | file://x:/photopub/docs/0000000350/27084b51-9725-431a-b7eb-2cb1794552c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dbdfae07_a99e_4f1d_97c6_a39312bd2110
ELIN-465871-2015 | EL-231370-2015 | 11/4/2015 3:57:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Live panel boards must have covers installed. Failure to do so could result in shock hazard or a panel may not contain a blast in case of a short circuit. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Open_panel_in_basement.png | file://x:/photopub/docs/0000000348/5c9f1a0e-76af-4287-b856-f3e162afc73c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d249b848_5d16_4100_9675_dc433619aed0
BPVOP-474389-2015 | 2860755 | 11/6/2015 1:07:30 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP201 | 5.1.0 In service proc/process - Burner setup incorrect | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Burner setup incorrect | Morrison_furnace_soot_.png | file://x:/photopub/docs/0000000349/d1c84728-6cfc-4377-aa1e-6eb4f64823ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4de59c68_5b56_4ff7_b43b_2648d8d80b7f
ELIN-471504-2015 | EL-175294-2014 | 11/9/2015 2:27:38 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | The original installation of a service mast into the service switch was done incorrectly, allowing condensation in the service mast to travel down the conductors and corroding all of the service switch components. Unpredictable failure of this damaged equipment could cause property damage. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Jury_rigged_fuseholder_block_from_previous_repair.png | file://x:/photopub/docs/0000000351/55d92657-f25c-4702-9017-4e31b286b9c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9a7c697_f768_4692_891c_3b48ee6a8eeb
ELIN-469169-2015 | 5294742 | 11/5/2015 7:12:06 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live exposed wiring is outdoor and can be accessed by a tall person standing on the ground and causing possible shock. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Nocove1.png | file://x:/photopub/docs/0000000349/49ce5018-4ad4-485c-bace-13483ee321ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5f9e04_5397_4aee_aa74_cd7bf807dd6b
ELIN-469169-2015 | 5294742 | 11/5/2015 7:12:06 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live exposed wiring is outdoor and can be accessed by a tall person standing on the ground and causing possible shock. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | nobox1.png | file://x:/photopub/docs/0000000349/b7996d59-68bd-4a22-9430-6fe50a6eb975.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5f9e04_5397_4aee_aa74_cd7bf807dd6b
ELIN-469169-2015 | 5294742 | 11/5/2015 7:12:06 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Live exposed wiring is outdoor and can be accessed by a tall person standing on the ground and causing possible shock. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | nocover2.png | file://x:/photopub/docs/0000000349/849cb148-537e-4d15-91ce-785741a53726.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5f9e04_5397_4aee_aa74_cd7bf807dd6b
ELIN-469696-2015 | EL-288674-2015 | 11/5/2015 8:02:24 AM | ASSESS: EL: Final | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Where grounding-type receptacles are used in existing installations to replace the ungrounded type the grounding terminal shall be effectively bonded to ground or the branch circuit feeding the receptacles must be ground fault circuit interrupter protected. This is required to prevent a shock hazard in the event that a portable appliance or fixture has a fault that causes the metal parts to become energized. This installation has two receptacles in the eating area of a house that do not have their grounding terminals bonded to ground. Left uncorrected this is a potential shock hazard. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Unbonded_circuit_and_receptacle_in_the_kitchen_eating_area.png | file://x:/photopub/docs/0000000349/95ae0d32-8ba1-4e77-8ee6-e9d2225a1b7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e15d9ec_50f7_4bf2_afcd_51c8e13eef00
ELIN-462590-2015 | EL-299950-2015 | 11/5/2015 12:53:10 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The 120/240 volt 100amp single family dwelling Gas line is not bonded to ground | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_line_in_basement.png | file://x:/photopub/docs/0000000349/48c19047-4ece-4b77-b601-71e39210f22d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e8651c6_226f_4388_924a_6f9b05b039f7
ELIN-471052-2015 | EL-243943-2015 | 11/4/2015 1:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Two 120 volt, 14/2non-metallic sheathed cables have been terminated in a track light connection end kit. The track light connection end kit is not approved to have more than one entry wire feed for power. This poses a potential equipment and fire hazard exists, and the manufacturers specifications have also been disregarded. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Track_light.png | file://x:/photopub/docs/0000000348/999221f9-4980-42e3-8830-38816ace8061.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25514812_6272_4dd7_acc8_a3d2b0daafbe
ELIN-459819-2015 | EL-157425-2014 | 11/5/2015 8:19:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Raceways installed come downhill from the gate and Pole service 10 - 20 meters elevation loss directly into the basement of this dwelling. Electrical raceways for utilities or other systems may leak water into the dwelling and typically are not water tight, particularly over time due to settling. Damage to the dwelling will occur when the raceway integrity fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Raceways_enter_house_below_grade.png | file://x:/photopub/docs/0000000349/ac9e3bd2-26d6-4cbc-9588-c64a230af05c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2967ecb8_cd01_4a67_8763_900e1517bf9b
ELIN-469986-2015 | EL-305301-2015 | 11/4/2015 7:53:43 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Water entering the service panel. System safety ground conductor termination wasn't tighten properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Partial_missing_service_entrance_section_barrier.png | file://x:/photopub/docs/0000000348/05971459-2e01-4b71-927b-ff761c4319f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2e520c_7dfa_45fe_8671_290b6149acac
ELIN-469986-2015 | EL-305301-2015 | 11/4/2015 7:53:43 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Water entering the service panel. System safety ground conductor termination wasn't tighten properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_dripping_off_of_neutral_conductor_inside_the_panel.png | file://x:/photopub/docs/0000000348/ba88bb08-8a72-44bf-bd83-718ee6dbe7b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2e520c_7dfa_45fe_8671_290b6149acac
ELIN-469986-2015 | EL-305301-2015 | 11/4/2015 7:53:43 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Water entering the service panel. System safety ground conductor termination wasn't tighten properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_weather_sealant_on_service_conduit_nipple.png | file://x:/photopub/docs/0000000348/d42c70a8-d56a-46e7-9b32-b28a674d043b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2e520c_7dfa_45fe_8671_290b6149acac
ELIN-469986-2015 | EL-305301-2015 | 11/4/2015 7:53:43 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Water entering the service panel. System safety ground conductor termination wasn't tighten properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Wooden_wedges_used_to_mount_meter_base.png | file://x:/photopub/docs/0000000348/dcbc5be1-5084-42c5-895f-af0a6c0f7c82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2e520c_7dfa_45fe_8671_290b6149acac
ELIN-469986-2015 | EL-305301-2015 | 11/4/2015 7:53:43 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Water entering the service panel. System safety ground conductor termination wasn't tighten properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_head_approx_1meter_above_point_of_attachment.png | file://x:/photopub/docs/0000000348/553d2327-a5d3-40c0-859f-5265b2874beb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2e520c_7dfa_45fe_8671_290b6149acac
ELIN-469986-2015 | EL-305301-2015 | 11/4/2015 7:53:43 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Water entering the service panel. System safety ground conductor termination wasn't tighten properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_pooling_on_main_breaker_1.png | file://x:/photopub/docs/0000000348/71939454-9c81-4076-a35e-4f859d48b98b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2e520c_7dfa_45fe_8671_290b6149acac
ELIN-494047-2015 | EL-308998-2015 | 12/14/2015 7:35:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The 50KVA 240-600 volt step up transformer has the bonding conductors terminated on and with the secondary identified conductor/grounding XO point. This has isolated the transformer enclosure from an effective bonding connection therefore can create a Shock Hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Step_up_transformer.png | file://x:/photopub/docs/0000000366/7523e978-560c-4e99-b2c8-97ab87f8aba7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bd30ad1_727a_43d1_99a2_37e61b2e49c8
ELIN-472284-2015 | EL-282661-2015 | 11/4/2015 6:56:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | 120 volt, 14 AWG non-metallic sheathed cable not terminated into a bath fan junction box. This is a thermal hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Conductor_not_entered_into_box.png | file://x:/photopub/docs/0000000349/90c63c60-b388-4637-8146-c659ff6337f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2bf73d1d_c884_4705_b17e_f720aae80e9e
ELIN-493009-2015 | EL-261571-2015 | 12/11/2015 7:46:10 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A 600 amp, 120/240 volt overhead service attachment point does not have a guy support installed. Parallel runs of 500 kcm RW90 are installed for the service connection point. The cantilever load may exceed 270 kg. This could lead to equipment failure and a shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Attachment_point_not_approved_.png | file://x:/photopub/docs/0000000365/0a90e2d5-813d-4a7f-be99-ff8922a7adcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddb623b3_81d2_4aed_9158_2279f3de0657
ELIN-493036-2015 | EL-321299-2015 | 12/10/2015 7:45:43 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | 120/240 volt 125 amp load center has unused opening in breaker cover which exposes the live bus bars. This is a thermal hazard. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Unused_opening_in_panel.png | file://x:/photopub/docs/0000000365/4965bf76-c08b-4bad-908f-80b99272853b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cf5c7db_649b_4bf0_b22f_6d265688cc68
ELIN-475333-2015 | EL-310361-2015 | 11/10/2015 10:06:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Circuit breaker knock out fillers and electrical panel knockout fillers were missing from the electrical panel this could cause someone to accidentally make contact with the live electrical busbars located behind the electrical panel or it is possible that water would infiltrate into the electrical panel and cause a short circuit. Electrical point of attachment is not located 6 to 12 inches below The weather head, rain does not have the ability to shead off the service conductors | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Circuit_breaker_fillers_missing-_breakers_miss_aligned.png | file://x:/photopub/docs/0000000351/6b1ad191-18a0-46de-bdc5-88c6432b0063.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca071607_54cf_46c2_b822_deb6f3bc417b
ELIN-475333-2015 | EL-310361-2015 | 11/10/2015 10:06:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Circuit breaker knock out fillers and electrical panel knockout fillers were missing from the electrical panel this could cause someone to accidentally make contact with the live electrical busbars located behind the electrical panel or it is possible that water would infiltrate into the electrical panel and cause a short circuit. Electrical point of attachment is not located 6 to 12 inches below The weather head, rain does not have the ability to shead off the service conductors | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Point_of_connection_6-12_inches_below_weather_head.png | file://x:/photopub/docs/0000000351/05487a14-aeb0-4c67-acb1-e7f933dd12d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca071607_54cf_46c2_b822_deb6f3bc417b
ELIN-475333-2015 | EL-310361-2015 | 11/10/2015 10:06:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Circuit breaker knock out fillers and electrical panel knockout fillers were missing from the electrical panel this could cause someone to accidentally make contact with the live electrical busbars located behind the electrical panel or it is possible that water would infiltrate into the electrical panel and cause a short circuit. Electrical point of attachment is not located 6 to 12 inches below The weather head, rain does not have the ability to shead off the service conductors | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Panel_fillers_missing.png | file://x:/photopub/docs/0000000351/ba663039-b711-4a8e-8526-6248abc339b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca071607_54cf_46c2_b822_deb6f3bc417b
ELOP-195736-2014 | 1198 | 11/5/2015 6:33:28 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Wiring fittings must be maintained to ensure accidental contact with live parts is minimized. Failure to do so could result in accidental shock. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Water_heater_connector_missing.png | file://x:/photopub/docs/0000000349/f3862f33-893f-499f-b7c1-bbe1dd28c16d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ee4428a_be83_4415_a21f_a998270bd601
ELOP-226726-2014 | 4020434 | 11/5/2015 6:34:02 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Sewage processing facilities can be designed to operate with constant air pressure to contain gases. Failure to do so could result in early equipment failure. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Cabinet_deteriorated.png | file://x:/photopub/docs/0000000349/9e69a0cb-86f2-43d0-af86-f0a56ce9a5c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ec7bcfc_d3d4_4410_ae6c_d3b953d3763d
ELIN-469814-2015 | EL-237453-2015 | 11/3/2015 7:27:55 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | 120 volt 15/20 amp receptacles in a residential application not tamper resistant. This is a shock hazard. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Receptacles_not_tamper_resistant.png | file://x:/photopub/docs/0000000348/485d3661-2b1b-466e-873c-580c6e704cb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc9ebf7d_45b6_45a5_b0d6_49485d1d5086
ELIN-471231-2015 | EL-292466-2015 | 11/6/2015 10:26:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Adequate means of protection from mechanical damage for the PVC portion of the service raceway has not been provided for in this installation. This could result in personal injury (shock) or property damage (thermal event) due to mechanical damage to the service raceway and the energized conductors contained within. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Detail01_service_conduit.png | file://x:/photopub/docs/0000000350/924e5d85-37cf-4abc-821f-d38acf88217f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33fd5ade_360d_4bfb_a970_72ac01a08dd6
ELIN-474711-2015 | EL-306884-2015 | 11/12/2015 3:12:59 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 4 | There is an exposed conductor energized at 120 volts. This would cause electric shock to anyone coming into contact with it. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Exposed_energized_conductor.png | file://x:/photopub/docs/0000000352/a9afe842-b99c-444b-8e2f-f2457df4f280.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c77a89a4_7e50_4826_8b12_f856ab07e096
GAIN-467729-2015 | GA-305898-2015 | 11/10/2015 10:11:29 AM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 |  | 2 | Appliance installed in a proposed hazardous location | Roofladder.png | file://x:/photopub/docs/0000000352/c69d32b2-3ddd-4555-9f34-db39743bfeda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ded8456_94c7_4729_95be_20fc5c9b1409
ELIN-469595-2015 | EL-293018-2015 | 11/3/2015 8:14:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Open breaker spaces in energized panels are required to be filled to prevent accidental contact with energized parts of the panel, to protect the interior of the panel from mechanical damage, and to contain thermal energy in the event of an electrical failure inside the panel. This installation has a 200A, 120/240V service panel on a new home construction site. The panel is energized and there is open breakers spaces in the panel cover. This is a potential shock hazard if a person or conductive object contacts the energized bus inside the panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | New_house_under_construction.png | file://x:/photopub/docs/0000000348/dcc8dd72-7248-4437-9ddf-cd2e75b4283c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9390f158_24d7_4d33_a863_bb28d5ceda89
ELIN-469595-2015 | EL-293018-2015 | 11/3/2015 8:14:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Open breaker spaces in energized panels are required to be filled to prevent accidental contact with energized parts of the panel, to protect the interior of the panel from mechanical damage, and to contain thermal energy in the event of an electrical failure inside the panel. This installation has a 200A, 120/240V service panel on a new home construction site. The panel is energized and there is open breakers spaces in the panel cover. This is a potential shock hazard if a person or conductive object contacts the energized bus inside the panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_breaker_spaces_in_panel.png | file://x:/photopub/docs/0000000348/10495a12-71e3-4022-b938-b4ae3f7c5073.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9390f158_24d7_4d33_a863_bb28d5ceda89
ELIN-472110-2015 | EL-295934-2015 | 11/4/2015 5:42:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System grounding conductor connected on load side of main system disconnecting means. This could result in failure of system protection measures leading to personal injury (shock) or property damage (thermal event). | 3 | Installation Grounding; Electrode or grounding conductor are not present. | View01_service_disconnect.png | file://x:/photopub/docs/0000000349/8d27bf3c-5425-4574-b862-f479de798328.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6b54b1a_87fb_4c1b_9538_2c9747997ce8
ELIN-469595-2015 | EL-293018-2015 | 11/3/2015 8:14:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Open breaker spaces in energized panels are required to be filled to prevent accidental contact with energized parts of the panel, to protect the interior of the panel from mechanical damage, and to contain thermal energy in the event of an electrical failure inside the panel. This installation has a 200A, 120/240V service panel on a new home construction site. The panel is energized and there is open breakers spaces in the panel cover. This is a potential shock hazard if a person or conductive object contacts the energized bus inside the panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_breaker_spaces_in_panel_.png | file://x:/photopub/docs/0000000348/190afe7d-788b-4c9e-8eac-cfc0f4bb4afc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9390f158_24d7_4d33_a863_bb28d5ceda89
PROP-472244-2015 | PR-065445-2013 | 11/5/2015 5:26:47 PM | ASSESS: PR OP: Annual | png | #asFound | PR033 | Defects found where the required strength may no longer exist. | 4 | 4 | On a chair lift (passenger ropeway) the ropes go over an assembly of grooved wheels (sheave assembly). The sheave assembly is used to guide & support the rope and this assembly is typically located at the top of the tower. The passenger carrier (in this case a chair) is attached to the rope, the carrier has to maintain clearance for safe operation. The side to side swing clearance of the carrier, in relation to the sheave assembly was found to be less than 15 degrees. A carrier swing clearance of less than 15 degrees is considered to be unsafe. There is an entanglement hazard between a swinging chair on a moving rope with the sheave assembly. This condition could result in significant damage to the carrier and passengers becoming crushed and/or ejected from their seat and fall from a significant height. | 4 | Defects found where the required strength may no longer exist. | Hanger_contacting_sheave_beam_at_12_degrees.png | file://x:/photopub/docs/0000000350/6cdec59a-9994-4e39-81e4-20e13955fc69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43381918_fe4e_4789_829b_898d47102908
PRIN-472192-2015 | PR-275972-2015 | 11/9/2015 4:45:16 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | The decelerating equipment (tires and drive belts) are not capable of providing deceleration control to fully loaded carriers. This results in a risk of carriers colliding or becoming derailed from the floor rails. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Decelerating_tires_where_carriers_were_slipping_through.png | file://x:/photopub/docs/0000000350/a2734ad3-d14f-402d-8b6f-72d007ae528f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1900419_cc96_4faa_87ba_0483c0cab420
ELIN-461457-2015 | EL-301788-2015 | 11/3/2015 4:06:41 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | A single-wide Mobile home, on its own private acre lot, with a 100amp single phase service was found to have 2 120volt 15amp circuits or wire endings, in their live condition (bare ended and circled over ready for connection) hanging out of their boxes. These are in the kitchen, on the counter-top at either side of the stove. This could lead to a dead short or an electrical shock, should someone accidently touch these. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Kitchen_GFCI2.png | file://x:/photopub/docs/0000000348/23d848c5-19b5-4076-a805-ca08f5d255c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca611973_d619_4ea3_8078_c18efea8ce47
ELIN-461457-2015 | EL-301788-2015 | 11/3/2015 4:06:41 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | A single-wide Mobile home, on its own private acre lot, with a 100amp single phase service was found to have 2 120volt 15amp circuits or wire endings, in their live condition (bare ended and circled over ready for connection) hanging out of their boxes. These are in the kitchen, on the counter-top at either side of the stove. This could lead to a dead short or an electrical shock, should someone accidently touch these. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | kitchen_GFCI.png | file://x:/photopub/docs/0000000348/9ad01918-e364-4326-b35d-fefcbd1d2c2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca611973_d619_4ea3_8078_c18efea8ce47
ELIN-474473-2015 | EL-298189-2015 | 11/9/2015 7:28:46 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Exposed receptacles terminals can cause shock by accidental contact by a person. | 0 | No Created Hazard Identified | Exposed-2.png | file://x:/photopub/docs/0000000351/893dd4c6-0dae-497f-a26b-d8e2be00e927.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__423fe6e0_7887_4273_b266_c6e2216a4e50
ELIN-474473-2015 | EL-298189-2015 | 11/9/2015 7:28:46 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Exposed receptacles terminals can cause shock by accidental contact by a person. | 0 | No Created Hazard Identified | Exposed-4.png | file://x:/photopub/docs/0000000351/679217c0-2bb4-464e-a24f-f8db4d46f83b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__423fe6e0_7887_4273_b266_c6e2216a4e50
ELIN-474473-2015 | EL-298189-2015 | 11/9/2015 7:28:46 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Exposed receptacles terminals can cause shock by accidental contact by a person. | 0 | No Created Hazard Identified | Exposed_-1.png | file://x:/photopub/docs/0000000351/af825848-bb2c-471b-bfd8-1efce6bb3322.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__423fe6e0_7887_4273_b266_c6e2216a4e50
ELIN-474473-2015 | EL-298189-2015 | 11/9/2015 7:28:46 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Exposed receptacles terminals can cause shock by accidental contact by a person. | 0 | No Created Hazard Identified | Exposed-3.png | file://x:/photopub/docs/0000000351/ad5be2fc-ce95-417d-a5c1-86607c3bac10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__423fe6e0_7887_4273_b266_c6e2216a4e50
ELIN-462661-2015 | EL-230600-2015 | 11/12/2015 4:59:20 PM | ASSESS: EL: Final | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 2 | 2 | 200 Amp 120/240 volt residential service. The service mast only has one attachment point visible. Possible equipment damage due to inadequate support. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Main_service_mast.png | file://x:/photopub/docs/0000000352/8330beb4-a2ce-4000-817e-75d06ba8d78d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7a8ccfe_a03f_4c3a_894d_c485ace5142f
ELOP-226720-2014 | 4020747 | 11/6/2015 5:52:17 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | A system ground must be installed at the first disconnect in the electrical service. In this installation the system ground was connected at the meter ahead of the first disconnect. Installing the system ground in a sealed meter enclosure means it cannot be checked or tested without attendance by the Utility. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Wrong_ground.png | file://x:/photopub/docs/0000000350/e76af1c5-e040-43e1-8cef-761f62ba0d70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6feb79e_2f96_4cfd_b349_31f0266703c0
ELOP-195898-2014 | 1210 | 11/6/2015 5:51:55 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL103 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | 3 | 3 | Conductors of mixed systems and voltages may not be combined in a common junction box. Failure to do so could result in accidental shock. | 3 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | 120_and_600.png | file://x:/photopub/docs/0000000350/b0dc55ba-794d-4f4a-b2d0-9da3e0202391.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0770366_a801_44e2_9500_dd156a96ca0d
ELOP-195646-2014 | 1228 | 11/6/2015 5:51:26 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Metallic gas lines must be bonded to ground. In this installation a propane storage facility feeding a permanent generator installation had not been bonded as required. Failure to do so could result in a potential for electric shock or fire. | 3 | Continuity Bonding conductor is not observed or broken | No_bond.png | file://x:/photopub/docs/0000000350/b9bea48e-eb0c-4591-861c-ecafd289d209.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__191cd32b_485f_40e0_9976_95090c30a69b
ELIN-476545-2015 | EL-311234-2015 | 11/12/2015 6:21:21 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Cables shall be required to be buried and marked with warning tape to ensure future safety for person/s from a shock hazard. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | ACWU_cable_u-grd_burial_.png | file://x:/photopub/docs/0000000352/6ae0036e-b7f6-49fb-bf5e-a7462c40fd98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78a3213a_273c_4682_a97c_b9fcbd25817d
GAIN-419111-2015 | GA-045846-2013 | 11/6/2015 6:48:42 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Observed 2 pound regulator installed in verticle position in drop pipe to furnace . There is no drip leg installed ahead of the regulator and the shut off valve is located on the wrong side of the regulator Should regulator fail 2 pound gas could effect the safe operation of the gas appliances. Control valves rated at 1/2 pound pressure could leak gas, improper combustion could produce carbon monoxide.. | 3 | Regulator vent not terminated as per manufacturers instruction | Kettle_Ave__Oliver.png | file://x:/photopub/docs/0000000350/f91fd4bb-34d6-49dd-b326-d9a1b9b3d6ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5d18b54_acd3_4a7e_a348_7353137a7516
GAIN-419111-2015 | GA-045846-2013 | 11/6/2015 6:48:42 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Observed 2 pound regulator installed in verticle position in drop pipe to furnace . There is no drip leg installed ahead of the regulator and the shut off valve is located on the wrong side of the regulator Should regulator fail 2 pound gas could effect the safe operation of the gas appliances. Control valves rated at 1/2 pound pressure could leak gas, improper combustion could produce carbon monoxide.. | 3 | Regulator vent not terminated as per manufacturers instruction | Kettle_Ave_Olliver.png | file://x:/photopub/docs/0000000350/6806c344-e9ce-4275-a952-ceb8ee02ad94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5d18b54_acd3_4a7e_a348_7353137a7516
ELIN-471504-2015 | EL-175294-2014 | 11/9/2015 2:27:38 PM | ASSESS: EL: Final | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | The original installation of a service mast into the service switch was done incorrectly, allowing condensation in the service mast to travel down the conductors and corroding all of the service switch components. Unpredictable failure of this damaged equipment could cause property damage. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Corroded_equipment.png | file://x:/photopub/docs/0000000351/177e2e7a-f4be-4133-ac11-edddc244385e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9a7c697_f768_4692_891c_3b48ee6a8eeb
ELIN-475494-2015 | EL-300809-2015 | 11/10/2015 2:58:07 PM | ASSESS: EL: Final | png | #asFound | EL175 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | 2 | 2 | car hoists do not have local disconnects for easy accessibility to de-energize power in case of equipment failure | 2 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | Car_hoist.png | file://x:/photopub/docs/0000000351/5faa58d2-33c0-49ba-9f97-7492da93340b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea529241_d345_40cd_8893_0ae89eb4fe69
GAIN-459305-2015 | GA-133671-2014 | 11/9/2015 4:09:42 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | The as found hazard was a venting system serving a new furnace which had not been assembled with the correct fittings where it passed through the appliance casing. This is a hazard because an incorrectly sealed venting system can allow products of combustion to escape into the appliance casing/living space. | 3 | Leaking or failing special venting system (Minor) | furnace.png | file://x:/photopub/docs/0000000351/ae2aca90-410e-4579-b577-e6c6e80de4a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ea5a98b_1593_4dde_9664_71bcb9c3c5ae
GAIN-459305-2015 | GA-133671-2014 | 11/9/2015 4:09:42 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | The as found hazard was a venting system serving a new furnace which had not been assembled with the correct fittings where it passed through the appliance casing. This is a hazard because an incorrectly sealed venting system can allow products of combustion to escape into the appliance casing/living space. | 3 | Leaking or failing special venting system (Minor) | vent_connection.png | file://x:/photopub/docs/0000000351/9b9cd9f9-8888-4ad3-bdf1-7db0f51e4d3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ea5a98b_1593_4dde_9664_71bcb9c3c5ae
ELIN-467697-2015 | EL-305913-2015 | 11/5/2015 2:47:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | The insulator required in the 120/240V service guy line is missing. Without the insulator the overhead lines are not properly isolated in the event of contact with the guy line by vehicles or persons this posses a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Pole_service.png | file://x:/photopub/docs/0000000349/38bbc985-290a-4594-94f7-c9a71378d405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a975681_f06d_405a_ba78_e8e677fda813
ELIN-461718-2015 | EL-300678-2015 | 11/5/2015 2:47:59 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 200A, 120/240V, 300ACWU service conductor has been damaged inside the Meterbase at the Service Pole when installed, if the damage is not repaired the cable could fail causing equipment damage and an electrocution hazard. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Cut_conductor.png | file://x:/photopub/docs/0000000349/6d10a556-a1d2-4c3f-a00a-0890b9b638da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__082a52bb_1445_490c_8469_4eea79d3a636
ELIN-461718-2015 | EL-300678-2015 | 11/5/2015 2:47:59 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 200A, 120/240V, 300ACWU service conductor has been damaged inside the Meterbase at the Service Pole when installed, if the damage is not repaired the cable could fail causing equipment damage and an electrocution hazard. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Bent_conductor.png | file://x:/photopub/docs/0000000349/c7f1ff44-02c0-40f3-9360-4cad3d45b3d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__082a52bb_1445_490c_8469_4eea79d3a636
BPVOP-474644-2015 | 4218886 | 11/4/2015 2:46:21 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | boiler_tubes_scale.png | file://x:/photopub/docs/0000000350/d09525ad-395e-4c5a-b03f-8f88f3319866.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05304732_6781_412e_8955_4fd1d38f31b0
BPVOP-474644-2015 | 4218886 | 11/4/2015 2:46:21 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | boiler_tubes_scale_2.png | file://x:/photopub/docs/0000000350/ae1f9f2f-4987-482e-8222-7f60ad69df9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05304732_6781_412e_8955_4fd1d38f31b0
ELIN-475863-2015 | EL-307036-2015 | 11/10/2015 5:43:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | A ground to neutral connection cannot be maker in a distributed load centre. Doing so provides a parallel path back to the main distribution for the unbalanced load. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | New_panel.png | file://x:/photopub/docs/0000000351/df6a6003-6eb6-487d-8f71-a777cc32c519.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da8e5104_247a_413c_bf2f_b397a34eba37
ELIN-474913-2015 | EL-239658-2015 | 11/10/2015 5:43:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Temporary installations must be approved for use in wet environments or enclosed in such a way as to protect the equipment from environmental damage. Failure to do so could result in catastrophic damage to the equipment and early failure. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel_open_to_elements.png | file://x:/photopub/docs/0000000351/f19af7d3-0dd3-4ad8-a4e1-04d77ffb997a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b0d5353_b3b9_477b_b781_a415262f720d
ELIN-475555-2015 | EL-275067-2015 | 11/10/2015 5:43:24 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL038 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | 3 | 3 | An operating permit is required for temporary construction power installations, and a declaration of compliance and service connection inspection request must be submitted before power is connected to a temporary installation. Failure to follow these procedures could result in a non complying installation being connected, and does not trigger an automatic permit expiry twelve months later. | 3 | Number of supply or consumer's services has been exceeded Number of Consumer services have been exceeded. | Connected_panel_and_receptacles.png | file://x:/photopub/docs/0000000351/3806fad6-57d0-4cda-a3bd-a2ee12176052.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6769b6f5_99a2_4d6e_89ae_3ca3eab9d1ec
ELIN-466259-2015 | EL-283443-2015 | 11/10/2015 5:43:34 PM | ASSESS: EL: Final | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 | Wiring and protective coverings must be continuous and approved for use it the environments in which they are installed. Failure to do so could result in thermal effects or shock hazards. | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | NMS_in_heater.png | file://x:/photopub/docs/0000000351/b0f27012-2b8a-472f-a2c8-7ff15e68f1a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f215299d_e1ac_4ff8_be42_b8bc3494cb5e
ELIN-475419-2015 | EL-283382-2015 | 12/8/2015 1:39:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 4 | Service conductors cross over roof peak within 2.5 m | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_conductors.png | file://x:/photopub/docs/0000000352/b72cd64c-5b57-4b95-894d-6491f2f16663.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__757624f0_47b1_4455_9116_69c644a4f2ad
ELIN-466337-2015 | EL-284404-2015 | 11/10/2015 7:01:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 15 amp, 120 volt outlet boxes greater then 100mm only supported on one side. This is a thermal hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Boxes_greater_then_100mm_supported_on_one_side_only.png | file://x:/photopub/docs/0000000351/c04b03b5-4544-4746-8629-f99fbab03140.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e0197a9_6a1b_4ab1_8857_d06b4c60bffd
ELIN-480731-2015 | EL-271834-2015 | 11/24/2015 6:53:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | A permit is required for new services. Fee schedules are provided. Failure to comply results in underpayment of fees for permits and inspections. | 0 | No Created Hazard Identified | New_service.png | file://x:/photopub/docs/0000000357/fd760dee-22e8-472e-8658-c696c5286417.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8ccb9d1_709e_4de3_94af_054faa096c43
ELIN-475498-2015 | EL-284294-2015 | 11/20/2015 11:42:13 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 3 | Homeowner had installed a 200 amp combination panel on what was intended to be a 100 amp service. The 200 amp breaker did not adequately protect the Underground cable which had been installed to supply the 100 amp service. If the load exceeded the capacity of this supply cable, overheating and cable insulation breakdown could occur causing thermal damage to the equipment. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 200_amp_main_breaker_does_not_protect_service_cable_as_installed_.png | file://x:/photopub/docs/0000000356/b2e23bca-4d64-4433-bef3-a655bee0b160.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9204c5d9_7faf_4e5c_93c1_65070091e88b
ELIN-476032-2015 | EL-158429-2014 | 11/20/2015 11:42:17 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | In a house under construction with the wiring roughed in, but not completed, the homeowner connected all the circuits to their breakers in the electrical panel before he had installed the plugs, switches and light fixtures. Though the breakers were turned off, the possibility exists for someone to inadvertently turn one on resulting in energized conductors being exposed to accidental contact and potential shock hazard for individuals. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Branch_circuits_terminated_on_breakers.png | file://x:/photopub/docs/0000000356/7fd01632-82a2-4c0f-850a-d556b50e98df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf9b8749_05e9_40ea_947f_ba635e8a8642
ELIN-476032-2015 | EL-158429-2014 | 11/20/2015 11:42:17 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | In a house under construction with the wiring roughed in, but not completed, the homeowner connected all the circuits to their breakers in the electrical panel before he had installed the plugs, switches and light fixtures. Though the breakers were turned off, the possibility exists for someone to inadvertently turn one on resulting in energized conductors being exposed to accidental contact and potential shock hazard for individuals. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | One_of_many_incomplete_branch_circuit_items.png | file://x:/photopub/docs/0000000356/ce2ac904-ebfd-4087-95ee-769aea076306.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf9b8749_05e9_40ea_947f_ba635e8a8642
ELIN-477306-2015 | EL-305975-2015 | 11/18/2015 8:47:27 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 2 | The ground conductor is terminated in the meterbase onto the case. This conductor is to be terminated in the service switch or panel onto the neutral bus. This could become a shock hazard to a person during a fault. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Meterbase.png | file://x:/photopub/docs/0000000354/57b0ca60-d191-4031-909c-10b6e9e2b8dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__daddfd43_44d2_47f7_8dfa_47494cfb5ad2
PRIN-478366-2015 | PR-247327-2015 | 11/13/2015 8:00:16 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | On a ropeway, the passenger carrier is attached to the wire rope (haul ropes) which moves and support it. This wire rope goes travels over an assembly of grooved wheels (sheave assembly) typically located at the top of a support tower. A switch (tower fault switch) is used to detect a derailment condition where the haul rope is no longer in contact with the sheave assembly. A derailment condition would actuate the tower fault switch, an announcement via a display screen (annunciate) would be made and the moving haul rope would be stopped. It was found that the tower fault switch would not annunciate upon activation. Upon disassembly it was discovered that the 2 conductors which lead to the switch had come into contact with each other inside the switch body. This "bridged" condition of the conductors, results in the tower fault switch becoming ineffective in detecting a derailment condition This could lead to the continued movement haul rope even after a derailment. This could result in major risk of inj | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Disassembled_switch_showing_condition_of_conductors_that_were_installed.png | file://x:/photopub/docs/0000000356/482b499a-cf87-493a-81f9-879239ec9844.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2ebe954_ef2d_4c82_a66d_d8b799fff7b7
GAIN-476495-2015 | GA-304590-2015 | 11/18/2015 3:43:31 PM | ASSESS: GA: Rough-In | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Exhaust vent piped with Incorrect venting material. Flue gas temperatures of this appliance may exceed the maximum temperatures allowed by the pipe manufacturer. Prolonged use may result in a damaged exhaust vent. | 3 | Unapproved venting material | Water_heater_venting_1.png | file://x:/photopub/docs/0000000354/1acce400-0561-403e-a957-b8c5d91068c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c103897_bf12_4f8b_a6a5_9f029b9d4e85
GAIN-469432-2015 | GA-228938-2015 | 11/13/2015 1:27:21 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Vent termination is too close to building opening. Flue products could be recirculated into building and possibly causing illness | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | vent_term.png | file://x:/photopub/docs/0000000353/7f6373d3-9bea-47b7-b696-0763ca2a6791.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa3eea2d_7ccd_4f66_af3c_1dd05e0ad2ad
ELIN-477305-2015 | EL-307032-2015 | 11/16/2015 12:21:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | The contractor entered a service connection request to BCSA and Hydro. The cable coming from the meter was coiled up and connected to a portable construction panel. This is an unfused service cable being used in a portable fashion. The cable is subject to damage and if energized presents a shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_cable.png | file://x:/photopub/docs/0000000353/0a353496-ff78-46ee-8faf-d7e95ddc29bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec7389f6_04f9_423c_aa9f_045f86af766f
ELIN-470332-2015 | EL-231037-2015 | 11/12/2015 11:17:49 AM | ASSESS: EL: Final | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | Two service grounding systems on the same building are not interconnected, a Shock hazard can be created due to an electrical fault coming in contact with ungrounded metal equipment. The attached picture shows 2 meters on the same wall, there is no bond wire run between these two services. | 3 | Continuity Multiple grounded systems are not interconnected. | 2_services.png | file://x:/photopub/docs/0000000352/adface44-9033-4612-9f93-094a5c8c7c08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92394e6e_1c92_495f_9a60_9d4294ae39a2
ELIN-474079-2015 | EL-309235-2015 | 11/10/2015 9:14:24 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | 16 gauge Flexible extension cord connected to 120 volt 15 amp outlet has been used as a substitute for permanent wiring and passes through wall of small shed on propriety Flexible cord can be damaged from mechanical, ultraviolet rays and weather and fail causing property damage. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_passes_through_wall_of_shed.png | file://x:/photopub/docs/0000000352/e086fd9d-f174-47db-a7ea-b8abd96f96e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f21354_d3ae_4673_8bde_da8d840cf508
ELIN-471502-2015 | EL-136768-2014 | 11/10/2015 9:14:31 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Expansion_joint_not_provided.png | file://x:/photopub/docs/0000000352/a22e79dc-a997-4cc5-91de-8bf4d9687b95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a518a8b9_0808_4fef_9107_80e78c977eaa
ELIN-477725-2015 | EL-312626-2015 | 11/19/2015 3:39:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 2 | Ground conductor is used to bond meter base first directly and not directly to grounded conductor. Fault current will flow to earth first and not to neutral and overcurrent devices. | 3 | Continuity Bonding; method for equipment is not adequate. | Ground_conductor_is_used_to_bond_meter_base.png | file://x:/photopub/docs/0000000355/f4c9c7d8-f5d1-42f8-94d9-cc6fe1642404.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5cc55ad_99aa_44f5_86b7_3a2ecafadb6b
ELIN-477725-2015 | EL-312626-2015 | 11/19/2015 3:39:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 2 | Ground conductor is used to bond meter base first directly and not directly to grounded conductor. Fault current will flow to earth first and not to neutral and overcurrent devices. | 3 | Continuity Bonding; method for equipment is not adequate. | Ground_conductor_passes_through_meter_base.png | file://x:/photopub/docs/0000000355/30e45f66-addb-4f96-b94e-897db331d76e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5cc55ad_99aa_44f5_86b7_3a2ecafadb6b
ELIN-475220-2015 | EL-239551-2015 | 11/19/2015 7:01:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Attachment_point_installed_above_service_head.png | file://x:/photopub/docs/0000000355/52d2a90c-7b28-4dcb-8b8f-ac47892a2d06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9b7dca6_9ffa_4f20_8cae_78c03aaa9012
ELIN-478674-2015 | EL-277397-2015 | 11/17/2015 9:45:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The grounding conductor was not terminated onto the neutral busbar, the grounding conductor however is required to be terminated at the neutral terminal., This will result in fault currents not being allowing to travel through to the ground plate. Knockout fillers are missing from the electrical panel, this will allow foreign objects such as insects to get within the electrical panel and cause damage. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_conductor_incorrectley_terminated__knock_out_fillers_missing.png | file://x:/photopub/docs/0000000353/2d7aa7c5-6211-44a7-a728-91528ed8b40a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19cb20f9_f939_4f0e_a9bb_0451312a66fd
ELIN-478678-2015 | EL-277397-2015 | 11/17/2015 9:44:46 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Grounding conductor was incorrectly terminated in the wrong spot in the electrical panel. This will result in fault currents not being able to go to ground and making all the elect electrical equipment at equal potential | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Inside_view__inside_view_of_electrical_panelgrounding_conductor__grounding_conductor_incorrectly_terminated.png | file://x:/photopub/docs/0000000353/5f20c79b-797a-48f2-a012-5565a66a2a2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ef8c5d1_2c24_4522_b0ce_abb1662680f4
ELIN-479178-2015 | EL-313045-2015 | 11/17/2015 8:54:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | No bond bushing and bond conductor installed at service equipment ( 3" metal nipples, hydro pull boxes). | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Pic2.png | file://x:/photopub/docs/0000000354/05b7c881-4134-4b78-bcfa-a29215608e6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__976f7228_5539_4b97_83bd_688454629e7f
ELIN-479178-2015 | EL-313045-2015 | 11/17/2015 8:54:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | No bond bushing and bond conductor installed at service equipment ( 3" metal nipples, hydro pull boxes). | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Pic1.png | file://x:/photopub/docs/0000000354/7f44b6ea-af01-4898-904f-c92c5fcbf651.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__976f7228_5539_4b97_83bd_688454629e7f
ELIN-475869-2015 | EL-286630-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors installed in exterior locations must be tightened properly in order to provide a weather tight seal to prevent water from entering electrical equipment. This installation has a service cable connector that as not tightened properly. As a result water is entering the service panel and coming in contact with conductors and terminations within the service panel. Left uncorrected wet connections may corrode and eventually create a fire hazard due to high resistance connections. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_entering_service_panel_through_LB_fitting.png | file://x:/photopub/docs/0000000353/d9c351a4-b3e1-44fd-aadf-43d8b26b40a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b75da6f3_8bdb_417b_8cf8_0dec06242d00
ELIN-478109-2015 | EL-309206-2015 | 11/18/2015 4:32:31 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Non metallic sheathed cable installed in a wet location and under 5' with no mechanical protection. This is a hazard because the cable is subject to damage. Also the cable is not rated to be in wet locations. It is also not resistant to sunlight. This will cause the insulation to breakdown prematurely which will expose the conductors creating a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | A.png | file://x:/photopub/docs/0000000354/d538d4ff-3767-4a00-8b62-998c1cf9eb76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__010a7399_b787_4bab_bbb4_d86ee8146a1b
ELIN-474198-2015 | EL-257846-2015 | 11/13/2015 12:39:20 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles within 1.5 meters of sinks are required to be ground fault circuit interrupter (GFCI) protected. This new house has a 15A, 120V bathroom receptacle that is not GFCI protected. When tested the receptacle shows "ungrounded". This is a potential shock hazard if the receptacle is not wired properly and the GFCI function does not trip when a person is getting a shock. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Bathroom_receptacle_incorrect_polarity_and_not_ground_fault_circuit_interrupter_protected_.png | file://x:/photopub/docs/0000000352/8634091f-b556-4352-bcec-2c27d4fdb010.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c39844da_ee6e_4ced_9af3_93781e212130
ELIN-475930-2015 | EL-216402-2015 | 11/16/2015 3:45:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | A new kitchen is missing required outlets for the counterspace. This would cause the use of any appliances to be centralized around the limited available outlets that have been roughed in creating a hazard. There is one only counter outlet wired with windows through to the end of the counterspace where the built in oven is to be installed. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_Counter_outlets.png | file://x:/photopub/docs/0000000353/9c4fda21-afff-4b7e-b8c9-d1fa76f954d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f27bf7af_17a4_47f0_8de7_4282e5576a23
ELIN-477880-2015 | EL-309737-2015 | 11/16/2015 7:17:39 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 15/20 amp 120 volt receptacles used for construction not protected by ground fault circuit interrupter. This may become a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Receptacles_not_GFCI_protected.png | file://x:/photopub/docs/0000000353/bf6f8880-287e-4d2b-b14d-1b29f055d464.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e7def09_50e0_48bc_bbec_30625a13cf67
ELIN-477826-2015 | EL-281516-2015 | 11/16/2015 7:16:38 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | 120/240 volt 200 amp service conductors exceed 1.5 meters within a building. This may result in equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_conductor_exceeds_maximum_length_within_building.png | file://x:/photopub/docs/0000000353/a4dfad2d-5ef6-498e-9643-4baeb513a3b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20cb17b8_65d0_4f47_9e81_4cdebe1876ff
ELIN-473339-2015 | EL-305397-2015 | 11/13/2015 11:53:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 2 | NonGFCI receptacles installed at panel in garage, when asked the FSR said he had installed 1 duplex GFCI receptacle. The hazard was created by persons unknown. The lack of GFCI protection could lead to a shock hazard IF someone plugged a metal tool into the circuit and did not use a grounded extension cord. The plug is accessible to all construction personnel, the reason this is flagged as a 3 reduced to 2 is because the Starlite hazard map does not have anything closely resembling a true valuation for the risk. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | GFCI_missing.png | file://x:/photopub/docs/0000000352/d90fece7-7c2e-4d9b-a926-f02827e2d0b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__350556e9_389c_4cbf_b480_58deabf30290
ELIN-478149-2015 | EL-279494-2015 | 11/20/2015 10:51:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The service cable rated 125 amps 240 volts was installed directly below slab at grade. Underground cable systems installed at grade are to be buried to minimum depths. When cables are not buried properly, cables can be damaged during renovations or other work in buildings in the future. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_at_grade_directly_below_or_in_concrete_floor.png | file://x:/photopub/docs/0000000355/3a6bc37e-d6e5-408f-a320-8a83c59623c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__829390dd_b485_464d_a3c9_1504461b194a
ELIN-469921-2015 | EL-279494-2015 | 11/20/2015 10:51:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The service cable rated 125 amps 240 volts was installed directly below slab at grade. Underground cable systems installed at grade are to be buried to minimum depths. When cables are not buried properly, cables can be damaged during renovations or other work in buildings in the future | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_slab_on_grade_directly_below_or_in_slab.png | file://x:/photopub/docs/0000000355/a6853619-a2cc-4627-bf8c-0c21322a4712.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ed797ab_588d_4b03_8dd5_563709591dfc
ELIN-459840-2015 | EL-239950-2015 | 11/14/2015 7:56:18 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Conductors not supported correctly and not high enough off the commercial parking lot. These conductors can be hit by larger commercial vehicles that deliver goods to the store. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Attachment.png | file://x:/photopub/docs/0000000353/4933f062-69bd-44ed-85b0-cea0689a5856.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8aafa06_990c_4709_917f_f91d41c28c4f
ELIN-475198-2015 | EL-292330-2015 | 11/13/2015 7:36:35 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Receptacle_for_heat_trace_not_GFCI.png | file://x:/photopub/docs/0000000353/c275fc23-7b3d-461f-b448-6d797f023651.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__454de1db_95e7_431a_92f0_0e811ed4cf6d
ELIN-475045-2015 | EL-306970-2015 | 11/13/2015 2:46:00 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | Each individual branch circuit is not clearly identified at the point the circuit is protected. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Main_panel_board_for_dwelling_.png | file://x:/photopub/docs/0000000352/3771e794-5940-459a-94ac-e9e358e89539.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a37f9177_108a_4efb_9b32_6a117142b1d1
ELIN-478602-2015 | EL-308326-2015 | 11/18/2015 8:17:03 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Shock hazard to construction workers. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No-gfci.png | file://x:/photopub/docs/0000000354/106e6c68-89fc-42b8-9884-21b00f84af6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8d5264_d6b5_43b7_afdc_76ad914ba40b
ELIN-478602-2015 | EL-308326-2015 | 11/18/2015 8:17:03 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Shock hazard to construction workers. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Open.png | file://x:/photopub/docs/0000000354/1bc30af6-7125-48ff-b4e9-a2abbce7c8fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8d5264_d6b5_43b7_afdc_76ad914ba40b
ELIN-478602-2015 | EL-308326-2015 | 11/18/2015 8:17:03 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Shock hazard to construction workers. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Weatherhead.png | file://x:/photopub/docs/0000000354/fb347709-c8d2-4385-840d-a0c21296b8cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a8d5264_d6b5_43b7_afdc_76ad914ba40b
ELIN-478445-2015 | EL-307125-2015 | 11/16/2015 4:43:42 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 2x 120volt 15amp receptacles are installed in open garage with no cover plates installed to offer protection. This could result in an accidental shock, should someone insert fingers or metal objects into box. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outlet_installed_with_no_cover.png | file://x:/photopub/docs/0000000353/be655149-d0d8-4198-9946-699b887bad66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a09f649_a555_45f3_9c9d_c3090f13f374
ELIN-462558-2015 | EL-212411-2015 | 11/16/2015 7:34:12 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Copper only lugs have aluminum wire installed. Conductors can overheat causing equipment or property damage. | 3 | General Equipment is not approved for the specific use | Copper_only_breaker.png | file://x:/photopub/docs/0000000353/3da9e820-b401-497b-9fd0-b97bb691b163.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9085347_0040_40b2_9590_c85c1c1450b5
ELIN-478090-2015 | EL-312876-2015 | 11/16/2015 10:43:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | An AC electrical system must be equipped with a connection to ground. In this case there was no system ground electrode installed. Failure to provide a system ground could result in unanticipated fluctuations in voltage at branch circuits and a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_ground.png | file://x:/photopub/docs/0000000353/a7b9aff7-139d-401c-8cb4-c11dc45d199d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f511b3db_6871_4ca4_b501_b1896d442073
BPVOP-477933-2015 | 4463192 | 11/5/2015 2:05:39 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for a fusible plug for the last 10 years on this steam boiler. Potential exists for the pressure relief device not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | fusible_plug_new.png | file://x:/photopub/docs/0000000352/e77ecea0-afd7-42c4-aee3-6578a95c24c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__697db8a8_5cfb_41ab_978a_d894de10bd2a
BPVOP-477933-2015 | 4463192 | 11/5/2015 2:05:39 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for a fusible plug for the last 10 years on this steam boiler. Potential exists for the pressure relief device not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | fusible_plug.png | file://x:/photopub/docs/0000000352/223dc714-72c6-4fbf-97ff-9c05b4f46efa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__697db8a8_5cfb_41ab_978a_d894de10bd2a
BPVOP-462916-2015 | 3584472 | 11/19/2015 10:45:28 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu /hr. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Pressure_relief_device__.png | file://x:/photopub/docs/0000000354/54add9d8-7a09-4eff-83fb-7b00fc03fb70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58d400e3_4e6b_4e5b_88d7_c865bd37a2ce
BPVOP-462916-2015 | 3584472 | 11/19/2015 10:45:28 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu /hr. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_.png | file://x:/photopub/docs/0000000354/8b229127-df4b-47cf-a3c9-827d51f9ade4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__58d400e3_4e6b_4e5b_88d7_c865bd37a2ce
BPVOP-462917-2015 | 3584473 | 11/19/2015 10:45:06 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu/hrs. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler.png | file://x:/photopub/docs/0000000354/4bab8b53-9f60-4052-a30f-9cba201f10a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084e3978_98c2_428f_bead_3f04ff918903
BPVOP-462917-2015 | 3584473 | 11/19/2015 10:45:06 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu/hrs. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Pressure_relief_device_.png | file://x:/photopub/docs/0000000354/a9ecdd6e-ed45-48a2-ab7b-9eda438d2398.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084e3978_98c2_428f_bead_3f04ff918903
BPVOP-462918-2015 | 3584474 | 11/19/2015 10:45:43 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu /hr. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | prd_.png | file://x:/photopub/docs/0000000354/c57ac9e3-bb6b-4915-877d-0c6fd5e0b9e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67668f17_33c7_4a26_9862_0bd3183971cd
BPVOP-462919-2015 | 3584475 | 11/19/2015 10:45:09 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu /hr. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Srv.png | file://x:/photopub/docs/0000000354/76c2dbab-4912-4a98-b800-c36912a7b3fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0d2a216_0960_4e25_a1de_8b6f13eda984
BPVOP-462919-2015 | 3584475 | 11/19/2015 10:45:09 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu /hr. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler__.png | file://x:/photopub/docs/0000000354/b1f2af2d-3f55-44ed-906a-d0bfdbebf0dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e0d2a216_0960_4e25_a1de_8b6f13eda984
BPVOP-462918-2015 | 3584474 | 11/19/2015 10:45:43 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve must match or exceed heating capacity of the boiler. I found that heat relieving capacity of the safety valve was less that what's required by 100000 Btu /hr. Pressure retaining components may overheat and rupture due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_1.png | file://x:/photopub/docs/0000000354/bec55d9c-669c-40d1-b51d-cbec10990592.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67668f17_33c7_4a26_9862_0bd3183971cd
ELOP-261769-2014 | 5289581 | 11/17/2015 9:40:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | Branch circuits TECK cables to iron working machines are not mechanically protected from the wall out to the machines and are on the floor. Damage from working materials is visible. TECK cable entering junction box is bent more than allowable radius and is broken at connector. TECK cables not supported in various areas including, but not limited to, the compressor area, infeed deck and iron working machines. TECK cables run on floor damaged by iron work | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | TECK_cable_damaged.png | file://x:/photopub/docs/0000000354/aef25c99-254a-4264-94c6-812095f4d3b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fced3ad1_f27e_4b03_9763_6d702b8190d1
ELIN-472967-2015 | EL-273819-2015 | 11/16/2015 4:23:20 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Contractor did not use provided knock out holes, made their own and did not install sealing rings to prevent water from entering outdoor panel and meterbase. This is a hazard because it could potentially cause a short. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Outdoor_rv_service.png | file://x:/photopub/docs/0000000353/d0b35eca-db9d-40d0-b959-b4ca3f5fa8ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0d8a2d2_0dac_4722_8d28_4224f229d332
PROP-419377-2015 | 2224077 | 11/17/2015 4:47:30 PM | ASSESS: PR OP: RAP | png | #asFound | PR013 | Defects found where the required mechanical integrity may no longer exist. May not be capable of providing support or retaining rope(s) | 4 | 3 | This ropeway utilizes a counterweight ("counterweight" a large mass hung in the vertical plane) connected to a return sheave (A large diameter, horizontally oriented, grooved wheel at the end of the lift) to provide a specified tension to the haul rope ("haul rope" the wire rope utilized in transporting the passenger carrying units). This counterweight height can be adjusted by the use of a winch and counterweight rope (A wire rope which is connected into the counterweight system). The connection of the winch to the counterweight system must be backed up with a safety device ahead of the winch so as to keep the tensioning system intact in the event of a failure or release of the winch. The safety device utilized, in this case, is an anchored wire rope strap which is connected ahead of the winch onto the counterweight rope by the use of 2 "U bolt clips" (A "U bolt clip" is a configuration of a U shaped bolt, a forged saddle and 2 nuts which surround the 2 mating wire ropes). In this case (1/2" diamet | 4 | Defects found where the required mechanical integrity may no longer exist. May not be capable of providing support or retaining rope(s) | Number_of_clips_used_on_safety_strap_not_meeting_manufacture_specification.png | file://x:/photopub/docs/0000000356/239f21fa-db51-44e5-bdfe-b5db162ba275.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1B705D0C_67A6_4510_806D_898F472B89E7
ELIN-481852-2015 | EL-024965-2013 | 11/20/2015 12:52:45 PM | ASSESS: EL: Final | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Multiple 20 amp 240 volt underground circuits feeding street lighting in strata title property installed using NMD 90 dry location use only cable. Underground installations are wet locations. Dry location cables when used in wet locations can fail leaving installations without power or cause damage to persons or property. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | NMD_90_cables_installed_underground_in_raceways__signs_of_damag.png | file://x:/photopub/docs/0000000355/fce815b1-45ef-42bb-b1ed-d36e9941228b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96761397_c59b_4b74_a4d0_4b7d8f350e8b
ELOP-261769-2014 | 5289581 | 11/17/2015 9:40:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | Branch circuits TECK cables to iron working machines are not mechanically protected from the wall out to the machines and are on the floor. Damage from working materials is visible. TECK cable entering junction box is bent more than allowable radius and is broken at connector. TECK cables not supported in various areas including, but not limited to, the compressor area, infeed deck and iron working machines. TECK cables run on floor damaged by iron work | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | TECK_radius_damage.png | file://x:/photopub/docs/0000000354/f5457ddb-7819-4e24-b69b-34d517f956db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fced3ad1_f27e_4b03_9763_6d702b8190d1
ELOP-261769-2014 | 5289581 | 11/17/2015 9:40:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | Branch circuits TECK cables to iron working machines are not mechanically protected from the wall out to the machines and are on the floor. Damage from working materials is visible. TECK cable entering junction box is bent more than allowable radius and is broken at connector. TECK cables not supported in various areas including, but not limited to, the compressor area, infeed deck and iron working machines. TECK cables run on floor damaged by iron work | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Tech_cable_damaged_2.png | file://x:/photopub/docs/0000000354/3b174cef-135f-474f-8cf4-1d3298a705ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fced3ad1_f27e_4b03_9763_6d702b8190d1
ELIN-472324-2015 | EL-263849-2015 | 11/23/2015 3:47:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The main service ground for this 200 amp 240 volt 1 phase service is connected to the panel enclosure with self drilling screw , no paint removed from the enclosure. When main system ground is not solidly connected to the main neutral, if a fault occurs it may not function as required and cause damage to persons or property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Main_ground_and_service_cable_bond_reversed.png | file://x:/photopub/docs/0000000356/b531d801-99aa-4252-8f77-90c43f6024be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__163eef0f_195f_400f_bd1e_3809459766c7
ELIN-480083-2015 | EL-314147-2015 | 11/19/2015 10:51:08 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | The feeder cable is undersized for the service installed which could create a thermal hazard should the service become overloaded | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Feeder_cable_to_building_panel.png | file://x:/photopub/docs/0000000355/3987fd5e-d59e-45ab-9cc7-1e90132a68e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64bf5d7b_78a8_486e_abe9_708df322bea9
BPVOP-476953-2015 | 2250851 | 11/12/2015 9:06:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler fire tubes are to be clear of deposits that could impede heat transfer to the surrounding fluid.I found excessive scale deposits on the surface of the fire tubes. This can lead to overheating and damaging the tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | water_side_tube_scale.png | file://x:/photopub/docs/0000000353/4ade2a4b-9caf-4dde-b7b6-82889cec5fcb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc47698d_5ec3_43d0_9d09_8694cbb571a6
BPVOP-476953-2015 | 2250851 | 11/12/2015 9:06:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler fire tubes are to be clear of deposits that could impede heat transfer to the surrounding fluid.I found excessive scale deposits on the surface of the fire tubes. This can lead to overheating and damaging the tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | tube_scale_deposits.png | file://x:/photopub/docs/0000000353/e2b52460-7102-4ead-953e-6c2deff43c1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc47698d_5ec3_43d0_9d09_8694cbb571a6
BPVOP-476953-2015 | 2250851 | 11/12/2015 9:06:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler fire tubes are to be clear of deposits that could impede heat transfer to the surrounding fluid.I found excessive scale deposits on the surface of the fire tubes. This can lead to overheating and damaging the tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | tube_scale_deposits_2.png | file://x:/photopub/docs/0000000353/db692503-590b-4144-b8a6-f52210907b30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc47698d_5ec3_43d0_9d09_8694cbb571a6
BPVOP-476953-2015 | 2250851 | 11/12/2015 9:06:13 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler fire tubes are to be clear of deposits that could impede heat transfer to the surrounding fluid.I found excessive scale deposits on the surface of the fire tubes. This can lead to overheating and damaging the tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | water_side_firtubes_manhole_.png | file://x:/photopub/docs/0000000353/a9a88a88-7480-4d17-9c66-2fd9dc45a2f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc47698d_5ec3_43d0_9d09_8694cbb571a6
ELIN-475903-2015 | EL-253005-2015 | 11/19/2015 3:54:57 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | The construction receptacles have no covers and they are energized. This could result in someone getting a shock if they touched the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Plug_for_construction_.png | file://x:/photopub/docs/0000000355/c332d876-6dd6-4237-be69-d261b412f472.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aeafd17_841f_4458_8b03_d016cb552e6c
ELIN-475903-2015 | EL-253005-2015 | 11/19/2015 3:54:57 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | The construction receptacles have no covers and they are energized. This could result in someone getting a shock if they touched the receptacle. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel.png | file://x:/photopub/docs/0000000355/cbc77e2a-b31e-4683-8d6e-8fc5c44d1d05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aeafd17_841f_4458_8b03_d016cb552e6c
ELIN-481553-2015 | EL-268344-2015 | 11/23/2015 9:56:36 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Branch circuitry that supplies receptacles installed in sleeping facilities of a dwelling unit not adequately protected by arc-fault circuit interrupter, increasing the risk of property damage (thermal event). | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | View01_main_distribution_A.png | file://x:/photopub/docs/0000000356/7624de4f-b6de-45e6-9711-55d6ae0a1d39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27a919b3_bffb_4cdf_a7ad_47ccb089b0d4
ELIN-480840-2015 | EL-280757-2015 | 11/19/2015 6:59:54 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused branch circuitry positions in main distribution panel not adequately closed to prevent contact with energized components. This presents a serious risk of personal injury (shock). | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | View01_main_distribution_A.png | file://x:/photopub/docs/0000000355/ad2622e4-3783-42ef-985f-ea97fd71b5e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__228c730f_15fd_4d5c_9c75_9760bca0c539
ELIN-480768-2015 | EL-307754-2015 | 11/19/2015 7:00:45 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected portion of consumer service cabling exceeds maximum allowable distance of 1.5m inside structure increasing the likelihood of mechanical damage occurring. This poses a risk of serious personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_main_distribution_B.png | file://x:/photopub/docs/0000000355/69dd5050-a7c3-42a7-9f37-383c1f8cfd76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__361776a6_f653_4611_ac7a_8933ce55c582
ELIN-480840-2015 | EL-280757-2015 | 11/19/2015 6:59:54 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused branch circuitry positions in main distribution panel not adequately closed to prevent contact with energized components. This presents a serious risk of personal injury (shock). | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Detail02_main_distribution.png | file://x:/photopub/docs/0000000355/00210bef-29ec-41cf-8007-36c70c2cabdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__228c730f_15fd_4d5c_9c75_9760bca0c539
ELIN-481527-2015 | EL-311186-2015 | 11/20/2015 5:26:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | Cables in contact with heating ducts will be operated than higher than rated 30 deg C temperatures, thus creating fire hazard. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Cable-1.png | file://x:/photopub/docs/0000000355/5383ed56-956e-43fa-88ab-f38e2d33f029.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b3e74d9_05c5_41a1_9c6f_ef790052dbc6
ELIN-481527-2015 | EL-311186-2015 | 11/20/2015 5:26:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | Cables in contact with heating ducts will be operated than higher than rated 30 deg C temperatures, thus creating fire hazard. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Cable-2.png | file://x:/photopub/docs/0000000355/c765b617-0d0a-446a-baa6-6d88ea29bb27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b3e74d9_05c5_41a1_9c6f_ef790052dbc6
ELIN-474998-2015 | EL-310640-2015 | 11/18/2015 6:56:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | A single family residence with a new 200amp 1phase 120/240volt overhead service mast assembly. The point of attachment and service conductors do not meet the required clearances. This could lead to equipment malfunction from excess snow load. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Overhead_mast.png | file://x:/photopub/docs/0000000354/a2ebc92e-b25e-41cd-b10b-1566889ed7e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab264878_0db8_443a_9060_87a5acf64721
ELIN-449178-2015 | EL-249590-2015 | 11/18/2015 6:57:08 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | At an industrial warehouse complex, a 120 volt 15 amp, emergency stop button was connected with flexible cord. Flexible cord is not approved for this application. This could result in unnecessary damage to the wiring which could lead to a shock or short circuit condition. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_in_permanent_installation_.png | file://x:/photopub/docs/0000000354/66e43c3f-670f-4bb6-9ceb-42cc9b87434e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccf4317b_c92f_4531_9c9f_df35be6b4efc
ELIN-473729-2015 | EL-309664-2015 | 11/17/2015 7:22:47 AM | ASSESS: EL: Service Connection | png | #asFound | EL034 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not located as close as practicable to point of conductor entry into building | 3 | 3 | Main service cable installed exceeds maximum length permitted for unfused conductors. Cables lacking effective overcurrent protection must be kept as short as possible to prevent damage that could result in property damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not located as close as practicable to point of conductor entry into building | 3_5_meters_service_cable.png | file://x:/photopub/docs/0000000354/46aab51c-3120-4aec-8759-984e7d89ee55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__485f77dd_e2ac_4160_adb0_c9b680e231a6
ELIN-475144-2015 | EL-151583-2014 | 11/18/2015 7:23:00 AM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 2 | EMT Connectors installed were not equipped with smoothly rounded throats or auxiliary bushings. Largest conductors emerging from the connectors noted, were rated 200 amps, 600 volts and connected to a 3 phase 4 wire distribution system. Conductors can be damaged due to exposure to sharp edges in contact with conductors and cause conductor, equipment or property damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | No_bushings_2.png | file://x:/photopub/docs/0000000354/69129f43-6880-4af0-aea7-81028909a203.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f33cfdf_1cb3_49a8_bd71_56524d90ce16
ELIN-475144-2015 | EL-151583-2014 | 11/18/2015 7:23:00 AM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 2 | EMT Connectors installed were not equipped with smoothly rounded throats or auxiliary bushings. Largest conductors emerging from the connectors noted, were rated 200 amps, 600 volts and connected to a 3 phase 4 wire distribution system. Conductors can be damaged due to exposure to sharp edges in contact with conductors and cause conductor, equipment or property damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | No_bushings_1.png | file://x:/photopub/docs/0000000354/c2b00628-2f10-4761-be11-e86823b2ef10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f33cfdf_1cb3_49a8_bd71_56524d90ce16
ELIN-481014-2015 | EL-269224-2015 | 11/23/2015 7:20:38 AM | ASSESS: EL: Final | png | #asFound | EL169 | Protection and control Disconnect is not of proper type or rating. | 3 | 3 | 15 amp 120-277 volt rated general use switch installed on a 20 amp over current device. This is a shock hazard. | 3 | Protection and control Disconnect is not of proper type or rating. | 15A_rated_switch_installed_on_a_20A_circuit.png | file://x:/photopub/docs/0000000356/bf645078-3018-4c05-9f08-f8142fb743c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1395d2c_1b32_44e0_bbe0_33ce4de8f0ca
ELIN-481005-2015 | EL-256967-2015 | 11/23/2015 7:21:03 AM | ASSESS: EL: Final | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 | 15 amp 208/230 volt rated air condition equipment is protected by a 20 amp overcurrent device. This is a thermal effect. | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | equipment_name_plate_with_max_overcurrent_protection.png | file://x:/photopub/docs/0000000356/8855664b-bdcb-4f6d-b217-8184402aad8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__139d5c4f_dd6c_4ac8_a6a6_073cba7b96d3
GAIN-448912-2015 | GA-293549-2015 | 11/20/2015 11:40:44 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a furnace which had been installed without correctly configuring the combustion air pipe as per the manufacturers installation instructions. This is a hazard because without the correct combustion air pipe configuration the furnace may not be able to draw in the correct amount of combustion air needed for operation. This can lead to incomplete combustion, increased carbon monoxide levels and appliance damage. | 3 | Appliance not installed according to installation instructions | Missing_combustion_air_pipe.png | file://x:/photopub/docs/0000000355/291ac12a-76ce-4ff6-ac55-a8977a9f756e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9f86a08_e57e_4c9f_8740_03f4e8e2b70e
ELIN-479886-2015 | EL-049597-2013 | 11/23/2015 6:38:06 AM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Service equipment must be rated for the conditions in which it is installed. This includes weatherproof fittings and approved components. Failure to do so could result in water accumulating in the equipment and leading to deterioration of the live parts. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Homemade_hub.png | file://x:/photopub/docs/0000000356/949be729-e7b2-4309-8e77-ea806956268a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__104bdce9_d680_4f8c_aa54_37b38f3f25a8
ELIN-483382-2015 | EL-312805-2015 | 11/24/2015 3:52:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Service not weatherproofed | 0 | No Created Hazard Identified | Service_not_weatherproofed2.png | file://x:/photopub/docs/0000000357/6192f2b2-bc5e-4bde-85a8-cc925b36249f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80d2f8e3_57f8_48ef_bd42_3f05b17c2cd6
ELIN-475869-2015 | EL-286630-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors installed in exterior locations must be tightened properly in order to provide a weather tight seal to prevent water from entering electrical equipment. This installation has a service cable connector that as not tightened properly. As a result water is entering the service panel and coming in contact with conductors and terminations within the service panel. Left uncorrected wet connections may corrode and eventually create a fire hazard due to high resistance connections. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Loose_teck_cable_connector.png | file://x:/photopub/docs/0000000353/b6f723b5-cc14-4a2b-97ba-f358359a463a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b75da6f3_8bdb_417b_8cf8_0dec06242d00
ELIN-477461-2015 | EL-312411-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Service conduits must be properly sealed where they enter the top of meter bases in exterior locations. This is required to prevent water from entering electrical equipment and conductor terminations. This installation has a service conduit entering the top of a meter base on the exterior of a new house under construction. Left uncorrected equipment and terminations may become corroded over time and deteriorate the integrity of the equipment and connections creating a shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_conduit_in_top_of_meter_base.png | file://x:/photopub/docs/0000000353/c964c81b-99ea-4c0d-b0b8-a3ce5b18a0da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fc2a928_9cf3_4673_81f7_98277f896195
ELIN-477708-2015 | EL-274102-2015 | 11/16/2015 7:05:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables inside walls must remain undamaged prior to being covered during construction. This is required to keep the conductors insulation integrity intact to prevent a fault between energized conductors or other objects. This installation has a damaged branch circuit cable inside of a wood framed wall. Left uncorrected the cable may fail potentially causing a fire or shock hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Damaged_cable_inside_wall_under_the_service_panel.png | file://x:/photopub/docs/0000000353/086052b9-fa98-4b8d-8ad3-aa3907677b7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea81f52c_e5ad_485e_83fc_920d3b95bc49
ELIN-475869-2015 | EL-286630-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors installed in exterior locations must be tightened properly in order to provide a weather tight seal to prevent water from entering electrical equipment. This installation has a service cable connector that as not tightened properly. As a result water is entering the service panel and coming in contact with conductors and terminations within the service panel. Left uncorrected wet connections may corrode and eventually create a fire hazard due to high resistance connections. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_cable_at_shipping_container.png | file://x:/photopub/docs/0000000353/951ad2a3-9290-4d79-8a2c-08c63a36307e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b75da6f3_8bdb_417b_8cf8_0dec06242d00
ELIN-475869-2015 | EL-286630-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors installed in exterior locations must be tightened properly in order to provide a weather tight seal to prevent water from entering electrical equipment. This installation has a service cable connector that as not tightened properly. As a result water is entering the service panel and coming in contact with conductors and terminations within the service panel. Left uncorrected wet connections may corrode and eventually create a fire hazard due to high resistance connections. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_pouring_out_of_LB_fitting_when_cover_screw_loosened.png | file://x:/photopub/docs/0000000353/db0b6eba-05fe-4ffe-836d-f5c157681126.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b75da6f3_8bdb_417b_8cf8_0dec06242d00
ELIN-477461-2015 | EL-312411-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Service conduits must be properly sealed where they enter the top of meter bases in exterior locations. This is required to prevent water from entering electrical equipment and conductor terminations. This installation has a service conduit entering the top of a meter base on the exterior of a new house under construction. Left uncorrected equipment and terminations may become corroded over time and deteriorate the integrity of the equipment and connections creating a shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Water_in_the_bottom_of_the_meter_base.png | file://x:/photopub/docs/0000000353/58c54ae9-7627-4790-b704-5170f07d8085.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6fc2a928_9cf3_4673_81f7_98277f896195
ELIN-475869-2015 | EL-286630-2015 | 11/16/2015 7:05:13 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors installed in exterior locations must be tightened properly in order to provide a weather tight seal to prevent water from entering electrical equipment. This installation has a service cable connector that as not tightened properly. As a result water is entering the service panel and coming in contact with conductors and terminations within the service panel. Left uncorrected wet connections may corrode and eventually create a fire hazard due to high resistance connections. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_entering_service_panel_.png | file://x:/photopub/docs/0000000353/aa030ccb-f32d-4a0e-ae8d-0e28af9cbd40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b75da6f3_8bdb_417b_8cf8_0dec06242d00
ELIN-480269-2015 | UW-314234-2015 | 11/19/2015 10:09:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Branch_circuit_modification.png | file://x:/photopub/docs/0000000354/34f06cfc-5f94-45f6-8d4f-381b09ebe8c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d12eb6d9_2af5_42fc_9542_bddc10316d96
ELIN-477151-2015 | EL-309217-2015 | 11/23/2015 5:13:14 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Service equipment must be properly sized to safely provide power to the equipment that is connected to it. This installation has an existing 100A service that has had new wiring added for 40A electric vehicle charging equipment. The existing service equipment already services two dwelling units within the house that have separate cooking and laundry facilities as well as an AC unit. The added load to the existing demand exceeds the rating of the service equipment. Left uncorrected this is a potential thermal hazard if the service equipment becomes over heated due to the additional load. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Vehicle_charging_equipment_.png | file://x:/photopub/docs/0000000356/ed444df4-3dd2-4a34-bac4-69345df2fd22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__effab636_ac7c_458a_b81b_8a142a604174
ELIN-477151-2015 | EL-309217-2015 | 11/23/2015 5:13:14 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Service equipment must be properly sized to safely provide power to the equipment that is connected to it. This installation has an existing 100A service that has had new wiring added for 40A electric vehicle charging equipment. The existing service equipment already services two dwelling units within the house that have separate cooking and laundry facilities as well as an AC unit. The added load to the existing demand exceeds the rating of the service equipment. Left uncorrected this is a potential thermal hazard if the service equipment becomes over heated due to the additional load. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Existing_100A_service_panel.png | file://x:/photopub/docs/0000000356/1b641514-586e-4322-92d1-c9bb074cc87e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__effab636_ac7c_458a_b81b_8a142a604174
ELIN-477151-2015 | EL-309217-2015 | 11/23/2015 5:13:14 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Service equipment must be properly sized to safely provide power to the equipment that is connected to it. This installation has an existing 100A service that has had new wiring added for 40A electric vehicle charging equipment. The existing service equipment already services two dwelling units within the house that have separate cooking and laundry facilities as well as an AC unit. The added load to the existing demand exceeds the rating of the service equipment. Left uncorrected this is a potential thermal hazard if the service equipment becomes over heated due to the additional load. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Label_on_vehicle_charger.png | file://x:/photopub/docs/0000000356/ecd7b4d6-1970-4a02-a3e3-e472f377bc74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__effab636_ac7c_458a_b81b_8a142a604174
ELIN-477151-2015 | EL-309217-2015 | 11/23/2015 5:13:14 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Service equipment must be properly sized to safely provide power to the equipment that is connected to it. This installation has an existing 100A service that has had new wiring added for 40A electric vehicle charging equipment. The existing service equipment already services two dwelling units within the house that have separate cooking and laundry facilities as well as an AC unit. The added load to the existing demand exceeds the rating of the service equipment. Left uncorrected this is a potential thermal hazard if the service equipment becomes over heated due to the additional load. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Manufacturer_installation_instructions_.png | file://x:/photopub/docs/0000000356/bb2f31ee-551f-43c3-a2d4-863eb095e02a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__effab636_ac7c_458a_b81b_8a142a604174
ELIN-477151-2015 | EL-309217-2015 | 11/23/2015 5:13:14 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Service equipment must be properly sized to safely provide power to the equipment that is connected to it. This installation has an existing 100A service that has had new wiring added for 40A electric vehicle charging equipment. The existing service equipment already services two dwelling units within the house that have separate cooking and laundry facilities as well as an AC unit. The added load to the existing demand exceeds the rating of the service equipment. Left uncorrected this is a potential thermal hazard if the service equipment becomes over heated due to the additional load. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Manufacturer_installation_instructions.png | file://x:/photopub/docs/0000000356/884ae6ee-1313-43fc-a63a-770ee9899346.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__effab636_ac7c_458a_b81b_8a142a604174
ELIN-480240-2015 | EL-313965-2015 | 11/23/2015 4:53:45 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Wrong cover | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Arden-1.png | file://x:/photopub/docs/0000000356/1ab6750c-51de-4688-bd3f-eab52b8e7630.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee2abe94_16a8_4271_a751_46f933193837
BPVOP-473981-2015 | 2282754 | 11/17/2015 5:01:33 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Deposits_inside_the_coil_.png | file://x:/photopub/docs/0000000353/dc1f66e2-842b-4eb8-a6fa-70c17e536494.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94917a3b_c6b9_48b9_999f_8b24a2ed2107
BPVOP-479701-2015 | 2250694 | 11/17/2015 4:30:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion.png | file://x:/photopub/docs/0000000353/b549e72b-15d6-4512-9e00-82bec88b9c04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72ec1195_671a_4670_ab3a_9f920811b27b
GAIN-480517-2015 | GA-145196-2014 | 11/20/2015 3:49:35 PM | ASSESS: GA: Final | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | Supply air to 2 x commercial gas dryers is supplied through an opening to the outdoors with electronically actuated louvers. The louvers are not interlocked with the operation on the appliances. The louvers need to be proven in the fully open position before the appliance can be allowed to energize its gas valve. Without an interlock in place the appliances would be able to operate with the air supply restricted or closed. Lack of air supply to the appliances could result in incomplete combustion and the production of carbon monoxide. | 3 | Mechanical Air/ventilation supply present, missing interlock | Dryer_air_supply_louvers.png | file://x:/photopub/docs/0000000355/514f6680-9bd6-40c9-b3f2-820b8cd3460e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a16b642_77fb_45ee_9968_58d0c0a21426
GAIN-480517-2015 | GA-145196-2014 | 11/20/2015 3:49:35 PM | ASSESS: GA: Final | png | #asFound | GA120 | Mechanical Air/ventilation supply present, missing interlock | 3 | 3 | Supply air to 2 x commercial gas dryers is supplied through an opening to the outdoors with electronically actuated louvers. The louvers are not interlocked with the operation on the appliances. The louvers need to be proven in the fully open position before the appliance can be allowed to energize its gas valve. Without an interlock in place the appliances would be able to operate with the air supply restricted or closed. Lack of air supply to the appliances could result in incomplete combustion and the production of carbon monoxide. | 3 | Mechanical Air/ventilation supply present, missing interlock | Closed_louvers.png | file://x:/photopub/docs/0000000355/d9b06fe3-4a6c-45f6-9b8b-d4db25871641.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a16b642_77fb_45ee_9968_58d0c0a21426
ELIN-482845-2015 | EL-274658-2015 | 11/24/2015 6:30:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The cabling is missing required straps that could create a strain on the cable jacketing damaging the cable and allow moisture to erode the protective armour. Deterioration of the cable armour can create a thermal or shock affect should a voltage and current become induced onto the armour | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pull_pit.png | file://x:/photopub/docs/0000000357/a8e25ff3-9e5f-4325-b4b4-997bf1bc8dfb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10ed2b10_a9a1_436c_aebd_67cf59c6e3ff
GAIN-480580-2015 | GA-159895-2014 | 11/23/2015 4:25:42 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | The as found hazard was a boiler which had been installed without the required flow switch. This is a hazard because in the event the circulation pump were to fail stopping the flow of water through the boiler there would be no safety in place to shut down the burners on the boiler. This could lead to excessive water temperatures, steam production and equipment damage. | 4 | Missing mandatory safety controls | Flow_switch_not_wired_in.png | file://x:/photopub/docs/0000000356/bc3631b9-f9b0-44c5-afbc-62ecd4a18011.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__390b8df2_437f_47da_99c2_2f1171bbe744
ELIN-470189-2015 | EL-301526-2015 | 11/12/2015 11:34:42 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Service not grounded correctly, service ground bonded to panel tub, instead of neutral. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Clifton_tcs1.png | file://x:/photopub/docs/0000000353/3a181622-53c3-4923-9bf0-980043a6d4e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__094d99cd_8190_42dc_a9cb_05e050a8f982
ELIN-470189-2015 | EL-301526-2015 | 11/12/2015 11:34:42 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Service not grounded correctly, service ground bonded to panel tub, instead of neutral. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Cliftontcs2.png | file://x:/photopub/docs/0000000353/37ecc79c-03ed-4efd-b5db-ec1a4fcfe174.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__094d99cd_8190_42dc_a9cb_05e050a8f982
ELIN-516955-2016 | EL-304457-2015 | 1/27/2016 7:07:42 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed energized conductor terminals using electrical equipment which is not approved or is not installed as per approved use of electrical equipment with all covers or plugs installed to cover all energized metal parts of energized conductors. When there are exposed energized metal parts of conductors that don't have the proper and adequate insulation covering equivalent to that of the remainder of conductor insulation, the electrical conductors could cause an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 71.png | file://x:/photopub/docs/0000000384/f75c6b76-4700-4616-bc9e-09bfe7d66454.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__635348cb_8c73_4fac_a601_f77a3166c7d4
ELIN-516955-2016 | EL-304457-2015 | 1/27/2016 7:07:42 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed energized conductor terminals using electrical equipment which is not approved or is not installed as per approved use of electrical equipment with all covers or plugs installed to cover all energized metal parts of energized conductors. When there are exposed energized metal parts of conductors that don't have the proper and adequate insulation covering equivalent to that of the remainder of conductor insulation, the electrical conductors could cause an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 72.png | file://x:/photopub/docs/0000000384/0112cc60-24a8-4602-938f-ce0b367f792d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__635348cb_8c73_4fac_a601_f77a3166c7d4
ELIN-516955-2016 | EL-304457-2015 | 1/27/2016 7:07:42 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed energized conductor terminals using electrical equipment which is not approved or is not installed as per approved use of electrical equipment with all covers or plugs installed to cover all energized metal parts of energized conductors. When there are exposed energized metal parts of conductors that don't have the proper and adequate insulation covering equivalent to that of the remainder of conductor insulation, the electrical conductors could cause an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 74.png | file://x:/photopub/docs/0000000384/b51cde31-67c6-4b1d-a75d-06d807d65724.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__635348cb_8c73_4fac_a601_f77a3166c7d4
ELIN-516955-2016 | EL-304457-2015 | 1/27/2016 7:07:42 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed energized conductor terminals using electrical equipment which is not approved or is not installed as per approved use of electrical equipment with all covers or plugs installed to cover all energized metal parts of energized conductors. When there are exposed energized metal parts of conductors that don't have the proper and adequate insulation covering equivalent to that of the remainder of conductor insulation, the electrical conductors could cause an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 73.png | file://x:/photopub/docs/0000000384/fcedfb77-776c-4b49-a55e-9be3247a63dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__635348cb_8c73_4fac_a601_f77a3166c7d4
ELIN-517637-2016 | UW-339816-2016 | 1/27/2016 7:07:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found damaged, unsafe, unapproved and non-compliant electrical equipment which had conductors exposed and wired without use of junction box and cable connectors for luminaire installation. When conductors are not approved and installed properly to prevent electrical equipment damages, the electrical equipment could become an electrical fire or shock hazard to people and property | 3 | Conductors Equipment is not approved for the specific use. | 43.png | file://x:/photopub/docs/0000000384/5581a624-fd38-4941-856a-3ffcd50c60ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5da2da59_0d09_4293_ad31_42975d1e6dc2
ELIN-516955-2016 | EL-304457-2015 | 1/27/2016 7:07:42 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed energized conductor terminals using electrical equipment which is not approved or is not installed as per approved use of electrical equipment with all covers or plugs installed to cover all energized metal parts of energized conductors. When there are exposed energized metal parts of conductors that don't have the proper and adequate insulation covering equivalent to that of the remainder of conductor insulation, the electrical conductors could cause an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 70.png | file://x:/photopub/docs/0000000384/886e761c-1d28-47f7-83c4-cf12ba0597ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__635348cb_8c73_4fac_a601_f77a3166c7d4
ELIN-517637-2016 | UW-339816-2016 | 1/27/2016 7:07:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found damaged, unsafe, unapproved and non-compliant electrical equipment which had conductors exposed and wired without use of junction box and cable connectors for luminaire installation. When conductors are not approved and installed properly to prevent electrical equipment damages, the electrical equipment could become an electrical fire or shock hazard to people and property | 3 | Conductors Equipment is not approved for the specific use. | 42.png | file://x:/photopub/docs/0000000384/18f711d7-cc86-40f4-9dd6-539c64b2727a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5da2da59_0d09_4293_ad31_42975d1e6dc2
ELIN-517637-2016 | UW-339816-2016 | 1/27/2016 7:07:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found damaged, unsafe, unapproved and non-compliant electrical equipment which had conductors exposed and wired without use of junction box and cable connectors for luminaire installation. When conductors are not approved and installed properly to prevent electrical equipment damages, the electrical equipment could become an electrical fire or shock hazard to people and property | 3 | Conductors Equipment is not approved for the specific use. | 44.png | file://x:/photopub/docs/0000000384/c25b701d-21ff-4cf5-b8cc-f4deef60c23f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5da2da59_0d09_4293_ad31_42975d1e6dc2
ELIN-482864-2015 | EL-208498-2015 | 11/26/2015 9:34:00 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed copper conductors inside baseboard heater fed with 240 volts single phase is not safe or properly insulated and conductors not properly covered with insulation to prevent an electrical shock or fire hazard. When current carrying conductors have energized and exposed copper showing for approximately 10-20 mm in length, the branch circuits conductors could make contact with people or metal enclosures or other property and the electrical equipment could cause an electrical fault condition. These unsafe, exposed and energized conductors could become an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3.png | file://x:/photopub/docs/0000000359/30205ea7-8103-4148-ba81-ac7e7ec7fec3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee636785_ee4f_41fc_a006_a837c9eb4bce
ELIN-482864-2015 | EL-208498-2015 | 11/26/2015 9:34:00 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed copper conductors inside baseboard heater fed with 240 volts single phase is not safe or properly insulated and conductors not properly covered with insulation to prevent an electrical shock or fire hazard. When current carrying conductors have energized and exposed copper showing for approximately 10-20 mm in length, the branch circuits conductors could make contact with people or metal enclosures or other property and the electrical equipment could cause an electrical fault condition. These unsafe, exposed and energized conductors could become an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 2.png | file://x:/photopub/docs/0000000359/178af1a4-10ff-459a-8905-c481328c9905.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee636785_ee4f_41fc_a006_a837c9eb4bce
ELIN-482864-2015 | EL-208498-2015 | 11/26/2015 9:34:00 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed copper conductors inside baseboard heater fed with 240 volts single phase is not safe or properly insulated and conductors not properly covered with insulation to prevent an electrical shock or fire hazard. When current carrying conductors have energized and exposed copper showing for approximately 10-20 mm in length, the branch circuits conductors could make contact with people or metal enclosures or other property and the electrical equipment could cause an electrical fault condition. These unsafe, exposed and energized conductors could become an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 1.png | file://x:/photopub/docs/0000000359/54c1d4a4-1444-4ac0-bacd-a7ef87221049.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee636785_ee4f_41fc_a006_a837c9eb4bce
ELIN-482864-2015 | EL-208498-2015 | 11/26/2015 9:34:00 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed copper conductors inside baseboard heater fed with 240 volts single phase is not safe or properly insulated and conductors not properly covered with insulation to prevent an electrical shock or fire hazard. When current carrying conductors have energized and exposed copper showing for approximately 10-20 mm in length, the branch circuits conductors could make contact with people or metal enclosures or other property and the electrical equipment could cause an electrical fault condition. These unsafe, exposed and energized conductors could become an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 4.png | file://x:/photopub/docs/0000000359/0ed6aaa7-ed2f-4b88-988d-2c5d6d6f9d70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee636785_ee4f_41fc_a006_a837c9eb4bce
PRIN-489147-2015 | PR-247327-2015 | 12/3/2015 3:23:59 PM | ASSESS: PR IN: Acceptance | png | #asFound. Red wire located at the unmarked #5 location was original in the #4 terminal location. With the wire in the #4 terminal the tower switch was made inoperable. | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | On a ropeway, passenger carriers are attached to a wire rope which is supported by a series of groves wheel assemblies situated on top of a support tower structure. Due to a miswiring in an electrical terminal box located at the tower, a switch that is utilized in detecting a derailment of rope from the grooved wheel assemblies was found not to annunciate when actuated. Under proper operation, this switch is to annunciate upon actuation causing an announcement on a display screen and causing the moving rope to stop. A condition in which a rope derailment is not detected would result in a major risk of injury to passengers and damage to ropeway equipment (i.e. ropeway structures, passenger carriers and rope). | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Condition_of_terminal_block_after_correction.png | file://x:/photopub/docs/0000000362/e700081d-775e-4ce1-984d-3b37d06cc4d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33e863d0_f83f_4cae_aa2a_44c24feebefa
ELIN-506241-2016 | EL-321196-2015 | 1/19/2016 1:13:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Service system rated 200 amp 120/240 volt single phase is grounded twice and has service cable bonding conductor terminated onto main service neutral bar. When service neutral and its grounding system has a bonding conductor terminated on the service neutral bar, there is a possible shock hazard to people because the conductors would have parallel paths for grounding and any fault condition could be imposed on non-current carrying equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 2.png | file://x:/photopub/docs/0000000381/c400aaf7-a089-453d-af9f-a04876656715.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f140ba33_9c35_4549_b531_1e94a4096447
ELIN-506241-2016 | EL-321196-2015 | 1/19/2016 1:13:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Service system rated 200 amp 120/240 volt single phase is grounded twice and has service cable bonding conductor terminated onto main service neutral bar. When service neutral and its grounding system has a bonding conductor terminated on the service neutral bar, there is a possible shock hazard to people because the conductors would have parallel paths for grounding and any fault condition could be imposed on non-current carrying equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 1.png | file://x:/photopub/docs/0000000381/dab96421-5634-423c-ad03-36f54998005f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f140ba33_9c35_4549_b531_1e94a4096447
ELIN-506241-2016 | EL-321196-2015 | 1/19/2016 1:13:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Service system rated 200 amp 120/240 volt single phase is grounded twice and has service cable bonding conductor terminated onto main service neutral bar. When service neutral and its grounding system has a bonding conductor terminated on the service neutral bar, there is a possible shock hazard to people because the conductors would have parallel paths for grounding and any fault condition could be imposed on non-current carrying equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 3.png | file://x:/photopub/docs/0000000381/83ed8824-3e95-44f5-bb87-0aeacdcce9cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f140ba33_9c35_4549_b531_1e94a4096447
ELIN-514081-2016 | EL-332339-2016 | 1/20/2016 5:19:17 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device was installed too high and was not installed between 150mm and 300 mm below service head as required by code. When service attachment device is not installed as required by code, water could possibly enter the service raceway or cable or service equipment and could create a possible electrical fire or shock hazard to people. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 41.png | file://x:/photopub/docs/0000000381/e55b9515-bba7-4884-8a23-01ac01b8cb9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1a2a9bb_89d8_4796_9d04_95dd44be7e2b
ELIN-514081-2016 | EL-332339-2016 | 1/20/2016 5:19:17 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device was installed too high and was not installed between 150mm and 300 mm below service head as required by code. When service attachment device is not installed as required by code, water could possibly enter the service raceway or cable or service equipment and could create a possible electrical fire or shock hazard to people. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 42.png | file://x:/photopub/docs/0000000381/bddc5868-9b56-40a3-933f-df675849ce3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1a2a9bb_89d8_4796_9d04_95dd44be7e2b
ELIN-514081-2016 | EL-332339-2016 | 1/20/2016 5:19:17 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device was installed too high and was not installed between 150mm and 300 mm below service head as required by code. When service attachment device is not installed as required by code, water could possibly enter the service raceway or cable or service equipment and could create a possible electrical fire or shock hazard to people. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 40.png | file://x:/photopub/docs/0000000381/fa886e66-e20b-4d3d-8cfe-1e1060c259cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1a2a9bb_89d8_4796_9d04_95dd44be7e2b
ELIN-482193-2015 | EL-128398-2014 | 12/11/2015 8:44:17 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Tamper resistant receptacles not installed on 15 and 20 amp receptacles at 120 volts throughout the dwelling. Children may insert conductive objects into standard receptacles and be injured when tamper resistant receptacles are not installed in those areas accessible to children below 2 meters above grade and finished floor. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Most_recptacles_not_tamper_resistant_type.png | file://x:/photopub/docs/0000000366/f42dd72e-9197-4959-aaac-60d04f371a2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a23f98e6_634e_4f50_b013_fdd6c4f835eb
BPVOP-521810-2016 | 2752929 | 1/28/2016 12:29:10 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP199 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | Data_plate_.png | file://x:/photopub/docs/0000000386/501631f9-9e69-4fa1-9285-1e9ab1859cc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eff05ef2_a29b_4fd4_841c_b29118dabd66
GAIN-283540-2014 | GA-153387-2014 | 1/21/2016 6:24:25 PM | ASSESS: GA: Rough-In | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | Pipe_at_meter_coop.png | file://x:/photopub/docs/0000000381/af08d261-9806-4bf0-9cf5-6a06b495d17f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f1a9d62_8b22_49b4_87d8_da14715a91a8
BPVOP-498759-2015 | 5083382 | 12/18/2015 3:44:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Deposits_on_tubes.png | file://x:/photopub/docs/0000000369/129cb40e-0a3a-41ff-b0c8-479d348519cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d885115d_763a_410a_bf1d_c2b4e8979664
ELIN-521698-2016 | EL-308682-2015 | 2/10/2016 8:48:24 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | NMD 90 is not mechanically protected below 1.5 meters in detached garage. This could be a shock/short circuit hazard if NMD 90 is used as hangers for tools and if equipment bumps or is stored against it due to the outer coating of NMD 90 not being made for such uses. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD_not_mechanically_protected.png | file://x:/photopub/docs/0000000389/10ed09b4-7b74-41fb-a7f8-e585bd8b14cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68bca69f_e246_4099_b1eb_3bb5674232d5
ELIN-494098-2015 | EL-311591-2015 | 12/14/2015 7:33:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 120/240 volt 200 amp residential service. Service conductor armored cable bond conductor terminated outside of service entry compartment. This could cause conductor or equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Bond_conductor_terminated_outside_of_service_conductor_enclosure.png | file://x:/photopub/docs/0000000366/18d0e3ac-535f-44e2-9ac3-674240e1c308.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97d44141_ce37_49be_ae5f_e7f7ca05cedf
ELIN-483141-2015 | EL-312415-2015 | 12/10/2015 8:14:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL095 | Continuity Bonding equipment, conductors, boxes etc. no longer provide adequate protection due to mechanical damage. | 3 | 3 | Lock nuts not tight on raceway nipples between CT cabinet and 600 amp splitter. These loose nuts do not provide an adequate bonding path for fault currents. Electrical equipment down stream from this point may become energized and present a shock hazard. | 3 | Continuity Bonding equipment, conductors, boxes etc. no longer provide adequate protection due to mechanical damage. | Loose_bonding_nuts.png | file://x:/photopub/docs/0000000365/47a63cd1-d911-479f-9198-8b6f5fb1c4e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac972529_50a2_4cff_89e8_ae5eccf5a056
ELIN-499063-2015 | EL-308079-2015 | 12/21/2015 1:55:07 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 15 amp 120 volt outlet box sized larger than 100 millimetres supported on one side only. This could cause a thermal effect to the electrical equipment. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Box_supported_on_one_side.png | file://x:/photopub/docs/0000000369/13e231c3-f386-43ca-b033-0b9bedf45002.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3bf99c5_e905_4415_af4d_ea5dfd693016
ELIN-485335-2015 | EL-314383-2015 | 11/27/2015 11:10:09 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Sign lighting fixtures have been supplied and installed on support pylons accessible to the general public. The sign structure is fed with a 3 phase 208 volt 100 amp supply. Electrical equipment that does not bear evidence of approval may present a hazard to persons or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Sign_fixtures_do_not_bear_evidence_of_approval_or_nameplates.png | file://x:/photopub/docs/0000000358/950c0bea-e152-4a4b-95e1-f5281f66c03b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22026cfc_1455_4cde_9a9e_3bce89e3cbd5
AMIN-486279-2015 | AM-248878-2015 | 1/19/2016 8:30:00 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM032 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 |  | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Emergency_Stop_Button.png | file://x:/photopub/docs/0000000379/7bcf7979-6b3f-47f4-bc00-ed7fe194ab4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64d09065_e0ae_4170_ae06_0eb3e6e7ba6f
GAIN-510656-2016 | GA-334986-2016 | 1/20/2016 12:12:05 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Counterflow gas furnace was left in operation with the return air not connected to the top of the furnace this will cause residual heat to buildup in the fan compartment after every heat cycle causing the electrical components to overheat and prematurely fail | 3 | Appliance not installed according to installation instructions | 20711_52_nd.png | file://x:/photopub/docs/0000000380/42144a77-cab3-4889-8a70-3c8cccff2bd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0573656_d066_42fd_b400_8e28889541cc
ELIN-520194-2016 | 3901937 | 2/5/2016 4:32:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | The metal jacket on armoured cables must be electrically and mechanically continuous to ensure a good bond one end to the other. In this installation PVC fittings were used on a metal cable run, interrupting the bond. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | TECK_to_PVC.png | file://x:/photopub/docs/0000000387/9801fc2a-5d70-4242-a133-da2888677623.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d51e6d2c_fc83_48ab_8521_a35addbf540d
ELIN-484618-2015 | EL-312580-2015 | 11/27/2015 10:35:58 AM | ASSESS: EL: Service Connection | png | #asFound |  |  | 4 | 4 | A new commercial 400amp 120/240volt service , Identified conductor at the main service is not grounded. This is a potential thermal hazard. |  |  | identified_conductor_is_not_grounded.png | file://x:/photopub/docs/0000000359/59dd9389-888b-4b57-9dde-03fd36e168ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__adf47a1a_3029_401e_b31b_f660f410a1c5
ELIN-491845-2015 | EL-322258-2015 | 12/10/2015 12:53:53 PM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Unapproved fixture that is incomplete. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Master_bedroom_walk-in_closet_.png | file://x:/photopub/docs/0000000365/58dd8e59-382e-43a0-8172-100a447f1000.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a349271_f774_4116_85a5_28670b34b67b
ELIN-520052-2016 | EL-330307-2015 | 2/10/2016 1:51:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 1.png | file://x:/photopub/docs/0000000389/3a7c9fde-4d38-4c03-8907-2ebea7c6c461.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc52b4eb_9ecb_4ae3_8806_b0588238cc6c
ELIN-520052-2016 | EL-330307-2015 | 2/10/2016 1:51:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 2.png | file://x:/photopub/docs/0000000389/2b9ec787-c16b-4ea6-9e3d-eddbb313380d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc52b4eb_9ecb_4ae3_8806_b0588238cc6c
ELIN-520052-2016 | EL-330307-2015 | 2/10/2016 1:51:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 6.png | file://x:/photopub/docs/0000000389/3fa522e4-87db-4f53-b7db-bbea5c8d2d2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc52b4eb_9ecb_4ae3_8806_b0588238cc6c
ELIN-520052-2016 | EL-330307-2015 | 2/10/2016 1:51:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3.png | file://x:/photopub/docs/0000000389/c1ab7637-cd79-4a5f-950b-1455bf6448ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc52b4eb_9ecb_4ae3_8806_b0588238cc6c
ELIN-520052-2016 | EL-330307-2015 | 2/10/2016 1:51:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 4.png | file://x:/photopub/docs/0000000389/23fe4dec-0aba-4d5d-b474-cc81d4dd7ba9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc52b4eb_9ecb_4ae3_8806_b0588238cc6c
ELIN-520052-2016 | EL-330307-2015 | 2/10/2016 1:51:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 5.png | file://x:/photopub/docs/0000000389/bdb020c7-6dfb-42ff-bfd7-5a3766c7d0dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc52b4eb_9ecb_4ae3_8806_b0588238cc6c
ELIN-483509-2015 | EL-300983-2015 | 12/1/2015 1:54:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a main service combination panel board rated 120/240 volt single phase 200 amps that contractor and field safety representative declared and authorized for connection to power supply system while service panelboard is missing panel cover and has exposed bus bars and conductors. Once above electrical equipment is connected to power supply system this system would not be safe or compliant due to exposed energized conductors and bus bars. This would be a possible electrical fire or shock hazard to people and property if there was ever contact made between exposed energized conductors and people or other equipment. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Exposed_conductors_and_bus_bars_not_safe_or_authorized_for_connection_to_power_supply_system.png | file://x:/photopub/docs/0000000360/f4c58c37-14b6-4f0b-915d-81e83d8040df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d951ecd8_9c4f_4258_9f90_f55a08e89d13
ELIN-483509-2015 | EL-300983-2015 | 12/1/2015 1:54:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a main service combination panel board rated 120/240 volt single phase 200 amps that contractor and field safety representative declared and authorized for connection to power supply system while service panelboard is missing panel cover and has exposed bus bars and conductors. Once above electrical equipment is connected to power supply system this system would not be safe or compliant due to exposed energized conductors and bus bars. This would be a possible electrical fire or shock hazard to people and property if there was ever contact made between exposed energized conductors and people or other equipment. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Exposed_conductors_and_bus_bars_in_panel_that_FSR_DECLARED_AS_AUTHORIZED_FOR_CONNECTION.png | file://x:/photopub/docs/0000000360/27144491-c6e8-460b-8043-1280d6691dc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d951ecd8_9c4f_4258_9f90_f55a08e89d13
ELIN-483509-2015 | EL-300983-2015 | 12/1/2015 1:54:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found a main service combination panel board rated 120/240 volt single phase 200 amps that contractor and field safety representative declared and authorized for connection to power supply system while service panelboard is missing panel cover and has exposed bus bars and conductors. Once above electrical equipment is connected to power supply system this system would not be safe or compliant due to exposed energized conductors and bus bars. This would be a possible electrical fire or shock hazard to people and property if there was ever contact made between exposed energized conductors and people or other equipment. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Panel_board_has_dust_and_debris_inside_panel.png | file://x:/photopub/docs/0000000360/5dfd7b61-b365-4435-8df9-99eabd92a39d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d951ecd8_9c4f_4258_9f90_f55a08e89d13
BPVOP-501587-2015 | BPV-007866-2013 | 12/24/2015 10:05:41 AM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP002 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | 5 | 5 | Upon assessment of steam boiler with heating surface of 58 square meters and Maximum Allowable Working Pressure (MAWP) of 150psig it is determined that quick opening blow off valve pressure and temperature rating is class 125 as per manufacturer's specification (minimum rating required is 188psig Wet Steam Pressure, closest available rating is 200psig Wet Steam Pressure). Under rated valve will fail in operation due to cyclic stress induced by water hammer involved with blow off operation and will lead to severe incident. | 5 | 1.0.1 Temp/Pressure ratings not met - Design conditions of equipment are not available. No visible certification or standard. | QUICK_OPENING_VALVE_WITHOUT_RATING.png | file://x:/photopub/docs/0000000371/4a7dda82-1dbe-4daf-9d20-7afe1222dabd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95e52293_7491_4d40_b4ef_b6f2a336dde5
ELIN-501632-2015 | EL-318166-2015 | 12/29/2015 4:04:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacle installed below the panel is exposed to rain. The receptacle has a dry location cover but that is inadequate to keep the equipment dry. This will cause the GFCI protection to fail exposing workers to electric shock. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_wp_cover.png | file://x:/photopub/docs/0000000371/a5b9501b-3033-4a4a-a2a6-583f9ef4b9a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__381e7569_6ab7_4a3b_913e_9f6bdeb277e7
ELIN-501632-2015 | EL-318166-2015 | 12/29/2015 4:04:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacle installed below the panel is exposed to rain. The receptacle has a dry location cover but that is inadequate to keep the equipment dry. This will cause the GFCI protection to fail exposing workers to electric shock. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Almost_weatherproof.png | file://x:/photopub/docs/0000000371/1e9770a4-e2cf-440f-b20b-7837f122911b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__381e7569_6ab7_4a3b_913e_9f6bdeb277e7
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_energized_conductors_of_flexible_cord.png | file://x:/photopub/docs/0000000376/aacdfac5-8029-4554-9f45-15c3072d78d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Temporary_wiring_spliced_in_non-weatherproof_junction_box.png | file://x:/photopub/docs/0000000376/d25eec24-1ad1-41f8-9869-c2f57c2c8ba6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | junction_box_not_bonded.png | file://x:/photopub/docs/0000000376/583174fe-adf0-4c8d-b2bb-6fa58fbee9a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Flexible_cord_connected_to_temporary_receptacles.png | file://x:/photopub/docs/0000000376/debeb7d9-b6bf-4742-b8c1-9c543f1d146b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Heat_pump_disconnect_switch.png | file://x:/photopub/docs/0000000376/dd108d17-240b-4a93-a0b1-396267cfc432.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Temporary_wiring_connected_to_heat_pump_disconnect_switch_on_exterior_of_house.png | file://x:/photopub/docs/0000000376/bd6d8443-86ab-4961-8f34-db3dcc48dd74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-504496-2016 | EL-274817-2015 | 1/7/2016 10:33:49 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Cables used for temporary construction use are required to be the correct type and installed in an acceptable manner. This installation has temporary wiring connected to a 40A, 120/240V heat pump disconnect switch on the exterior of a new house. The cable installed is not the correct type or size and is unapproved for exposure to weather and mechanical damage. The cables and conductors are energized and located in an accessible location. This is a potential shock hazard if the insulation on the exposed cables or conductors gets damaged. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Front_of_house.png | file://x:/photopub/docs/0000000376/719d1541-0d97-44b7-9f3d-c0cc6acccba6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d83daca_e5e6_4b7e_8410_08ebfb45a3d0
ELIN-499091-2015 | EL-314539-2015 | 12/30/2015 3:18:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 2 | See C of I | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Gabriola_-1.png | file://x:/photopub/docs/0000000373/22f4bafa-347b-4dc8-b548-5eeb4a636a45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae6656b6_a6ac_477b_8fa0_1cc712035c6c
BPVIN-500604-2015 | UW-329145-2015 | 12/22/2015 7:33:58 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 3 | Upon assessment of Domestic Hot Water Storage Tank with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that tank is not installed with a drain valve. In the event of failure of vessel pressure retaining components, it will be impossible to completely empty tank and flashing hot water may lead to severe incident. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | DHW_TANK_WITHOUT_DRAIN_VALVE.png | file://x:/photopub/docs/0000000373/4e301acf-dbfd-4f3d-a12c-81b782fec486.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31c5c131_cd9b_4cca_b554_e26d33fea769
BPVIN-500611-2015 | UW-329147-2015 | 12/22/2015 8:37:29 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 3 | Upon assessment of Domestic Hot Water Storage Tank with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that tank is not installed with a drain valve. In the event of failure of vessel pressure retaining components, it will be impossible to completely empty tank and flashing hot water may lead to severe incident. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | No_Bottom_Drain_Valve_for_the_tank.png | file://x:/photopub/docs/0000000373/27a10d5a-c387-4a46-b882-f84181e69e7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5608e857_9e38_4f88_81ac_bc38d87923e1
BPVIN-503795-2016 | BPV-330301-2015 | 12/22/2015 8:57:07 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment of pressurized expansion tank installed in Domestic Hot Water system with Maximum Allowable Working Pressure (MAWP) of 80psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that tank is non ASME. Non-ASME tank may fail due to lack of quality control and flashing hot water can lead to incident. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | NON_ASME_EXPANSION_TANK.png | file://x:/photopub/docs/0000000373/e441be78-b789-4b93-9d67-000890c4941b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6062440_36c8_4084_9e40_5e77498754da
GAIN-503714-2016 | GA-283886-2015 | 1/7/2016 12:56:15 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearance to combustibles are not met with Rinnai water heater. Minimum clearance for above is 9". Installation is currently at 2" | 3 | Clearance to combustible not met | Rinnai_Clearance.png | file://x:/photopub/docs/0000000376/129f674d-0879-48ab-b083-e60f5c58292a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__278cefd9_96c9_4e98_915b_6fbc2a08ad36
GAIN-503714-2016 | GA-283886-2015 | 1/7/2016 12:56:15 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearance to combustibles are not met with Rinnai water heater. Minimum clearance for above is 9". Installation is currently at 2" | 3 | Clearance to combustible not met | Vent_Clearance.png | file://x:/photopub/docs/0000000376/78caaf1b-806e-4de4-8262-510805d08454.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__278cefd9_96c9_4e98_915b_6fbc2a08ad36
ELIN-516052-2016 | UW-338097-2016 | 1/26/2016 9:16:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | Conductors undersized for the load. This is a fire hazard as the conductors can over heat if too much current passes through it. |  |  | D.png | file://x:/photopub/docs/0000000382/c18686b5-a40b-41f3-86dd-c94337bd804d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07baf03f_31a4_4b47_81e0_4f22406c4726
ELIN-516052-2016 | UW-338097-2016 | 1/26/2016 9:16:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | Conductors undersized for the load. This is a fire hazard as the conductors can over heat if too much current passes through it. |  |  | C.png | file://x:/photopub/docs/0000000382/dd68054d-b8de-474c-92f4-d188655184a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07baf03f_31a4_4b47_81e0_4f22406c4726
ELIN-516052-2016 | UW-338097-2016 | 1/26/2016 9:16:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | Conductors undersized for the load. This is a fire hazard as the conductors can over heat if too much current passes through it. |  |  | E.png | file://x:/photopub/docs/0000000382/c0b91dd9-d689-4939-9fa1-862663c08a67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07baf03f_31a4_4b47_81e0_4f22406c4726
ELIN-516052-2016 | UW-338097-2016 | 1/26/2016 9:16:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | Conductors undersized for the load. This is a fire hazard as the conductors can over heat if too much current passes through it. |  |  | B.png | file://x:/photopub/docs/0000000382/474416d0-4f14-485b-8626-78e1632a0c48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07baf03f_31a4_4b47_81e0_4f22406c4726
BPVIN-508698-2016 | UW-333748-2016 | 1/12/2016 3:20:42 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | Upon assessment of expansion tank (dimensions: length-1.1meter and diameter-0.46meter) with Maximum Allowable Working Pressure of 125psig it is determined that vessel is not firmly anchored to floor or braced. In the event of earthquake of significant scale vessel may trip or shift and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | EXPANSION_TANK.png | file://x:/photopub/docs/0000000377/36d7efc2-792c-40c0-be50-07651aecb08f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef4b12e_0a70_47b7_9ef8_e857aed145ec
GAIN-463929-2015 | GA-293854-2015 | 12/1/2015 1:31:56 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearance not met to combustibles. Should unit catch fire, the adjacent structure may also catch fire, possibly causing injury. | 3 | Clearance to combustible not met | Non-compliant_valves.png | file://x:/photopub/docs/0000000361/251d260e-4f91-49a7-bd2d-9ae1dc9d168b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a345c474_62cc_44e0_b03d_988bb7b2df18
GAIN-463929-2015 | GA-293854-2015 | 12/1/2015 1:31:56 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearance not met to combustibles. Should unit catch fire, the adjacent structure may also catch fire, possibly causing injury. | 3 | Clearance to combustible not met | Generator_Clearance.png | file://x:/photopub/docs/0000000361/fb142ba8-2f20-4afb-a46a-c31b976a2547.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a345c474_62cc_44e0_b03d_988bb7b2df18
GAIN-463922-2015 | GA-285977-2015 | 12/1/2015 1:31:56 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | WaterHtrVent.png | file://x:/photopub/docs/0000000361/24db0dd3-de8e-4c9a-94f6-2041e142e615.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1895e7d_f647_467d_af6a_e7999c8c4dec
ELIN-516052-2016 | UW-338097-2016 | 1/26/2016 9:16:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | Conductors undersized for the load. This is a fire hazard as the conductors can over heat if too much current passes through it. |  |  | A.png | file://x:/photopub/docs/0000000382/2d35ec3a-c3ba-4a67-999c-2ca867bb17f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07baf03f_31a4_4b47_81e0_4f22406c4726
ELIN-522024-2016 | UW-342764-2016 | 1/28/2016 12:24:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Interior rated electrical equipment has been exposed to the weather for a prolonger period time. Electrical equipment exposed to water may lead to an electrical shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | disrepair_electrical_shelter.png | file://x:/photopub/docs/0000000388/67001261-0ac8-4c85-8410-167b36762d8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b0c2cd_6279_486d_96e2_cc836acab878
ELIN-522024-2016 | UW-342764-2016 | 1/28/2016 12:24:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Interior rated electrical equipment has been exposed to the weather for a prolonger period time. Electrical equipment exposed to water may lead to an electrical shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | disrepair_shelter_around_electrical_equipment.png | file://x:/photopub/docs/0000000388/a3cb5d34-0353-444c-822a-a943eb021ee9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b0c2cd_6279_486d_96e2_cc836acab878
ELIN-522024-2016 | UW-342764-2016 | 1/28/2016 12:24:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Interior rated electrical equipment has been exposed to the weather for a prolonger period time. Electrical equipment exposed to water may lead to an electrical shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | water_damaged_electrical_equipment.png | file://x:/photopub/docs/0000000388/cbe1d505-16ba-4cbb-84ff-a2dc9fb7fa14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b0c2cd_6279_486d_96e2_cc836acab878
ELIN-510921-2016 | EL-317827-2015 | 1/15/2016 4:49:55 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Electrical service equipment is required to be secured to stable structures. Should the structure not be stable a considerable amount of strain can be imposed upon conductors and terminations. This could lead to equipment damage and or failure. During an inspection of a 240volt, 200amp, temporary construction service, the safety officer discovered that the original service pole had been removed and attached with rope to an adjacent pole. Should the rope fail, the original pole, which contains energized service equipment, would fall onto either the street or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Overhead_Service.png | file://x:/photopub/docs/0000000378/809e0593-ecd8-4b26-b4b3-d5888dc1b3d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__232832a5_5672_48c4_bfef_7c8293d443b9
ELIN-510921-2016 | EL-317827-2015 | 1/15/2016 4:49:55 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Electrical service equipment is required to be secured to stable structures. Should the structure not be stable a considerable amount of strain can be imposed upon conductors and terminations. This could lead to equipment damage and or failure. During an inspection of a 240volt, 200amp, temporary construction service, the safety officer discovered that the original service pole had been removed and attached with rope to an adjacent pole. Should the rope fail, the original pole, which contains energized service equipment, would fall onto either the street or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_pole_damaged.png | file://x:/photopub/docs/0000000378/a7261d21-b281-4c2a-b65a-8cb0fa9c74a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__232832a5_5672_48c4_bfef_7c8293d443b9
ELIN-515367-2016 | EL-304323-2015 | 1/25/2016 2:57:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Temp receptacle power does not have the protective cover plate installed leaving possibility to accidental contact to live terminals, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Basement_temp_outlet.png | file://x:/photopub/docs/0000000382/4d2492db-45da-4e5b-a188-33dfaac56a2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__511ba089_dc11_4aab_a6c8_bafc385227f3
ELIN-513650-2016 | EL-308998-2015 | 1/25/2016 2:57:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Temporary heat connections not terminated with appropriate methods exposing live conductors to contact with persons, temporary receptacles do not include cover plates, these are a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_recept__2.png | file://x:/photopub/docs/0000000382/7e614a02-fdb9-4d7c-8429-33ec3be3e40b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3183fce6_5706_4b8a_b0e3_e6b39c607c19
ELIN-524820-2016 | EL-331737-2016 | 2/11/2016 7:00:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a new single family dwelling with a 200amp 120/240volt single phase service, the electrode has been placed in a trench which is only 380mm in depth. This could result in a thermal situation. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | 380mm_depth.png | file://x:/photopub/docs/0000000390/7d3fa8ac-045f-4fdc-8ec3-00bd8e57eae4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3afb9a80_d4b7_4e12_937f_87bc02f9670c
PROP-465939-2015 | 2224039 | 12/17/2015 3:10:19 PM | ASSESS: PR OP: RAP | png | #asFound | PR040 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | U bolts clips utilized in the termination of a counterweight rope are installed in reverse of U bolt manufacturer's directions. U bolts clips utilized in creating a turned back loop termination are to be installed with the U bolt portion of the clip against the non-tensioned side of the loop. By reversing the U bolt there is risk of damaging rope at the tension point | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Counter_weight_rope_U_bolts.png | file://x:/photopub/docs/0000000370/424e96e0-44df-4574-8cc0-05730e3eecf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__D30D4D6B_B59E_493C_9178_F04FA78BF10D
PROP-465946-2015 | 2224174 | 12/16/2015 4:40:15 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | A single sheave that provides downward force to the haul rope (combo sheave) of a support sheave assembly (holds rope up) was identified as not providing enough down holding force. The purpose of the combo sheave is ensure haul rope stay firmly on the support sheave assembly in the event of a light load condition. There is a risk of haul rope derailment in the event of a light or negative load condition of the support sheave assembly. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Combo_sheave.png | file://x:/photopub/docs/0000000370/4328fd6b-2e53-4ed8-88fe-2fe1fa96b9bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95929234_AF7E_4D24_9C3E_AB6B14309D0A
ELIN-506043-2016 | EL-251396-2015 | 2/2/2016 4:05:33 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The code requires receptacles installed within 1.5M of sinks to be ground fault circuit interrupter (GFCI) protected. This is required to prevent persons from getting shocked/electrocuted when using portable appliances around water. This installation in a single family dwelling unit has two 15A, 120V receptacles installed within 1.5 meters of the laundry sink. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Front_of_house.png | file://x:/photopub/docs/0000000385/f67a950e-ef29-49a4-aaf8-5460babf6022.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2efcb73b_6c90_4dbe_b564_d99f38e1217e
ELIN-522024-2016 | UW-342764-2016 | 1/28/2016 12:24:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Interior rated electrical equipment has been exposed to the weather for a prolonger period time. Electrical equipment exposed to water may lead to an electrical shock or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | service_and_sub_service.png | file://x:/photopub/docs/0000000388/1e67db9d-7df4-45b8-aaad-15f7c745a4fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b0c2cd_6279_486d_96e2_cc836acab878
ELIN-524874-2016 | EL-154283-2014 | 2/11/2016 11:55:21 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Unused openings in electrical boxes and cabinets must be closed to prevent accidental contact with live parts. In this installation junction box covers had been left off an exterior lighting circuit. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_jb.png | file://x:/photopub/docs/0000000389/c0a8fa54-a937-4f4a-92b6-aecce663c8cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21a1ef3c_a035_4069_8961_e17a43805639
ELIN-524874-2016 | EL-154283-2014 | 2/11/2016 11:55:21 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Unused openings in electrical boxes and cabinets must be closed to prevent accidental contact with live parts. In this installation junction box covers had been left off an exterior lighting circuit. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Fixture_jb.png | file://x:/photopub/docs/0000000389/8be214be-5956-4e19-b9d1-95c80e05b8c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21a1ef3c_a035_4069_8961_e17a43805639
ELIN-513650-2016 | EL-308998-2015 | 1/25/2016 2:57:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Temporary heat connections not terminated with appropriate methods exposing live conductors to contact with persons, temporary receptacles do not include cover plates, these are a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_recept__1.png | file://x:/photopub/docs/0000000382/30cb5864-0107-41a9-b207-635a04d67d42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3183fce6_5706_4b8a_b0e3_e6b39c607c19
ELIN-513650-2016 | EL-308998-2015 | 1/25/2016 2:57:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Temporary heat connections not terminated with appropriate methods exposing live conductors to contact with persons, temporary receptacles do not include cover plates, these are a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_heat_connection.png | file://x:/photopub/docs/0000000382/a0274647-81db-402c-b37b-93401b544681.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3183fce6_5706_4b8a_b0e3_e6b39c607c19
ELIN-515367-2016 | EL-304323-2015 | 1/25/2016 2:57:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Temp receptacle power does not have the protective cover plate installed leaving possibility to accidental contact to live terminals, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Main_floor_temp_outlet.png | file://x:/photopub/docs/0000000382/41b92c1e-3ea1-4bf3-8fdc-08227fa1223d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__511ba089_dc11_4aab_a6c8_bafc385227f3
ELIN-513650-2016 | EL-308998-2015 | 1/25/2016 2:57:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Temporary heat connections not terminated with appropriate methods exposing live conductors to contact with persons, temporary receptacles do not include cover plates, these are a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_heat_connection__2.png | file://x:/photopub/docs/0000000382/953e5b53-f841-4ebc-8f05-80c0ce1e53c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3183fce6_5706_4b8a_b0e3_e6b39c607c19
ELIN-516202-2016 | UW-338970-2016 | 1/25/2016 8:05:21 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | Extension cord has internal bond wire that was bypassed by owner. | 3 | Conductors Equipment is not approved for the specific use. | Ships_point_cable_-1.png | file://x:/photopub/docs/0000000382/d72d14f6-6116-4f81-b0d1-53300cba69e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b73484a6_599a_4224_992d_4bd470eb0241
ELIN-516202-2016 | UW-338970-2016 | 1/25/2016 8:05:21 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | Extension cord has internal bond wire that was bypassed by owner. | 3 | Conductors Equipment is not approved for the specific use. | Ships_point_cable_-2.png | file://x:/photopub/docs/0000000382/111a1f78-1eec-45d4-970b-52d6b4a06b5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b73484a6_599a_4224_992d_4bd470eb0241
PROP-419378-2015 | 2224088 | 12/16/2015 4:57:09 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | A single sheave that provides downward force to the haul rope (combo sheave) of a support sheave assembly (holds rope up) was identified as not providing enough down holding force. The purpose of the combo sheave is ensure haul rope stay firmly on the support sheave assembly in the event of a light load condition. There is a risk of haul rope derailment in the event of a light or negative load condition of the support sheave assembly. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Combo_sheaves.png | file://x:/photopub/docs/0000000370/851c8f70-a4e1-4686-8b23-3c4be311cb81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3E6A8D03_C66E_4C95_8F0A_070B6AF02AE7
ELIN-510798-2016 | EL-335050-2016 | 1/20/2016 7:35:48 AM | ASSESS: EL: Final | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Metal part of lighting fixture found without bond to ground .when electrical equipment with metal parts is not bonded to ground, metal parts can become energized and overcurrent protection may not function. This can lead to property damage or potential injury to persons | 3 | Continuity Bonding conductor is not observed or broken | Light_fixtures_not_bonded_no_anti_abraion_.png | file://x:/photopub/docs/0000000382/0d11050a-cbba-45c6-8f23-e49b3a76d731.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a21d0cb_6da9_4bf6_9824_c189f1437c21
ELIN-506043-2016 | EL-251396-2015 | 2/2/2016 4:05:33 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The code requires receptacles installed within 1.5M of sinks to be ground fault circuit interrupter (GFCI) protected. This is required to prevent persons from getting shocked/electrocuted when using portable appliances around water. This installation in a single family dwelling unit has two 15A, 120V receptacles installed within 1.5 meters of the laundry sink. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacles_within_1500_mm_of_laundry_sink_without_GFCI_protection.png | file://x:/photopub/docs/0000000385/c4c175db-3d18-4c4c-9c4e-85d413756d51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2efcb73b_6c90_4dbe_b564_d99f38e1217e
BPVOP-521814-2016 | 2258668 | 1/28/2016 1:22:32 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP199 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | Data_plate_.png | file://x:/photopub/docs/0000000386/20f59885-9f16-43eb-be52-7920f820ef5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6a2e29_9212_4ff8_8844_d63da4902c65
BPVOP-502922-2015 | 3097554 | 12/30/2015 8:43:23 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 240*Fahrenheit, it is determined that safety relief valve exceeded 6yr interval for servicing or replacement (Regular testing and servicing ensures proper operation of safety relief valve). Failure to have safety relief valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary and lead to incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000376/9e7c4173-9c5a-408e-8c75-278a7a8142a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6ac7ea6_0529_44f7_b306_9aac10ac7d98
BPVIN-507332-2016 | UW-332976-2016 | 12/30/2015 8:43:20 AM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment of hot water heating system operating at 100psig it is determined that expansion tank is not rated for the operating pressure. Pressure boundary of expansion tank may fail and failure of pressure boundary can lead to incident. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Expansion_tank.png | file://x:/photopub/docs/0000000376/9c167e30-6213-41d1-9fd8-64893c97ca66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06821fb9_930f_4f77_aa6a_94997d9162a6
ELIN-508466-2016 | EL-331849-2016 | 1/13/2016 9:21:16 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Shock hazard in case of equipment failure. | 0 | No Created Hazard Identified | Service_panel.png | file://x:/photopub/docs/0000000377/4853495c-77e0-4005-a69b-25dc272edc46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f9fa24_a36f_4020_91de_7448475904c3
ELIN-508466-2016 | EL-331849-2016 | 1/13/2016 9:21:16 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Shock hazard in case of equipment failure. | 0 | No Created Hazard Identified | Service.png | file://x:/photopub/docs/0000000377/992c1e10-239b-439c-b570-c1d99fb7ac30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f9fa24_a36f_4020_91de_7448475904c3
ELIN-508466-2016 | EL-331849-2016 | 1/13/2016 9:21:16 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Shock hazard in case of equipment failure. | 0 | No Created Hazard Identified | Groundwire.png | file://x:/photopub/docs/0000000377/ff2206e3-ad37-4637-b0eb-f253886696be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f9fa24_a36f_4020_91de_7448475904c3
ELIN-508466-2016 | EL-331849-2016 | 1/13/2016 9:21:16 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Shock hazard in case of equipment failure. | 0 | No Created Hazard Identified | Cable_jacket.png | file://x:/photopub/docs/0000000377/d9fa660b-65c2-42b3-a8ab-607509d2e2eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11f9fa24_a36f_4020_91de_7448475904c3
BPVIN-519018-2016 | UW-340631-2016 | 1/29/2016 5:40:08 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | Upon assessment of expansion tank (dimensions: length-1.12meter and diameter-0.61meter) with Maximum Allowable Working Pressure of 125psig it is determined that vessel is not firmly anchored to floor or braced. In the event of earthquake of significant scale vessel may trip or move and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | IMPROPER_BRACING.png | file://x:/photopub/docs/0000000384/48e19ef5-dc6b-4201-a695-61f5154f9243.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8db0b406_530c_42c0_8bfa_eca25273b6c3
BPVIN-519032-2016 | UW-340646-2016 | 1/29/2016 5:39:23 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | Upon assessment of expansion tank (dimensions: length-1.12meter and diameter-0.61meter) with Maximum Allowable Working Pressure of 125psig it is determined that vessel is not firmly anchored to floor or braced. In the event of earthquake of significant scale vessel may trip or move and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | IMPROPER_BRACING_OF_VESSEL.png | file://x:/photopub/docs/0000000384/5caf6ea1-6686-4e2f-b802-d5c82984bdfe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e642eb0_c9ba_4fb5_8d58_d2ee49dc4ffe
ELIN-508838-2016 | EL-333827-2016 | 1/13/2016 2:50:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Switches and thermostat installed to close to bathtub. This is a shock hazard because there is a potential for the switches to be operated while standing in water. | 0 | No Created Hazard Identified | A.png | file://x:/photopub/docs/0000000377/6f82f6bc-8800-4d5f-b2c4-aec324ae3aae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811b3bd9_d9aa_4419_8a6e_df26ee58c18a
ELIN-503838-2016 | EL-328932-2015 | 1/4/2016 12:42:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Grounding.png | file://x:/photopub/docs/0000000373/de924fb3-8aa2-4f52-aeec-799d3be279ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39bff4f0_766c_45df_b230_03151f981099
GAIN-501884-2015 | GA-317326-2015 | 1/4/2016 4:01:19 PM | ASSESS: GA: Rough-In | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | A new boiler was installed in a mechanical room. The existing openings providing outdoor air supply to the appliance were of insufficient size for the requirements of the appliance. Lack of outdoor air supply could result in incomplete combustion. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Outdoor_air_supply_openings.png | file://x:/photopub/docs/0000000373/bff6ec12-1f59-4e98-b58d-e98185d98bb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd58f3b3_115b_45f4_ab07_41073f851aac
GAIN-501884-2015 | GA-317326-2015 | 1/4/2016 4:01:19 PM | ASSESS: GA: Rough-In | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | A new boiler was installed in a mechanical room. The existing openings providing outdoor air supply to the appliance were of insufficient size for the requirements of the appliance. Lack of outdoor air supply could result in incomplete combustion. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Boiler_x_1.png | file://x:/photopub/docs/0000000373/33023da3-1824-4d67-8cb1-a8ae204ae58c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd58f3b3_115b_45f4_ab07_41073f851aac
ELIN-517637-2016 | UW-339816-2016 | 1/27/2016 7:07:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found damaged, unsafe, unapproved and non-compliant electrical equipment which had conductors exposed and wired without use of junction box and cable connectors for luminaire installation. When conductors are not approved and installed properly to prevent electrical equipment damages, the electrical equipment could become an electrical fire or shock hazard to people and property | 3 | Conductors Equipment is not approved for the specific use. | 41.png | file://x:/photopub/docs/0000000384/e0aa0f30-e94a-4fb6-9481-bd29f4bf6d0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5da2da59_0d09_4293_ad31_42975d1e6dc2
ELIN-490003-2015 | EL-270999-2015 | 12/7/2015 10:49:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | The AC system must be grounded at the neutral to reduce the risk of shock, in the event of a fault. This assessment found the AC system ungrounded. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ungrounded_service_panel.png | file://x:/photopub/docs/0000000363/1e054b0f-ff60-4c67-a6dd-01af7c46e816.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__749e5812_fbd7_44d1_b6e2_b39dd1ed5ad6
GAIN-505327-2016 | GA-272143-2015 | 1/19/2016 7:40:50 PM | ASSESS: GA: Rough-In | png | #asFound | GA074 | Not accessible for replacement/adjustment | 1 | 1 | Unable to control gas flow to regulator without leaving the building. | 1 | Not accessible for replacement/adjustment | Missing_shut_off_valve.png | file://x:/photopub/docs/0000000379/46954920-a426-44e8-9a7e-b1616eb7e1a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3c1f658_04ab_4fdb_8fcc_f64f8b1a0acf
BPVOP-502308-2015 | 2260775 | 12/29/2015 9:49:37 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | BOILER_HW71966.png | file://x:/photopub/docs/0000000373/87627eed-2828-421b-808b-240a7ca36a3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f5abfbc_4600_4e81_b4b4_d005657ef241
ELIN-509062-2016 | EL-264067-2015 | 2/3/2016 8:30:01 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 200 amp, 120/240 Volt combination panel has branch circuit conductors passing through service box. This cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Branch_circuits_passing_through_main_breaker_compartment.png | file://x:/photopub/docs/0000000386/823f7fef-aa89-487e-9ae7-9065302d402a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a2d3250_44f9_4daa_91c4_c6c009e2bc31
ELIN-507081-2016 | EL-263526-2015 | 1/18/2016 2:35:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | 15A 120V branch wiring has been run to close to the bottom edge of the floor joist allowing possible mechanical damage from drywall installation, which could result in cable failure or fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_wiring.png | file://x:/photopub/docs/0000000379/f36bdd2d-2851-4937-b70b-b75c6c2e7318.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f711ca1_01b8_49e0_8cbe_5cbe7f191e9d
ELIN-496241-2015 | EL-290102-2015 | 12/23/2015 5:03:32 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 15A 120V cable has exposed ends that have not been protected from accidentally contact by persons which could result in a shock hazard. Cable could be energized as the breaker feeding this cable is not locked out. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Exposed_conductors.png | file://x:/photopub/docs/0000000370/97238f93-b1aa-4e32-9c7c-6d5349163d43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a2ce7fa_42cf_4a97_863c_0089fe5ab5c4
GAOP-492039-2015 | GA-323066-2015 | 1/11/2016 12:12:03 PM | ASSESS: GA OP: Periodic | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 2 | Fusible link missing and spring broken, emergency shut off will not automatically close | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 27358_58.png | file://x:/photopub/docs/0000000376/54989766-559d-4517-ae9a-fbd0a84458c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed58bf02_f9dc_44e1_b6ae_6ba4c1e8d032
GAOP-492039-2015 | GA-323066-2015 | 1/11/2016 12:12:03 PM | ASSESS: GA OP: Periodic | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 2 | Fusible link missing and spring broken, emergency shut off will not automatically close | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 27358_58th.png | file://x:/photopub/docs/0000000376/6d44cabc-3727-4c71-b0e6-246165388e88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed58bf02_f9dc_44e1_b6ae_6ba4c1e8d032
ELIN-502981-2015 | EL-315848-2015 | 1/14/2016 4:40:25 AM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Water will track into weather head. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | West_view_service.png | file://x:/photopub/docs/0000000378/005e8b65-0c0a-4c32-85a9-a961374ffa86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c949fa4a_5e30_4ad6_8f9e_d291e0603a2e
ELIN-518048-2016 | EL-325400-2015 | 1/29/2016 1:54:08 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The 120/240V alternating current system in the home has not been grounded. Without a connection to a grounding electrode the branch breakers may not operate as intended resulting in a shock hazard and possible equipment damage or fire. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding.png | file://x:/photopub/docs/0000000384/4a0a67cd-6c9b-4b8b-a843-9dee5cfec017.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__233ecafb_d41c_4605_bf63_605679c10333
BPVOP-480408-2015 | 2258845 | 11/24/2015 7:40:37 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | The Safety Relief Valve installation date was more than 6 years as specified in CSA B51. All pressure relief devices require periodic inspection, testing and service. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | expired_SRV.png | file://x:/photopub/docs/0000000357/b45a8eca-0edc-4494-a0d0-d405bb8ee870.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6ffa6ad_8b18_4b5c_b076_f0fad288b515
BPVOP-479979-2015 | 2993384 | 11/24/2015 7:40:07 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found that the replacement for safety valve(s) was not done as per CSA B-51. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Expired_SRV.png | file://x:/photopub/docs/0000000357/cbbca769-54bc-4c22-8921-be0a5d68ced6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d88b0c6_cd8d_4248_b074_bfa1f805f0cf
ELIN-511662-2016 | EL-326292-2015 | 1/25/2016 10:31:56 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Temporary lighting circuit energized. Hot lamp touching painted combustible surface. Possibility of fire due to pyrolysis. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_lighting_in_contact_with_drywall.png | file://x:/photopub/docs/0000000382/6b237eae-2576-4b1d-9b35-b3f672eac3a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56303d00_13b3_4ab6_8386_faf75dd75b04
ELIN-502811-2015 | EL-318657-2015 | 1/6/2016 10:07:15 AM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Realtor_sign.png | file://x:/photopub/docs/0000000375/949e277a-22db-484f-bf1d-c6e9c06ab36b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7d053d3_e6b6_4833_bb22_645aa5499b15
ELIN-502199-2015 | EL-300454-2015 | 1/7/2016 1:45:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service raceway exceeds 1.5m of total unprotected length inside structure increasing exposure to mechanical damage. Mechanical damage of unused portions of consumer service raceway could lead to serious personal injury (shock) or catastrophic property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View02_service_raceway.png | file://x:/photopub/docs/0000000376/6646d1d8-b884-4115-8c6c-63941db89efd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1392dc4_f525_4977_b920_c1c11ede6f26
ELIN-502199-2015 | EL-300454-2015 | 1/7/2016 1:45:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service raceway exceeds 1.5m of total unprotected length inside structure increasing exposure to mechanical damage. Mechanical damage of unused portions of consumer service raceway could lead to serious personal injury (shock) or catastrophic property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_service_raceway.png | file://x:/photopub/docs/0000000376/d7930512-f79a-4e5a-86d7-6c39f66f3c3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1392dc4_f525_4977_b920_c1c11ede6f26
ELIN-498837-2015 | UW-328106-2015 | 12/18/2015 4:41:18 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Electronic 1000W ballasts installed on combustible surfaces. Lighting ballasts are sources of heat and cannot be installed on combustible surfaces. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | A.png | file://x:/photopub/docs/0000000369/d3092439-802f-4bf9-a66a-c877c9264a6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c348c17_ece3_4010_8e97_6222cc0b56b5
BPVOP-505923-2016 | BPV-108374-2014 | 1/12/2016 5:29:55 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP098 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | 4 | 4 | I found the bottom connection on the water column completely blocked by scale. Potential exists for an incident to occur due to the Low Water Cutoff Device and the water gauge not to provided the intended control.The second Low Water Cutoff device was functional. | 4 | 2.0.1 Control system may overrun - Operating Controls bypassed or failed but backup corresponding safety devices operational | Bottom_of_water_column.png | file://x:/photopub/docs/0000000376/e4804bb9-3035-4bb1-8c13-496fcc05c144.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7790ca32_8362_444b_8f52_8ccf4a30f649
BPVOP-508053-2016 | BPV-108375-2014 | 1/12/2016 2:36:22 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD.png | file://x:/photopub/docs/0000000377/9180434d-8cfa-48cd-a658-fc6685b843ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0370ee0a_1ece_4e04_83de_9b4e89ffe778
BPVOP-492590-2015 | BPV-163601-2014 | 12/9/2015 9:17:33 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Upon assessment of high pressure steam boiler with Maximum Allowable Working Pressure (MAWP) of 150psig, it is determined that boiler shell has two localized corrosion patch. If corrosion in these areas is not eliminated, pressure boundary may fail at pressure well below MAWP and may cause severe incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | CORROSION_PATCH.png | file://x:/photopub/docs/0000000364/14a0b6b2-ecb8-4330-8247-7b8e1cbf5e4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__031ecbc2_fdd3_4292_adb9_f9c6d155dd7b
ELIN-487482-2015 | EL-280752-2015 | 12/1/2015 3:15:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The installation of non metallic sheath cable conductors requires 25 mm of separation from heating ducts. Damage can occur when conductors are in contact creating a shock or fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Lighting_requires_mechanical_protection.png | file://x:/photopub/docs/0000000360/1eff5396-bcb9-4d95-b52c-d476a9a67413.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8294689b_95d8_414d_9f84_0b33dd632585
ELIN-487482-2015 | EL-280752-2015 | 12/1/2015 3:15:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The installation of non metallic sheath cable conductors requires 25 mm of separation from heating ducts. Damage can occur when conductors are in contact creating a shock or fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | No_supports_on_flexible_conduit.png | file://x:/photopub/docs/0000000360/c8817c4b-c522-4a76-b65a-142b5ff6866f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8294689b_95d8_414d_9f84_0b33dd632585
ELIN-487482-2015 | EL-280752-2015 | 12/1/2015 3:15:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The installation of non metallic sheath cable conductors requires 25 mm of separation from heating ducts. Damage can occur when conductors are in contact creating a shock or fire hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD_90_on_heating_ducts.png | file://x:/photopub/docs/0000000360/ad250b38-fef6-42d1-a2a2-4458f0f136c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8294689b_95d8_414d_9f84_0b33dd632585
ELIN-487484-2015 | EL-280752-2015 | 12/1/2015 3:15:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The service conduit requires adequate support to ensure the equipment is secure. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Unsupported_service_conduit.png | file://x:/photopub/docs/0000000360/4aee0eab-e14d-47cc-94d3-6dc7d949cf0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6204fe9e_5ca8_457d_90e1_7be033b532e5
ELIN-471527-2015 | EL-101692-2014 | 11/27/2015 5:26:04 PM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | The sheaths on armoured cables must be electrically and mechanically continuos to protect the conductors and to provide a cable bond. In this installation no connector had been installed at a plastic junction box where an armoured cable exited one building and ran to a second. Failure to provide electrical and mechanical continuity could result in a shock hazard. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | No_connector.png | file://x:/photopub/docs/0000000359/151800a8-825a-492b-b0cf-bb6a31eac748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83b69e85_6c7b_416f_8d46_1908d2a7f767
BPVOP-484813-2015 | 4637998 | 11/19/2015 11:29:29 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP071 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | piping_corrosion.png | file://x:/photopub/docs/0000000359/9da11a72-2a99-47f6-a4b5-fe0f8db9bcc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d67ec443_261d_4ed3_afaa_19d86c720241
BPVOP-484813-2015 | 4637998 | 11/19/2015 11:29:29 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP071 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | piping_corrosion_2.png | file://x:/photopub/docs/0000000359/1158ceb2-9dad-4590-a35c-e01a4039b629.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d67ec443_261d_4ed3_afaa_19d86c720241
GAIN-507415-2016 | GA-333004-2016 | 1/12/2016 11:42:12 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Two newly installed gas ranges have been left in operation but the restraint devices have not been installed and when ranges are moved for cleaning stained could be put on the gas hose connector causing them to leak | 2 | Physical protection of piping and tubing absent. | 21667_216.png | file://x:/photopub/docs/0000000376/e4bdcdb7-05c0-4db2-8371-d4792feb9a2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceee8ada_fe70_4911_a90d_4583d7d56ab5
GAIN-504779-2016 | GA-330771-2015 | 1/27/2016 3:20:13 PM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | Underground 2 Psi gas line enters building Barlow grade. | 3 | Underground piping entering a building below grade (unapproved) | 3380_Eek_Road_Rock_Creek.png | file://x:/photopub/docs/0000000383/a6273087-9c54-4172-8dc9-49398eba441e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f93fd259_69ad_4f09_9a82_bd72133b484b
ELIN-518805-2016 | EL-340492-2016 | 2/1/2016 7:26:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 100 amp, 120/240 volt combination panel has conductors passing through service box. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Conductor_passes_through_service_compartment_.png | file://x:/photopub/docs/0000000385/d2f15f12-a707-439d-aeee-70e4f23eed3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb8b9697_2ca2_4d92_89aa_c239b00d47be
ELIN-498116-2015 | EL-325476-2015 | 12/17/2015 1:44:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary Type R2 Panels are exposed to weather without a lockable door. Building is accessible to public. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panels_not_protected_and_no_lockable_door.png | file://x:/photopub/docs/0000000368/3874713b-037e-43fb-838b-c9cfd6248efe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a915c6a_58c1_4d22_9025_2facc6476faa
ELIN-524997-2016 | UW-344366-2016 | 2/10/2016 10:54:08 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | A mobile home with a 200 amp 240 volt main service was found collapsed with the roof laying on furniture and floor of building. The electrical panel was totally inaccessible due to damage to the structure. The utility took action to eliminate the immediate risk to the occupant of the property and surrounding properties. The branch circuit wiring was observed as physically damaged in multiple locations and this would have likely have resulted in an unsafe condition that could lead to a fire or injury to persons and in this case surrounding properties. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Ongoing_corrosiom_main_service_equipment.png | file://x:/photopub/docs/0000000389/390f0c30-830f-429c-9fb8-51128ac8561c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3dfc5cc_d4bc_48f4_a8ef_011de27428be
ELIN-524997-2016 | UW-344366-2016 | 2/10/2016 10:54:08 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | A mobile home with a 200 amp 240 volt main service was found collapsed with the roof laying on furniture and floor of building. The electrical panel was totally inaccessible due to damage to the structure. The utility took action to eliminate the immediate risk to the occupant of the property and surrounding properties. The branch circuit wiring was observed as physically damaged in multiple locations and this would have likely have resulted in an unsafe condition that could lead to a fire or injury to persons and in this case surrounding properties. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Mobile_home_collsed_under_snow_load_panel_inaccessible.png | file://x:/photopub/docs/0000000389/f69afd68-aa1e-4f08-8070-9a0c2c213358.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3dfc5cc_d4bc_48f4_a8ef_011de27428be
ELIN-501367-2015 | EL-307032-2015 | 12/29/2015 4:41:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The gas pipe was not bonded as required. Should the gas pipe become energized there's a potential for a person to receive a shock; as the AC system may not recognize a fault and trip the breaker. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Range_receptacl__range_receptacle.png | file://x:/photopub/docs/0000000371/003424de-43a3-458d-855a-f18b70de6623.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ac6ee2b_c706_4361_8299_f523adfd5870
ELIN-501367-2015 | EL-307032-2015 | 12/29/2015 4:41:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The gas pipe was not bonded as required. Should the gas pipe become energized there's a potential for a person to receive a shock; as the AC system may not recognize a fault and trip the breaker. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_pipe_and_panel.png | file://x:/photopub/docs/0000000371/30b560b6-e966-4cce-96d0-7dde5db12458.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ac6ee2b_c706_4361_8299_f523adfd5870
EDOP-502911-2015 | 2038176 | 12/24/2015 9:21:44 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If a car is stopped/stuck outside of a landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety manual opening of the elevator car doors when an elevator car is outside the unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of Fidelity's due to this condition. The picture of the car door restrictor is a sample picture. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000372/be2326e3-eaaf-4237-8cbe-ec7177f758a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__422e37d7_6e37_4718_9977_c09bbf860ad5
ELIN-515559-2016 | 5437857 | 1/28/2016 7:46:33 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt exterior receptacles use standard weatherproof cover plates and not in use cover plates. This could become a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_receptacles.png | file://x:/photopub/docs/0000000384/1cd05d14-1e48-4c62-8f8d-4f935cb8ff20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a45e257_2f1f_4e80_ace4_e803d6e7a458
ELIN-518039-2016 | EL-251101-2015 | 2/2/2016 7:20:14 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A 200 amp 240 volt 1 phase consumers service mast has been enclosed in combustible material and is inside building. Consumers service conductors lack effective overcurrent protection and can cause damage to property or injury to persons when they fail when installed inside the building envelope | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Mast_enclosed_inside_building_combustible_construction.png | file://x:/photopub/docs/0000000385/9760b4d3-ca63-4bbc-bd46-23defd23fdce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0334178_e765_4018_b68c_c950c66e3de0
ELIN-517325-2016 | EL-339593-2016 | 2/1/2016 7:20:10 AM | ASSESS: EL: Final | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Receptacles for 120 volt 15 amp outlets are not provided in finished walls of heated living area to minimum spacings. Owners or occupants will resort to the use of flexible extension cords where receptacles are not provided. Both is leads to increased risk for property damage or electric shock potential | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacles_not_provided_minimum_spacings.png | file://x:/photopub/docs/0000000385/7f8f8d47-c644-4530-8c83-2c5cbe4a8bd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__272f1106_7780_4936_b7ab_ec979cb74da4
ELIN-503841-2016 | EL-305399-2015 | 1/6/2016 1:20:52 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Metal device boxes are required to be bonded to ground to ensure proper operation of over current devices. During a rough wire inspection, two metal range receptacle boxes were not bonded. In the event of a ground fault, the over current device may not open the circuit (trip) due to a potential high impedance path to ground. This could lead to a possible fire / shock hazard. Note, safety office was unable to adjust the hazard rating to a level three. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Metal_range_box_s_not_bonded_to_ground.png | file://x:/photopub/docs/0000000374/5bbdc7c4-3e7f-44c6-a421-96fbbe1b5230.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__751fb092_57e0_4e7b_a859_2721f751c84f
ELIN-519593-2016 | EL-340401-2016 | 2/3/2016 7:06:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | 60 amp 120/240 volt service conductor cable installed on ground. No mechanical protection installed. This could cause equipment damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_conductors_installed_at_ground.png | file://x:/photopub/docs/0000000386/22ddfa14-4a59-4169-9665-ae0f4d7395c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a6a326f_d488_4c70_ba43_23f7e148126b
ELIN-522949-2016 | EL-334478-2016 | 2/9/2016 9:59:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 2 | A new 200amp 120/240volt single family dwelling supply service is installed without an expansion coupling in place. This can lead to equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Only_1_expansion_coupling.png | file://x:/photopub/docs/0000000388/0e128a5e-1d06-4f73-9f50-c5dfb5cb8fcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51cb48ad_db1c_4aed_8e76_926afcd7fc9e
GAIN-521755-2016 | GA-336799-2016 | 2/10/2016 4:41:02 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Concentric_adapter.png | file://x:/photopub/docs/0000000390/7cef3def-36af-4c74-bc72-6e4f0eb2a037.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8820f7db_3cd0_41a2_aeca_cfe60410594e
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Open_splice_flexible_cord_to_permanent_wiring_for_lighting.png | file://x:/photopub/docs/0000000389/806e703a-88df-4446-9957-ca82a8fadc09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Open_splice_on_flexible_cord_to_permanent_wiring_system_for_lighting.png | file://x:/photopub/docs/0000000389/a26e3b41-f245-43fa-8072-b7123c2c19f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_open_splice_for_exterior_lightng.png | file://x:/photopub/docs/0000000389/e35e1333-fa4c-42b2-a80b-49b6aef53803.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Front_of_building.png | file://x:/photopub/docs/0000000389/86b02098-389c-458e-bfca-80de4980888f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_permanent_wiring.png | file://x:/photopub/docs/0000000389/8c2a3ad2-5729-46ae-86f1-5e4020245172.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_lighting.png | file://x:/photopub/docs/0000000389/836bf7ba-71b5-4fe7-be04-5a6565bb269e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_lighting_.png | file://x:/photopub/docs/0000000389/8e234f3b-9ee4-4e81-ba5a-239c0b2e9f1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_for_exterior_lighting_running_through_door_and_spliced.png | file://x:/photopub/docs/0000000389/9bbc14f3-b4cb-444a-b129-4a336b8aea02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_open_splice_for_exterior_lighting.png | file://x:/photopub/docs/0000000389/c2c586a0-090f-4b24-aa2f-f13a54c61e2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_permanent_wiring_for_panel_feeder_to_suite_panel.png | file://x:/photopub/docs/0000000389/9aa8e999-76a7-4e76-97ba-e96869591d83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_permanent_wiring_for_lighting.png | file://x:/photopub/docs/0000000389/d2263343-c8d6-4865-9e83-e5ae328f2652.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_exterior_lighting_.png | file://x:/photopub/docs/0000000389/75b873e9-9070-496e-9392-626b8c16a900.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_permanent_wiring_attached_to_wall_and_passing_through_walls.png | file://x:/photopub/docs/0000000389/e27f3332-a042-443a-ade0-c72caded9e9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_per_ament_wiring_for_exterior_lighting.png | file://x:/photopub/docs/0000000389/5b4befb0-21ed-46e8-abfd-6ec6779e9fe6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELIN-524137-2016 | UW-343868-2016 | 2/9/2016 9:43:57 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not permitted to be used as a substitute for fixed wiring of structures and are not permitted to be permanently secured to structural members, run through holes in walls, ceilings, or doorways. This is because flexible cords are not tested and approved for this application and in most cases lack the appropriate insulation integrity and durability for permanent wiring use. This existing installation in an older mixed use commercial/residential building had flexible cords used in multiple locations as a substitute for permanent wiring. Flexible cords are attached to the structure, run through holes in walls, ceilings, and doorways. Flexible cords are open spliced for junctions to other flexible cords, light fixtures and permanent wiring systems. This is a potential fire and shock hazard if flexible cords get damaged and if persons or objects come in to contact with damaged flexible cords or open splices on flexible wiring. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_prmanent_wiring_for_suite_panel_feeder.png | file://x:/photopub/docs/0000000389/5ab54238-169a-4314-9de0-ba95e3b5b540.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92308a92_0546_40d6_b88d_6c10fccaea92
ELOP-489203-2015 | EL-320952-2015 | 12/4/2015 7:52:43 AM | ASSESS: EL OP: Acceptance | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Generators for temporary power and the associated connections where exposed to access from the general public. The temporary panel feeding the kitchen cooking equipment was 'stuffed' under a temporary table that was being used for the deep fryers and hot plates without allowing proper access to any of the over urgent devices. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Generator_and_cabling_exposed_to_general_public-1.png | file://x:/photopub/docs/0000000363/4cb73952-3c45-410f-a5fa-cecef69505a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30be88b2_5893_42b2_a000_7f45832c3d57
ELOP-489203-2015 | EL-320952-2015 | 12/4/2015 7:52:43 AM | ASSESS: EL OP: Acceptance | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Generators for temporary power and the associated connections where exposed to access from the general public. The temporary panel feeding the kitchen cooking equipment was 'stuffed' under a temporary table that was being used for the deep fryers and hot plates without allowing proper access to any of the over urgent devices. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Power_cables_run_through_the_exterior_sheathing_of_the_building.png | file://x:/photopub/docs/0000000363/5b58220f-cc2b-42ef-adde-24994f236b35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30be88b2_5893_42b2_a000_7f45832c3d57
ELIN-496199-2015 | EL-313123-2015 | 12/16/2015 1:37:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240 volt 200 amp indoor rated panel installed were panel is subject to outdoor weather elements. This could cause damage to equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution_installed_without_weatherproof_lockable_enclosure.png | file://x:/photopub/docs/0000000367/ba8c2958-9b76-4e60-bacd-5708218b386f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9087fcb5_13b9_4299_b303_55fa58a10bee
ELIN-511515-2016 | EL-334866-2016 | 1/28/2016 10:32:25 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head supply and consumer service conductors are required to be a minimum of 3.5 meters above grade. This is required to prevent accidental or intentional contact with energized conductors and to prevent mechanical damage to the conductor connections and insulation. This existing mobile home service installation has over head consumer service conductors that are located 2.3 meters from grade in an accessible location. Left uncorrected this is a potential shock and fire hazard if persons or objects contact the conductors and damage the connections or conductor insulation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | East_side_of_mobile_where_service_is.png | file://x:/photopub/docs/0000000384/517b9d93-d479-4488-9448-44a5ce3dadea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e791e2_e67e_49e3_adbc_85b9f03022bf
ELIN-511515-2016 | EL-334866-2016 | 1/28/2016 10:32:25 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head supply and consumer service conductors are required to be a minimum of 3.5 meters above grade. This is required to prevent accidental or intentional contact with energized conductors and to prevent mechanical damage to the conductor connections and insulation. This existing mobile home service installation has over head consumer service conductors that are located 2.3 meters from grade in an accessible location. Left uncorrected this is a potential shock and fire hazard if persons or objects contact the conductors and damage the connections or conductor insulation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Side_of_mobile_home_where_service_is.png | file://x:/photopub/docs/0000000384/481167de-ed24-49cf-b88b-441ebb5ac6fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e791e2_e67e_49e3_adbc_85b9f03022bf
ELIN-511515-2016 | EL-334866-2016 | 1/28/2016 10:32:25 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head supply and consumer service conductors are required to be a minimum of 3.5 meters above grade. This is required to prevent accidental or intentional contact with energized conductors and to prevent mechanical damage to the conductor connections and insulation. This existing mobile home service installation has over head consumer service conductors that are located 2.3 meters from grade in an accessible location. Left uncorrected this is a potential shock and fire hazard if persons or objects contact the conductors and damage the connections or conductor insulation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Tape_measure_showing_distance_from_ground_to_service_conductors_2300mm.png | file://x:/photopub/docs/0000000384/70e81d15-dc5c-4ae2-9ef1-263ec6aeab78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e791e2_e67e_49e3_adbc_85b9f03022bf
ELIN-511515-2016 | EL-334866-2016 | 1/28/2016 10:32:25 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head supply and consumer service conductors are required to be a minimum of 3.5 meters above grade. This is required to prevent accidental or intentional contact with energized conductors and to prevent mechanical damage to the conductor connections and insulation. This existing mobile home service installation has over head consumer service conductors that are located 2.3 meters from grade in an accessible location. Left uncorrected this is a potential shock and fire hazard if persons or objects contact the conductors and damage the connections or conductor insulation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Picture_of_my_hand_touching_the_service_cable.png | file://x:/photopub/docs/0000000384/fd9a16dd-02c5-4308-9558-f1d7ac5d49b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e791e2_e67e_49e3_adbc_85b9f03022bf
ELIN-511515-2016 | EL-334866-2016 | 1/28/2016 10:32:25 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head supply and consumer service conductors are required to be a minimum of 3.5 meters above grade. This is required to prevent accidental or intentional contact with energized conductors and to prevent mechanical damage to the conductor connections and insulation. This existing mobile home service installation has over head consumer service conductors that are located 2.3 meters from grade in an accessible location. Left uncorrected this is a potential shock and fire hazard if persons or objects contact the conductors and damage the connections or conductor insulation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Mobile_home.png | file://x:/photopub/docs/0000000384/047ea469-4167-42dd-8225-e32c12dd6045.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e791e2_e67e_49e3_adbc_85b9f03022bf
ELIN-522947-2016 | EL-328433-2015 | 2/9/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 2 | A new 200amp 120/240volt single family dwelling supply service is installed without an expansion coupling in place. This can lead to equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | No_expansion_joints.png | file://x:/photopub/docs/0000000388/83cee3ac-a773-4b9e-b9bd-da2854e19dcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82a16dfb_2cef_44af_b700_3d4f1af191e7
ELIN-513755-2016 | EL-321234-2015 | 2/9/2016 3:55:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 | In a new residence, a 240volt 20amp construction heater is hard wired after removing the receptacle the electrician provided. This is a shock hazard. | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | Heater_connection.png | file://x:/photopub/docs/0000000388/84ed5c0f-e780-4ed6-afe1-7c1d07130bcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__735c43a1_3aec_4ed1_b45e_dc63b8ae824a
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 3.png | file://x:/photopub/docs/0000000390/30ea0ae2-3ccb-42f2-ab68-111c89918432.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 2.png | file://x:/photopub/docs/0000000390/4ad6939b-a1e5-4e96-84f3-620492d66550.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 5.png | file://x:/photopub/docs/0000000390/ef32304a-5143-434d-b46e-9d2589e3d04f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 12.png | file://x:/photopub/docs/0000000390/8a1a91b1-1179-4805-92e3-f8e3fd15886a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 7.png | file://x:/photopub/docs/0000000390/18fa87d2-cc15-4189-9cef-d2d899c80bdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 9.png | file://x:/photopub/docs/0000000390/fbb6dac9-d65f-42d9-9e93-e20333d828a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 8a.png | file://x:/photopub/docs/0000000390/d89cb8f4-07b2-4013-a99f-ebd9d3e0ddd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 13.png | file://x:/photopub/docs/0000000390/95494e88-de3c-4fb8-a6f3-6e5fd72e39b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 11.png | file://x:/photopub/docs/0000000390/31354d8b-0dcd-49a1-bfcb-bf32c30d21e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 10.png | file://x:/photopub/docs/0000000390/4cc17a1e-320a-4d57-bb22-7f0b98c52ced.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 4.png | file://x:/photopub/docs/0000000390/bd2abfda-e696-4b82-a2bd-7b5878b60753.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 1.png | file://x:/photopub/docs/0000000390/cdd7325a-cfc6-4f73-ae76-8a650555b52e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
ELIN-514788-2016 | UW-337460-2016 | 1/20/2016 10:55:27 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found installation done for temporary lighting electrical equipment rated 120 volt 15 amps for luminaires that had unapproved wiring method done using AC90 armoured cable with a cord cap end on end of armoured cable. The AC90 cable conductors had missing armour with exposed energized conductors and improper continuous bonding of electrical equipment. When approved electrical equipment is altered, is non-compliant, is unapproved wiring and is unsafe by code standards , the unapproved electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 6.png | file://x:/photopub/docs/0000000390/0177b52c-5542-4824-bf6c-934cf3bbf988.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3972af_f3dc_478c_9f3f_68b1d3611336
GAUP-522728-2016 | UW-343005-2016 | 2/4/2016 1:00:23 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | Commercial range pilot had extinguished due to causes unknown, cleaning staff accidentally opened gas valve allowing gas to flow into kitchen, gas went up into exhaust hood and was vented into outside air but due to location and prevailing winds gas blows directly back to side of building above causing residents to "smell gas". If raw gas finds a source of ignition possible small fire or fireball could result. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Range.png | file://x:/photopub/docs/0000000390/3a28def5-695c-48b4-a5e0-3ff892f4ddca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8613995_7637_4ccb_8ded_574c73fe5ee4
ELIN-486314-2015 | EL-279165-2015 | 11/30/2015 4:39:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Potential damage to cable if minimum clearances are not maintained or mechanical protection not provided for cable. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Armored_cable_location_.png | file://x:/photopub/docs/0000000359/0007d349-2250-4d85-9516-bfa95a0dac9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9015d800_37ca_4793_a912_79843abf48ff
ELIN-483485-2015 | EL-313630-2015 | 11/30/2015 4:39:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 | The treated 6x6 post with the service equipment mounted on it does not have any support bracing. | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | TCS_POST.png | file://x:/photopub/docs/0000000359/88aa6eb9-98e4-407f-a0ff-ad6177b7072f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7baa9633_95d4_49c4_b024_d685279b1181
ELOP-489203-2015 | EL-320952-2015 | 12/4/2015 7:52:43 AM | ASSESS: EL OP: Acceptance | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Generators for temporary power and the associated connections where exposed to access from the general public. The temporary panel feeding the kitchen cooking equipment was 'stuffed' under a temporary table that was being used for the deep fryers and hot plates without allowing proper access to any of the over urgent devices. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Power_cabling_connections-1.png | file://x:/photopub/docs/0000000363/74c60368-be12-4bca-a21c-e991fb060e93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30be88b2_5893_42b2_a000_7f45832c3d57
ELIN-491711-2015 | EL-304810-2015 | 12/9/2015 4:49:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL048 | General Equipment is not protected from sprinklers in area. | 2 | 2 | Electrical equipment installed in rooms equipped with sprinklers for fire protection must be protected against streams of water entering the equipment. In this installation a ventilated electrical panel was installed directly in the line of spray in a sprinkler-protected room. | 2 | General Equipment is not protected from sprinklers in area. | Ventilated_equipment.png | file://x:/photopub/docs/0000000364/eb92ebfd-6d5e-46cd-b067-93f484845525.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a157e606_d0db_49da_a710_e6d2355660ee
BPVOP-513005-2016 | 4298216 | 1/20/2016 4:04:05 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP080 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | 4 | 4 | Refractory is required to protect boiler components from overheating and to protect personnel from burns. I found that there was a sign of external cover overheating because of damaged refractory on this low pressure steam boiler. This condition creates fire and injury hazard. | 4 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | Signs_of_overheating_.png | file://x:/photopub/docs/0000000380/e47f2ee7-2cb8-4a78-8c99-ec19d48945cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07806d11_c3ae_4c42_9d17_c6a06fbd8e03
ELIN-506912-2016 | EL-317789-2015 | 2/2/2016 2:18:00 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The bonding is missing on the gas line to which the 15 amp 120 volt circuit for the gas furnace could fault and energize the gas line creating a shock hazard | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_line_bonding_missing.png | file://x:/photopub/docs/0000000385/cad70ddd-185f-4b47-b99f-741e3ca58460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72932c7a_6d8d_43b8_8863_8bab1599e572
ELIN-523522-2016 | UW-343583-2016 | 2/11/2016 1:06:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL175 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | 2 | 3 | The 20amp 240 volt condensing unit on the exterior of the mobile home has the service disconnect location at near grade level behind the unsuitable mounting of the condensing unit. This can lead to equipment damage and possible shock and thermal issues. | 2 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | Exterior_condensing_unit_and_disconnect.png | file://x:/photopub/docs/0000000389/de5c6acd-43c2-474e-aebb-99e4e02d05fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7caace2f_fb78_4b19_9284_2b319239fca1
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 102.png | file://x:/photopub/docs/0000000385/5bcdb034-481f-481f-bca2-89866052842a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 100.png | file://x:/photopub/docs/0000000385/8313bdf9-a292-4495-9ea9-72024a8c035b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 101.png | file://x:/photopub/docs/0000000385/68e4766c-5e51-47e0-ad3e-624a628164dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 106.png | file://x:/photopub/docs/0000000385/0a9d95c9-20a4-472c-9320-a173895679e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 104.png | file://x:/photopub/docs/0000000385/4820b0d2-2a61-4d7a-aff5-b769168d662c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 105.png | file://x:/photopub/docs/0000000385/da0227ce-4276-4f4b-87dc-347bb43f9883.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520397-2016 | UW-341765-2016 | 1/29/2016 11:59:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found a temporary construction wooden enclosure with panelboard rated 120/240 volts 100amp is energized and has exposed bus bars showing where there are several empty breaker spaces. When panel boards have exposed energized conductors that a person or other equipment can come into contact with energized bus bars, then this is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 103.png | file://x:/photopub/docs/0000000385/7f051357-f934-4f07-a9d1-834c8af738e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a7091d8_6bf2_4c56_b3f6_38997498ffb7
ELIN-520934-2016 | EL-309388-2015 | 2/1/2016 8:10:29 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Non_treated_backing.png | file://x:/photopub/docs/0000000386/3bb6cb54-8688-448c-a1c0-507b64bf4f89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b700c3a8_fdec_4a33_9265_61ae8b36dff1
ELIN-523517-2016 | UW-343580-2016 | 2/5/2016 4:28:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 5 | The 100 amp 240 volt service had a sub feeder cable tapped off of the main breaker under same lugs as main consumer service cable, both the use of mixing dissimilar metals of copper and aluminum conductors along with not protecting the smaller conductor with the properly rated breaker protection has made this both a thermal and equipment damage concern | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Main_unit_panelboard.png | file://x:/photopub/docs/0000000389/e48a9469-d401-448b-a678-8d6dde691762.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__984b2815_00ce_42a2_8632_e042bae4066f
ELIN-523522-2016 | UW-343583-2016 | 2/11/2016 1:06:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL175 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | 2 | 3 | The 20amp 240 volt condensing unit on the exterior of the mobile home has the service disconnect location at near grade level behind the unsuitable mounting of the condensing unit. This can lead to equipment damage and possible shock and thermal issues. | 2 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | Heat_trace_cable.png | file://x:/photopub/docs/0000000389/71601d67-34d7-4ca5-b93c-16da452cf2cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7caace2f_fb78_4b19_9284_2b319239fca1
ELIN-523162-2016 | EL-273547-2015 | 2/15/2016 9:11:22 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | 120 volt 15 amp jetted tub installed without GFCI protection. Current leakage can not be detected. This is a shock hazard. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | Distribution_panel_without_GFCI_protection_for_jetted_tub_.png | file://x:/photopub/docs/0000000391/1cec1895-b69d-4622-8ad4-655a256fcd5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2655e3f_abad_4cb2_8c8f_233697a65d45
ELIN-490137-2015 | UW-321731-2015 | 12/4/2015 9:51:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized parts require mechanical protection to prevent accident contact. A person or conductive material coming in contact with energized parts would result in shock and or equipment damage. During an inspection of un-permitted work, several energized 208volt three phase load centers did not have their covers installed. There were individuals working in proximity of these panels. This situation created a possible Shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_Panel_Missing_Panel_Filler.png | file://x:/photopub/docs/0000000361/29a3443c-6a55-49df-af2b-48b18dc28e02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc898f5e_b504_404b_897d_806abea4ebf5
ELIN-490137-2015 | UW-321731-2015 | 12/4/2015 9:51:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized parts require mechanical protection to prevent accident contact. A person or conductive material coming in contact with energized parts would result in shock and or equipment damage. During an inspection of un-permitted work, several energized 208volt three phase load centers did not have their covers installed. There were individuals working in proximity of these panels. This situation created a possible Shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Energized_Panel_Without_Cover.png | file://x:/photopub/docs/0000000361/7b717a4d-dbf2-4c58-8229-7ddc915876cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc898f5e_b504_404b_897d_806abea4ebf5
ELIN-483505-2015 | EL-259266-2015 | 12/7/2015 9:04:08 AM | ASSESS: EL: Final | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 2 | Receptacles installed in a new house are required to work to prevent having to use extension cords in the place of permanent wiring. This installation has two receptacles in a bedroom that do not work. Wiring inside the wall may be damaged. Left uncorrected this may be a potential fire hazard. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | Receptacle_in_new_house_does_not_work.png | file://x:/photopub/docs/0000000363/bd01bfd6-10da-41e5-b483-87629069ef9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf426b59_e904_4a29_9c94_ced9c0efed76
PROP-465950-2015 | 2224113 | 12/10/2015 8:05:48 PM | ASSESS: PR OP: RAP | png | #asFound | PR044 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | On a passenger ropeway a tower switch or derailment switch is utilized to detect a rope derailment condition. The tower switches on this device utilize a non-resettable device called a break fork. This metal device is design to break upon contact with a triggering device as a result of a rope derailment and open an electric safety circuit which in-turn will shut down the operating ropeway. The break fork utilized is normally notched so as to creat a weakness in the material where it is designed to fail upon actuation. A fork was identified at tower 11 with no notches. It is therefore probable that this particular fork would not break upon actuation and would not cause the fault condition designed to cause the ropeway to stop. That being said, the tower fault system will detect a ground fault condition. It is probable that even if the break fork were not to break upon actuation it would make contact with the metal triggering device and cause a ground fault which in-turn would cause the ropeway to stop opera | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Break_fork_without_notches.png | file://x:/photopub/docs/0000000370/68f8afcc-2e89-4a48-9354-41a1c693bf11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0E039893_0165_4C1B_BADE_DF7447DEC32C
PROP-465983-2015 | 4308067 | 12/10/2015 1:16:13 AM | ASSESS: PR OP: RAP | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | At the belt transition of the unload area a shift plate is utilized to shut down the conveyor in the event that a passenger's body part or equipment becomes entrapped as the belt moves under the decking at the unload point. The shift plate actuates a shut down when it shifts forward from its normal position. The with the shift plates maximum distance of less than 75 mm the stopping distance is to be less than 75% of the of the shift plate movement. The stopping at the time of inspection was 220 mm (significantly longer than the allowable 75% of the 75mm). This condition results in an entrapment hazard for passenger that may have tripped and fallen at the belt transition point. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Automatic_stopping_device.png | file://x:/photopub/docs/0000000370/0c1b7b0f-26b6-4540-b289-c849a79c46a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__836230AE_1B36_437A_BEFC_A7C7B1D01366
PROP-465974-2015 | 2908803 | 12/11/2015 11:59:30 PM | ASSESS: PR OP: RAP | png | #asFound | PR030 | Malfunction that is: reasonably detectable by maintenance program/operation | 2 | 2 | During the inspection it was noted that there was no operating smoke detector in the drive station machine room. The ropeway was not operating for the public at the time of inspection. In the event that the smoke alarm is not functional during public operations an undetected fire in the machine room would present a significant hazard to passengers, staff and equipment. An attendant may not have an early warning that would allow for adequate time to implement effective fire emergency procedures. A fire in a drive station of a machine room could have a worst case scenario of the haul rope parting resulting in catastrophic damage to ropeway equipment and significant injury risks to passengers. | 2 | Malfunction that is: reasonably detectable by maintenance program/operation | Smoke_detector_missing_in_machine_room.png | file://x:/photopub/docs/0000000370/887a14ce-c83e-42fe-b329-c4056aece30a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__E0118B30_7996_49B4_B5E4_6831D8FDC141
PROP-465963-2015 | 3937130 | 12/10/2015 12:40:37 AM | ASSESS: PR OP: RAP | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | A gap located at the unload area between the attendant hut and the conveyor is not provided with skirting. There is a risk of a passenger of small size (child) falling into the gap and under the conveyor and into the conveyor equipment. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Gap_in_skirting_at_top_station.png | file://x:/photopub/docs/0000000370/665a5f75-9e11-4dea-8324-13bbf89827b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1AAA4A56_7F06_4919_AD30_BC944C3C1801
ELIN-483505-2015 | EL-259266-2015 | 12/7/2015 9:04:08 AM | ASSESS: EL: Final | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 2 | Receptacles installed in a new house are required to work to prevent having to use extension cords in the place of permanent wiring. This installation has two receptacles in a bedroom that do not work. Wiring inside the wall may be damaged. Left uncorrected this may be a potential fire hazard. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | Receptacle_in_a_mew_house_does_not_work.png | file://x:/photopub/docs/0000000363/a5aab53e-94df-477e-92dc-c4613e71d10f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf426b59_e904_4a29_9c94_ced9c0efed76
ELOP-226702-2014 | 4020698 | 12/3/2015 5:34:09 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended as a replacement for permanent wiring. In this installation flexible cord was used above a walk-in freezer to feed a compressor and power circuit. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_above_freezer.png | file://x:/photopub/docs/0000000368/9ec21049-0261-4704-a33b-903459966981.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__261e508a_339b_49ab_aa82_f9bb7ed35a6f
ELOP-226702-2014 | 4020698 | 12/3/2015 5:34:09 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended as a replacement for permanent wiring. In this installation flexible cord was used above a walk-in freezer to feed a compressor and power circuit. | 4 | Conductors, Misuse of flexible cords. | Compressor_connection.png | file://x:/photopub/docs/0000000368/c908d49b-9677-43b3-8089-bff9896483af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__261e508a_339b_49ab_aa82_f9bb7ed35a6f
ELIN-514955-2016 | EL-328163-2015 | 2/19/2016 3:36:13 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings on energized electrical equipment are left without covers and fillers, creating a shock hazard due to accidental contact by a person. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Termination.png | file://x:/photopub/docs/0000000393/98aff2d8-7d62-4da4-9911-30fba8913947.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0895628a_5066_43f6_b288_f04e4947c9d2
ELIN-514955-2016 | EL-328163-2015 | 2/19/2016 3:36:13 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings on energized electrical equipment are left without covers and fillers, creating a shock hazard due to accidental contact by a person. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Cover.png | file://x:/photopub/docs/0000000393/9c64c3ce-bee3-415b-87cb-5a51f2a5b80f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0895628a_5066_43f6_b288_f04e4947c9d2
ELIN-514955-2016 | EL-328163-2015 | 2/19/2016 3:36:13 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings on energized electrical equipment are left without covers and fillers, creating a shock hazard due to accidental contact by a person. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Unused_opening.png | file://x:/photopub/docs/0000000393/6cd4e70b-cbf3-43e5-be46-1e89636129b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0895628a_5066_43f6_b288_f04e4947c9d2
ELIN-514955-2016 | EL-328163-2015 | 2/19/2016 3:36:13 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings on energized electrical equipment are left without covers and fillers, creating a shock hazard due to accidental contact by a person. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Clearance.png | file://x:/photopub/docs/0000000393/a4665538-a57d-427d-ba9d-58947fd75630.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0895628a_5066_43f6_b288_f04e4947c9d2
ELIN-514955-2016 | EL-328163-2015 | 2/19/2016 3:36:13 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings on energized electrical equipment are left without covers and fillers, creating a shock hazard due to accidental contact by a person. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Nocover.png | file://x:/photopub/docs/0000000393/378444b5-6cdc-4f9e-9443-1adaeb3369f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0895628a_5066_43f6_b288_f04e4947c9d2
ELIN-514955-2016 | EL-328163-2015 | 2/19/2016 3:36:13 PM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings on energized electrical equipment are left without covers and fillers, creating a shock hazard due to accidental contact by a person. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | No_support.png | file://x:/photopub/docs/0000000393/b7afdbb0-be3b-45d4-afcc-93c40b27e757.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0895628a_5066_43f6_b288_f04e4947c9d2
ELIN-505020-2016 | EL-305191-2015 | 1/6/2016 4:20:09 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | The signs powered from 15amp 120 volt circuits do not bear nameplates or certification labels, unknown (nameplate) ratings could lead to a thermal hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Main_exterior_sign_at_front.png | file://x:/photopub/docs/0000000374/db021fc8-22d2-45d0-a813-b9d3950b33d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f65deb2_db2d_4743_b7ab_eadf804beb30
BPVOP-504505-2016 | 2302147 | 12/30/2015 9:10:02 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 240*Fahrenheit, it is determined that safety relief valve exceeded 6yr interval for servicing or replacement (Regular testing and servicing ensures proper operation of safety relief valve). Failure to have safety relief valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary and lead to incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_OF_HW84226.png | file://x:/photopub/docs/0000000376/0765206c-4d4f-4c9a-903d-3f39b445ed9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b230e20_059f_478b_83a5_dd9ab959591f
BPVOP-504506-2016 | 2302146 | 12/30/2015 9:10:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 240*Fahrenheit, it is determined that safety relief valve exceeded 6yr interval for servicing or replacement (Regular testing and servicing ensures proper operation of safety relief valve). Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary and lead to incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE__OF_HW84225.png | file://x:/photopub/docs/0000000376/edce0f2d-e07d-4ccf-bfc8-7e79cce467f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1630889f_857d_413f_986a_5e0c7d73a9c3
ELIN-521063-2016 | UW-342142-2016 | 2/2/2016 6:28:18 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 | The 70 KVar 600 volt power factor capacitor is missing the required Warning label. Should the unit be de-energized, the potential energy remains until discharged, this is a shock hazard | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | Power_factor_correction.png | file://x:/photopub/docs/0000000386/5f7e9e19-9b96-44a9-8a20-f7c0b75d7d44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdbf6ba6_fd3d_43fc_9003_216b7aacdea2
ELIN-479731-2015 | EL-265871-2015 | 12/8/2015 7:38:52 AM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The bonding conductor from the feeder cable was terminated at the grounded service conductor termination point in the fused switch alongside the ground conductor and the grounded (neutral) conductor-not the panel can itself. This in effect creates no real hazard itself. | 3 | Continuity Bonding; method for equipment is not adequate. | Main_disconnect_.png | file://x:/photopub/docs/0000000364/3fdb4d1d-4c97-467c-8761-78c56daad26c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f289aa5e_02a7_47d8_afe5_1c8ad931be19
ELIN-526207-2016 | EL-342932-2016 | 2/15/2016 9:08:24 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | #6 copper ground conductor has not been properly protected from mechanical damage. This could result in a loos of the grounding system which enables the branch breakers to function properly and protects persons from shock hazards. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_wire.png | file://x:/photopub/docs/0000000391/e3d00902-ac2e-4b65-9508-d177370b9573.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd6bd0d1_6112_440e_b49d_abcbace074a9
ELIN-505020-2016 | EL-305191-2015 | 1/6/2016 4:20:09 PM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | The signs powered from 15amp 120 volt circuits do not bear nameplates or certification labels, unknown (nameplate) ratings could lead to a thermal hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Interior_control__Box.png | file://x:/photopub/docs/0000000374/f2bbda02-d307-43bb-b661-6c30ce7c6b09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f65deb2_db2d_4743_b7ab_eadf804beb30
ELIN-506100-2016 | EL-325235-2015 | 1/11/2016 9:23:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Electrical panel not rated for wet location. Plastic not acceptable weatherproofing. No lockable enclosure provided to limit access to authorized persons only. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 1_.png | file://x:/photopub/docs/0000000376/70cb84e7-23fe-489e-9c94-1ad8b3a2d024.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57328ef6_29ac_4639_9ee2_f1c802cb7f38
ELIN-506100-2016 | EL-325235-2015 | 1/11/2016 9:23:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Electrical panel not rated for wet location. Plastic not acceptable weatherproofing. No lockable enclosure provided to limit access to authorized persons only. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 2-.png | file://x:/photopub/docs/0000000376/6d006f59-f327-4c94-aa86-4cd25a4d2349.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57328ef6_29ac_4639_9ee2_f1c802cb7f38
ELIN-506102-2016 | EL-325233-2015 | 1/11/2016 9:23:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Electrical panel not approved for wet location. Plastic covering not accepted as weatherproofing. No lockable enclosure provided as to limit access to authorized persons only. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 1.png | file://x:/photopub/docs/0000000376/a0555625-3d1b-440f-be93-ee6052cd5b5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e940ce2_5f18_4ac4_af5d_a6ec3fd8e29f
ELIN-506102-2016 | EL-325233-2015 | 1/11/2016 9:23:31 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Electrical panel not approved for wet location. Plastic covering not accepted as weatherproofing. No lockable enclosure provided as to limit access to authorized persons only. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 2.png | file://x:/photopub/docs/0000000376/6feca888-e8e1-4c06-8c88-e0b3eb320a81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e940ce2_5f18_4ac4_af5d_a6ec3fd8e29f
ELIN-518182-2016 | EL-330307-2015 | 2/10/2016 3:56:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 100.png | file://x:/photopub/docs/0000000389/97ab7907-d29e-4f85-9aba-68bdf3c0cae2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e5da4f_73bf_43b3_ae00_c8d04f9c94d6
ELIN-518182-2016 | EL-330307-2015 | 2/10/2016 3:56:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 102.png | file://x:/photopub/docs/0000000389/a483a907-f807-4c08-8306-5ff17392f748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e5da4f_73bf_43b3_ae00_c8d04f9c94d6
ELIN-518182-2016 | EL-330307-2015 | 2/10/2016 3:56:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 104.png | file://x:/photopub/docs/0000000389/8d1ae82f-7f7d-41f0-8f59-376c83af786c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e5da4f_73bf_43b3_ae00_c8d04f9c94d6
BPVIN-496306-2015 | UW-326638-2015 | 12/15/2015 12:24:52 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | During assessment of expansion tank (diameter 0.63m and length 2m )with Maximum Allowable Working Pressure of 150psig it is determined that vessel is not firmly anchored to foundation. In the event of earthquake of significant scale vessel may trip or shift and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | EXPANSION_TANK.png | file://x:/photopub/docs/0000000367/f32ac59d-936b-426e-bec6-f4f427104137.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cb04b298_9967_4d65_a131_d352aec94396
ELIN-508944-2016 | EL-328456-2015 | 1/15/2016 8:32:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | System ground wire terminated in meter base which is wrong location. A fault in the panelboard supplied by this meter could result in potential shock or high temperatures in the service conductors. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | System_ground_termination_point.png | file://x:/photopub/docs/0000000379/622bc721-bb08-4cde-92cd-baa146fb2a0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa70fc92_82a5_4ddf_81ea_09b8ce7a8466
ELIN-508944-2016 | EL-328456-2015 | 1/15/2016 8:32:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | System ground wire terminated in meter base which is wrong location. A fault in the panelboard supplied by this meter could result in potential shock or high temperatures in the service conductors. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | System_ground_terminated_in_meter_base.png | file://x:/photopub/docs/0000000379/78fa137a-862e-4890-95eb-124113bd46b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa70fc92_82a5_4ddf_81ea_09b8ce7a8466
ELIN-525616-2016 | EL-296236-2015 | 2/16/2016 8:40:01 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | An installed 20 amp, 120V receptacle had the plastic face broken off leaving the copper contacts exposed. Inadvertent contact with these exposed energized parts could result in a shock injury. This item was made safe at the time of inspection. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Broken_energized_receptacle.png | file://x:/photopub/docs/0000000392/ce383241-5c4d-47e5-88ff-aa0ee2983145.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8904b07_1303_4873_8be1_7e3f619e6957
ELIN-523935-2016 | EL-317593-2015 | 2/18/2016 7:47:21 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A sign pylon in an area accessible to the public connected to a 15 amp circuit at 120 volts was found with flexible cord used inside pylon. Metal structure was not bonded to ground. Flexible cord and cord connections when used as a substitute for fixed wiring methods can deteriorate and fault to adjacent structures or conductors. In this case sign pylon was not bonded to ground which could have resulted in potential for injury to persons or damage to property | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_inside_sign.png | file://x:/photopub/docs/0000000392/33cd7a67-ff34-466d-9648-5daec3da2a16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b20ec50_4431_40da_81e0_b1b8a9ea17f6
ELIN-523935-2016 | EL-317593-2015 | 2/18/2016 7:47:21 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A sign pylon in an area accessible to the public connected to a 15 amp circuit at 120 volts was found with flexible cord used inside pylon. Metal structure was not bonded to ground. Flexible cord and cord connections when used as a substitute for fixed wiring methods can deteriorate and fault to adjacent structures or conductors. In this case sign pylon was not bonded to ground which could have resulted in potential for injury to persons or damage to property | 4 | Conductors, Misuse of flexible cords. | Open_conductors_defunct_sign_found_with_cord_cap_to_connect_in_sign_pylon_bas_.png | file://x:/photopub/docs/0000000392/2ac39b41-0d8f-4ed3-b87f-2a1980ea35a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b20ec50_4431_40da_81e0_b1b8a9ea17f6
ELIN-528342-2016 | EL-274912-2015 | 2/17/2016 2:35:09 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | In a renovated dwelling with a 200 amp 240 volt single phase service, a gas line which passes directly over main panel and is in contact with branch circuit wiring in a number of locations has not been bonded to ground. Static charge or in some cases faulting to the gas line from branch circuit wiring can occur. If the gas line is not bonded to ground a potential for property damage or injury to persons can occur. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_line_not_bonded_and_shows_unprotected_nmd_90.png | file://x:/photopub/docs/0000000392/3eb5d25e-65a7-4769-8079-a0ad5eec0fad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87479fb9_ed48_4fad_9465_e0a057853692
ELIN-523935-2016 | EL-317593-2015 | 2/18/2016 7:47:21 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A sign pylon in an area accessible to the public connected to a 15 amp circuit at 120 volts was found with flexible cord used inside pylon. Metal structure was not bonded to ground. Flexible cord and cord connections when used as a substitute for fixed wiring methods can deteriorate and fault to adjacent structures or conductors. In this case sign pylon was not bonded to ground which could have resulted in potential for injury to persons or damage to property | 4 | Conductors, Misuse of flexible cords. | Receptacle_inside_sign_abrasion_hazard.png | file://x:/photopub/docs/0000000392/eb8c924b-ec8d-4eb0-bdba-88bbdbfd32d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b20ec50_4431_40da_81e0_b1b8a9ea17f6
ELIN-518182-2016 | EL-330307-2015 | 2/10/2016 3:56:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 101.png | file://x:/photopub/docs/0000000389/54a0ff75-a163-464a-a707-32960c94e2fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e5da4f_73bf_43b3_ae00_c8d04f9c94d6
ELIN-518182-2016 | EL-330307-2015 | 2/10/2016 3:56:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 103.png | file://x:/photopub/docs/0000000389/7f78887e-1274-42ed-82e2-b56606bd861d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e5da4f_73bf_43b3_ae00_c8d04f9c94d6
ELIN-518182-2016 | EL-330307-2015 | 2/10/2016 3:56:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found energized exposed conductors were left exposed and unsafe during electrical installations and alterations for one outlet receptacle non-compliance which is not approved wiring method, is not safe and is not authorized for connection. When energized conductors are left exposed and subjected to possible contact with people or property, this can become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 105.png | file://x:/photopub/docs/0000000389/35df16d9-cae3-4ff0-ad9b-e0552182cada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28e5da4f_73bf_43b3_ae00_c8d04f9c94d6
ELIN-516954-2016 | EL-332342-2016 | 1/28/2016 1:09:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The receptacle cover was missing and a 15 amp receptacle was used on a 20 amp circuit. Missing covers expose energized parts presenting a shock hazard. Receptacles with an ampere rating lower than the breaker presents an overheating hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Receptacles.png | file://x:/photopub/docs/0000000383/a2889e3c-08d1-4abd-8751-45166dff33e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9e17bbe_d683_4e35_927b_9b60541d8a91
ELIN-515067-2016 | EL-334872-2016 | 1/27/2016 1:09:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Panels located outdoors are required to be protected from the weather. Plastic was over the panel but not the required roof. Should the main breaker become wet it may not operate as intended. In a fault situation this presents a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Enclosure.png | file://x:/photopub/docs/0000000383/002adec3-b2ea-4d11-aacd-39dacfd5ddb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d280177_14c7_47de_941e_9299143beeb1
GAIN-476094-2015 | GA-311424-2015 | 2/18/2016 9:22:28 AM | ASSESS: GA: Final | png | #asFound | GA052 | Unprotected temporary hose installations | 3 | 3 | Logging camp has gas line (hose) laying on the ground. There is no protection for the gas line as well as the electrical line laying on the ground. During the snow lowing process, it is possible to catch the gas line as well as the electrical line. Possible explosion or electrocution | 3 | Unprotected temporary hose installations | Mossvill_camp.png | file://x:/photopub/docs/0000000392/0a53bddf-78fd-4b1b-bc56-e55fe6d60692.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9542ef4f_b81b_4f65_8144_04ffcef2eea6
GAIN-476094-2015 | GA-311424-2015 | 2/18/2016 9:22:28 AM | ASSESS: GA: Final | png | #asFound | GA052 | Unprotected temporary hose installations | 3 | 3 | Logging camp has gas line (hose) laying on the ground. There is no protection for the gas line as well as the electrical line laying on the ground. During the snow lowing process, it is possible to catch the gas line as well as the electrical line. Possible explosion or electrocution | 3 | Unprotected temporary hose installations | Gas_line_feeding_camp.png | file://x:/photopub/docs/0000000392/5d1b442a-657b-4822-b4b8-0799e084f4d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9542ef4f_b81b_4f65_8144_04ffcef2eea6
ELIN-516407-2016 | EL-281490-2015 | 2/18/2016 12:25:26 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Circuit breakers that are installed in panels are required to be of a type that is approved for use with the specific panel they are being installed in. This is required because circuit breakers are manufactured, tested, and certified to be used only with panels they are compatible with. Using breakers that are not compatible with the specific panel they are installed in can pose a risk of equipment failure. This installation has a 40A, 2 pole, GFCI breaker and two 15A single pole breakers that were installed in a panel that they are not approved to be installed in. Left uncorrected this may pose a fire or shock hazard if either the breakers or the panel fail to operate correctly as a result of incompatibility. | 3 | Conductors Equipment is not approved for the specific use. | Label_on_the_breaker.png | file://x:/photopub/docs/0000000393/8dec0cdc-c2bb-4b28-a76a-5cbffc1233a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bfbc52c_a4ba_4dac_8869_8b7062d1e8fc
ELIN-516407-2016 | EL-281490-2015 | 2/18/2016 12:25:26 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Circuit breakers that are installed in panels are required to be of a type that is approved for use with the specific panel they are being installed in. This is required because circuit breakers are manufactured, tested, and certified to be used only with panels they are compatible with. Using breakers that are not compatible with the specific panel they are installed in can pose a risk of equipment failure. This installation has a 40A, 2 pole, GFCI breaker and two 15A single pole breakers that were installed in a panel that they are not approved to be installed in. Left uncorrected this may pose a fire or shock hazard if either the breakers or the panel fail to operate correctly as a result of incompatibility. | 3 | Conductors Equipment is not approved for the specific use. | Breakers_for_jacuzzi_tub_are_not_approved_for_use_with_the_panel.png | file://x:/photopub/docs/0000000393/b717147a-3495-4771-9845-4ab9d4d96381.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bfbc52c_a4ba_4dac_8869_8b7062d1e8fc
ELIN-516407-2016 | EL-281490-2015 | 2/18/2016 12:25:26 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Circuit breakers that are installed in panels are required to be of a type that is approved for use with the specific panel they are being installed in. This is required because circuit breakers are manufactured, tested, and certified to be used only with panels they are compatible with. Using breakers that are not compatible with the specific panel they are installed in can pose a risk of equipment failure. This installation has a 40A, 2 pole, GFCI breaker and two 15A single pole breakers that were installed in a panel that they are not approved to be installed in. Left uncorrected this may pose a fire or shock hazard if either the breakers or the panel fail to operate correctly as a result of incompatibility. | 3 | Conductors Equipment is not approved for the specific use. | Breaker_installed_for_the_hot_tub_is_not_approved_for_use_in_the_panel.png | file://x:/photopub/docs/0000000393/073fb67c-5f9f-492c-be8e-284f6b599020.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bfbc52c_a4ba_4dac_8869_8b7062d1e8fc
ELIN-516407-2016 | EL-281490-2015 | 2/18/2016 12:25:26 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Circuit breakers that are installed in panels are required to be of a type that is approved for use with the specific panel they are being installed in. This is required because circuit breakers are manufactured, tested, and certified to be used only with panels they are compatible with. Using breakers that are not compatible with the specific panel they are installed in can pose a risk of equipment failure. This installation has a 40A, 2 pole, GFCI breaker and two 15A single pole breakers that were installed in a panel that they are not approved to be installed in. Left uncorrected this may pose a fire or shock hazard if either the breakers or the panel fail to operate correctly as a result of incompatibility. | 3 | Conductors Equipment is not approved for the specific use. | Existing_ITE_panel_in_house.png | file://x:/photopub/docs/0000000393/1c6b31bf-0433-4431-8770-de81dc78eb6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bfbc52c_a4ba_4dac_8869_8b7062d1e8fc
ELIN-504704-2016 | EL-208460-2015 | 1/11/2016 3:17:56 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Locknuts on metal conduits, cables, and fittings are required to be made up tight to provide an adequate bonding path between equipment in the event of a fault on the system. This is required to facilitate the operation of over current devices to prevent equipment from becoming and staying energized. This installation has locknuts installed on metal nipples between a 600A, 120/240V service switch and a metal pull box. The locknuts are only finger tight and a may not provide a proper bonding path if there is a fault on the system. Left uncorrected this is a potential shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Service_switch_and_pull_box.png | file://x:/photopub/docs/0000000376/d9f93751-45cd-42f3-8359-3699ea938feb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2ea56f5_fd36_40af_ba78_d4ee6113059d
ELIN-505600-2016 | EL-330329-2015 | 1/11/2016 3:17:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Service panels and receptacles installed to provide power to houses under construction are required be approved for installation in a wet location or installed inside of a weather proof enclosure. This is required to ensure electrical equipment does not get wet and create a shock hazard and to prevent damage to equipment from rust or corrosion. This installation has a new 200A 120/240V service panel and two 20A 120V receptacles that are energized and installed in a location where they are exposed to the weather. The equipment is not approved for this location and a weather proof enclosure has not been provided to protect the equipment from exposure to the weather. Left uncorrected this is a potential shock and fire hazard if persons come in contact with wet equipment or if equipment becomes rusted or corroded and fails. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_panel_and_receptacles_for_a_new_house_are_installed_exposed_to_the_weather_.png | file://x:/photopub/docs/0000000376/ac41ea37-66bd-40d2-9be8-2146300b60c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1a2c39b_45be_4e53_a1f9_15c0fbed6bc8
ELIN-469723-2015 | EL-248504-2015 | 1/11/2016 10:40:21 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Electrical sign and hid fixtures retrofit to LED have not been certification labeled as directed by safety officer at previous Evaluation of work done prior to permit issuance. Lighting equipment which does not bear acceptable evidence of approval may not be safe for persons or property | 0 | No Created Hazard Identified | Sign_originally_found_with_no_certification_label_now_with_label.png | file://x:/photopub/docs/0000000376/759a406b-2c71-4953-8875-675a017fc939.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c240b87_e91d_43a1_9b02_66cf9281cec1
BPVIN-484297-2015 | UW-303181-2015 | 11/24/2015 9:28:22 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 248*Fahrenheit, it was determined that safety relief valve exceeded 6yr interval for servicing or replacement (Regular testing and servicing ensures proper operation of safety relief valve). Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure boundary and gushing hot water may cause severe incident (severe personnel burning, equipment damage etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_B2.png | file://x:/photopub/docs/0000000361/ecc18f9a-b3bd-410c-809a-74887cc75729.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecefddc2_88e4_4a29_bf15_7aa14635ed9d
BPVIN-484294-2015 | UW-303177-2015 | 11/24/2015 9:28:22 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 248*Fahrenheit, it was determined that safety relief valve exceeded 6yr interval for servicing or replacement (Regular testing and servicing ensures proper operation of safety relief valve). Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure boundary and gushing hot water may cause severe incident (severe personnel burning, equipment damage etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_B1.png | file://x:/photopub/docs/0000000361/fe972fc4-616c-4e37-8a4a-f510ab400688.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff49ee3d_ec9a_491e_86d7_5362a036a57c
ELIN-491625-2015 | EL-314750-2015 | 12/10/2015 10:37:36 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | 120/240V 200A service entrance conduit is not properly bonded which could pose a shock hazard to persons. | 0 | No Created Hazard Identified | Service_conduit.png | file://x:/photopub/docs/0000000365/2b81f268-9235-47f2-9bdd-f684354f8c7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2b27f0e_636f_41c4_95f5_79d9547fc690
ELIN-528185-2016 | EL-346263-2016 | 2/17/2016 8:40:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | Consumers main service was found energized on a inspection request for service. Code requires energized equipment to be de-energized to conduct repairs or alterations. Working on energized electrical equipment provides a risk of arc flash, shock, fire,and damage to property or persons. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Panel_energized_for_service_inspection.png | file://x:/photopub/docs/0000000392/c9aef01f-5da0-4d0f-9360-11217bd6eed0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8124f127_701d_437a_bc78_de6454747b42
ELIN-528185-2016 | EL-346263-2016 | 2/17/2016 8:40:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | Consumers main service was found energized on a inspection request for service. Code requires energized equipment to be de-energized to conduct repairs or alterations. Working on energized electrical equipment provides a risk of arc flash, shock, fire,and damage to property or persons. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Meter_tag_cut_in_order_to_remove_and_reinstall.png | file://x:/photopub/docs/0000000392/76805f39-5230-45bd-a81c-eb81b17a7a45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8124f127_701d_437a_bc78_de6454747b42
ELIN-528230-2016 | EL-346263-2016 | 2/17/2016 9:50:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #8 stranded conductor is terminated under a wire binding screw, #10 is the largest size of conductor allowed to be terminated in this manner,# 8 being larger in wire size requires a solder less wire connection. The #8 stranded conductors do not completely remain in good contact with the wire binding screw, if a fault were to occur inadequate bonding to ground would be a result. Which may cause failure of equipment and/ or shock and fire. | 3 | Continuity Bonding; method for equipment is not adequate. | 8awg_stranded_under_wire_binding_screw.png | file://x:/photopub/docs/0000000392/230113a5-b1d9-4e40-8381-b0d8598dab11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d28c0717_ead1_4215_907e_db1543e27184
ELOP-474417-2015 | 5234898 | 12/15/2015 2:13:07 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables are required to be properly installed into equipment and secured so that they remain secure and undamaged. This installation has an armored cable that is installed into a foot switch for a 120 volt control circuit for a conveyor system at a mill. The cable armor has pulled out of the connector and the energized conductors are now subject to damage. Left uncorrected this poses a potential fire and shock hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cable_pulled_out_of_connector_at_foot_switch.png | file://x:/photopub/docs/0000000367/312b076d-9a92-44d9-94c6-7ba61b8b9e3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__679ec197_86f1_4980_beec_cb13f6346677
ELOP-470401-2015 | 5239499 | 12/15/2015 2:13:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables are required to be installed into connectors properly, supported properly, and secured to prevent damage to the cables, connectors, and conductor insulation. This installation has energized cables that are pulled out of connectors, and improperly secured at equipment. This has created a fire and shock hazard should the cable conductors insulation become damaged and either fault to ground creating an arc or come in contact with a persons skin or a conductive object. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cable_termination_at_a_transformer_has_a_broken_out_knock_out.png | file://x:/photopub/docs/0000000367/42958184-864e-412a-ae5c-bd04c0888877.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a8d5cf3_468a_4a41_bad9_901ffa0a855a
GAIN-496875-2015 | GA-278640-2015 | 1/11/2016 2:37:15 PM | ASSESS: GA: Final | png | #asFound | GA083 | Installed in a corrosive/hazardous location | 3 | 2 | 2 PSI natural gas regulators installed to close to appliance high temperature and corrosive exhaust outlet. | 3 | Installed in a corrosive/hazardous location | Roof_top_units.png | file://x:/photopub/docs/0000000380/8d2e6866-42e5-48b3-bb05-52e39a019239.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__951102ad_9c89_4c4a_b1e2_ed37f9e6754c
GAIN-388275-2015 | GA-257783-2015 | 1/11/2016 2:37:31 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | Piping and fittings at gas meter do not make up a function swing joint to protect gas meter in the event of ground or structure movement. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | No_swing_joint.png | file://x:/photopub/docs/0000000380/d18d926c-dab7-43bf-b334-bf0b9c180b2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f51fa923_856b_4e08_b2db_b82fd096565f
BPVOP-526676-2016 | 4461724 | 2/12/2016 3:18:30 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Two areas of concern. First area (shown in attached picture) is in external shell for fire side of boiler where a section has been burned out and numerous areas exhibit heat stress cracking. Second area (not accessible to photograph) of concern is on the water side. Signs of a pin hole leak have developed and water and steam was observed wisping from under the boiler. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Kettle_foods.png | file://x:/photopub/docs/0000000390/cd7c1080-8f0d-48c9-a93e-27254315faa7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a7457fd_e0d0_4416_995a_48b1111d36ef
ELIN-522316-2016 | EL-209126-2015 | 2/12/2016 2:09:53 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | McPhee-2.png | file://x:/photopub/docs/0000000390/3c906f26-84e5-4ee5-b22c-c449a8e35c79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a6faba_c3b6_4e9c_8da2_ea22ec92e2a2
ELIN-522316-2016 | EL-209126-2015 | 2/12/2016 2:09:53 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | McPhee_-1.png | file://x:/photopub/docs/0000000390/e9491fd5-e017-44bd-a9fe-300a9343ade5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a6faba_c3b6_4e9c_8da2_ea22ec92e2a2
ELIN-522316-2016 | EL-209126-2015 | 2/12/2016 2:09:53 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | McPhee-3.png | file://x:/photopub/docs/0000000390/29def504-2efd-4bbf-a62c-31c26045befa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12a6faba_c3b6_4e9c_8da2_ea22ec92e2a2
BPVOP-488240-2015 | 2254256 | 12/2/2015 9:52:39 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 248*Fahrenheit, pinhole was detected in weld between lower water header and riser tube. Crack may initiate and propagate if pinhole is not removed with correct repair procedure. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | DEFECT_IN_WELD_BEFORE_REPAIR.png | file://x:/photopub/docs/0000000360/1ab4d13f-1d1f-4e29-b9f9-06df0e5c169e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2df322c_3a63_480f_bc73_391785e11622
ELIN-482489-2015 | EL-312298-2015 | 11/25/2015 4:49:30 PM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | An automotive dealer had three 240 volt charger stations for electric vehicles installed at their location. These units do not bear a recognized approval agency label for allowable use in BC | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Exterior_charging_station.png | file://x:/photopub/docs/0000000357/203d6a2e-5dd7-4428-8d04-bb75fb7220d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4170a14c_63d4_4a7b_b6a0_43e6f4870ebe
ELIN-482489-2015 | EL-312298-2015 | 11/25/2015 4:49:30 PM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | An automotive dealer had three 240 volt charger stations for electric vehicles installed at their location. These units do not bear a recognized approval agency label for allowable use in BC | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Cable_approval_only.png | file://x:/photopub/docs/0000000357/6d82f3d3-5f2c-461b-a96b-cbd5e3284966.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4170a14c_63d4_4a7b_b6a0_43e6f4870ebe
BPVOP-506298-2016 | 4073420 | 1/7/2016 2:58:12 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of vertical air receiver (1.8m long and 0.6m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 350psig, it is determined that vessel has safety valve that exceeded 5 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE.png | file://x:/photopub/docs/0000000375/c1609489-0bac-4499-a196-c722d9723da0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d96c116_6475_4018_a44e_570d58d25088
ELIN-489680-2015 | EL-311959-2015 | 12/4/2015 5:08:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The armoured consumer service cable is not supported and protected from potential damage that could occur. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | ACWU_on_exterior.png | file://x:/photopub/docs/0000000362/821e1552-4610-4a3b-9216-36306e3070a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df11a1f0_3a09_40de_ba97_14ae07be6517
ELOP-233404-2014 | 449 | 11/24/2015 11:13:48 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Plywood used for mounting bracket of existing cables. A 600 volt, 600 amp, central distribution panel, in the electrical room of a cedar log lumber facility, was mounted using an unapproved mounting bracket to house the connections of 3 parallel teck cable feeders. This is a thermal hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | mounting_plate.png | file://x:/photopub/docs/0000000357/cc85b33f-a65b-4b05-a339-c4e87d81ded2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d3a23f6_392f_42f7_9af1_a72ccbb955ea
ELOP-233404-2014 | 449 | 11/24/2015 11:13:48 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Plywood used for mounting bracket of existing cables. A 600 volt, 600 amp, central distribution panel, in the electrical room of a cedar log lumber facility, was mounted using an unapproved mounting bracket to house the connections of 3 parallel teck cable feeders. This is a thermal hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | CDP_openings.png | file://x:/photopub/docs/0000000357/43deee9d-781a-40b9-a4a6-324c1a0a0daa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d3a23f6_392f_42f7_9af1_a72ccbb955ea
BPVOP-521877-2016 | 2273483 | 2/2/2016 10:21:45 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of domestic hot water boiler with Maximum Allowable Working Pressure (MAWP) of 60psig, Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit and 40sq. meters of heating surface, it is determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_WITH_DATE_OF_MANUFACTURE.png | file://x:/photopub/docs/0000000387/8d9a0249-98e6-4694-83e8-c1f46adbb8e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6782feb5_f561_48c8_88cf_8680ab62f393
ELIN-525998-2016 | EL-293496-2015 | 2/12/2016 4:49:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | A 240 volt, 20 amp, temporary heat outlet does not have an approved cover installed and has exposed terminals accessible to the public. The outlet is not energized. This is a shock hazard if the circuit is energized. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Temporary_heat_outlet.png | file://x:/photopub/docs/0000000390/41f38da2-7b80-4cfb-b41f-4584784a884c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4693cead_3d6e_4062_9b5f_51b3a6d1d606
GAIN-516687-2016 | GA-315663-2015 | 2/15/2016 4:25:11 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | At time of inspection copper tubing wasn't supported to wall, putting stress on piping and regulator. This s could be a hazard if the range is pulled out for cleaning, gas piping could be kinked or broken, releasing natural gas. | 2 | Physical protection of piping and tubing absent. | 1.png | file://x:/photopub/docs/0000000391/cbda7211-df02-4d3c-9760-d0407a99988a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53dd5345_0454_42be_bd37_80f508b05c34
ELIN-525544-2016 | EL-344709-2016 | 2/15/2016 3:23:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 15A, 120/240V rated cable installed on 20A overcurrent device. This is a thermal hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | overcurrent_device_rating_exceeds_conductor_size.png | file://x:/photopub/docs/0000000391/cfc0d413-4252-4680-aa5e-a7a1560d0490.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b35a6adf_02ba_4881_9808_9cdf828412ce
ELIN-495990-2015 | EL-233444-2015 | 12/17/2015 3:14:54 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Energized kitchen appliance cables without proper termination are a shock hazard. Kitchen counters without required receptacles can result in use of temporary cords to supply small appliances located in those areas. This would cause a thermal effect. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Mis-located_counter_and_fridge_plug.png | file://x:/photopub/docs/0000000368/232803d9-665c-4478-9cd3-adbe973e7a5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c60d05f_e68d_464d_9030_6d57ee951510
ELIN-495990-2015 | EL-233444-2015 | 12/17/2015 3:14:54 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Energized kitchen appliance cables without proper termination are a shock hazard. Kitchen counters without required receptacles can result in use of temporary cords to supply small appliances located in those areas. This would cause a thermal effect. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Energized_Dishwasher_cable_without_JB_and_cover.png | file://x:/photopub/docs/0000000368/ec268d50-c13e-4891-8716-168e44cce251.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c60d05f_e68d_464d_9030_6d57ee951510
ELIN-495990-2015 | EL-233444-2015 | 12/17/2015 3:14:54 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Energized kitchen appliance cables without proper termination are a shock hazard. Kitchen counters without required receptacles can result in use of temporary cords to supply small appliances located in those areas. This would cause a thermal effect. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Hood_fan_cable_energized_without_proper_termination.png | file://x:/photopub/docs/0000000368/f9e2c428-e6b8-44e6-9dd0-540d6026f37e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c60d05f_e68d_464d_9030_6d57ee951510
ELIN-488312-2015 | EL-164726-2014 | 1/8/2016 12:19:43 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 20 amp outdoor receptacles for use with block heaters for farm equipment were not provided weatherproof covers that prevent water from entering receptacles and associated wiring with a cord plugged into the receptacles. Water can enter this equipment when cords are plugged into them, cause corrosion to the wiring and equipment that can result in equipment and wire damage or potential arc fault in equipment and possible property damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | In_use_covers_not_provided.png | file://x:/photopub/docs/0000000375/549a2869-344b-4f5f-aa9b-8c656ab5e18e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8951549_ceef_47cf_a3a2_7751ce33139a
ELIN-505942-2016 | UW-331089-2016 | 1/8/2016 12:19:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Damaged electrical equipment was found at this location. Damaged electrical equipment may fail unpredictably causing damage to property or injury to persons in particular where exposed conductors are accessible | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Water_damage_exposed_conductors_broken_light.png | file://x:/photopub/docs/0000000375/cdecce81-aa81-4c96-8357-a19cdb5b7515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a9442d7_6a6c_4db2_8272_b09821cd5de0
ELIN-520403-2016 | UW-341775-2016 | 2/1/2016 7:52:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found unapproved, damaged, unsafe and non-compliant temporary construction 120/240volt 100a panelboard in wooden enclosure which had energized exposed bus bars due to covers missing on bus bars. When temporary electrical equipment is unapproved, damaged, unsafe and non-compliant this electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Energized_exposed_bus_bars_and_damaged_equipment.png | file://x:/photopub/docs/0000000385/b1b4b05f-97f0-4017-a796-e3967ffd3e7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bee25fa_465e_441a_97f7_00652304f8ba
ELIN-529548-2016 | EL-335997-2016 | 2/19/2016 10:58:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Sometimes the permanent electrical systems in new construction are used to supply temporary power during construction. When this is done the equipment must be enclosed in weatherproof construction. In this case plastic sheets were used to cover the panel but the panel could not be accessed without cutting open the plastic, rendering the weatherproofing unusable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Exterior_of_building.png | file://x:/photopub/docs/0000000393/58a13cda-3f7e-4f51-8dc1-7390fa9f8421.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__044cfc44_d53a_4315_a59e_de341eb943a1
ELIN-483165-2015 | EL-250932-2015 | 11/26/2015 5:31:43 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | 200A 120/240V Main Panel is not protected from the weather which could result in equipment damage and failure. | 0 | No Created Hazard Identified | Main_panel.png | file://x:/photopub/docs/0000000359/ce67a522-6c49-4a03-8cc1-0fa6eb3701c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__953e31a0_7696_456d_8c8f_071ba1fd40ba
ELIN-483180-2015 | EL-316791-2015 | 11/30/2015 5:31:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200A 120/240V Main Panel is exposed to the weather, the equipment is not rated for this and damage or failure to the equipment could result. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_distribution.png | file://x:/photopub/docs/0000000359/4ca7d16e-a92d-40af-884c-dcefdd1a68b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6d1ce80_79d3_475e_8f54_f9e6236c13e7
BPVIN-526901-2016 | UW-345588-2016 | 2/15/2016 3:38:31 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | All pressure vessels must maintain minimal required shell thickness in order to contain a substance at maximum allowable working pressure. I found that this liquid ammonia transfer vessel is severely affected by general corrosion on the exterior which exceeds acceptance criteria for such type of pressure vessels. A potential for an incident exists , such as rupture or ammonia leak, due to a poor condition of this pressure vessel. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | DEEP_PITTING.png | file://x:/photopub/docs/0000000391/2ad816ad-0b8f-4c5f-b7dc-a1d9c235f41b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf08cf1c_bbfa_42dd_989c_a0d9fca25fa7
BPVOP-518383-2016 | 2250767 | 2/15/2016 3:18:10 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | All pressure vessels must maintain minimal required shell thickness in order to contain a substance at maximum allowable working pressure. I found that this liquid ammonia transfer vessel is severely affected by general corrosion on the exterior which exceeds acceptance criteria for such type of pressure vessels. A potential for an incident, such as rupture or ammonia leak. exists due to a poor condition of this pressure vessel. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | Deep_pitting.png | file://x:/photopub/docs/0000000391/1706dc27-b1f5-435c-b952-4cd32e56483c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__880b7582_274a_4f8f_b7bf_14cd013650be
BPVOP-492768-2015 | 4075667 | 12/9/2015 7:11:25 PM | ASSESS: BPV OP: Re-Inspection Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000366/242e6c1f-d71a-4573-8528-70545aa216a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__531e70e3_b897_4ec9_b1c8_3d8b12797d3a
ELIN-485758-2015 | EL-293435-2015 | 11/30/2015 11:38:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Support for over head service conductors is required to be below the point where conductors issue from service heads on service conduits and service cables. This is required to prevent connections and equipment from getting wet by allowing water to run down or through conductors into electrical equipment. This installation has the point of attachment for overhead conductors approximately two feet above the service heads on a pole and at a house. Left uncorrected over time water may enter electrical equipment and corrode connections and equipment. A failed connection in the future is a potential fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_connection_above_service_heads_at_pole.png | file://x:/photopub/docs/0000000359/6bd43236-9601-49bd-9126-76a704ffc154.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e069ee_a44f_48c0_a0a7_d72eb310a406
ELIN-485758-2015 | EL-293435-2015 | 11/30/2015 11:38:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Support for over head service conductors is required to be below the point where conductors issue from service heads on service conduits and service cables. This is required to prevent connections and equipment from getting wet by allowing water to run down or through conductors into electrical equipment. This installation has the point of attachment for overhead conductors approximately two feet above the service heads on a pole and at a house. Left uncorrected over time water may enter electrical equipment and corrode connections and equipment. A failed connection in the future is a potential fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_connection_above_service_head_at_house.png | file://x:/photopub/docs/0000000359/1736dd75-8ead-4373-87d7-734a887fd962.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15e069ee_a44f_48c0_a0a7_d72eb310a406
ELIN-519777-2016 | EL-338093-2016 | 2/2/2016 7:47:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | 200 amp 120/240 volt main distribution panel missing barrier for service conductor termination section. This could cause a thermal effect. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Barrier_missing_for_service_conductors.png | file://x:/photopub/docs/0000000386/3443eed6-a2ad-4416-b847-12c8e7fab29e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4643e8b5_6830_4b54_b230_868dcdf099f1
ELIN-518398-2016 | EL-331067-2016 | 2/2/2016 7:46:38 AM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | 15 amp, 120 volt rated conductor installed on a 20 amp overcurrent device. This could cause a thermal effect. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 20A_breaker_installed_on_a_14awg_conductor.png | file://x:/photopub/docs/0000000386/9583609b-892a-4753-ac02-660be62e4f64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba08d725_8ff3_445a_8f2c_e404a2183b9f
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 9.png | file://x:/photopub/docs/0000000380/f2ef1737-5845-40ca-bb84-4b0e3f5122a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 8.png | file://x:/photopub/docs/0000000380/4e51cae2-7688-421c-b861-ed245514cd70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 6.png | file://x:/photopub/docs/0000000380/dd4d1cd3-2ad4-4fd7-98c5-734ad5486e88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 7.png | file://x:/photopub/docs/0000000380/70a4fa3b-b349-4d10-8950-516dd60c0999.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 2.png | file://x:/photopub/docs/0000000380/3a576e13-23b3-4306-aa00-cb6d9b6a5c58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 11.png | file://x:/photopub/docs/0000000380/7d61707b-5ced-4068-9ce1-0ca02339e734.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-529548-2016 | EL-335997-2016 | 2/19/2016 10:58:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Sometimes the permanent electrical systems in new construction are used to supply temporary power during construction. When this is done the equipment must be enclosed in weatherproof construction. In this case plastic sheets were used to cover the panel but the panel could not be accessed without cutting open the plastic, rendering the weatherproofing unusable. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Interior_of_building.png | file://x:/photopub/docs/0000000393/072332a5-c3bf-4918-8ba1-c36574b71c33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__044cfc44_d53a_4315_a59e_de341eb943a1
ELIN-523278-2016 | UW-343418-2016 | 2/4/2016 1:29:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The site has a customer owned high-voltage service, for a derelict sawmill operation. The primary service shows signs of dereliction and vandalizing. The secondary service has been drastically compromised with most covers and protective equipment missing, damaged, vandalized or altered. Bare energized electrical equipment was found in eight buildings of various types of use. The site was subject a safety order to disconnect. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Main_PDC_center.png | file://x:/photopub/docs/0000000387/a7809529-d883-402c-896b-b9233b72e232.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6428f2_826c_4bc4_a026_4651b5c6f087
ELIN-523278-2016 | UW-343418-2016 | 2/4/2016 1:29:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The site has a customer owned high-voltage service, for a derelict sawmill operation. The primary service shows signs of dereliction and vandalizing. The secondary service has been drastically compromised with most covers and protective equipment missing, damaged, vandalized or altered. Bare energized electrical equipment was found in eight buildings of various types of use. The site was subject a safety order to disconnect. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | SFD_under_construction_at_site.png | file://x:/photopub/docs/0000000387/88e8d3db-d7d9-4d9b-8d29-20d183951b73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6428f2_826c_4bc4_a026_4651b5c6f087
ELIN-523278-2016 | UW-343418-2016 | 2/4/2016 1:29:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The site has a customer owned high-voltage service, for a derelict sawmill operation. The primary service shows signs of dereliction and vandalizing. The secondary service has been drastically compromised with most covers and protective equipment missing, damaged, vandalized or altered. Bare energized electrical equipment was found in eight buildings of various types of use. The site was subject a safety order to disconnect. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Ground_fault_safety_indicating_lights.png | file://x:/photopub/docs/0000000387/74f563c9-2e64-499b-9604-df6568663f91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6428f2_826c_4bc4_a026_4651b5c6f087
ELIN-523278-2016 | UW-343418-2016 | 2/4/2016 1:29:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The site has a customer owned high-voltage service, for a derelict sawmill operation. The primary service shows signs of dereliction and vandalizing. The secondary service has been drastically compromised with most covers and protective equipment missing, damaged, vandalized or altered. Bare energized electrical equipment was found in eight buildings of various types of use. The site was subject a safety order to disconnect. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Bare_energized_buss.png | file://x:/photopub/docs/0000000387/251710bf-dbd4-44ba-9863-143791193a6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6428f2_826c_4bc4_a026_4651b5c6f087
ELIN-523278-2016 | UW-343418-2016 | 2/4/2016 1:29:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The site has a customer owned high-voltage service, for a derelict sawmill operation. The primary service shows signs of dereliction and vandalizing. The secondary service has been drastically compromised with most covers and protective equipment missing, damaged, vandalized or altered. Bare energized electrical equipment was found in eight buildings of various types of use. The site was subject a safety order to disconnect. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Primary_service.png | file://x:/photopub/docs/0000000387/281064d2-5fb1-49cc-9806-fe6637e53e71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6428f2_826c_4bc4_a026_4651b5c6f087
ELIN-523278-2016 | UW-343418-2016 | 2/4/2016 1:29:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The site has a customer owned high-voltage service, for a derelict sawmill operation. The primary service shows signs of dereliction and vandalizing. The secondary service has been drastically compromised with most covers and protective equipment missing, damaged, vandalized or altered. Bare energized electrical equipment was found in eight buildings of various types of use. The site was subject a safety order to disconnect. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Typical_secondary_distribution_.png | file://x:/photopub/docs/0000000387/d2408203-606e-4689-a953-32615e5658b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a6428f2_826c_4bc4_a026_4651b5c6f087
ELIN-487367-2015 | EL-300581-2015 | 12/1/2015 1:35:46 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 2 | Electrical distribution systems are typically only grounded at one point, the supply. This is to ensure a direct path for fault currents and to eliminate neutral currents circulating through the bonding system. This is important to ensure proper operation of over current devices. During an inspection, a sub panel was discovered grounded. Doing so created two grounding points in the system. | 3 | Continuity Bonding; method for equipment is not adequate. | Neutral_buss_bonded_.png | file://x:/photopub/docs/0000000360/313aeb37-1d05-42fd-bc61-f3e3738d62fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__628353e2_b6e7_4af6_99a7_1b15e8d08ead
ELIN-486181-2015 | EL-318968-2015 | 12/1/2015 1:35:49 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 2 | Electrical cable ampacity must not exceed maximum allowable ampacity. Under sizing conductors can lead to cable over heating and deterioration at points of connection. Installed feeders are undersized for commercial application. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | number_2_aluminum_conductor_terminated_to_100amp_fuses.png | file://x:/photopub/docs/0000000360/435fbb77-5354-430f-ab35-08ff929671e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ce56eea_00c5_43fa_a190_5d997cbaa510
GAIN-517405-2016 | GA-324383-2015 | 2/2/2016 2:53:38 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Radiant_tube_heater.png | file://x:/photopub/docs/0000000388/7fa07910-516e-4a7f-a160-b06d98b5c8ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73219a0f_695b_494c_a717_fadb54eceeb9
GAIN-517405-2016 | GA-324383-2015 | 2/2/2016 2:53:38 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Radiant_tube_heater_.png | file://x:/photopub/docs/0000000388/b1d0a8ce-19f6-4c10-9d2a-a5657dce5202.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73219a0f_695b_494c_a717_fadb54eceeb9
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 5.png | file://x:/photopub/docs/0000000380/abb755bc-d699-4c92-8781-b0880968ee3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 4.png | file://x:/photopub/docs/0000000380/ecd320b0-eda0-4b71-b461-ddefd1815017.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-506237-2016 | EL-321196-2015 | 1/20/2016 12:33:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Found seven unapproved, non-compliant and hazardous 120 volt wired high-bay lighting luminaires wired with armoured cables (Type AC90 cables with 120 volt rated cord plug-in cord cap end) was connected to power supply system for temporary use. The above luminaires did not come from the factory assembled and approved as a complete approved assembly as found installed by uncertified worker. When unapproved, non-compliant and hazardous electrical equipment is installed, connected and used then there is a possibility of an electrical fire or shock hazard to people and property. | 0 | No Created Hazard Identified | 3.png | file://x:/photopub/docs/0000000380/c007d3cc-1ce4-443d-9a47-bd2e9254112f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0b337b4_dfae_4bc9_bb34_d26a7120d084
ELIN-490153-2015 | EL-254719-2015 | 12/8/2015 2:38:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | 120/240V 70A service conductors and compartment are not separated from the branch wiring and breaker, this poses a safety hazard to persons servicing the equipment, as there is no protection on the supply service conductors. | 0 | No Created Hazard Identified | Load_Center.png | file://x:/photopub/docs/0000000363/d3ea6261-cbc4-4a1f-a963-ed880b93c149.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e9f5f58_b616_4229_a802_33f9de862263
GAIN-523006-2016 | GA-343306-2016 | 2/9/2016 3:44:23 PM | ASSESS: GA: Rough-In | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | The gas safety officer found a gas leak at a coupling on the gas piping above the meter. The gas leak creates the potential for a fire at the meter location. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 19550_72a.png | file://x:/photopub/docs/0000000389/840257eb-b28c-408b-b337-e3a78451db0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46ec9c96_e2a4_4442_8866_1cf0df00f138
ELIN-524310-2016 | EL-304696-2015 | 2/10/2016 1:17:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Service_mast_enter_top_of_switch.png | file://x:/photopub/docs/0000000389/a63b3a0d-f6f2-4ae3-93f6-c1fbdad47dcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7106bff9_b849_4556_91c0_8dcc1191e6bf
ELIN-478155-2015 | EL-276546-2015 | 12/4/2015 9:09:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | RV_panel.png | file://x:/photopub/docs/0000000375/b2ef16f2-afaf-46d9-9edf-52e95a442082.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__575df983_1e70_4f3d_8f3a_74dbf2c0e71d
ELIN-505330-2016 | EL-326637-2015 | 1/7/2016 5:19:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Mast is bent on the building and is energized. The bent mast can cause the service conductors to short to the mast causing a fire and shock hazard. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Service.png | file://x:/photopub/docs/0000000375/1cf8c87b-f47c-4ba7-b19d-14ab9392c25a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9540f5d8_4523_4bff_95c8_97757f7483e6
ELIN-494318-2015 | EL-296734-2015 | 12/14/2015 11:46:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | Branch circuits lacking mechanical protection may get damaged by drywall screws etc. and cause fires in future. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Nmd3.png | file://x:/photopub/docs/0000000366/c4679063-14f1-4a39-9ee6-1371166352c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87b9fb27_ada6_4a81_81c6_dd8efd8ad54b
ELIN-494318-2015 | EL-296734-2015 | 12/14/2015 11:46:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | Branch circuits lacking mechanical protection may get damaged by drywall screws etc. and cause fires in future. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Nmd1.png | file://x:/photopub/docs/0000000366/8d58d662-6d9b-464a-8ac1-2d0f79f37ec2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87b9fb27_ada6_4a81_81c6_dd8efd8ad54b
ELIN-494318-2015 | EL-296734-2015 | 12/14/2015 11:46:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | Branch circuits lacking mechanical protection may get damaged by drywall screws etc. and cause fires in future. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Box1.png | file://x:/photopub/docs/0000000366/69a89756-467b-4179-a4b3-ace90c48eb81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87b9fb27_ada6_4a81_81c6_dd8efd8ad54b
ELIN-494318-2015 | EL-296734-2015 | 12/14/2015 11:46:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL007 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | 3 | 3 | Branch circuits lacking mechanical protection may get damaged by drywall screws etc. and cause fires in future. | 3 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures within their intended ratings, and building materials are located in an unacceptable location. | Nmd2.png | file://x:/photopub/docs/0000000366/8a4c27f2-0537-4bc4-b1df-ba449a7aa7db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87b9fb27_ada6_4a81_81c6_dd8efd8ad54b
GAIN-497028-2015 | GA-322978-2015 | 12/30/2015 11:19:17 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_term.png | file://x:/photopub/docs/0000000373/080025f4-4368-4301-9724-225fb48a9f54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca929fa_5ffd_44bc_9cd4_372be3bb0d1a
ELIN-490312-2015 | EL-107876-2014 | 12/7/2015 11:32:47 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cable in direct contact with heating system ducting throughout installation resulting in a compromise of the integrity of the conductor insulation due to thermal damage. This greatly increases the potential for serious property damage (thermal event). | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | View01_branch_circuitry.png | file://x:/photopub/docs/0000000364/bd96dbe4-3ecb-4efc-9763-067694371917.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7288887d_cf6c_48e7_a758_5848e5cd7273
GAIN-488696-2015 | GA-320792-2015 | 12/3/2015 1:41:28 PM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The 2"x 4" wooden headers on either side of the fireplace must be installed level with or above the manufacturer's standoffs to avoid raising the temperature of the combustable headers above their kindling point, thereby creating a possibility of ignition. | 3 | Appliance not installed according to installation instructions | Clearance_2.png | file://x:/photopub/docs/0000000361/63b5ce4a-3d82-4ae6-aad6-3266d64d7fa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc87ee5_9586_4b18_b301_1ceb509e173e
GAIN-488696-2015 | GA-320792-2015 | 12/3/2015 1:41:28 PM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The 2"x 4" wooden headers on either side of the fireplace must be installed level with or above the manufacturer's standoffs to avoid raising the temperature of the combustable headers above their kindling point, thereby creating a possibility of ignition. | 3 | Appliance not installed according to installation instructions | Clearance_1.png | file://x:/photopub/docs/0000000361/aba435d0-1760-4664-8c70-62c06dadffb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9bc87ee5_9586_4b18_b301_1ceb509e173e
ELIN-523937-2016 | EL-343763-2016 | 2/16/2016 12:41:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | Dryer and wall oven device boxes not adequately supported to ensure security of these devices over years of use. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Wall_oven_box.png | file://x:/photopub/docs/0000000391/f65cf91b-c498-4bee-993b-1bafdce25de7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7da89cb_917c_4752_9e5c_14820181ebf2
ELIN-523937-2016 | EL-343763-2016 | 2/16/2016 12:41:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | Dryer and wall oven device boxes not adequately supported to ensure security of these devices over years of use. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dryer_box.png | file://x:/photopub/docs/0000000391/24ec01fc-8105-45e7-a9a9-7878257fc034.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7da89cb_917c_4752_9e5c_14820181ebf2
BPVOP-522403-2016 | 4151541 | 2/4/2016 6:26:35 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig, Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit and 9.39 sq. meters of heating surface, it is determined that safety relief valve has exceeded the required 2year interval for testing. Failure to have safety valve tested as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000387/f0c0ab07-eecd-4268-b25d-7cfb405eb32b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__437bbe58_93af_4fad_be58_152620e1076c
BPVOP-522415-2016 | 4151551 | 2/4/2016 6:27:21 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of domestic hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig, Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit and 3.9 sq. meters of heating surface, it is determined that safety relief valve has exceeded the required 2year interval for testing. Failure to have safety valve tested as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_OF_BOILER_WITHOUT_DATE_OF_INSTALLATION_AND_SERVICING_TAG.png | file://x:/photopub/docs/0000000387/22cb2d82-44fd-4b98-a059-0f399f06c544.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__937941f2_8b0e_45c3_9f1b_d08d26dd7f26
ELIN-498489-2015 | EL-294581-2015 | 12/22/2015 3:15:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | A new 200amp 120/240volt 1phase residential underground service is installed with the utility duct and unfused Service cables are resting against the exterior plywood wall with no mechanical protection installed or in place. This could do some equipment damage which could include a thermal hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cable_on_plywood.png | file://x:/photopub/docs/0000000370/2a2abe84-d773-4436-b51a-874a2914d9fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed3b63f1_381e_4de1_9d1f_4a7899d3e5f4
GAIN-521003-2016 | GA-294139-2015 | 2/15/2016 7:46:07 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Gas piping is not bonded properly. Bond conductor is connected to Fortis gas meter manifold missing all the house piping. This could result in serious injury to occupants of the multi units. | 3 | Code prohibited practices or materials | 580_Ellis_St.png | file://x:/photopub/docs/0000000391/98475c96-de30-4d0f-a2c1-216db223bf10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81173054_d885_450b_b2c6_9e42a2fe8bcf
BPVOP-767210-2017 | 2280922 | 2/10/2017 11:16:25 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | #Safety_relief_valve.png Upon assessment of Hot Water storage tank (Length-2.4m, diameter-1.2m) with Maximum Allowable Working Pressure (MAWP) of 125psig, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject pressure vessel to pressure above MAWP if operating control fails to maintain system pressure below MAWP or in an unforeseen event like fire. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000565/23f5172f-c336-40c7-b558-175bee2f2c5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ec83f7a_a3c5_4fb6_8a03_404032acd674
ELIN-765004-2017 | EL-493008-2017 | 3/2/2017 12:07:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | #Pinot3.png 120 v branch circuit cables not isolated from heat sources or strapped in approved manner and can lead to cable failure. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Pinot3.png | file://x:/photopub/docs/0000000565/19bc5cf3-e9d5-4ffa-bbd2-8f586b362612.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d49477ec_35ac_4cce_b137_d586965e1b47
ELIN-512761-2016 | EL-335294-2016 | 1/19/2016 3:07:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Consumers service conductors are exposed to possible mechanical damage coming from trench into building. This could have potential to be a short circuit if damaged. If damage occurs then the potential of a fire or electrocution to person or property could be disastrous, due to the common practice of over sizing the fuses by the supply authority. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Subject_to_mechanical_damage.png | file://x:/photopub/docs/0000000379/83257612-e540-4fd8-8bc3-f49e4801e6c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba7e094f_37f0_4c5c_b147_f80f189c89d1
ELIN-495704-2015 | EL-326083-2015 | 12/16/2015 1:29:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 3 | 240 v , 200 a temporary service pole and underground raceway not sufficiently secured at base: movement may cause damage to equipment. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Temp_pole.png | file://x:/photopub/docs/0000000367/94a226d6-4ba3-492e-9b96-1fade814d100.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20d2999f_81bd_4fb0_975f_d5d6f2c7aa5f
ELIN-503265-2015 | EL-329663-2015 | 12/31/2015 2:59:35 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical panels in residential occupancies are required to have all covers installed and openings covered. During an inspection for a 240 volt, 200 amp residential service upgrade, the safety officer discovered the panel cover was not installed, bounding not terminated, and consumer service cable not terminated on main breaker. Should this service had been energized, a fire shock hazard would have been created. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | New_Panel_Photo_1.png | file://x:/photopub/docs/0000000372/e343ee84-2081-4f5f-b501-b27dc1e89d74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee47be19_1460_45d8_93ac_2d79a6d87df0
ELIN-503265-2015 | EL-329663-2015 | 12/31/2015 2:59:35 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical panels in residential occupancies are required to have all covers installed and openings covered. During an inspection for a 240 volt, 200 amp residential service upgrade, the safety officer discovered the panel cover was not installed, bounding not terminated, and consumer service cable not terminated on main breaker. Should this service had been energized, a fire shock hazard would have been created. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Conductor_not_terminated.png | file://x:/photopub/docs/0000000372/c9b6161f-4e23-422d-8d69-3493df254a98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee47be19_1460_45d8_93ac_2d79a6d87df0
ELIN-503265-2015 | EL-329663-2015 | 12/31/2015 2:59:35 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Electrical panels in residential occupancies are required to have all covers installed and openings covered. During an inspection for a 240 volt, 200 amp residential service upgrade, the safety officer discovered the panel cover was not installed, bounding not terminated, and consumer service cable not terminated on main breaker. Should this service had been energized, a fire shock hazard would have been created. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Condensation_in_panel.png | file://x:/photopub/docs/0000000372/185731de-e06f-4833-84a6-d0ef4ec47760.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee47be19_1460_45d8_93ac_2d79a6d87df0
BPVOP-504314-2016 | 2250760 | 1/26/2016 1:16:13 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP221 | 5.1.2 Validation: work performed - Mandatory testing non-compliant with code or standard | 3 | 3 | Regulated equipment must undergo regular testing. I found that there was no mandatory testing schedule and no testing done on this ammonia refrigeration system for corrosion damage for the last decade. Potential for an incident exists since the amount of corrosion damage is unknown. | 3 | 5.1.2 Validation: work performed - Mandatory testing non-compliant with code or standard | Suspected_corrosion_under_insulation_.png | file://x:/photopub/docs/0000000382/572fb807-5bfd-49c5-828c-27365b2b2cf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__50a9323f_6be6_4d58_8646_55e9a47fecf9
ELIN-497959-2015 | EL-261917-2015 | 12/17/2015 8:20:44 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Armoured cables are not approved for use on ground. In this installation a Cable was installed in a raceway 3" below a driveway and on the surface through a wooded area to an RV receptacle. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | On_surface.png | file://x:/photopub/docs/0000000369/56b93146-b8df-4e99-a009-61ff9b9e1deb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__935c7f7b_3e8b_4c30_a5cd_a7643ffb5af7
ELIN-497959-2015 | EL-261917-2015 | 12/17/2015 8:20:44 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Armoured cables are not approved for use on ground. In this installation a Cable was installed in a raceway 3" below a driveway and on the surface through a wooded area to an RV receptacle. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | To_receptacle.png | file://x:/photopub/docs/0000000369/c54300e8-5f02-44d3-a522-a1bf2fa2abd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__935c7f7b_3e8b_4c30_a5cd_a7643ffb5af7
ELIN-497959-2015 | EL-261917-2015 | 12/17/2015 8:20:44 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Armoured cables are not approved for use on ground. In this installation a Cable was installed in a raceway 3" below a driveway and on the surface through a wooded area to an RV receptacle. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Through_the_bush.png | file://x:/photopub/docs/0000000369/5a1e0f9d-e97a-45f1-93d7-49e1bd7aac65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__935c7f7b_3e8b_4c30_a5cd_a7643ffb5af7
ELIN-528173-2016 | EL-346282-2016 | 2/18/2016 11:51:22 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | Lo | 0 | No Created Hazard Identified | Outlet_box_in_carport.png | file://x:/photopub/docs/0000000392/f3b27e49-7a82-430e-a137-5eaa079c679d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df61caa3_94e7_4671_b7ad_1755abc13008
ELIN-528173-2016 | EL-346282-2016 | 2/18/2016 11:51:22 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | Lo | 0 | No Created Hazard Identified | Damaged_receptacle_in_carport.png | file://x:/photopub/docs/0000000392/b390c2a7-9fc5-4dad-8cc4-f566a3f0ae49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df61caa3_94e7_4671_b7ad_1755abc13008
GAIN-494184-2015 | GA-324717-2015 | 12/21/2015 10:22:33 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Drip leg not installed in piping before appliance inlet. This could allow condensation or debris to enter the inlet of the appliance gas valve possibly allowing it not close properly letting gas to leak through when shut off. | 3 | Code prohibited practices or materials | Furnace_piping.png | file://x:/photopub/docs/0000000369/2052fa1d-f3e8-46d7-aa6b-33aff4332c08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f49b49a7_ed78_4243_a432_8b9575260d67
BPVOP-489436-2015 | 2261080 | 1/12/2016 7:15:06 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Rocks2.png | file://x:/photopub/docs/0000000377/16a445ab-2ecb-438e-9190-5c3665073c6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25a29b34_7871_45db_bccc_1a49888bd0e6
BPVOP-489436-2015 | 2261080 | 1/12/2016 7:15:06 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Rocks.png | file://x:/photopub/docs/0000000377/140e477c-7f95-4801-bb13-3297bf4e979a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25a29b34_7871_45db_bccc_1a49888bd0e6
ELIN-520677-2016 | EL-339543-2016 | 2/4/2016 3:41:58 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Attachment point for consumers service conductors is located above the weather head. This could cause a short from water hydraulicing into the service conductor raceway because the drip loop is above the weatherhead. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Attachment_point.png | file://x:/photopub/docs/0000000387/b26c11af-d405-456b-9fb9-a4de4ff8f969.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99f048f9_2842_43dd_b07e_c7bd00a8d8e0
ELOP-470401-2015 | 5239499 | 12/15/2015 2:13:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables are required to be installed into connectors properly, supported properly, and secured to prevent damage to the cables, connectors, and conductor insulation. This installation has energized cables that are pulled out of connectors, and improperly secured at equipment. This has created a fire and shock hazard should the cable conductors insulation become damaged and either fault to ground creating an arc or come in contact with a persons skin or a conductive object. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cable_pulled_out_of_connector_at_motor.png | file://x:/photopub/docs/0000000367/44567c81-d2a7-4250-b82c-04014a36648c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a8d5cf3_468a_4a41_bad9_901ffa0a855a
GAIN-510971-2016 | GA-296012-2015 | 1/21/2016 2:59:28 PM | ASSESS: GA: Final | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | Clearance between cylinder and building opening not met. In the event of a propane leak, propane could enter the occupied space through the building opening. | 2 | Installation clearances or set backs to propane containers not met | 3827_carey.png | file://x:/photopub/docs/0000000381/b703acd8-c696-428d-a7ef-a6399821f6de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__596afff2_14bd_49b4_aa20_95e6e500e2ca
ELIN-525144-2016 | EL-344480-2016 | 2/16/2016 3:09:47 PM | ASSESS: EL: Final | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 120/240 - 100 amp volt meter base mounted on a pole that is in poor condition. Failure of the pole could lead to equipment damage or be a shock hazard. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Dip_service.png | file://x:/photopub/docs/0000000391/80d96e0c-5454-431c-a2ae-dafdee92b72c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca98fb10_d2f8_450c_827d_c67d39dba4c8
ELIN-522966-2016 | EL-340372-2016 | 2/16/2016 12:23:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | 120/240 volt - 3 conductor #6 awg copper feeder cable protected by 200 amp. This could result in Europe EMT damage. This is a thermal concern. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Panel_feeder.png | file://x:/photopub/docs/0000000391/03ee0c81-e657-41fd-b16d-76a934e7dd48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__772b05f9_c25f_4133_9dfa_683decbb7a79
ELOP-461753-2015 | 1194 | 12/3/2015 10:59:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical equipment must be approved for use. In this installation a number of displays and effects have been constructed which do not employ approved wiring components and which are not approved for use or certified as approved for use in BC. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Not_certified.png | file://x:/photopub/docs/0000000362/054f4942-063f-4a23-88e5-97b62f603297.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__384f0b0e_df12_4e0d_8c94_87cb359bc713
ELOP-461753-2015 | 1194 | 12/3/2015 10:59:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical equipment must be approved for use. In this installation a number of displays and effects have been constructed which do not employ approved wiring components and which are not approved for use or certified as approved for use in BC. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Uncertified_equipment.png | file://x:/photopub/docs/0000000362/a35c877e-a07d-4eb7-aa1b-2ba82926a0b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__384f0b0e_df12_4e0d_8c94_87cb359bc713
GAIN-509280-2016 | GA-334226-2016 | 1/19/2016 1:18:55 PM | ASSESS: GA: Final | png | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 4 | The as found hazard was a gas log set which had been installed in an approved wood burning fireplace without permanently securing the vent damper in the open position. This is a hazard because if the appliance were to be energized with the damper closed the appliance would not be able to vent the products of combustion to the outdoors and there would be a high risk of the products of combustion entering the living space. Potential risk of carbon monoxide poisoning. | 4 | Gas log set installed with damper not permanently secured in open position | Unsecured_damper.png | file://x:/photopub/docs/0000000379/f9ac96e3-5ff0-4eb9-88fa-aeb6874d7460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f73a63f5_20d3_4487_8f3f_795a1c30f01c
GAIN-509280-2016 | GA-334226-2016 | 1/19/2016 1:18:55 PM | ASSESS: GA: Final | png | #asFound | GA149 | Gas log set installed with damper not permanently secured in open position | 4 | 4 | The as found hazard was a gas log set which had been installed in an approved wood burning fireplace without permanently securing the vent damper in the open position. This is a hazard because if the appliance were to be energized with the damper closed the appliance would not be able to vent the products of combustion to the outdoors and there would be a high risk of the products of combustion entering the living space. Potential risk of carbon monoxide poisoning. | 4 | Gas log set installed with damper not permanently secured in open position | Fireplace.png | file://x:/photopub/docs/0000000379/6e4e1371-3344-4583-9729-59baae6e9b31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f73a63f5_20d3_4487_8f3f_795a1c30f01c
BPVOP-512676-2016 | 4048117 | 1/19/2016 5:09:37 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Upon assessment it is determined that machine mounted vertical air receiver (1.12m long and .51m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | SAFETY_VALVE.png | file://x:/photopub/docs/0000000379/3f12b70f-2884-4114-ad76-7db6eafd5572.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc3bc16b_86dc_422b_9c49_f027a11cf624
ELIN-487040-2015 | EL-279383-2015 | 12/3/2015 4:48:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Service_connection_requested.png | file://x:/photopub/docs/0000000361/fa73bb63-d61e-48f5-804e-cefcbb709612.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cb30749_0d2b_4171_8966_de2ac8108b53
BPVIN-499436-2015 | UW-327435-2015 | 12/16/2015 6:46:13 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device (PRV) installed incorrectly. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | PRV_installed_incorrectly.png | file://x:/photopub/docs/0000000369/92d632b9-3635-450f-8e68-52287fb9ede1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__084da88d_70e3_476c_be81_ae0a9b06f423
ELIN-492901-2015 | EL-281273-2015 | 12/9/2015 6:38:04 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Temporary construction service on larger site with multiple non compliances. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | TCS_4.png | file://x:/photopub/docs/0000000365/b3ca4c05-7123-466c-931a-ec9835518f43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f212e47_0917_40d6_a735_fa1b49873568
ELIN-492901-2015 | EL-281273-2015 | 12/9/2015 6:38:04 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Temporary construction service on larger site with multiple non compliances. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | TCS_5.png | file://x:/photopub/docs/0000000365/4420b683-05ad-4c2c-b3d9-805e999e04a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f212e47_0917_40d6_a735_fa1b49873568
ELIN-492901-2015 | EL-281273-2015 | 12/9/2015 6:38:04 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Temporary construction service on larger site with multiple non compliances. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | TCS_1.png | file://x:/photopub/docs/0000000365/8f9a08bf-b7aa-4045-9bea-448c3ac98953.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f212e47_0917_40d6_a735_fa1b49873568
ELIN-492901-2015 | EL-281273-2015 | 12/9/2015 6:38:04 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Temporary construction service on larger site with multiple non compliances. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | TCS_2.png | file://x:/photopub/docs/0000000365/f9dbece6-b409-4e30-878c-ab9a7e4a0ff7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f212e47_0917_40d6_a735_fa1b49873568
ELIN-492901-2015 | EL-281273-2015 | 12/9/2015 6:38:04 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Temporary construction service on larger site with multiple non compliances. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | TCS_3.png | file://x:/photopub/docs/0000000365/10267e3e-8a51-4086-ae05-5ab457e4d302.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f212e47_0917_40d6_a735_fa1b49873568
BPVIN-511068-2016 | UW-335193-2016 | 1/15/2016 4:45:18 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP017 | 1.0.2 Clearances/Maintenance - No start up or commissioning report | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - No start up or commissioning report | Boiler_switch_not_lockable.png | file://x:/photopub/docs/0000000378/6f1b25cb-4d14-47db-bdcf-3a5a8c72a915.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eec19db_0476_4bc3_afe3_5a63513022d4
GAUP-510943-2016 | UW-335146-2016 | 1/14/2016 8:42:25 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Mechanical air supply too close to fireplace vent. When both appliances are running recirculation of flu products could occur causing incomplete combustion | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_clearance.png | file://x:/photopub/docs/0000000380/2eb7b56f-1740-4e9e-81ac-b5a4f4a6f118.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c71a1198_b5d9_4626_a052_e934a23fd760
ELIN-513660-2016 | EL-331279-2016 | 1/25/2016 9:51:23 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Wires enter a flourescent light fixture connected to a 15 amp 120 volt branch circuit without anti abrasion and the fixture is not bonded to ground. Conductors can fault to the fixture and the overcurrent device may not react and cause property damage or injury to persons | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | No_bonding_to_light_fixture_and_no_anti_abrasion.png | file://x:/photopub/docs/0000000384/3bfe5426-7bf9-4cdb-aa30-ec69dce07fc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__037394b6_9cdc_46a7_b3ed_63dc31c7093a
BPVOP-507822-2016 | 3585153 | 1/19/2016 11:43:30 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP080 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | 4 | 4 | The boiler casing is a gas-tight structure surrounding the component parts of the boiler. I found evidence of overheating and blistering on the boiler casing. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | Boiler_casing_.png | file://x:/photopub/docs/0000000385/eb0f19e3-eeba-4217-9b49-2d71c09ad863.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b20346c_fef3_4c58_8cab_6ef1a35279e6
BPVOP-507822-2016 | 3585153 | 1/19/2016 11:43:30 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP080 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | 4 | 4 | The boiler casing is a gas-tight structure surrounding the component parts of the boiler. I found evidence of overheating and blistering on the boiler casing. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | Hot_water_heating_boilers.png | file://x:/photopub/docs/0000000385/cd15bf48-f950-418b-bb7a-a6e4f7815101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b20346c_fef3_4c58_8cab_6ef1a35279e6
BPVOP-507822-2016 | 3585153 | 1/19/2016 11:43:30 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP080 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | 4 | 4 | The boiler casing is a gas-tight structure surrounding the component parts of the boiler. I found evidence of overheating and blistering on the boiler casing. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | Boiler_nameplate_1.png | file://x:/photopub/docs/0000000385/8eeb9026-fb39-43cc-b00b-836178ca20ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b20346c_fef3_4c58_8cab_6ef1a35279e6
PRIN-502558-2015 | PR-329664-2015 | 1/7/2016 3:40:15 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR024 | Procedures not posted Improper training or procedure | 1 | 1 | The procedure in loading the board onto the modified carriers did not provide a method to ensure that a leash attached to the board does not drag on the surface of the loading unloading area. This condition would cause an entanglement hazard which could result in the sudden an violent swinging reaction of a carrier. | 1 | Procedures not posted Improper training or procedure | Bromley_Board_Leash_Dragging_on_Deck.png | file://x:/photopub/docs/0000000385/314ac9c2-e6a2-4bf3-8cc4-d85f2788bc21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d05d1ba_b540_4ab3_9b26_6b36073857cb
GAUP-511600-2016 | UW-335433-2016 | 1/18/2016 7:59:31 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | The as found hazard was two furnaces which had been installed in a crawl space with no provisions to supply combustion air to the units. This is a hazard because without adequate combustion air there is a risk of the furnaces creating a reduced ambient pressure condition within the space preventing proper combustion/operation which creates a risk of flue products entering the home and/or equipment damage. | 4 | Combustion air supply missing | Furnace.png | file://x:/photopub/docs/0000000379/d741aa93-adb9-4b9a-8fcb-0f6af0d71a67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06c19957_4113_48de_9ecb_d6db2a81602d
GAIN-511589-2016 | GA-331095-2016 | 1/18/2016 7:59:19 AM | ASSESS: GA: Rough-In | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | The as found hazard was a water heater which had been installed with no provisions to supply combustion air to the units. This is a hazard because without adequate combustion air there is a risk of the water heater creating a reduced ambient pressure condition within the space preventing proper combustion/operation which creates a risk of flue products entering the home and/or equipment damage. | 4 | Combustion air supply missing | Crawl_space_where_navien_air_intake_draws_from.png | file://x:/photopub/docs/0000000379/0ee56f5a-d215-48e4-929e-1e8136282212.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6e1de6c_4fe1_4650_ac42_309d3cbd7013
BPVOP-448087-2015 | 3045551 | 1/28/2016 12:20:46 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 4 | Pitting observed at 3 different locations on shell ranging in size between 1/4" - 7/8" across and 3/32" - 1/8" deep. Will re-inspect internals of boiler in 6-9 months time to re-assess. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | De_Elegance_Cleaners.png | file://x:/photopub/docs/0000000383/dba81486-eaab-41e0-a5fe-0d4e91268e70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4449e9f1_aeb0_48e0_984b_c8a35e0f2bac
ELIN-484880-2015 | EL-011128-2013 | 11/30/2015 11:51:01 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Open energized spaces on panel boards present a shock hazard. The voltage is 120/208 volts. This equipment is located in a secured area. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Open_energized_spaces_on_Panel_G.png | file://x:/photopub/docs/0000000359/630ebc19-174f-4755-9954-0793c987c231.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25178bb1_1b19_4d97_8059_33e87f415a1a
ELIN-482810-2015 | EL-291409-2015 | 11/26/2015 5:12:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The code requires non-metallic sheathed cables (NMSC) to be installed at least 32mm from the face of structural members where the pass through them. This is required to prevent the cables from being damaged by drywall screws during the drywall installation or other screws, nails or fasteners used in the future to secure other materials to the walls/ceilings. This installation has multiple locations where NMSC branch circuit wiring for a new house is installed closer than 32mm to the face of studs where wiring passes through studs. This is a potential shock or fire hazard if cables get damaged either during construction or afterwards. | 3 | Conductors, No expansion joint or not installed correctly. | Wiring_to_close_to_face_of_studs_.png | file://x:/photopub/docs/0000000358/dc642d24-92c7-445b-b38a-a64bb3348979.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03980a23_89a9_47dd_8c2b_570e53cf9bad
ELIN-517969-2016 | EL-289998-2015 | 2/4/2016 8:42:21 AM | ASSESS: EL: Final | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | A new restaurant with a cumulative 800 amp 3 phase service has 2 consumer service panels that have not been provided with main disconnecting means that is readily accessible. In emergencies or for maintenance where main disconnecting means are not readily accessible, workers or the public can be exposed to risk of electric shock when working on or near panels. | 4 | Damage to equipment may result in overheating. | No_main_disconnecting_means_not_readily_accessible.png | file://x:/photopub/docs/0000000387/cf9502f6-722d-4128-8526-11d497a3b905.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc3efd71_e288_4b68_ba38_a9e96a9920e1
ELIN-489163-2015 | EL-301461-2015 | 12/18/2015 8:32:21 PM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | The hazard , is the lack of receptacles. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_missing_receptacle.png | file://x:/photopub/docs/0000000369/be26d457-f389-449b-88cc-6170fb1ca64a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f4e400c_8e2d_4b31_b2e5_bc308aafd39c
ELIN-495310-2015 | EL-325476-2015 | 12/15/2015 4:31:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Distribution panels are installed in building without a roof and are not weatherproof. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | No_weatherproofing_and_service_conductor_in_excess_of_1_5m.png | file://x:/photopub/docs/0000000367/17a261ff-6d0f-4fea-afd3-91230fef26f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c31b7017_7b1b_4599_b60f_43050f9d7ee6
ELIN-482810-2015 | EL-291409-2015 | 11/26/2015 5:12:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The code requires non-metallic sheathed cables (NMSC) to be installed at least 32mm from the face of structural members where the pass through them. This is required to prevent the cables from being damaged by drywall screws during the drywall installation or other screws, nails or fasteners used in the future to secure other materials to the walls/ceilings. This installation has multiple locations where NMSC branch circuit wiring for a new house is installed closer than 32mm to the face of studs where wiring passes through studs. This is a potential shock or fire hazard if cables get damaged either during construction or afterwards. | 3 | Conductors, No expansion joint or not installed correctly. | Wiring_to_close_to_face_of_studs__.png | file://x:/photopub/docs/0000000358/802f1e92-8c6b-4023-b0b2-d2ac3e430d62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__03980a23_89a9_47dd_8c2b_570e53cf9bad
ELIN-497595-2015 | EL-205040-2015 | 12/17/2015 12:47:42 PM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | The installation is not complete, as declared by the FSR, several unsafe conditions are left including conductors in a lighting box left unterminated in an unsafe manner. Using the light switch at the entrance will create an energized conductor in an unterminated condition. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Heat_pump_conductor_unsupported_and_NMD_90_coming_out_of_ground.png | file://x:/photopub/docs/0000000368/6185db4a-742b-4384-89ef-7831f6f116f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2311bc2_8924_4434_aa5f_b80a4b0487f0
ELIN-497595-2015 | EL-205040-2015 | 12/17/2015 12:47:42 PM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | The installation is not complete, as declared by the FSR, several unsafe conditions are left including conductors in a lighting box left unterminated in an unsafe manner. Using the light switch at the entrance will create an energized conductor in an unterminated condition. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Entrance_light_fixture_left_incomplete.png | file://x:/photopub/docs/0000000368/4c238cee-cac2-4980-b05a-f02e8de31fc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2311bc2_8924_4434_aa5f_b80a4b0487f0
ELIN-501777-2015 | EL-270940-2015 | 1/6/2016 5:00:43 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet and lighting boxes are required to have devices or covers installed on them to prevent contact with energized wiring, to contain thermal energy in the event of a fault, and to protect wiring from mechanical damage. This installation in the accessory shop building on a residential property has open outlet boxes with energized branch circuit wiring. The circuits are 15A, 120V rated. Left uncorrected this is a potential shock and fire hazard in the event that energized circuits are contacted or damaged. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_outlet_box_on_ceiling_of_shop.png | file://x:/photopub/docs/0000000374/33ab87e0-d83a-4179-81c4-2972c11e21c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c3be6d_21fa_4520_9e3a_4121074eeaa7
ELIN-501777-2015 | EL-270940-2015 | 1/6/2016 5:00:43 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet and lighting boxes are required to have devices or covers installed on them to prevent contact with energized wiring, to contain thermal energy in the event of a fault, and to protect wiring from mechanical damage. This installation in the accessory shop building on a residential property has open outlet boxes with energized branch circuit wiring. The circuits are 15A, 120V rated. Left uncorrected this is a potential shock and fire hazard in the event that energized circuits are contacted or damaged. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_outlet_box_in_shop_.png | file://x:/photopub/docs/0000000374/40cf231a-c88c-4546-af44-f3d49a5579f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c3be6d_21fa_4520_9e3a_4121074eeaa7
ELIN-517244-2016 | UW-339557-2016 | 1/27/2016 6:51:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 | Tenant noted work was completed by friend of owner | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Baseboard_heater_1.png | file://x:/photopub/docs/0000000383/805f5a6c-ec3d-4c9b-9298-d3c1775eafd6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a37fd5f_a490_4058_8a3c_ce9c432668e6
ELIN-517244-2016 | UW-339557-2016 | 1/27/2016 6:51:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 | Tenant noted work was completed by friend of owner | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Radiant_heater.png | file://x:/photopub/docs/0000000383/6634ce1d-639d-46a5-a807-e868c8f43c67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a37fd5f_a490_4058_8a3c_ce9c432668e6
ELIN-517244-2016 | UW-339557-2016 | 1/27/2016 6:51:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 | Tenant noted work was completed by friend of owner | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Baseboard_heater_2.png | file://x:/photopub/docs/0000000383/0305e4a7-a39b-4a44-b81e-36d687348250.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a37fd5f_a490_4058_8a3c_ce9c432668e6
ELIN-501777-2015 | EL-270940-2015 | 1/6/2016 5:00:43 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet and lighting boxes are required to have devices or covers installed on them to prevent contact with energized wiring, to contain thermal energy in the event of a fault, and to protect wiring from mechanical damage. This installation in the accessory shop building on a residential property has open outlet boxes with energized branch circuit wiring. The circuits are 15A, 120V rated. Left uncorrected this is a potential shock and fire hazard in the event that energized circuits are contacted or damaged. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Front_of_detached_shop.png | file://x:/photopub/docs/0000000374/cbc37335-3358-4b94-8836-f192c01d7129.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c3be6d_21fa_4520_9e3a_4121074eeaa7
ELIN-501777-2015 | EL-270940-2015 | 1/6/2016 5:00:43 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Outlet and lighting boxes are required to have devices or covers installed on them to prevent contact with energized wiring, to contain thermal energy in the event of a fault, and to protect wiring from mechanical damage. This installation in the accessory shop building on a residential property has open outlet boxes with energized branch circuit wiring. The circuits are 15A, 120V rated. Left uncorrected this is a potential shock and fire hazard in the event that energized circuits are contacted or damaged. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_outlet_boxes_in_the_shop.png | file://x:/photopub/docs/0000000374/912e8d4c-4ade-478f-9a9e-8479ae00852b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c3be6d_21fa_4520_9e3a_4121074eeaa7
GAIN-507614-2016 | GA-331811-2016 | 1/20/2016 8:54:17 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Exhaust duct is tight to combustibles construction. If dryer were to overheat or catch fire, adjacent materials may catch fire | 3 | Clearance to combustible not met | Duct_clearance.png | file://x:/photopub/docs/0000000380/dcf26aaf-bfdf-4fff-a853-9488a54d71c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8dd047b_217a_42ee_a4d9_b908c07a7d98
ELIN-502113-2015 | EL-254108-2015 | 12/29/2015 1:44:31 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles located in close proximity of wash basins are required to be protected by ground fault circuit interrupters (GFCI). These device will de-energize an appliances should it come into contact with water to prevent a shock. During any inspection, a standard 120 volt, 20amp receptacle was located within close proximity to a wash basin and was not GFCI protected. This presents a possible shock hazard should an appliance such as a radio fall into the washbasin or stream of water. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_beside_washbasin.png | file://x:/photopub/docs/0000000371/98c9662b-c14b-4a9a-b10f-0a1012ade3b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96955b11_3ffd_42b8_8b17_1afdaf46b16d
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Receptacle_that_was_arcing.png | file://x:/photopub/docs/0000000384/d3affabf-69f9-4c5e-9600-e9156ad53aa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Receptacle_.png | file://x:/photopub/docs/0000000384/0c511fad-0602-4964-bb2e-0c679a802f7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Receptacle_that_was_arcing_.png | file://x:/photopub/docs/0000000384/a39e64ec-81f1-45d7-a9fe-df2e96dd0550.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Back_of_receptacle_.png | file://x:/photopub/docs/0000000384/03182119-fcce-413c-a1cd-2a26ef2770ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Front_of_receptacle_.png | file://x:/photopub/docs/0000000384/d0f5ba03-f61f-42da-86da-40c56864b9e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Front_of_the_house.png | file://x:/photopub/docs/0000000384/b1aa91f8-0a15-40dc-8a9b-29e77766a59d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-517828-2016 | UW-339893-2016 | 1/28/2016 3:02:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Branch circuit wiring is required to be spliced properly using the correct wire connectors with care taken to ensure that the circuit neutral conductor and the bonding conductor are not connected together or in contact with each other. This is required to ensure the integrity of connections is secure and the conductors of the circuit are not used for purposes that they are not intended or approved for. This installation has aluminum wiring with wire connectors that are not approved for aluminum connections. While testing a receptacle arcing was observed between the receptacle mounting strap and the screw used to connect the receptacle to the outlet box. Arcing was observed when the receptacle strap contacted the mounting strap which was intermittent due to screws not being tightened properly. An adjacent bedroom light fixture intermittently flickered when this connection was made and then broken causing a visible arc and snapping sound. Circuit current was traveling through the receptacle strap and the bondin | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Back_of_receptacle_and_charred_neutral_conductor.png | file://x:/photopub/docs/0000000384/9eaaf7b6-d54b-4a84-bd30-ea1bd4a423fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__111efc19_263f_4a84_8f9d_54c7c3df19a9
ELIN-484700-2015 | EL-165137-2014 | 12/7/2015 11:58:06 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | An electric furnace drawing up to 66 amps at 240 volts is connected to a 70 amp circuit breaker. Circuit breakers are able to sustain loads of a maximum of 80 % of their rating, in this case more than 56 amps. The circuit breaker can fail leaving the home without heating. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 66_amp_furnace_.png | file://x:/photopub/docs/0000000363/109e9cfb-5da3-457c-9d04-bda1e51d51a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eaaa8cc_0230_4a84_93f1_33606e1a650e
ELIN-488682-2015 | EL-297226-2015 | 12/7/2015 11:58:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 3 | Ready access to the main disconnecting means for a 400 amp 240 volt 1 phase consumers service in a residence has not been provided in the residence. A main service disconnecting means has been installed outside the dwelling on a pole. The service conductors enter inside the dwelling into a 400 amp 240 volt rated splitter intended for adding future loads. Without ready access to a disconnecting means in the residence ahead of this splitter workers may be subject to injury when working on this equipment. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Splitter_first_thing_in_residence_main_disconnecting_means_on_pole.png | file://x:/photopub/docs/0000000363/e54945d5-8904-4def-9ec2-7ac6461e36a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7506fa1_e016_4804_a330_50c0ec177b87
ELIN-495422-2015 | EL-270715-2015 | 12/18/2015 12:52:25 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found receptacle outlet covers missing on garburator under sink while electrical equipment is energized and electricians are not returning because all work was declared as being complete. When covers are missing on receptacle outlets in areas not readily accessible like under a sink, then there is a possibility the cover will stay missing and this could become a possible electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Receptacle_cover_missing_on_garburator_outlet_under_sink_and_possibly_would_stay_this_way_unsafe.png | file://x:/photopub/docs/0000000368/86d12c2f-5317-4af7-b9f7-eda073925154.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7e93438_3e89_4579_b258_15b5b241e5cd
ELIN-495424-2015 | EL-270718-2015 | 12/18/2015 12:53:15 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found 120 volt 15 amp outdoor receptacle outlet is missing the proper approved bubble type cover to fully cover a cord cap end of an extension cord plugged into this receptacle located outdoors in wet location. When a proper approved outdoor receptacle cover is not installed, then this is a possible electrical shock hazard to people using energized electrical equipment outdoors in wet locations. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outdoor_receptacle_cover_cant_open_and_does_not_cover_cord_end.png | file://x:/photopub/docs/0000000368/8ba185bf-31b3-42d9-ba48-31bfd9cb0ccb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85e730b0_92a7_44a8_b640_3a463d64186e
ELIN-495422-2015 | EL-270715-2015 | 12/18/2015 12:52:25 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found receptacle outlet covers missing on garburator under sink while electrical equipment is energized and electricians are not returning because all work was declared as being complete. When covers are missing on receptacle outlets in areas not readily accessible like under a sink, then there is a possibility the cover will stay missing and this could become a possible electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Island_receptacle_with_no_cover_while_energized.png | file://x:/photopub/docs/0000000368/4279de80-56cf-4a6d-a1ea-2cf02a99847b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7e93438_3e89_4579_b258_15b5b241e5cd
ELIN-488404-2015 | EL-320539-2015 | 12/3/2015 6:45:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 15 amp 120v rated receptacle installed on a 20 amp 120V rated overcurrent device. This could cause a thermal effect. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | Panel_not_installed_lockable_weatherproof_enclosure_Receptacle_not_rated_for_overcurrent_device.png | file://x:/photopub/docs/0000000361/d06350fb-3d60-49c8-8d5d-0952709765b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d78fe66_917a_4be4_b76f_cf44399a30a3
BPVIN-512574-2016 | UW-336094-2016 | 1/19/2016 1:28:29 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Exp_tank_clearance.png | file://x:/photopub/docs/0000000385/3915ced4-fb8d-4114-8513-472841b4c09b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d714083_9cd4_4417_851c_96f26bd09b65
ELIN-515330-2016 | EL-330689-2015 | 1/29/2016 3:52:19 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The retractable cords are being used for a large resistive load, that may easily exceed the rating of the cord. The cords are fastened to a steel permanent structure, and may be subject to mechanical damage through daily use. The cord retractor is above the ceiling tile and out of view of staff & public this creates a hazard for the equipment being subject to high thermal conditions. The pendant light was not approved and was previously painted, and missing lamps the risk being electric shock . | 4 | Conductors, Misuse of flexible cords. | Del_Rio_-4.png | file://x:/photopub/docs/0000000384/015158bd-608d-4608-b09d-7a914f58380c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__013efbdc_c174_48b4_bed9_6f17ec411e19
ELIN-515330-2016 | EL-330689-2015 | 1/29/2016 3:52:19 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The retractable cords are being used for a large resistive load, that may easily exceed the rating of the cord. The cords are fastened to a steel permanent structure, and may be subject to mechanical damage through daily use. The cord retractor is above the ceiling tile and out of view of staff & public this creates a hazard for the equipment being subject to high thermal conditions. The pendant light was not approved and was previously painted, and missing lamps the risk being electric shock . | 4 | Conductors, Misuse of flexible cords. | DelRio-3.png | file://x:/photopub/docs/0000000384/50f32c97-7ff3-4f07-bd22-9d2d267ff709.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__013efbdc_c174_48b4_bed9_6f17ec411e19
ELIN-515330-2016 | EL-330689-2015 | 1/29/2016 3:52:19 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The retractable cords are being used for a large resistive load, that may easily exceed the rating of the cord. The cords are fastened to a steel permanent structure, and may be subject to mechanical damage through daily use. The cord retractor is above the ceiling tile and out of view of staff & public this creates a hazard for the equipment being subject to high thermal conditions. The pendant light was not approved and was previously painted, and missing lamps the risk being electric shock . | 4 | Conductors, Misuse of flexible cords. | Del_Rio-1.png | file://x:/photopub/docs/0000000384/bbfc809d-66f8-41fc-a8fb-1f4506e6c1b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__013efbdc_c174_48b4_bed9_6f17ec411e19
ELIN-515330-2016 | EL-330689-2015 | 1/29/2016 3:52:19 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | The retractable cords are being used for a large resistive load, that may easily exceed the rating of the cord. The cords are fastened to a steel permanent structure, and may be subject to mechanical damage through daily use. The cord retractor is above the ceiling tile and out of view of staff & public this creates a hazard for the equipment being subject to high thermal conditions. The pendant light was not approved and was previously painted, and missing lamps the risk being electric shock . | 4 | Conductors, Misuse of flexible cords. | Del_Rio-2.png | file://x:/photopub/docs/0000000384/bf0b4828-09ac-4151-8afa-a42ad79be454.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__013efbdc_c174_48b4_bed9_6f17ec411e19
ELIN-489686-2015 | EL-254099-2015 | 12/9/2015 1:38:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Consumer service conductors located on the load side of the main service disconnect are protected by the Utility, rather than consumer service over current devices. As such, these conductors are subject to a high fault current. To protect persons and property, and to ensure proper operation of Utility over current devices, more restrictive bonding (connection to ground) requirements are required for equipment installed on the load side of the main service disconnect. During a physical inspection of a new 240 volt / 200 amp service installation, the attending safety office discovered the raceway containing consumer service conductors was not sufficiently bonded. Should a fault occur, a high impedance (restrictive) path to ground may be induced. This could limit the effectiveness of Utility over current devices and damage consumer service equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_bushing_on_panel_side.png | file://x:/photopub/docs/0000000364/74efb526-1d10-4822-a168-ce3bea7aa272.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__966b94b7_edd6_42c0_a90d_aee0026193b5
ELIN-489686-2015 | EL-254099-2015 | 12/9/2015 1:38:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Consumer service conductors located on the load side of the main service disconnect are protected by the Utility, rather than consumer service over current devices. As such, these conductors are subject to a high fault current. To protect persons and property, and to ensure proper operation of Utility over current devices, more restrictive bonding (connection to ground) requirements are required for equipment installed on the load side of the main service disconnect. During a physical inspection of a new 240 volt / 200 amp service installation, the attending safety office discovered the raceway containing consumer service conductors was not sufficiently bonded. Should a fault occur, a high impedance (restrictive) path to ground may be induced. This could limit the effectiveness of Utility over current devices and damage consumer service equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_bushing_on_meter_side.png | file://x:/photopub/docs/0000000364/434a98e6-f84d-4273-9d78-170e36db9f99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__966b94b7_edd6_42c0_a90d_aee0026193b5
ELIN-512823-2016 | EL-330375-2015 | 1/20/2016 8:26:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | In a new single family dwelling, 4x 15amp 120volt outlets and 1x 15amp 120volt switch are observed in an energized state without protective cover plates installed. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outside_outlet_with_no_cover_plates.png | file://x:/photopub/docs/0000000382/50cdcd37-16d4-41d9-ac11-761848c13c45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__339e2974_66ef_4b10_baf8_1a3780b8de39
ELIN-478155-2015 | EL-276546-2015 | 12/4/2015 9:09:35 AM | ASSESS: EL: Service Connection | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Meter_Base.png | file://x:/photopub/docs/0000000361/00091e46-ef05-4a12-8a32-0ac6dfaf102a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__575df983_1e70_4f3d_8f3a_74dbf2c0e71d
GAIN-489007-2015 | GA-320998-2015 | 12/9/2015 1:56:43 PM | ASSESS: GA: Rough-In | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Combustible header and press board facing installed too close to appliance, creating possibility of overheating combustible material to ignition temperature. | 3 | Clearance to combustible not met | Clearance.png | file://x:/photopub/docs/0000000364/6856e1f3-c430-4bbf-9162-dd1c3659d164.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff199ead_dc77_44ff_91cf_b591a43ab9e6
ELIN-504552-2016 | EL-302930-2015 | 1/8/2016 3:32:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | 120/240 Volt 100 Amp energized combination panel has exposed buss bars and is accessible to persons. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_removed_from_energized_panel.png | file://x:/photopub/docs/0000000375/69a740ad-761a-423f-b41e-06cbb6443d86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a654800_0bdd_4b68_b6f5_3b6f08c798c8
BPVOP-501408-2015 | 2292572 | 12/23/2015 9:40:22 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Upon assessment of machine mounted vertical air receiver (0.90m long and 0.40m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, it is determined that vessel has exceeded 20 years of service life and did not have a complete examination (complete examination for vessel over 20 years shall include the use of surface and volumetric NDE testing as applicable, to determine thickness and identify defects such as cracking, corrosion and pitting) as required by Safety Order. Minimum thickness of pressure boundary (shell, head nozzle, longitudinal or circular seam welds etc. of vessel) determines the MAWP and if there is presence of corrosion, cracking or pitting, this may cause failure of pressure boundary at a pressure well below MAWP. In the event of failure of pressure boundary, shooting/propelling effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | ASME_NAMEPLATE_WITH_YEAR_BUILT.png | file://x:/photopub/docs/0000000371/1fd0add7-5127-42c0-bd86-58f32785bd98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54b7db1e_c6c9_4ec1_a85f_229b5b25adfe
GAIN-521105-2016 | GA-316960-2015 | 2/4/2016 4:12:09 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Regulator installed outdoors with a brass vent limiter. | 2 | Not installed according to certified installation instructions | Appliance_regulator.png | file://x:/photopub/docs/0000000387/b055bc65-05b3-4450-a230-dd34ad52ea5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83a51732_a45a_4521_9927_986cd6d0cd9a
ELIN-515370-2016 | EL-305397-2015 | 1/25/2016 3:46:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have their covers installed. This is to ensure that persons and or conductive materials do not come in contact with energized parts . Exposed energized parts pose a shock hazard to individuals. In addition, should conductive material come in contact with energized parts, a fault condition could occur damaging the equipment. During a rough wire inspection, a safety officer identified an energized, 240 volt, 200 amp, main distribution panel located in the garage with it's cover removed and bussing exposed. The panel was accessible, as the garage door was not installed. In addition, the house was located in an occupied residential sub division. The attending safety officer located the panel cover and installed to remediate the safety hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_without_cover.png | file://x:/photopub/docs/0000000382/695576c9-5150-4776-a85d-741b2e4ff32c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cafc039_d210_4e91_b64a_463058363fe0
ELIN-515370-2016 | EL-305397-2015 | 1/25/2016 3:46:24 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Energized electrical panels are required to have their covers installed. This is to ensure that persons and or conductive materials do not come in contact with energized parts . Exposed energized parts pose a shock hazard to individuals. In addition, should conductive material come in contact with energized parts, a fault condition could occur damaging the equipment. During a rough wire inspection, a safety officer identified an energized, 240 volt, 200 amp, main distribution panel located in the garage with it's cover removed and bussing exposed. The panel was accessible, as the garage door was not installed. In addition, the house was located in an occupied residential sub division. The attending safety officer located the panel cover and installed to remediate the safety hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Cover_installed_by_safety_officer.png | file://x:/photopub/docs/0000000382/8a427563-88cf-4741-a66a-8a7342ed4a08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cafc039_d210_4e91_b64a_463058363fe0
ELIN-516006-2016 | UW-338630-2016 | 1/25/2016 7:56:33 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL194 | Energized work by qualified persons, Risk Reg EL-26-2017 Extra low voltage: • shock, arc flash, or arc blast hazard from another system is within limited approach. | 2 | 2 | Extra low voltage work being performed without Permit. There is no potential shock or thermal hazard present with the class 2 wiring | 2 | Energized work by qualified persons, Risk Reg EL-26-2017 Extra low voltage: • shock, arc flash, or arc blast hazard from another system is within limited approach. | Utilities_entrance_termination_boxes.png | file://x:/photopub/docs/0000000382/6df8cf1b-3bca-4d0a-a658-0448dec2d92f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5308ee78_88b2_4c8e_88cb_c3d786b3a245
ELIN-515365-2016 | EL-304323-2015 | 1/25/2016 7:56:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | The main distribution panelboard Is installed and operational with no lockable cover in place and exposed to public access. This equipment is subject to mechanical damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Main_distribution_panel.png | file://x:/photopub/docs/0000000382/3b0a6d11-1d05-4e57-8d5d-a3f8be1b680d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9edeb5b8_709f_4f2c_a9bd_0b74772f6e70
ELIN-516006-2016 | UW-338630-2016 | 1/25/2016 7:56:33 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL194 | Energized work by qualified persons, Risk Reg EL-26-2017 Extra low voltage: • shock, arc flash, or arc blast hazard from another system is within limited approach. | 2 | 2 | Extra low voltage work being performed without Permit. There is no potential shock or thermal hazard present with the class 2 wiring | 2 | Energized work by qualified persons, Risk Reg EL-26-2017 Extra low voltage: • shock, arc flash, or arc blast hazard from another system is within limited approach. | Main_media_panel.png | file://x:/photopub/docs/0000000382/a8efb895-d6ef-44dc-b6a9-92a60f56199e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5308ee78_88b2_4c8e_88cb_c3d786b3a245
ELOP-520972-2016 | 5032810 | 2/3/2016 10:05:43 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized electrical panels are require to have all unused openings closed off with approved fillers or plates. This is to ensure people and or conductive materials do not come into contact with energized parts. During an electrical operating permit assessment, the attending safety officer discovered an energized, 240volt, 100amp, electrical panel mounted in a temporary wood enclosure located outside. This panel was supplying power for an adjacent construction site. Several panel fillers were missing. As such, an individual and or conductive material could come into contact with energized parts of this panel. This could result in either a shock or equipment damage. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Missing_panel_fillers.png | file://x:/photopub/docs/0000000386/6f9aed01-b6bb-4967-8f30-a5db53f9230d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c5b4629_dc13_4a9a_b6ba_cf225261daa2
EDIN-501684-2015 | ED-121791-2014 | 12/21/2015 2:14:38 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator brake was not set properly during the installation of the escalator. The brake torque was set well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 98Nm (Newton Meter). The actual brake torque was set at 95Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was not being used for public use. A picture of the Brake Data Plate showing the maximum and minimum brake torque settings has been included. | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate.png | file://x:/photopub/docs/0000000371/a68a6d83-4b57-44ac-9cad-e36d7c3e6320.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b1448304_9cb3_42dd_a2a9_6a504abf3c1f
EDIN-501681-2015 | ED-121925-2014 | 12/22/2015 2:14:34 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator brake was not set properly during the installation of the escalator. The brake torque was set well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 90.9Nm (Newton Meter). The actual brake torque was set at 72Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was not being used for public use. A picture of the Brake Data Plate showing the maximum and minimum brake torque settings has been included. | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate_29192.png | file://x:/photopub/docs/0000000371/2799f138-960a-40cd-9ca6-a11e0ef11213.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65725b66_afea_43d0_9b9d_c49f4f3e4e25
EDIN-501683-2015 | ED-121921-2014 | 12/21/2015 2:14:20 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator brake was not set properly during the installation of the escalator. The brake torque was set well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 98Nm (Newton Meter). The actual brake torque was set at 79Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was not being used for public use. A picture of the Brake Data Plate showing the maximum and minimum brake torque settings has been included. | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate_29190.png | file://x:/photopub/docs/0000000371/6c7338e3-4164-4640-8953-debbd3034e74.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__223e618b_42ca_4f00_822a_d3472adf69df
EDIN-501682-2015 | ED-121923-2014 | 12/22/2015 2:14:44 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator brake was not set properly during the installation of the escalator. The brake torque was set well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 90.9Nm (Newton Meter). The actual brake torque was set at 58Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was not being used for public use. A picture of the Brake Data Plate showing the maximum and minimum brake torque settings has been included. | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate_29191.png | file://x:/photopub/docs/0000000371/8795a6b4-1d97-4a26-bf95-cb08dc5148a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__322891bf_9138_40b8_92b5_2466902e1a1a
EDIN-501679-2015 | ED-121929-2014 | 12/21/2015 2:14:47 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator brake was not set properly during the installation of the escalator. The brake torque was set well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 100.9Nm (Newton Meter). The actual brake torque was set at 71Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was not being used for public use. A picture of the Brake Data Plate showing the maximum and minimum brake torque settings has been included. | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate_29193.png | file://x:/photopub/docs/0000000371/30fb17e7-7a78-4a08-999d-8c7c0242340a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e52571d8_1f8f_456b_8b39_37191fb6105f
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 2pole_20Amp_breaker_hangng_out_of_panel_energized.png | file://x:/photopub/docs/0000000378/048c5522-6886-4ddf-b5f3-075f8281f4fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Branch_circuits_in_living_area_exposed_to_mechanical_damage.png | file://x:/photopub/docs/0000000378/04bfa943-e3da-4602-a0f3-2ff092939e26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
GAIN-489447-2015 | GA-249113-2015 | 12/7/2015 8:12:15 PM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Piping installed from propane tank service valve to regulator is not an approved material for the operating pressure of the propane tank. The pipe or fittings could fail as a result of overpressure causing a large release of propane and possible fire or explosion. | 3 | Non-compliant material/fittings installed | Regulator_piping.png | file://x:/photopub/docs/0000000363/932dc21f-49b2-45cd-9cfa-653e90b2c890.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f320b20_1806_4ad4_8aa5_b222340d5770
ELIN-498758-2015 | EL-286697-2015 | 12/23/2015 9:49:16 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The ground conductor for the 1200 amp 347/600 volt 3 phase 4 wire system is terminated on the distribution grounding buss and not to the identified conductor, this will rely on any faults to flow through additional connections through the existing service bonding conductor to the supply authorities neutral connection- this can cause equipment damage. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | MDC_ground__2.png | file://x:/photopub/docs/0000000371/50f05a9c-8804-4a49-8b1f-1dde5101488b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__838fd522_01fb_4cfc_bc01_864042cc2115
ELIN-498758-2015 | EL-286697-2015 | 12/23/2015 9:49:16 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The ground conductor for the 1200 amp 347/600 volt 3 phase 4 wire system is terminated on the distribution grounding buss and not to the identified conductor, this will rely on any faults to flow through additional connections through the existing service bonding conductor to the supply authorities neutral connection- this can cause equipment damage. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | MDC_ground__1.png | file://x:/photopub/docs/0000000371/7af18bf1-e196-494d-833c-7275943c8053.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__838fd522_01fb_4cfc_bc01_864042cc2115
ELIN-514897-2016 | EL-324878-2015 | 1/25/2016 8:00:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 200 amp, 120/240 volt main distribution has ground conductor for tel and cable boxes terminated in service conductor compartment. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | ground_conductor_for_tel__and_cable_boxes_terminated_in_service_conductor_compartment.png | file://x:/photopub/docs/0000000382/22cad80e-2a3b-43a0-9bbd-a5622c78800f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8dcba54b_630f_4cb5_848f_dc827ca3700f
ELIN-515378-2016 | EL-328169-2015 | 1/26/2016 3:01:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | An existing single family dwelling is adding a secondary suite and thus upgrading the electrical service to accommodate. The new 200amp 120/240volt single phase service construction is not complete. The system ground has not been connected or installed. This is a thermal hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Point_of_attachment.png | file://x:/photopub/docs/0000000382/ec9c7d6e-af14-4e46-89d1-7bf670be200c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2241138d_9dff_43b6_8f83_c005809f6d9b
ELIN-515378-2016 | EL-328169-2015 | 1/26/2016 3:01:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | An existing single family dwelling is adding a secondary suite and thus upgrading the electrical service to accommodate. The new 200amp 120/240volt single phase service construction is not complete. The system ground has not been connected or installed. This is a thermal hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_system_ground.png | file://x:/photopub/docs/0000000382/eb43418b-9627-495c-ad0b-97964893c4c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2241138d_9dff_43b6_8f83_c005809f6d9b
ELIN-494166-2015 | EL-129956-2014 | 12/14/2015 4:27:49 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Physical damage to unprotected service cable on the service pole near ground can cause fire and shock. Imminent danger is not present. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_2.png | file://x:/photopub/docs/0000000366/896890a3-632d-4f2c-844d-43d00570065d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f85cf4ba_b456_4b9d_b7e9_1c970274553a
ELIN-494166-2015 | EL-129956-2014 | 12/14/2015 4:27:49 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Physical damage to unprotected service cable on the service pole near ground can cause fire and shock. Imminent danger is not present. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service1.png | file://x:/photopub/docs/0000000366/271170fd-0035-4756-bb83-c4607690177e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f85cf4ba_b456_4b9d_b7e9_1c970274553a
GAIN-500865-2015 | GA-267488-2015 | 1/26/2016 7:07:46 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | No combustion air is provided for boiler. This could cause a roll out of flames due to lack of air. Also, the draft hood located on nearby hot water tank could reverse and bring air into room along with flue gases possibly causing CO poisoning to people in the home. | 4 | Combustion air supply missing | Mechanical_enclosure.png | file://x:/photopub/docs/0000000382/a4e8674f-93db-43a9-90cf-b62cc215d177.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f74ddadf_6859_4bdf_8ce4_013481037152
GAIN-500865-2015 | GA-267488-2015 | 1/26/2016 7:07:46 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | No combustion air is provided for boiler. This could cause a roll out of flames due to lack of air. Also, the draft hood located on nearby hot water tank could reverse and bring air into room along with flue gases possibly causing CO poisoning to people in the home. | 4 | Combustion air supply missing | Boiler.png | file://x:/photopub/docs/0000000382/a1723ede-d718-45d8-8122-5583758c73f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f74ddadf_6859_4bdf_8ce4_013481037152
ELIN-505698-2016 | EL-321155-2015 | 1/7/2016 4:51:31 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | EMT_mast.png | file://x:/photopub/docs/0000000375/7a546cf8-4366-4b82-b188-b60b2500805b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6280d583_db7d_4bb5_bfff_41613acfc612
BPVOP-506143-2016 | BPV-091785-2014 | 1/25/2016 10:09:01 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Deposits_.png | file://x:/photopub/docs/0000000382/36831a1c-6537-4aef-ac9f-a7324a2c0d28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ece7856_c63b_4b8b_9724_fa71c33d28ca
ELIN-505549-2016 | EL-324541-2015 | 1/8/2016 1:42:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The 15 amp, 120 volt permanent receptacles used for construction power do not include protective cover plates, this is a shock hazard. | 3 | Conductors, No expansion joint or not installed correctly. | Temporary_construction_receptacle_.png | file://x:/photopub/docs/0000000375/f7d3c3a9-30bf-469a-9488-81ab911ae196.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc513be_d39f_4ff7_84b8_beff4e346fe7
ELIN-505391-2016 | EL-274388-2015 | 1/8/2016 1:42:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The 400 amp 208 volt 3 phase service equipment is not properly bonded with a grounding/ bonding bushing on the unfused (line) side of the service disconnect. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Main_Service_disconnect.png | file://x:/photopub/docs/0000000375/f180fd11-3344-48e9-b0cf-c654f137af24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceb05297_61e7_40cb_949d_213b173cc7ca
ELOP-226698-2014 | 4020505 | 12/2/2015 5:50:24 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | Electrical service equipment must be maintained in good working order to avoid early failure. In this installation the service equipment has been subjected to excessive moisture buildup and it is badly corroded. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | Main_switch.png | file://x:/photopub/docs/0000000361/63818b9e-fef3-49d1-9be8-4106df7725f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8287656b_3c39_4213_a730_aaf74f1a952f
ELOP-195665-2014 | 1195 | 12/3/2015 6:07:58 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Electrical equipment must be approved for use. The service switch installed at this location is not approved for service entrance. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Not_approved.png | file://x:/photopub/docs/0000000361/4152de93-fc78-4eba-9a0d-66b88822f4d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4e67585_cf57_4598_b269_72d1adf52c5f
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Point_of_connection_at_service_pole_to_high.png | file://x:/photopub/docs/0000000362/5071fa70-cc65-4da9-9811-ec5e8622c0b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Water_entering_meter_base_between_copper_conductor_and_insulation_on_the_cable.png | file://x:/photopub/docs/0000000362/c9956b7e-fb2f-4697-a3fe-b25788b25a1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Water_dripping_from_neutral_connection_in_service_panel.png | file://x:/photopub/docs/0000000362/5ab5ce49-098e-4075-808e-1754b7888bc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Bottom_of_meter_base_is_wet.png | file://x:/photopub/docs/0000000362/27dd688b-6469-4133-98cf-12895d8a3b46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_panel_in_shipping_container.png | file://x:/photopub/docs/0000000362/ddcc82d8-5821-492e-8300-3f44ea765734.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Water_dripping_from_service_neutral_conductor_in_the_service_panel.png | file://x:/photopub/docs/0000000362/ea9f74e7-c0f0-4512-bc71-89a14a769fee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Point_of_attachment_above_service_head.png | file://x:/photopub/docs/0000000362/c0605e4e-f3e7-4d21-bc94-89045e2334fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_base.png | file://x:/photopub/docs/0000000362/689bb67a-cdde-4b2d-9aac-8f239d19a748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_base_corroded_and_rusted.png | file://x:/photopub/docs/0000000362/31a36286-8543-408c-adb1-9f5648c798d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-504769-2016 | EL-331422-2016 | 1/6/2016 4:48:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A new 200amp 120/240volt residential house panel is installed in the garage location, to be, without any protective barrier, lock out and weatherproof housing. This can result in weather and/or construction damage to the permanent installation of this panel. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_open_to_the_elements.png | file://x:/photopub/docs/0000000374/0feac889-168f-4f53-bb72-74b0c3fc8d8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32f83696_dcf8_4b3e_8779_b89392daaf0d
GAIN-504832-2016 | GA-279850-2015 | 1/7/2016 11:46:20 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Counterflow Furnace has not been installed to manufacture instructions the return air must be connected to the top opening to allow the residual heat to escape from the fan compartment, long term exposure of heat in fan compartment will cause the electric motor and exposed wiring to overheat and cause a fire inside the fan compartment. | 3 | Appliance not installed according to installation instructions | 5749_245a.png | file://x:/photopub/docs/0000000375/f27780ad-41b6-42e9-91be-c4cd87017360.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__817350a7_231a_4929_8350_7a8929538216
ELIN-485051-2015 | EL-318197-2015 | 11/26/2015 5:42:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Attachment point and service conductors are located within 1 meter of an opening window. This could be hazard if a person was to grab the service conductors. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Part_2.png | file://x:/photopub/docs/0000000358/cc95f86c-6834-40f5-9154-0395abf7364a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21c276f7_f9f2_4431_bba4_a38d5660360f
ELIN-485051-2015 | EL-318197-2015 | 11/26/2015 5:42:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Attachment point and service conductors are located within 1 meter of an opening window. This could be hazard if a person was to grab the service conductors. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Attachment_point_and_service_conductors_located_near_opening_window.png | file://x:/photopub/docs/0000000358/8c626902-4e58-4990-baca-915150738e5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21c276f7_f9f2_4431_bba4_a38d5660360f
GAIN-494524-2015 | GA-322645-2015 | 12/16/2015 9:02:55 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | 1) The relief opening for all regulators shall terminate in a safe area away from building inlets. 2) Regulator relief opening located to close to roof top unit economizer ( mechanical air inlet to building) 3) Flammable natural gas could be drawn undetected into a building or occupied space. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Regulator_and_gasline.png | file://x:/photopub/docs/0000000373/8fd00c41-546e-4131-b9ef-464d52000b4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e759dadb_80fb_4500_87d6_fd051538d540
GAIN-494524-2015 | GA-322645-2015 | 12/16/2015 9:02:55 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | 1) The relief opening for all regulators shall terminate in a safe area away from building inlets. 2) Regulator relief opening located to close to roof top unit economizer ( mechanical air inlet to building) 3) Flammable natural gas could be drawn undetected into a building or occupied space. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Shut-off_.png | file://x:/photopub/docs/0000000373/99878f74-49f0-41ae-9e93-18edb3f74cc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e759dadb_80fb_4500_87d6_fd051538d540
GAIN-494524-2015 | GA-322645-2015 | 12/16/2015 9:02:55 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | 1) The relief opening for all regulators shall terminate in a safe area away from building inlets. 2) Regulator relief opening located to close to roof top unit economizer ( mechanical air inlet to building) 3) Flammable natural gas could be drawn undetected into a building or occupied space. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Mechanical_air.png | file://x:/photopub/docs/0000000373/dd981ec8-74a5-436c-81ca-3672872b91ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e759dadb_80fb_4500_87d6_fd051538d540
GAIN-501129-2015 | GA-319391-2015 | 1/6/2016 1:22:32 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | These tube heaters requires 6' clearance from tubes to any stationary object that can be damaged from the radiant heat, these unit have been left turned off. If left in operation and a stationary object (vehicle on a trailer)is left under the tube heater the radiant heat will burn the roof causing damage and possibly a fire. | 3 | Appliance not installed according to installation instructions | Sky_train_repair_rea.png | file://x:/photopub/docs/0000000374/32f9d65f-1aba-47df-903d-861165b952f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10b5b85d_0f6c_464b_9b91_4d7691bafb8b
GAIN-501129-2015 | GA-319391-2015 | 1/6/2016 1:22:32 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | These tube heaters requires 6' clearance from tubes to any stationary object that can be damaged from the radiant heat, these unit have been left turned off. If left in operation and a stationary object (vehicle on a trailer)is left under the tube heater the radiant heat will burn the roof causing damage and possibly a fire. | 3 | Appliance not installed according to installation instructions | Sky_train_repair_bay.png | file://x:/photopub/docs/0000000374/4cb4caa3-6fd8-4ed6-94fd-d0ec6d1c8c22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10b5b85d_0f6c_464b_9b91_4d7691bafb8b
ELIN-491201-2015 | EL-294924-2015 | 12/17/2015 9:05:44 AM | ASSESS: EL: Final | png | #asFound | EL042 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | 2 | 2 | Energized components subject to water and environmental hazards. Poor accessibility for maintenance. Poor bonding technique | 2 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | LB.png | file://x:/photopub/docs/0000000369/de37fbdc-eaa6-4ff7-8ebd-26000dd8985a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49c4f57c_fd4d_4fb8_bdae_cdb0f595b9a7
ELIN-491201-2015 | EL-294924-2015 | 12/17/2015 9:05:44 AM | ASSESS: EL: Final | png | #asFound | EL042 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | 2 | 2 | Energized components subject to water and environmental hazards. Poor accessibility for maintenance. Poor bonding technique | 2 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | Roof_mounting.png | file://x:/photopub/docs/0000000369/10575040-6680-49c4-a260-b0e9cfd8c576.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49c4f57c_fd4d_4fb8_bdae_cdb0f595b9a7
ELIN-491201-2015 | EL-294924-2015 | 12/17/2015 9:05:44 AM | ASSESS: EL: Final | png | #asFound | EL042 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | 2 | 2 | Energized components subject to water and environmental hazards. Poor accessibility for maintenance. Poor bonding technique | 2 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | Inverter_with_snow_.png | file://x:/photopub/docs/0000000369/5bf99851-dd27-45c9-a345-21208b6c7e96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49c4f57c_fd4d_4fb8_bdae_cdb0f595b9a7
EDOP-478665-2015 | 2167620 | 11/12/2015 9:48:50 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED014 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 3 | 3 | During a regular inspection it was found water pipes passing through the elevator machine room. If these pipes burst the operation of the elevator could be affected in such a manner as to make it unsafe. Water could cause the malfunctioning of hoistway door interlocks allowing an elevator to leave a floor with the hoistway door open. | 3 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | Unit_21329_water-pipes.png | file://x:/photopub/docs/0000000357/dda69b19-2f7a-4658-9e30-d4033c0bc477.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__207e2adc_5683_4d9f_a8ea_7bfa336059a2
ELIN-484651-2015 | EL-305301-2015 | 11/26/2015 7:05:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Maximum opening of hinged wooden weather resistant door does not allow for access to the service panel. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Maximum_opening_of_hinged_door.png | file://x:/photopub/docs/0000000358/71410c52-f5b8-4567-aca1-66d80d610fb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c59116f3_d027_420f_8ac3_95fc688f5333
ELIN-484651-2015 | EL-305301-2015 | 11/26/2015 7:05:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | Maximum opening of hinged wooden weather resistant door does not allow for access to the service panel. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Top_hinged_wooden_enclosure_door_1.png | file://x:/photopub/docs/0000000358/3e2c8760-78a3-4c41-ad95-c65c7bc0a3d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c59116f3_d027_420f_8ac3_95fc688f5333
BPVOP-480405-2015 | 2257389 | 11/24/2015 5:23:55 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found that the instalation date is June 2009 and the replacement of the safety relief valve was not done every 6 years as specified in CSA B-51. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Expired_SRV.png | file://x:/photopub/docs/0000000357/90ed5ada-a0aa-49c8-8819-5622779aa306.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb1a955a_fa57_40ed_8c2c_779faef97c5a
GAIN-481477-2015 | GA-293755-2015 | 12/1/2015 3:48:07 PM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 | A gas connector shall not pass through a partition wall, including the wall of an appliance. The gas appliance connector used for final connection to the fireplace passes through the wall of the fireplace. | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Gas_connector_hose.png | file://x:/photopub/docs/0000000360/ab8d1052-7c79-4c4a-8b45-583c98ea7456.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__003c2b17_91b3_4b0b_97ff_ea68a6e21fff
PROP-419381-2015 | 2224102 | 12/8/2015 11:04:57 PM | ASSESS: PR OP: RAP | png | #asFound | PR015 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | A pair of diagonal braces installed on to the top (return) station are connected to a ground level anchor point by the use of 2 sandwiching link plates with a pair of bolts running through them. These braces connect a structural I beam located at the top front portion of the station to the anchor points at ground level. These link plates are dimensional not identical and therefore are not under the same tensile loading (at one example point the link plate bares no tensile load). This results in the overloading of the higher loaded link plate and an angular loading to the bolts connecting the link plates. It is suspected that this condition has existed for a significant period of time. Maybe from the point of original construction. It is deemed that over the long term, there may be a failure of the link plate components if the condition remain uncorrected. Failure of this component could result in major structural damage to the top station. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Diagonal_bracing_link_plates.png | file://x:/photopub/docs/0000000366/d42108cf-b4f3-4264-ad76-e4e57bc43d8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36FF9FEB_B40B_4FA9_B75A_04643589E262
BPVOP-518186-2016 | 2250767 | 1/28/2016 1:36:17 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP045 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | 4 | 4 | Pressure retaining components must be fit for service and maintain minimal required shell thickness in order to withstand maximum rated working pressure. I found that this pressure retaining component (ammonia carrying line) is not fit for service because of an active general corrosion, which exceeds the allowable amount. Potential exists for an incident due to deteriorated condition of pressure retaining part. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness but component passes fitness for service evaluation | Corrosion_amount_.png | file://x:/photopub/docs/0000000383/1c6422a3-c34c-44c0-a65f-6d2a9c1dd285.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9498f213_b6df_4f7d_9f21_e133efbdde8a
BPVOP-517817-2016 | 2250771 | 1/28/2016 1:36:45 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion_.png | file://x:/photopub/docs/0000000383/861c63fe-bef7-4e9a-96b3-219727c61ffe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8153f2c_a341_43e8_90a8_0c7c5dff0daa
BPVOP-518167-2016 | 2284211 | 1/28/2016 1:36:46 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion___.png | file://x:/photopub/docs/0000000383/84cc68db-dafa-4e26-b927-4baa0d657f15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6365766_b4d8_4e7f_972b_cbab8b46587b
GAIN-491558-2015 | GA-272969-2015 | 1/7/2016 5:18:37 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | At time of inspection found the hot water tank vent, single wall galvanized was a few inches from the plastic water lines, and the basement door rubs and stops against the vent. This can be a hazard as any objects too close to the hot flue pipe could melt or catch fire. | 3 | Non compliant Type C Vent clearance | 1868_.png | file://x:/photopub/docs/0000000375/d1350cd6-372f-4a7a-a0f9-0f81d0e269f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__547ed2cc_fc17_417a_b200_54e43da433d1
GAIN-491558-2015 | GA-272969-2015 | 1/7/2016 5:18:37 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | At time of inspection found the hot water tank vent, single wall galvanized was a few inches from the plastic water lines, and the basement door rubs and stops against the vent. This can be a hazard as any objects too close to the hot flue pipe could melt or catch fire. | 3 | Non compliant Type C Vent clearance | 1868-2.png | file://x:/photopub/docs/0000000375/51090e64-9fed-42bd-8979-e49e8fcfc7bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__547ed2cc_fc17_417a_b200_54e43da433d1
GAIN-472637-2015 | GA-239341-2015 | 11/25/2015 12:03:25 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | range_clearance.png | file://x:/photopub/docs/0000000358/505b63b3-1742-40b9-a751-054c6b990bb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd44ef5_db29_4f89_86d8_fa5898f5a817
GAIN-462028-2015 | GA-297022-2015 | 11/25/2015 12:03:33 PM | ASSESS: GA: Rough-In | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | vent_termination.png | file://x:/photopub/docs/0000000358/37833247-4f99-474e-9707-12687b563c09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9acfb59c_e222_4b58_8503_d3711140a905
GAIN-472637-2015 | GA-239341-2015 | 11/25/2015 12:03:25 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | unprotected_riser.png | file://x:/photopub/docs/0000000358/a242afcd-1e82-48a3-b71d-29dfe2711175.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd44ef5_db29_4f89_86d8_fa5898f5a817
GAIN-472637-2015 | GA-239341-2015 | 11/25/2015 12:03:25 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | vent_term.png | file://x:/photopub/docs/0000000358/cccbac84-4862-4a42-981b-b10d1cde0242.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd44ef5_db29_4f89_86d8_fa5898f5a817
BPVOP-518178-2016 | 2283956 | 1/28/2016 1:36:32 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion__.png | file://x:/photopub/docs/0000000383/eb0fa474-bf12-4c04-b243-4d1c14d04b96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e9005d1_c852_4476_9162_73fb14033bba
ELIN-522321-2016 | UW-342909-2016 | 2/4/2016 10:46:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 2 | Energized electrical panels are required to have fillers or plates installed over all un-used openings. This prevent persons and or conductive materials from making contact with energized parts. During an inspection of work performed without permit, the safety officer identified numerous non-compliances. One of which was an energized 240 volt, 100 amp electrical panel which had missing panel fillers. this presented a shock hazard should a person come into contact with energized parts. In addition, should conductive material come into contact with energized parts this could lead to equipment damage. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Missing_panel_filler.png | file://x:/photopub/docs/0000000387/232edc60-7068-4b22-8643-e5c088c0edb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be74a8e9_e2de_438a_9e95_31b435fee371
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Drawing_of_capacitor_bank_and_distribution.png | file://x:/photopub/docs/0000000379/34c8c549-d6d8-4fac-93a0-92cbb183a800.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-489123-2015 | EL-287049-2015 | 12/4/2015 10:20:48 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | 15A 120V 14/2 NMD exposed and accessible by persons which could pose a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Hoodfan.png | file://x:/photopub/docs/0000000361/e189764f-21ce-4c6e-b96b-c5352c2a002f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdb9df2b_a994_49a4_96f4_6d99bf20cf37
ELOP-296464-2015 | 6278 | 1/6/2016 11:36:18 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Attachment_point_not_connected_to_building.png | file://x:/photopub/docs/0000000373/ec53cc64-0e44-44cf-9622-1185ad4b7fe3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de27f222_2e69_4166_9232_f979b2437130
GAIN-516781-2016 | GA-310462-2015 | 2/6/2016 3:39:41 PM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | At time of inspection found an open gas line to a future generator connection connected to an energized system 10 PSIG at the lodge, and at the lower house. This could create a hazard if someone opens the valve, high pressure propane gas will be released by the building and could catch fire or explode. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | H2.png | file://x:/photopub/docs/0000000388/2053cb8c-b2bb-4077-9ab8-a61e1ca5e61c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65d646b9_69fe_449c_a94c_f3f91a2e0bdd
GAIN-516781-2016 | GA-310462-2015 | 2/6/2016 3:39:41 PM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | At time of inspection found an open gas line to a future generator connection connected to an energized system 10 PSIG at the lodge, and at the lower house. This could create a hazard if someone opens the valve, high pressure propane gas will be released by the building and could catch fire or explode. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | H3.png | file://x:/photopub/docs/0000000388/86aa7f27-1885-49a8-9111-bea3029c1e56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65d646b9_69fe_449c_a94c_f3f91a2e0bdd
GAIN-516781-2016 | GA-310462-2015 | 2/6/2016 3:39:41 PM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | At time of inspection found an open gas line to a future generator connection connected to an energized system 10 PSIG at the lodge, and at the lower house. This could create a hazard if someone opens the valve, high pressure propane gas will be released by the building and could catch fire or explode. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | H1.png | file://x:/photopub/docs/0000000388/ce083cb3-aea2-44f1-8be2-b5d0cd9f5877.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65d646b9_69fe_449c_a94c_f3f91a2e0bdd
BPVOP-524232-2016 | 3984443 | 2/9/2016 1:15:29 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment Hot Water Heating Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that High Temperature Safety Cut-out is set above MAWT. If operating temperature controller fails to shut down boiler when boiler is running, it will operate above MAWT and consequently boiler may fail with likelihood of severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | HIGH_TEMPERATURE_SAFETY_CUTOUT_OF_BOILER.png | file://x:/photopub/docs/0000000388/8c6d79ea-55d2-4b74-b3bc-7b033fd3d0b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2f23752_dc00_433b_b207_8f1914806e08
BPVOP-524242-2016 | 3984444 | 2/9/2016 12:09:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment Hot Water Heating Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that High Temperature Safety Cut-out is set above MAWT. If operating temperature controller fails to shut down boiler when boiler is running, it will operate above MAWT and consequently boiler may fail with likelihood of severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | HIGH_TEMPERATURE_SAFETY_CUTOUT.png | file://x:/photopub/docs/0000000388/4306671c-0815-4297-a2ab-11a318800e40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bfba81e_90af_47a8_bf72_5c93a429da30
BPVOP-524216-2016 | 3984446 | 2/9/2016 11:08:35 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment it is determined that expansion tank design pressure is lower than safety relief valve set pressure of the system. Tank pressure boundary may fail if system pressure exceeds design pressure of expansion tank and can lead to incident. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | NAMEPLATE.png | file://x:/photopub/docs/0000000388/39a42320-73e7-4abd-a40d-611d538de07a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0853a4b_016e_4dae_a60f_d19fb34a0ec1
ELIN-497370-2015 | EL-327354-2015 | 12/23/2015 5:22:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Service ground conductors are required to be undamaged throughout their entire length before terminating at the service equipment. This is required to ensure a solid connection to ground in the even of a fault on the system. This installation of a new 200A, 120/240V service for a house under construction has a ground conductor that is damaged inside the service panel adjacent to where it terminates. This is a potential shock hazard if the ground conductor can not effectively maintain an equipotential on the service equipment in the event of a fault on the system. The service is energized. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Damaged_ground_conductor___.png | file://x:/photopub/docs/0000000370/c0294f33-cb81-4655-8f53-e1e2fba595bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8fc2b4d_e445_41c4_bd14_2643fd591994
ELIN-511032-2016 | EL-220840-2015 | 1/18/2016 6:09:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Receptacles are not provided at minimum intervals along wall lines. This can lead to excessive use of extension cords and lead to potential for property damage or injury to persons. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_receptacle_far_wall.png | file://x:/photopub/docs/0000000379/dc0ba40d-bae1-43f6-8a31-b35f23522fcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a03a0124_b8a0_49c2_94a7_addd59095ae8
ELIN-509205-2016 | EL-302046-2015 | 1/18/2016 6:08:46 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Tamper resistant receptacle not provided for 120 volt 15 amp exterior receptacle on residential garage. Objects can be inserted into non tamper resistant receptacles and can lead to injuries for children and others. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Not_tamper_resistant_on_residential_garage.png | file://x:/photopub/docs/0000000379/2896284b-f4c8-4f1a-bea8-b2702f6740db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8df5f741_a688_496a_9f74_919ea5ed39e2
ELIN-508464-2016 | EL-333610-2016 | 1/14/2016 3:27:23 PM | ASSESS: EL: Service Connection | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Temporary_service.png | file://x:/photopub/docs/0000000378/e8dca3f3-6ea5-443e-a807-dc441f638ca8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f38aad41_73ae_46e3_865f_eed7a72ae55a
BPVOP-508050-2016 | 2303184 | 1/12/2016 6:36:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve (125 psi setting) which was installed on a HW boiler (MAWP 160 psi). Potential danger exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRV_to_be_serviced.png | file://x:/photopub/docs/0000000378/2363a17e-25d4-4834-8873-ddb646147f69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a490771_278c_4486_b7fb_776e8f601ddf
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_head_is_not_sealed_from_exposure_to_weather.png | file://x:/photopub/docs/0000000362/5bd2404a-13d6-473d-afd9-8317edaa5ce0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_pole_and_meter_base_points_of_connection_to_high.png | file://x:/photopub/docs/0000000362/cb81aeb2-7d81-466b-9fea-f8ad38c1f94d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Interior_of_meter_base.png | file://x:/photopub/docs/0000000362/cac84f6c-891d-42eb-a502-c85f2bcdcd4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | service_located_in_shipping_container.png | file://x:/photopub/docs/0000000362/9d34a3fd-aed7-49c5-a2d0-30c641ea24ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Point_of_attachment_for_over_head_service_conductors_is_above_service_head_on_cable_located_on_the_pole.png | file://x:/photopub/docs/0000000362/8991c96e-3b2d-44ce-b2c8-e3639f21860d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-479548-2015 | EL-286630-2015 | 12/4/2015 5:22:28 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm and 300mm below the service head. This installation of over head wiring and service cables on poles has the point of connection for over head wiring above the service heads. This has caused water to enter the neutral conductor and run into the service panel. Left uncorrected the service neutral termination as well as other components inside the service panel will corrode and eventually fail potentially creating a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Water_in_bottom_of_service_panel_.png | file://x:/photopub/docs/0000000362/cb0498f1-2c02-4fc4-a5da-2efd7b197830.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f96b22d_0e95_4a48_8722_f3a0d8fd7aa6
ELIN-489602-2015 | EL-311627-2015 | 12/4/2015 5:22:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Consumer's service heads are required to be above the point of attachment for BC Hydro's service supply conductors. Also service heads must be sealed properly from exposure to weather. This is required to prevent water from entering electrical equipment and damaging components and connections. This existing service installation for a house has the service head located below the point of attachment and the service head is not properly sealed. The result is that over time water has entered the meter base located on a pole. The conductor terminations are corroded and the internal components of the meter base are rusted. Left uncorrected this is a potential fire hazard if the conductor terminations corrode to the point where they become high resistance connections. High resistance connections cause excessive heat and damage to electrical equipment and adjacent combustible materials. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_pole.png | file://x:/photopub/docs/0000000362/8d113976-e69d-43a3-937c-4407d9339d6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4769cbc7_fe09_4a02_b212_53a07d359a73
ELIN-497985-2015 | EL-311384-2015 | 12/23/2015 5:23:40 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the conductors emerge from the service cable. This is required to prevent water from entering the service conductor connections, cable, and service equipment. This installation for a service upgrade to a house has a point of attachment installed a couple inches above the point where conductors emerge from a 200A service cable. Left uncorrected water may enter the cable/conductors and make its way into the meter base. This may cause rust and corrosion at the meter base and conductor terminations which may over time result in high resistance connections and a potential fire hazard. This service is currently energized. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_cable_fastened_to_mast_with_point_of_attachment_above_service_Cable_head.png | file://x:/photopub/docs/0000000370/63dff9df-fd9e-47bf-b5f3-457b59edc9c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdc673ce_9ee3_4b3a_9c0a_d422e6b5cb86
ELIN-497985-2015 | EL-311384-2015 | 12/23/2015 5:23:40 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the conductors emerge from the service cable. This is required to prevent water from entering the service conductor connections, cable, and service equipment. This installation for a service upgrade to a house has a point of attachment installed a couple inches above the point where conductors emerge from a 200A service cable. Left uncorrected water may enter the cable/conductors and make its way into the meter base. This may cause rust and corrosion at the meter base and conductor terminations which may over time result in high resistance connections and a potential fire hazard. This service is currently energized. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Point_of_attachment_above_service_cable_head.png | file://x:/photopub/docs/0000000370/24747e73-3f65-4dc3-9087-472e6488899e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdc673ce_9ee3_4b3a_9c0a_d422e6b5cb86
ELIN-497370-2015 | EL-327354-2015 | 12/23/2015 5:22:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Service ground conductors are required to be undamaged throughout their entire length before terminating at the service equipment. This is required to ensure a solid connection to ground in the even of a fault on the system. This installation of a new 200A, 120/240V service for a house under construction has a ground conductor that is damaged inside the service panel adjacent to where it terminates. This is a potential shock hazard if the ground conductor can not effectively maintain an equipotential on the service equipment in the event of a fault on the system. The service is energized. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Front_of_the_house.png | file://x:/photopub/docs/0000000370/4e24d92c-aa2c-4a4e-874b-70932f2d50b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8fc2b4d_e445_41c4_bd14_2643fd591994
ELIN-497370-2015 | EL-327354-2015 | 12/23/2015 5:22:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Service ground conductors are required to be undamaged throughout their entire length before terminating at the service equipment. This is required to ensure a solid connection to ground in the even of a fault on the system. This installation of a new 200A, 120/240V service for a house under construction has a ground conductor that is damaged inside the service panel adjacent to where it terminates. This is a potential shock hazard if the ground conductor can not effectively maintain an equipotential on the service equipment in the event of a fault on the system. The service is energized. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Service_panel.png | file://x:/photopub/docs/0000000370/f773eb6a-40a3-4b48-945e-555ac4506230.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8fc2b4d_e445_41c4_bd14_2643fd591994
ELIN-497370-2015 | EL-327354-2015 | 12/23/2015 5:22:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Service ground conductors are required to be undamaged throughout their entire length before terminating at the service equipment. This is required to ensure a solid connection to ground in the even of a fault on the system. This installation of a new 200A, 120/240V service for a house under construction has a ground conductor that is damaged inside the service panel adjacent to where it terminates. This is a potential shock hazard if the ground conductor can not effectively maintain an equipotential on the service equipment in the event of a fault on the system. The service is energized. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Damaged_ground_conductor__.png | file://x:/photopub/docs/0000000370/4ee16d3d-a0fe-4e10-ae7f-bcac3cddc295.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8fc2b4d_e445_41c4_bd14_2643fd591994
ELIN-497985-2015 | EL-311384-2015 | 12/23/2015 5:23:40 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the conductors emerge from the service cable. This is required to prevent water from entering the service conductor connections, cable, and service equipment. This installation for a service upgrade to a house has a point of attachment installed a couple inches above the point where conductors emerge from a 200A service cable. Left uncorrected water may enter the cable/conductors and make its way into the meter base. This may cause rust and corrosion at the meter base and conductor terminations which may over time result in high resistance connections and a potential fire hazard. This service is currently energized. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Front_of_house_.png | file://x:/photopub/docs/0000000370/277f3a6a-d8a4-4e7e-9417-18883cc5382a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdc673ce_9ee3_4b3a_9c0a_d422e6b5cb86
ELIN-497382-2015 | EL-327354-2015 | 12/23/2015 5:23:36 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Nmd90_in_contact_with_metal_heating_ducts.png | file://x:/photopub/docs/0000000370/1c63e9ef-a1ce-42aa-8f2e-38014d09dda8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd3dbed3_aba0_467d_999a_2dffe295b96e
ELIN-503905-2016 | EL-330729-2015 | 1/7/2016 8:01:48 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Fire Alarm cables must be protected from potential mechanical injury by using armour or metallic conduit to cover the plastic coated cables. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Typical_initiating_circuit_wiring_exposed_FAScable.png | file://x:/photopub/docs/0000000375/3ad70241-015a-4d8a-b29e-98c5e2edc0d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84e225e8_3e68_48c1_ac61_e101cdbe81cb
ELIN-503905-2016 | EL-330729-2015 | 1/7/2016 8:01:48 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Fire Alarm cables must be protected from potential mechanical injury by using armour or metallic conduit to cover the plastic coated cables. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Initiating_circuit_and_Tel_cable_installation_across_washroom_ceiling.png | file://x:/photopub/docs/0000000375/25e061a5-bc02-41f2-847f-416508b585ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84e225e8_3e68_48c1_ac61_e101cdbe81cb
ELIN-503905-2016 | EL-330729-2015 | 1/7/2016 8:01:48 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Fire Alarm cables must be protected from potential mechanical injury by using armour or metallic conduit to cover the plastic coated cables. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Main_FA_control_panel_and_wiring.png | file://x:/photopub/docs/0000000375/9743f78e-299b-4a99-bd44-d52a54fa6e0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84e225e8_3e68_48c1_ac61_e101cdbe81cb
GAUP-522912-2016 | UW-343266-2016 | 2/4/2016 2:06:01 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | [7 empty] | Snow_Load.png | file://x:/photopub/docs/0000000387/75157b2e-cc19-4545-976b-64bc9f323647.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1cfb8836_815a_488b_8092_e2d0286c8ede
BPVIN-489160-2015 | UW-321030-2015 | 12/4/2015 4:47:39 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP120 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | 5 | 5 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a safety device (Low Water Cut Out on a boiler) not installed. The contractor installed one for all 3 boilers,instead of one for each bolier. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 5 | 3.0.1 Safeties will not function - Safety devices not functional, by-passed or missing with no back up corresponding safety/ operating control device | Only_a_LWCO_for_the_3_boilers_installed.png | file://x:/photopub/docs/0000000362/b5d9c5f2-0ed7-4578-9273-5584726f0149.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8526b8cd_9a07_45e1_9307_cc9f5c8b1fbb
ELIN-509831-2016 | EL-302925-2015 | 1/20/2016 7:08:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | View01_service_raceway.png | file://x:/photopub/docs/0000000381/06d297fb-fd10-4f1b-a285-69aa910b0110.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e5cc9d0_9aa5_4d59_b95b_061671389321
BPVOP-502307-2015 | 2260084 | 1/4/2016 3:39:25 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP115 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | 4 | 3 | Upon assessment of boiler with Allowable Working Pressure (AWP) of 30psig and Allowable Working Temperature (MAWT) of 220*Fahrenheit, I did not find low water fuel cut device (Low water fuel cut out are required to protect boiler from overheating and consequent failure). In the event of low water condition in boiler, tubes will be overheated resulting in failure with likelihood of severe incident. | 4 | 3.0.1 Safeties will not function - Safety Devices bypassed or failed but the back up corresponding safety devices operational | BOILER_WITHOUT_LOW_WATER_FUEL_CUTOUT_DEVICE.png | file://x:/photopub/docs/0000000373/f47f20f5-39c8-457d-a5e9-739a3c9f608e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78ac92bf_4037_4679_ada1_f9c496dc5618
EDIN-514465-2016 | ED-122608-2014 | 1/20/2016 4:24:43 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator was not set properly. The brake torque was set during the installation, but is now believed that the colder temperatures at which the brake torque was set at is causing an incorrect torque reading. At the time of inspection, the brake torque setting was well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 100.9Nm (Newton Meter). The actual brake torque was set at 92Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in ope | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate5.png | file://x:/photopub/docs/0000000383/042f3186-826c-49a8-b1b0-3b7bcc327b8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc0ab1c5_c121_470c_80f8_b8115e02081a
EDIN-514467-2016 | ED-122645-2014 | 1/21/2016 4:24:23 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator was not set properly. The brake torque was set during the installation, but is now believed that the colder temperatures at which the brake torque was set at is causing an incorrect torque reading. At the time of inspection, the brake torque setting was well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 108.1Nm (Newton Meter). The actual brake torque was set at 98Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in ope | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate.png | file://x:/photopub/docs/0000000383/29000a0e-1af3-43a9-907a-9b6a1ae5b650.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f68a81e3_42de_488f_83d5_49cbdbf37971
EDIN-514463-2016 | ED-122629-2014 | 1/19/2016 4:24:01 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator was not set properly. The brake torque was set during the installation, but is now believed that the colder temperatures at which the brake torque was set at is causing an incorrect torque reading. At the time of inspection, the brake torque setting was well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 98Nm (Newton Meter). The actual brake torque was set at 83Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operat | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Br_Data_Plate.png | file://x:/photopub/docs/0000000383/b0acf302-cb51-4181-a677-a168a6d01fde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48cb040f_6e05_4d1f_9251_bfcb99428727
EDIN-514464-2016 | ED-122615-2014 | 1/20/2016 4:24:44 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator was not set properly. The brake torque was set during the installation, but is now believed that the colder temperatures at which the brake torque was set at is causing an incorrect torque reading. At the time of inspection, the brake torque setting was well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 98Nm (Newton Meter). The actual brake torque was set at 83Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operat | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data.png | file://x:/photopub/docs/0000000383/c553fe6a-927f-46bf-944a-33c205696875.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9153d115_fbfd_4c03_927a_f73d748ab7bb
EDIN-514469-2016 | ED-122651-2014 | 1/21/2016 4:24:55 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a break in the safety circuit. During an inspection, it was found that the torque setting of the escalator was not set properly. The brake torque was set during the installation, but is now believed that the colder temperatures at which the brake torque was set at is causing an incorrect torque reading. At the time of inspection, the brake torque setting was well below the minimum brake torque setting listed on the brake data plate. The minimum brake torque setting listed on the brake data plate is 108.1Nm (Newton Meter). The actual brake torque was set at 68Nm. When the escalator is loaded and an emergency stop is activated, the brake would not be able to stop the escalator steps from moving. The escalator steps would travel uncontrolled towards the lower landing. There are no other redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in ope | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate2.png | file://x:/photopub/docs/0000000383/532d3161-532f-4d57-b5b6-49e17c787c50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1b450c5_6c82_4ac9_a6be_73c53de7d75b
BPVOP-481250-2015 | 4272364 | 11/18/2015 4:00:00 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP022 | 1.0.2 Clearances/Maintenance - Insufficient clearance for operation, maintenance and inspection. | 2 | 2 |  | 2 | 1.0.2 Clearances/Maintenance - Insufficient clearance for operation, maintenance and inspection. | Cushion_tank_.png | file://x:/photopub/docs/0000000359/0ff26c5e-291c-418a-ab6f-49e5bded4e14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__045cad3e_02b8_423f_b946_85cb460f57d5
ELIN-489507-2015 | EL-298209-2015 | 12/7/2015 2:46:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Main_panel.png | file://x:/photopub/docs/0000000363/e9592b41-c5de-40db-bc9e-199caa1b974d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db26a4e4_d7c9_4e0e_bec4_fb0bc40683a1
ELIN-506037-2016 | EL-332224-2016 | 1/13/2016 4:41:35 PM | ASSESS: EL: Final | png | #asFound | EL066 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | Overcurrent devices have not been identified to ensure safe operation of branch circuits to energize and de-energize if required. | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Loadcenter_breakers.png | file://x:/photopub/docs/0000000377/0d432eda-3b7d-42fe-bf8f-788e9bc5785b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9b66885_6b0f_4052_99d1_bb68e30ba158
ELIN-512160-2016 | EL-335295-2016 | 1/19/2016 12:45:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 15A 120V outlets provided for temporary construction power are not GFCI protected, which could result in a shock hazard to persons using these outlets or equipment damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temp_outlets.png | file://x:/photopub/docs/0000000379/5ddabcfe-b9e7-49fc-8287-d1d075c495de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14d95dd7_357c_43e8_8d07_d65f3f688b22
BPVOP-484828-2015 | 2276774 | 11/25/2015 10:09:42 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP051 | 1.2.1 Vessell characteristics - Excessive skin temperatures of boilers and vessels that are internally insulated. | 3 | 3 | Boiler casing should be free from cracks,combustion gas, fluid leaks and excessive corrosion. During inspection I found a hole in the back of the boiler caused by localization of heat. This may lead to escaping fluid or gas and improper operation of the firing equipment. | 3 | 1.2.1 Vessell characteristics - Excessive skin temperatures of boilers and vessels that are internally insulated. | Boiler_casing_degradation.png | file://x:/photopub/docs/0000000360/1e2d0cbc-4cdd-4302-852f-8445fa9a76b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__304cfea9_a817_4b3a_91e4_d7383ebb968c
BPVOP-484828-2015 | 2276774 | 11/25/2015 10:09:42 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP051 | 1.2.1 Vessell characteristics - Excessive skin temperatures of boilers and vessels that are internally insulated. | 3 | 3 | Boiler casing should be free from cracks,combustion gas, fluid leaks and excessive corrosion. During inspection I found a hole in the back of the boiler caused by localization of heat. This may lead to escaping fluid or gas and improper operation of the firing equipment. | 3 | 1.2.1 Vessell characteristics - Excessive skin temperatures of boilers and vessels that are internally insulated. | boiler_casing_degradation_2.png | file://x:/photopub/docs/0000000360/29e8393c-44bc-43d8-be16-f457d1a66a7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__304cfea9_a817_4b3a_91e4_d7383ebb968c
BPVOP-484828-2015 | 2276774 | 11/25/2015 10:09:42 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP051 | 1.2.1 Vessell characteristics - Excessive skin temperatures of boilers and vessels that are internally insulated. | 3 | 3 | Boiler casing should be free from cracks,combustion gas, fluid leaks and excessive corrosion. During inspection I found a hole in the back of the boiler caused by localization of heat. This may lead to escaping fluid or gas and improper operation of the firing equipment. | 3 | 1.2.1 Vessell characteristics - Excessive skin temperatures of boilers and vessels that are internally insulated. | boiler_casing_degradation_3.png | file://x:/photopub/docs/0000000360/58530185-e9f8-474f-ac30-e874d9ecb729.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__304cfea9_a817_4b3a_91e4_d7383ebb968c
GAIN-484652-2015 | GA-317933-2015 | 12/1/2015 12:27:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Restraints not installed on pizza oven, repeated moving of appliance will cause undue strain on gas connector causing it to fail. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Fryer_reg.png | file://x:/photopub/docs/0000000360/f3fce305-8bab-45cc-9788-5dbae012ca0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897d33ef_dbf2_41ef_bfee_bdd2be8cb671
GAIN-484652-2015 | GA-317933-2015 | 12/1/2015 12:27:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Restraints not installed on pizza oven, repeated moving of appliance will cause undue strain on gas connector causing it to fail. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Oven_reg.png | file://x:/photopub/docs/0000000360/4a2463de-53fb-496f-86d8-009d972489f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897d33ef_dbf2_41ef_bfee_bdd2be8cb671
GAIN-484652-2015 | GA-317933-2015 | 12/1/2015 12:27:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Restraints not installed on pizza oven, repeated moving of appliance will cause undue strain on gas connector causing it to fail. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Makeup_air.png | file://x:/photopub/docs/0000000360/1e365c93-207d-4634-9837-17e077c42e70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897d33ef_dbf2_41ef_bfee_bdd2be8cb671
GAIN-484652-2015 | GA-317933-2015 | 12/1/2015 12:27:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Restraints not installed on pizza oven, repeated moving of appliance will cause undue strain on gas connector causing it to fail. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Rooftop_reg.png | file://x:/photopub/docs/0000000360/0c7e4ef0-990b-4ed7-9c6e-8a7770df0aa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897d33ef_dbf2_41ef_bfee_bdd2be8cb671
GAIN-484869-2015 | GA-318051-2015 | 12/1/2015 12:27:56 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The regulator vent is installed too close to the appliance combustion air intake. Should the device relieve when the unit is running, gas will be drawn in to unit causing it to over fire or explode. | 2 | Not installed according to certified installation instructions | Reg_vent2.png | file://x:/photopub/docs/0000000360/50aa9725-3aa7-495d-b3c8-ea9d1d03faf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f3fb0c1_b009_42b8_8fa0_246b12c3f1aa
GAIN-484869-2015 | GA-318051-2015 | 12/1/2015 12:27:56 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The regulator vent is installed too close to the appliance combustion air intake. Should the device relieve when the unit is running, gas will be drawn in to unit causing it to over fire or explode. | 2 | Not installed according to certified installation instructions | Reg_vent1.png | file://x:/photopub/docs/0000000360/306c384f-df93-4d00-bc85-1ad9b1060a84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f3fb0c1_b009_42b8_8fa0_246b12c3f1aa
GAIN-484652-2015 | GA-317933-2015 | 12/1/2015 12:27:59 PM | ASSESS: GA: Rough-In | png | #asFound | GA056 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | 3 | 3 | Restraints not installed on pizza oven, repeated moving of appliance will cause undue strain on gas connector causing it to fail. | 3 | Corrugated Stainless Steel Tubing or tubing connected to an appliance not secured in place | Oven_connector.png | file://x:/photopub/docs/0000000360/c12b5f4f-e768-46ec-96fb-d215fe3baacf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__897d33ef_dbf2_41ef_bfee_bdd2be8cb671
GAIN-488239-2015 | GA-278783-2015 | 12/7/2015 3:41:49 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Vent_inspection.png | file://x:/photopub/docs/0000000363/ddc4110d-46b3-4055-a950-7c8695d61e24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6f308ee_a3f0_47f8_b707_3b30c76dea49
BPVOP-502448-2015 | 2293911 | 12/29/2015 8:33:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler heat exchange surfaces should be clear from scale and other deposits that could impede thermal transfer. I found excessive scale and deposits on the water side of the boiler. This can lead to over heating and failure of the boiler tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | LWCO_assembly_.png | file://x:/photopub/docs/0000000372/97891071-bb86-4cab-8d45-92b51a5b3fcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0cbec63_217c_40a4_a4c9_50a142a8f37e
BPVOP-502448-2015 | 2293911 | 12/29/2015 8:33:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler heat exchange surfaces should be clear from scale and other deposits that could impede thermal transfer. I found excessive scale and deposits on the water side of the boiler. This can lead to over heating and failure of the boiler tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | boiler_fire_tube_2.png | file://x:/photopub/docs/0000000372/f86dca32-2e7e-4924-9a19-04929cd38c18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0cbec63_217c_40a4_a4c9_50a142a8f37e
BPVOP-502448-2015 | 2293911 | 12/29/2015 8:33:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Boiler heat exchange surfaces should be clear from scale and other deposits that could impede thermal transfer. I found excessive scale and deposits on the water side of the boiler. This can lead to over heating and failure of the boiler tubes. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | boiler_fire_tube_1.png | file://x:/photopub/docs/0000000372/ef87f9d3-7063-49af-b7ae-4a08a3dfdb85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0cbec63_217c_40a4_a4c9_50a142a8f37e
ELIN-508746-2016 | EL-333686-2016 | 1/19/2016 4:23:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | View01_service_A.png | file://x:/photopub/docs/0000000379/65de9b13-5e34-4297-b4d1-b661a494df9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__320bb59b_72ab_40a3_a548_b8a00f1fa24a
ELIN-490972-2015 | EL-234501-2015 | 1/19/2016 4:23:47 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized branch circuit cabling below deck is not terminated in a device box or using similar approved means to ensure that accidental contact with persons or property is prevented. This could result in serious personal injury (shock) or property damage (thermal event). | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | View01_branch_circuitry.png | file://x:/photopub/docs/0000000379/d7dd668b-544c-4e50-8cda-6f5cc3b58413.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84fa8b74_8805_4ccd_907d_afe3618eee49
ELIN-485061-2015 | EL-316954-2015 | 12/1/2015 7:42:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The ordinary location panel and outlet box is not protected from the weather. This could result in water damage and the breaker not operating as designed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_exposed_to_weather.png | file://x:/photopub/docs/0000000360/595d5de6-671e-4e18-985a-eafcd76edbb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98292ed9_363a_4183_b1ca_e6809fb7e5f9
BPVOP-009039-2013 | 2284107 | 1/5/2016 12:52:32 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP089 | 2.0.1 Control system may overrun - No evidence that manufacturer recommended scheduled maintenance program established for service and testing of Operating controls | 2 | 2 | Controls to be tested in accordance with Manufactures recommendations to ensure that the controls will function in event of an overrun situation. Failure to test controls may result in an incident. | 2 | 2.0.1 Control system may overrun - No evidence that manufacturer recommended scheduled maintenance program established for service and testing of Operating controls | low_water_cut_out_probe_tag.png | file://x:/photopub/docs/0000000376/2df8a3b7-d0e0-438b-bd01-96542a38f606.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BC5C7B8C_679D_4B7B_A44E_5152D2DEAD11
BPVOP-009039-2013 | 2284107 | 1/5/2016 12:52:32 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP089 | 2.0.1 Control system may overrun - No evidence that manufacturer recommended scheduled maintenance program established for service and testing of Operating controls | 2 | 2 | Controls to be tested in accordance with Manufactures recommendations to ensure that the controls will function in event of an overrun situation. Failure to test controls may result in an incident. | 2 | 2.0.1 Control system may overrun - No evidence that manufacturer recommended scheduled maintenance program established for service and testing of Operating controls | Differential_flow_switch.png | file://x:/photopub/docs/0000000376/86bca101-e6aa-46cc-98be-bd57b7e214d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BC5C7B8C_679D_4B7B_A44E_5152D2DEAD11
BPVOP-009039-2013 | 2284107 | 1/5/2016 12:52:32 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP089 | 2.0.1 Control system may overrun - No evidence that manufacturer recommended scheduled maintenance program established for service and testing of Operating controls | 2 | 2 | Controls to be tested in accordance with Manufactures recommendations to ensure that the controls will function in event of an overrun situation. Failure to test controls may result in an incident. | 2 | 2.0.1 Control system may overrun - No evidence that manufacturer recommended scheduled maintenance program established for service and testing of Operating controls | flow_switch_tagged_date.png | file://x:/photopub/docs/0000000376/e038f9af-4c87-4a69-894e-c07788848ea3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__BC5C7B8C_679D_4B7B_A44E_5152D2DEAD11
BPVOP-484818-2015 | 2252646 | 11/23/2015 10:45:16 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 |  | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Non_asme_expansion_tank.png | file://x:/photopub/docs/0000000359/ec848e88-4b29-47fd-97a7-b463ecafa05a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4896fe81_a9e2_4c95_a7f1_d91d5f5aea63
ELIN-512813-2016 | EL-302291-2015 | 1/20/2016 11:24:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 2 | Not enough convenience receptacles which could result in hazardous use of extension cords | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacle_installed__receptacle_installed_while_safety_officer_still_on_site.png | file://x:/photopub/docs/0000000380/fe60074e-21d1-4cc0-a1a2-297666e7c968.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a12e91ad_07e1_4602_8c67_ef8b1fccba88
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damaged_receptacle_____.png | file://x:/photopub/docs/0000000360/da44080b-7658-4480-ad21-1449b4e2cde2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damaged_receptacle___.png | file://x:/photopub/docs/0000000360/11abcd3c-f705-477a-92f2-34bb2153fc54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Living_room_receptacle.png | file://x:/photopub/docs/0000000360/5b0ecafd-4c15-490f-a26a-fd117249a817.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damaged_receptacle_not_approved_for_connection_to_aluminum_wiring.png | file://x:/photopub/docs/0000000360/90a5e57c-bbf6-4b8b-ad3e-577d25d52c5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damaged_receptacle_.png | file://x:/photopub/docs/0000000360/b5c1e909-0ea7-4348-9585-65e65c87fe58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-502560-2015 | EL-328242-2015 | 12/30/2015 11:07:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized parts of electrical equipment are to be located behind barriers to prevent accident contact with persons and conductive material. During a rough wire inspection for a home owner permit, the attending safety officer discovered several 120 volt, 15 amp, energized receptacles and switches hanging off their conductors. This presents a shock hazard to workers and occupants. Note, the permit holder is not a qualified individual and a child was present at time of inspection. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacle_1.png | file://x:/photopub/docs/0000000372/773098cb-65ad-404f-870b-c80340709731.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6c08a34_c781_4a07_94d0_710cddb43a57
ELIN-502560-2015 | EL-328242-2015 | 12/30/2015 11:07:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized parts of electrical equipment are to be located behind barriers to prevent accident contact with persons and conductive material. During a rough wire inspection for a home owner permit, the attending safety officer discovered several 120 volt, 15 amp, energized receptacles and switches hanging off their conductors. This presents a shock hazard to workers and occupants. Note, the permit holder is not a qualified individual and a child was present at time of inspection. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_switch__.png | file://x:/photopub/docs/0000000372/6b128a3e-b5aa-4937-82f0-7a1e6dee5984.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6c08a34_c781_4a07_94d0_710cddb43a57
ELIN-502560-2015 | EL-328242-2015 | 12/30/2015 11:07:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized parts of electrical equipment are to be located behind barriers to prevent accident contact with persons and conductive material. During a rough wire inspection for a home owner permit, the attending safety officer discovered several 120 volt, 15 amp, energized receptacles and switches hanging off their conductors. This presents a shock hazard to workers and occupants. Note, the permit holder is not a qualified individual and a child was present at time of inspection. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacle_.png | file://x:/photopub/docs/0000000372/a2bc1245-9473-481f-b029-0c0c461726f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6c08a34_c781_4a07_94d0_710cddb43a57
ELIN-502560-2015 | EL-328242-2015 | 12/30/2015 11:07:42 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized parts of electrical equipment are to be located behind barriers to prevent accident contact with persons and conductive material. During a rough wire inspection for a home owner permit, the attending safety officer discovered several 120 volt, 15 amp, energized receptacles and switches hanging off their conductors. This presents a shock hazard to workers and occupants. Note, the permit holder is not a qualified individual and a child was present at time of inspection. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_switch_1.png | file://x:/photopub/docs/0000000372/10612c60-3b6c-413f-84c6-687884b95bf9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6c08a34_c781_4a07_94d0_710cddb43a57
PRIN-468798-2015 | PR-292201-2015 | 11/24/2015 2:10:33 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR043 | Safety critical monitoring bypassed or failed in manner not reasonably detectable by maintenance / operation program Lift not in operation | 4 | 4 | The smoke detector in the machine room is not configured to annunciate in the operator's station. This results in a hazard in which a fire in the machine room could go unnoticed by the operator. A worst case scenario for a machine room fire is a condition in which the rope from which passenger carrying units are suspended from overheats and pulls apart. | 4 | Safety critical monitoring bypassed or failed in manner not reasonably detectable by maintenance / operation program Lift not in operation | Smoke_detector_not_linked_to_another_smoke_detector_or_annunciator.png | file://x:/photopub/docs/0000000360/327943bf-9cd7-45fb-bc4e-ea93350d2a4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80a8d320_cc84_4dc5_92d2_82aaf661a9a8
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Living_room_receptacle_.png | file://x:/photopub/docs/0000000360/fb47a25c-ae0e-42f7-a955-d9a3f0799ef3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Front_of_the_house.png | file://x:/photopub/docs/0000000360/aebda78a-ecce-404c-bd22-e51d05054faa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Receptacle_removed_from_outlet_box.png | file://x:/photopub/docs/0000000360/ebdc16af-f3ce-446a-8e91-2b389d1f5514.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damaged_receptacle__.png | file://x:/photopub/docs/0000000360/5ce2bbb5-36f6-4b43-9b25-77af15f485bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-487671-2015 | UW-320027-2015 | 12/2/2015 5:47:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL009 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | 5 | 5 | Electrical equipment and devices including receptacles must be approved for the type of conductors that they are connected to. This is required to ensure that the conductor terminations remain tight and in good contact with the device terminations. This will in most cases prevent high resistance connections that can cause thermal damage to devices, conductor insulation and adjacent combustible materials. This installation has aluminum branch circuit conductors terminated onto a receptacle that is tested and approved for copper conductor terminations only. The connection, receptacle, and conductor insulation are thermally damaged due to the incorrect installation of aluminum conductors onto the receptacle. The circuit is currently de-energized however simply turning the circuit breaker on which is in an accessible area would re-energized the circuit. This is an immediate fire hazard. | 5 | Equipment may not contain thermal energy during fault or overheating event. Equipment is operating at temperatures in excess of their intended rating; and combustible materials are located in an unacceptable location. Evidence of charring, discolouration of combustible materials. | Damaged_receptacle____.png | file://x:/photopub/docs/0000000360/f5f3d943-55ef-4182-9731-2102fb38a041.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0fe4875_87ca_495c_93fe_2f88abc8599b
ELIN-486921-2015 | 4862238 | 12/2/2015 5:47:38 PM | ASSESS: EL: Final | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Branch circuits are connected to circuit breakers to protect them from over current and over load conditions. This wiring installation for a new house has a 15A 120V bedroom receptacle circuit that trips the circuit breaker when it is turned on. This is a potential fire hazard if the non-metallic sheathed cable branch circuit wiring is damaged or incorrectly spliced and attempts are made to turn the breaker on repeatedly without locating and correcting the problem. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Circuit_28_trips_when_th_breaker_is_turned_on.png | file://x:/photopub/docs/0000000360/d40a5937-5997-4dcc-b345-8db9dd282cca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f0bace9_b8ca_4cb9_a6f4_2b74e2cfa2d0
ELIN-503900-2016 | EL-236502-2015 | 1/7/2016 5:04:54 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Outlet boxes are required to have covers on them when wiring is energized to prevent accidental contact, contain thermal energy in the event of a fault, and to protect wiring from mechanical damage. This installation in a new house at the finishing stages of construction has an open thermostat outlet box with energized wiring hanging outside the box. The house is occupied and the wiring is exposed to accidental contact. This is a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_conductor_in_master_bedroom_ensuite_thermostat_outlet_box.png | file://x:/photopub/docs/0000000375/b52abb23-17a5-4d17-89e0-3f7d448a639d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b1fc620_fbc0_46a5_b2a1_1b43eb640800
BPVOP-514689-2016 | UW-337349-2016 | 1/18/2016 11:42:31 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | All pressure vessels shall be protected by pressure relief devices from overpressure occurrences . I found that intervening shut off valves were installed between the relief valve and pressure vessel. This can lead to the pressure relief device being isolated from the vessel its protecting and lead to an overpressure condition. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Relief_device_with_intervening_valve.png | file://x:/photopub/docs/0000000381/7d906244-9796-43d2-9dc7-9cb72cc0d917.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f02286eb_2072_40ad_b156_c63de60b873b
BPVOP-514689-2016 | UW-337349-2016 | 1/18/2016 11:42:31 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | All pressure vessels shall be protected by pressure relief devices from overpressure occurrences . I found that intervening shut off valves were installed between the relief valve and pressure vessel. This can lead to the pressure relief device being isolated from the vessel its protecting and lead to an overpressure condition. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Relief_valve_nameplate.png | file://x:/photopub/docs/0000000381/62848138-d2f0-447d-bc1d-cc9a2593c817.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f02286eb_2072_40ad_b156_c63de60b873b
BPVOP-514689-2016 | UW-337349-2016 | 1/18/2016 11:42:31 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | All pressure vessels shall be protected by pressure relief devices from overpressure occurrences . I found that intervening shut off valves were installed between the relief valve and pressure vessel. This can lead to the pressure relief device being isolated from the vessel its protecting and lead to an overpressure condition. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Pressure_vessel_with_relief_valves.png | file://x:/photopub/docs/0000000381/f14aca78-372b-422e-866a-85a00dea62c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f02286eb_2072_40ad_b156_c63de60b873b
BPVOP-514689-2016 | UW-337349-2016 | 1/18/2016 11:42:31 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | All pressure vessels shall be protected by pressure relief devices from overpressure occurrences . I found that intervening shut off valves were installed between the relief valve and pressure vessel. This can lead to the pressure relief device being isolated from the vessel its protecting and lead to an overpressure condition. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Relief_device2_intervening_valve.png | file://x:/photopub/docs/0000000381/c303459e-64b9-4b3c-84b1-427d8b15d655.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f02286eb_2072_40ad_b156_c63de60b873b
ELIN-522336-2016 | EL-309061-2015 | 2/9/2016 8:52:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt panel does is not effectively protected from weather conditions and is not rated of the use. This can lead to equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_installation_.png | file://x:/photopub/docs/0000000389/35049b01-9ec8-4530-b978-35eb7cde7c4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9687df7_aa77_4592_ba28_a952b57a1b58
ELIN-444327-2015 | EL-072558-2013 | 12/29/2015 1:55:09 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 4 | The conductors enter a heating unit with fan through an opening with sharp metal edges without mechanical conduit/nipple protection, this creates a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Heating_unit_nameplate.png | file://x:/photopub/docs/0000000371/e968e22e-0ed4-4fba-a0fb-173d6e7b507d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c68bf046_3081_44b2_92fd_6eac2a7dfe5b
ELIN-444327-2015 | EL-072558-2013 | 12/29/2015 1:55:09 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 4 | The conductors enter a heating unit with fan through an opening with sharp metal edges without mechanical conduit/nipple protection, this creates a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Heating_unit_disconnect.png | file://x:/photopub/docs/0000000371/f0c50010-1aeb-4b94-8c8d-fc4501b69e4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c68bf046_3081_44b2_92fd_6eac2a7dfe5b
ELIN-503900-2016 | EL-236502-2015 | 1/7/2016 5:04:54 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Outlet boxes are required to have covers on them when wiring is energized to prevent accidental contact, contain thermal energy in the event of a fault, and to protect wiring from mechanical damage. This installation in a new house at the finishing stages of construction has an open thermostat outlet box with energized wiring hanging outside the box. The house is occupied and the wiring is exposed to accidental contact. This is a potential shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Front_of_house__.png | file://x:/photopub/docs/0000000375/c91817bb-027c-4a6c-819e-416e8b80b8ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b1fc620_fbc0_46a5_b2a1_1b43eb640800
BPVOP-514689-2016 | UW-337349-2016 | 1/18/2016 11:42:31 AM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | All pressure vessels shall be protected by pressure relief devices from overpressure occurrences . I found that intervening shut off valves were installed between the relief valve and pressure vessel. This can lead to the pressure relief device being isolated from the vessel its protecting and lead to an overpressure condition. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Relief__valve_nameplate_2.png | file://x:/photopub/docs/0000000381/f2d061b1-3025-4b4a-ab82-6b1dfe541c79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f02286eb_2072_40ad_b156_c63de60b873b
ELIN-490007-2015 | EL-312844-2015 | 12/7/2015 7:07:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 120/240 volt 200 amp indoor rated panel installed in a outdoor environment. This may result in equipment damage from outdoor elements. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | service_equipment_not_installed_in_weatherproof_enclosure.png | file://x:/photopub/docs/0000000363/1291eaa0-e0db-40a1-9afc-1066738a18c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0195548_9beb_46a9_a13c_396c83699c96
ELIN-521295-2016 | EL-333902-2016 | 2/3/2016 3:33:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200A 120/240V Main Panel has not been provided with proper weatherproof protection, this could result in equipment damage, failure of equipment, and shock hazard to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_Panel.png | file://x:/photopub/docs/0000000386/b723e81f-bba3-4d1e-bd8c-b7fb284f106e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75dee61d_e582_4432_bdb3_a6e7ae40c91f
ELIN-501085-2015 | EL-322362-2015 | 1/7/2016 8:09:56 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | The 200A, 120/240V residential panel does not have the cover installed exposing live parts. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_distribution_panel_.png | file://x:/photopub/docs/0000000375/ee125c94-248a-4309-87e1-0d5ee33fe58e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4e10926_e9ce_424e_815c_b08124e382f1
BPVOP-009038-2013 | 2284108 | 1/5/2016 3:16:37 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | This is a Third Class Plant as defined in the Power Engineers, Boilers, Pressure Vessel and Refrigeration Safety Regulations. A Chief Power Engineer must be appointed with a Third Class Power Engineering Certificate in order to ensure that the hazards associated with operating this Third Class Plant are controlled. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | high_temperature_shut_down_set_point.png | file://x:/photopub/docs/0000000379/43365f9a-ebfb-47af-8374-3be4bfbdd8a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5FA47C5F_81A2_41CE_956A_87D780D1073C
BPVOP-009038-2013 | 2284108 | 1/5/2016 3:16:37 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | This is a Third Class Plant as defined in the Power Engineers, Boilers, Pressure Vessel and Refrigeration Safety Regulations. A Chief Power Engineer must be appointed with a Third Class Power Engineering Certificate in order to ensure that the hazards associated with operating this Third Class Plant are controlled. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | operating_and_high_temp_controls.png | file://x:/photopub/docs/0000000379/8d4ccb5b-10d9-4f4c-9624-4b3f40e6f7cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5FA47C5F_81A2_41CE_956A_87D780D1073C
BPVOP-009038-2013 | 2284108 | 1/5/2016 3:16:37 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | This is a Third Class Plant as defined in the Power Engineers, Boilers, Pressure Vessel and Refrigeration Safety Regulations. A Chief Power Engineer must be appointed with a Third Class Power Engineering Certificate in order to ensure that the hazards associated with operating this Third Class Plant are controlled. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | Differential_flow_switch_tagged_May_1991.png | file://x:/photopub/docs/0000000379/2377f459-ac13-4d0b-9f56-ec73d57ca8b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5FA47C5F_81A2_41CE_956A_87D780D1073C
BPVOP-009038-2013 | 2284108 | 1/5/2016 3:16:37 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | This is a Third Class Plant as defined in the Power Engineers, Boilers, Pressure Vessel and Refrigeration Safety Regulations. A Chief Power Engineer must be appointed with a Third Class Power Engineering Certificate in order to ensure that the hazards associated with operating this Third Class Plant are controlled. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | LWCO_probe_and_dated_decal.png | file://x:/photopub/docs/0000000379/fef33e5b-2623-4b1e-b3ba-d4d592b7186f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5FA47C5F_81A2_41CE_956A_87D780D1073C
BPVOP-009038-2013 | 2284108 | 1/5/2016 3:16:37 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | This is a Third Class Plant as defined in the Power Engineers, Boilers, Pressure Vessel and Refrigeration Safety Regulations. A Chief Power Engineer must be appointed with a Third Class Power Engineering Certificate in order to ensure that the hazards associated with operating this Third Class Plant are controlled. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | operating_temp_control_decal_reading_10_deg__higher_than_set_point.png | file://x:/photopub/docs/0000000379/b7738330-fd4f-4824-937c-afa75bc1b8ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5FA47C5F_81A2_41CE_956A_87D780D1073C
ELIN-491632-2015 | EL-308939-2015 | 12/8/2015 8:26:06 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Staples_not_correct_size_or_for_cables_or_approved_for_the_use.png | file://x:/photopub/docs/0000000365/35a82353-5cac-40b2-b82b-75d125633057.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c8b35ea_5b80_4ec0_90c9_c633ae8fb75f
ELIN-509252-2016 | EL-332146-2016 | 1/14/2016 4:31:02 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | During an inspection of a 240 volt, 100amp, temporary construction service, the attending safety officer discovered that the service neutral was not grounded at the service box. The service was energized prior to requesting an inspection. In addition, the FSR who requested the inspection disclosed that he did not check the work prior to requesting the inspection or submitting a request to connect to BC Hydro. The neutral is required to be connecting to ground at the service box. This is to ensure the voltage does not exceed 120 volts to ground in this three wire system. Failure to ground the neutral could result in equipment damage and a possible shock hazard. The safety officer ordered BC Hydro to disconnect this service. | 4 | Installation Grounding; conductor is not continuous. | Interior_of_main_disconnect_switch.png | file://x:/photopub/docs/0000000378/7cdb878c-3078-44d2-955f-4a14fa6d2216.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f36664d6_c063_4890_b78e_87379a54268f
ELIN-523180-2016 | EL-340044-2016 | 2/10/2016 9:46:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Transition to a LB Required on utility supply side, proper top entry meterbase is available. Ground for this new service is connected to old service ground | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_drop_at_186_drake.png | file://x:/photopub/docs/0000000390/cd361efd-87c6-4c32-b36f-e64e89b0daad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51f2125b_0d49_41f5_804f_d26ee9901312
ELIN-523180-2016 | EL-340044-2016 | 2/10/2016 9:46:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Transition to a LB Required on utility supply side, proper top entry meterbase is available. Ground for this new service is connected to old service ground | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 186_drake_mast__one_u_bolt_installed__3_in_total_required.png | file://x:/photopub/docs/0000000390/6a128f78-03f5-42ec-8ce0-b069af2fe56d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51f2125b_0d49_41f5_804f_d26ee9901312
ELIN-493181-2015 | UW-323909-2015 | 12/9/2015 7:50:20 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Branch circuits for receptacles are required to be the right type, size, and must contain the correct amount of conductors for the circuit to operate correctly and safely. This installation had a branch circuit for a 40 amp, 120/240 volt rated range receptacle in a secondary suite located in the basement of a house. The branch circuit consisted of a cable that was a flexible cord with three #10 awg copper conductors. The three conductors were used for the two line conductors and the neutral conductor connected to the receptacle. The circuit did not contain a bonding conductor. Left uncorrected with out a bonding conductor/connection this was a potential shock and fire hazard in the event of a fault or overload on the receptacle or branch circuit. | 3 | Continuity Bonding conductor is not observed or broken | Flexible_cord_used_as_branch_circuit_wiring_to_a_secondary_suite_range.png | file://x:/photopub/docs/0000000364/4efdf10a-0d28-4179-9c76-96989fba8a81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__986d4c33_7e6f_4ca9_9d0f_09ed23634317
ELIN-481857-2015 | EL-239551-2015 | 12/9/2015 7:30:07 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | 120/240 volt 100 amp over head service conductors have been attached above the service head. This could allow the migration of water into the service equipment. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_conductor_attachment_point_installed_above_service_head.png | file://x:/photopub/docs/0000000365/02acb4be-a3c6-4dd4-a1fe-ae0b729ad9eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e36e386_da04_446b_b651_eb40b8dd5917
ELIN-492048-2015 | EL-302234-2015 | 12/9/2015 7:30:40 AM | ASSESS: EL: Final | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 120/240 volt 200 amp panel board has service conductors extended past service conductor enclosure. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Service_bond_conductor_extends_past_service_conductor_enclosure.png | file://x:/photopub/docs/0000000365/5b3a3609-0aa1-4747-a536-94ddd81147c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4c20f20_a210_4108_a404_446b0aa8b670
ELIN-505272-2016 | EL-323394-2015 | 1/7/2016 7:36:25 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | A receptacle is required at the location of the gas pipe. This assessment found the receptacle to be missing. There is a hazard that an unqualified person would attempt to wire the gas stove after the fact, if the receptacle is not provided, or involve the use of extension cords. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Wiring_covered.png | file://x:/photopub/docs/0000000375/6e7df87c-3206-4a98-817a-92bdb1fe8301.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afcf28d9_8b27_445f_8865_0c0ecd6ad847
ELIN-505272-2016 | EL-323394-2015 | 1/7/2016 7:36:25 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | A receptacle is required at the location of the gas pipe. This assessment found the receptacle to be missing. There is a hazard that an unqualified person would attempt to wire the gas stove after the fact, if the receptacle is not provided, or involve the use of extension cords. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Gas_receptacle.png | file://x:/photopub/docs/0000000375/d55da139-73dc-480f-a1b1-646cdfd2b6a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afcf28d9_8b27_445f_8865_0c0ecd6ad847
ELIN-495579-2015 | UW-326034-2015 | 12/14/2015 7:54:54 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Main service breaker was replaced by a contractor, contractor amp probed the main service conductors and found them to be loaded to 95% of the main service breaker. The main service breaker is rated for continuous duty at 80% percent. If main service breaker is overloaded past its limit of 80% then it could cause a possible fire hazard/shock/property damage due to the main service breaker failing and BC Hydro's practice of over fusing. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Main_breaker.png | file://x:/photopub/docs/0000000366/0c53e62e-8f89-48a6-8889-b36812f99482.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76eaa659_b722_4c5e_96ef_9acaf4f96a48
ELIN-487893-2015 | EL-284294-2015 | 12/8/2015 7:03:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 2 | Homeowner requested service connection with panel covers not installed. If connected in this state, a shock hazard would result from the exposed energized buss in the panel. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service_cable_sheath_not_stripped_for_bonding_.png | file://x:/photopub/docs/0000000365/bc66b400-aed0-46e6-9cd0-a8722a7f5b3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be69e373_f7f1_4590_84cf_ab60b46ee7c0
ELIN-487893-2015 | EL-284294-2015 | 12/8/2015 7:03:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 2 | Homeowner requested service connection with panel covers not installed. If connected in this state, a shock hazard would result from the exposed energized buss in the panel. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_covers_not_installed_.png | file://x:/photopub/docs/0000000365/41b548fb-9e4d-4bfe-be18-ce988a32925f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be69e373_f7f1_4590_84cf_ab60b46ee7c0
ELOP-329692-2015 | 6388 | 1/8/2016 6:14:37 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 3 | Pot light 120 volt , low voltage lamp and ballast. LED lamp, In a locked area perched on a wall after what appears to be a ceiling removal. | 4 | Installation of electrical equipment Fixtures without suitable support. | QF_comox_-1.png | file://x:/photopub/docs/0000000376/48ddb633-e6a2-4a15-8261-38413a3f292b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33a0513e_4551_42f1_a980_be0e3743a0c6
ELOP-329692-2015 | 6388 | 1/8/2016 6:14:37 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 3 | Pot light 120 volt , low voltage lamp and ballast. LED lamp, In a locked area perched on a wall after what appears to be a ceiling removal. | 4 | Installation of electrical equipment Fixtures without suitable support. | QF_comox-5.png | file://x:/photopub/docs/0000000376/7f575471-b0e8-4fe6-9f53-a52b79d28846.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33a0513e_4551_42f1_a980_be0e3743a0c6
ELOP-329692-2015 | 6388 | 1/8/2016 6:14:37 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 3 | Pot light 120 volt , low voltage lamp and ballast. LED lamp, In a locked area perched on a wall after what appears to be a ceiling removal. | 4 | Installation of electrical equipment Fixtures without suitable support. | QF_comox-4.png | file://x:/photopub/docs/0000000376/063380e2-5e21-44b2-ab06-0d754a6600b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33a0513e_4551_42f1_a980_be0e3743a0c6
ELIN-505506-2016 | UW-331871-2016 | 1/6/2016 2:35:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Conductors and devices, not installed or supported correctly and exposed to mechanical damage, are energized at time of inspection. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Energized_receptacle_curcuits_not_installed_correctly.png | file://x:/photopub/docs/0000000374/9311e961-9567-4d65-a23d-5939e7c19bdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55342f5a_cf34_406c_8013_3e1700ca07d0
ELIN-505506-2016 | UW-331871-2016 | 1/6/2016 2:35:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Conductors and devices, not installed or supported correctly and exposed to mechanical damage, are energized at time of inspection. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Energized__switch_circuits_not_installed_correctly.png | file://x:/photopub/docs/0000000374/ffea6670-e20e-4467-a345-939dff3b1f61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55342f5a_cf34_406c_8013_3e1700ca07d0
ELIN-505506-2016 | UW-331871-2016 | 1/6/2016 2:35:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Conductors and devices, not installed or supported correctly and exposed to mechanical damage, are energized at time of inspection. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Energized_circuits_not_installed_correctly.png | file://x:/photopub/docs/0000000374/60d6d81d-d933-48d8-b903-0a8fe608214d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55342f5a_cf34_406c_8013_3e1700ca07d0
ELIN-505506-2016 | UW-331871-2016 | 1/6/2016 2:35:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Conductors and devices, not installed or supported correctly and exposed to mechanical damage, are energized at time of inspection. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Circuits_red_tagged_off_main_panel.png | file://x:/photopub/docs/0000000374/c240702d-6ada-4df5-a9c9-44011a8c9236.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55342f5a_cf34_406c_8013_3e1700ca07d0
ELIN-505506-2016 | UW-331871-2016 | 1/6/2016 2:35:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Conductors and devices, not installed or supported correctly and exposed to mechanical damage, are energized at time of inspection. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Circuits_red_tagged_off.png | file://x:/photopub/docs/0000000374/ce907551-5540-4368-a991-5fc9371a32b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55342f5a_cf34_406c_8013_3e1700ca07d0
ELIN-505506-2016 | UW-331871-2016 | 1/6/2016 2:35:19 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Conductors and devices, not installed or supported correctly and exposed to mechanical damage, are energized at time of inspection. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Energized_wiring_in_ceilings_not_installed_correctly.png | file://x:/photopub/docs/0000000374/d1cb7a7f-2528-4940-82d2-535831f9d20a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55342f5a_cf34_406c_8013_3e1700ca07d0
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_lighting_and_junction_box_in_suite.png | file://x:/photopub/docs/0000000390/b4ecd481-9bc2-48fc-9f35-89a9f07c8b3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Three_gang_switch_cover_missing_.png | file://x:/photopub/docs/0000000390/7dafb02f-2c3a-49ee-9f1f-d05da05b77d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_splice_on_cable_conductors_in_master_bedroom_ceiling_valence.png | file://x:/photopub/docs/0000000390/28dd954d-e314-46f7-98a2-8bcda9da2031.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_box_in_suite_kitchen_cabinet_.png | file://x:/photopub/docs/0000000390/7561428b-b1b4-47ad-9d3c-29b43cbf4b1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_wall_mounted_lighting_boxes_in_master_bedroom.png | file://x:/photopub/docs/0000000390/e1cee14c-48e2-47ed-b458-92cc2d3a89f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_box_in_suite_kitchen_cabinet.png | file://x:/photopub/docs/0000000390/eb1d6c52-638f-42da-a262-8cfb4bc03db8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELIN-525742-2016 | UW-344832-2016 | 2/12/2016 12:41:09 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Lighting boxes, junction boxes, switch and receptacle boxes are required to have covers plates or luminaire canopies on them. Cable and conductor splices are required to be contained in boxes with covers. This is required to prevent accidental contact with live conductors and terminals, to prevent damage to wiring and equipment, and to contain thermal energy in the event of a fault or overload on the circuit. This installation in an existing house contains multiple lighting, switch, and junction boxes on 15A, 120V branch circuits that do not have cover plates or luminaire canopies on them. An open cable/conductor splice was also observed. The power to the service was turned off at the time of inspection after a fire but was previously energized and will be energized again. This is a potential shock and fire hazard if wiring or energized parts are contacted, damaged, or if there is a fault or overload on the circuit. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_ceiling_lighting_box_in_suite.png | file://x:/photopub/docs/0000000390/1d21cfe4-f0f8-4e4a-a454-2fbf7fc14f9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0999139f_bd95_47bf_b258_dae8d46f61af
ELOP-453705-2015 | 5376383 | 2/12/2016 12:45:43 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | Electrical equipment. Use be kept in safe working order. In this RV park a few receptacles require replacement and a cable has been installed outdoors where it is not approved for use. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Maintenance_still_required.png | file://x:/photopub/docs/0000000390/c0855d2e-98c9-416e-9889-32bbebd26b31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da89bf71_97ed_4a02_9279_89e930831bd2
ELOP-453761-2015 | 5376382 | 2/12/2016 1:00:05 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | Electrical equipment must be kept in safe working order. In this RV park some receptacles require replacement and a cable has been installed outdoors where it is not approved for use. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Fix_me.png | file://x:/photopub/docs/0000000390/657fd812-2ef0-4676-921a-0aa61f678685.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25a1588f_e49c_4648_ab6d_791514bf7d4b
ELOP-226536-2014 | 5376382 | 2/12/2016 12:39:24 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | Electrical equipment must be kept in safe working order. In this RV park installation a few receptacles require attention, and there is evidence of conductors used outdoors where they are not approved for use. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Maintenance_required.png | file://x:/photopub/docs/0000000390/844ea4c3-ad40-4b45-9e35-84986acc177e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52912f9e_6239_459f_8089_ae89278cab76
ELIN-496511-2015 | EL-249255-2015 | 12/29/2015 4:29:50 AM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 2 | See photo | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 2145_Mckenzie-2.png | file://x:/photopub/docs/0000000372/6dc7379e-3f29-4cbd-9538-43c8aa9773f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39aacc66_9582_40bd_a0ae_f235d8df0916
ELIN-496511-2015 | EL-249255-2015 | 12/29/2015 4:29:50 AM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 2 | See photo | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 2145_mckenzie-1.png | file://x:/photopub/docs/0000000372/92a63206-462e-4f89-87d2-40aae9957ff8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39aacc66_9582_40bd_a0ae_f235d8df0916
ELIN-501000-2015 | EL-317948-2015 | 12/30/2015 11:13:56 AM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | 100A service fed with a #4 awg Teck cable. This is a fire hazard as the cable is only rated for 85 amps. Overloading a cable can result in damage to the insulation from excessive heating. Damage and fire can also occur as the under sized cable will cause hot spots where it terminates to the panel. This is because panels have a temperature rating of 75 degrees c, this means that cables have to be sized to limit the max temperature of the cable to 75 degrees c. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | A.png | file://x:/photopub/docs/0000000372/05432d92-b0c9-4a69-a02b-ecf9e482e3aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5499850f_8ab5_44c4_8a56_0139786b1a85
ELIN-504261-2016 | EL-207348-2015 | 1/5/2016 1:24:13 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Construction cables being used as a extension cable without bonding. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | cable.png | file://x:/photopub/docs/0000000374/3cd846a3-e32e-4589-9fb9-77f2308ecb03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71635b57_2cff_49f5_afb5_1cb6929849da
ELOP-329692-2015 | 6388 | 1/8/2016 6:14:37 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 3 | Pot light 120 volt , low voltage lamp and ballast. LED lamp, In a locked area perched on a wall after what appears to be a ceiling removal. | 4 | Installation of electrical equipment Fixtures without suitable support. | QF_comox-2.png | file://x:/photopub/docs/0000000376/3cd7fdf0-3772-4431-9466-7115f06a5bfb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33a0513e_4551_42f1_a980_be0e3743a0c6
ELOP-329692-2015 | 6388 | 1/8/2016 6:14:37 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 3 | Pot light 120 volt , low voltage lamp and ballast. LED lamp, In a locked area perched on a wall after what appears to be a ceiling removal. | 4 | Installation of electrical equipment Fixtures without suitable support. | QF_comox-3.png | file://x:/photopub/docs/0000000376/69a9cc04-03cf-4eec-97fe-c02555937d94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33a0513e_4551_42f1_a980_be0e3743a0c6
ELOP-471981-2015 | EL-308727-2015 | 1/8/2016 6:14:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | ""Live unguarded conductor in janitors room. " The cable was 3' from floor level and had Marr wire caps on energized, conductor. There was a high risk for shock hazard or accidently energizing portable equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 1475_noel-3.png | file://x:/photopub/docs/0000000376/195bcfc8-fa90-40ed-9e9c-b302f1dcc10d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f2a100_f81a_4600_a21d_b4ab552f3987
ELOP-471981-2015 | EL-308727-2015 | 1/8/2016 6:14:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | ""Live unguarded conductor in janitors room. " The cable was 3' from floor level and had Marr wire caps on energized, conductor. There was a high risk for shock hazard or accidently energizing portable equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 1475_noel-1.png | file://x:/photopub/docs/0000000376/e1a1d64f-7d12-4569-a053-92433b186c5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f2a100_f81a_4600_a21d_b4ab552f3987
ELOP-471981-2015 | EL-308727-2015 | 1/8/2016 6:14:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | ""Live unguarded conductor in janitors room. " The cable was 3' from floor level and had Marr wire caps on energized, conductor. There was a high risk for shock hazard or accidently energizing portable equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 1475_noel-2.png | file://x:/photopub/docs/0000000376/13785186-45b7-49ad-8b7d-229a9f08cc20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c1f2a100_f81a_4600_a21d_b4ab552f3987
BPVOP-486731-2015 | 4025878 | 11/30/2015 8:56:53 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | All flammable s and combustibles materials should be properly stored. Found combustibles(wood 2x4's) below the hot water boiler and red nylon strap holding the controls cables left after a repair. This could result in a boiler room fire. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | nylon_strap_holding_cables_above_boiler.png | file://x:/photopub/docs/0000000360/d8a9e81c-cbe7-49b7-89be-464cc018dcda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af3114e2_0ff5_4265_a782_16bc2f646e34
BPVOP-486731-2015 | 4025878 | 11/30/2015 8:56:53 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | All flammable s and combustibles materials should be properly stored. Found combustibles(wood 2x4's) below the hot water boiler and red nylon strap holding the controls cables left after a repair. This could result in a boiler room fire. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | wood_below_boiler.png | file://x:/photopub/docs/0000000360/da34d54c-5454-426d-a680-326b7475263d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af3114e2_0ff5_4265_a782_16bc2f646e34
GAIN-464049-2015 | GA-285237-2015 | 12/10/2015 11:31:40 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Unapproved common venting of instant hot water boilers, plastic pipe connected to stainless steel header, tape used to connect plastic pipe to header,vent leaking condensate, instant hot water tanks commonly have 400 ppm of carbon monoxide each, vent pipe and common header is not sealed and will allow carbon monoxide to enter room causing possible sickness and or death if enough buildup occurs inside room | 3 | Unapproved venting material | 3711_2_salmon.png | file://x:/photopub/docs/0000000365/695cea81-cee7-4204-bad3-d1b49ae76c6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ee6c4f3_c146_4c4f_b23a_6a15af037970
GAIN-464049-2015 | GA-285237-2015 | 12/10/2015 11:31:40 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Unapproved common venting of instant hot water boilers, plastic pipe connected to stainless steel header, tape used to connect plastic pipe to header,vent leaking condensate, instant hot water tanks commonly have 400 ppm of carbon monoxide each, vent pipe and common header is not sealed and will allow carbon monoxide to enter room causing possible sickness and or death if enough buildup occurs inside room | 3 | Unapproved venting material | 3711_salmon.png | file://x:/photopub/docs/0000000365/4f42d3b4-a333-4b09-b613-3e952ab1464a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ee6c4f3_c146_4c4f_b23a_6a15af037970
ELIN-510719-2016 | EL-276546-2015 | 1/20/2016 3:44:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The ground conductor is incorrectly terminated in meterbase. This could result in a high resistance fault path resulting in a voltage rise on the metal parts during a fault. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | RV_service.png | file://x:/photopub/docs/0000000380/219d3948-0881-4c7a-998d-e8303d1422f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43419e4e_88c6_41b4_9a77_33fb84a6f806
ELIN-512544-2016 | EL-324635-2015 | 1/26/2016 8:23:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In the roof line there are 5 pot lights that are not insulated, the owner intends to use LED type lamps but the fixture has a rating for a 75 watt par type lamp that could potentially cause a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Charelton-3.png | file://x:/photopub/docs/0000000383/21e5d176-868c-4625-afa1-995d65d0b010.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d965c1_e982_4174_ad03_3cb1cc28bae0
ELIN-512544-2016 | EL-324635-2015 | 1/26/2016 8:23:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In the roof line there are 5 pot lights that are not insulated, the owner intends to use LED type lamps but the fixture has a rating for a 75 watt par type lamp that could potentially cause a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Charelton-1.png | file://x:/photopub/docs/0000000383/d3d1a0fd-2086-49e5-8c91-55562ba7bb50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d965c1_e982_4174_ad03_3cb1cc28bae0
ELIN-512544-2016 | EL-324635-2015 | 1/26/2016 8:23:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In the roof line there are 5 pot lights that are not insulated, the owner intends to use LED type lamps but the fixture has a rating for a 75 watt par type lamp that could potentially cause a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Charelton-2.png | file://x:/photopub/docs/0000000383/a7a3e81d-0ac6-44bb-b889-ba942f27653d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d965c1_e982_4174_ad03_3cb1cc28bae0
ELIN-512544-2016 | EL-324635-2015 | 1/26/2016 8:23:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In the roof line there are 5 pot lights that are not insulated, the owner intends to use LED type lamps but the fixture has a rating for a 75 watt par type lamp that could potentially cause a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Charelton-4.png | file://x:/photopub/docs/0000000383/6ae83420-1f0f-448e-b7e3-1d15a32e2b28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d965c1_e982_4174_ad03_3cb1cc28bae0
ELIN-512544-2016 | EL-324635-2015 | 1/26/2016 8:23:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In the roof line there are 5 pot lights that are not insulated, the owner intends to use LED type lamps but the fixture has a rating for a 75 watt par type lamp that could potentially cause a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Charelton-5.png | file://x:/photopub/docs/0000000383/4c649786-2689-4e69-ae8d-77c8a734652f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d965c1_e982_4174_ad03_3cb1cc28bae0
ELIN-512544-2016 | EL-324635-2015 | 1/26/2016 8:23:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In the roof line there are 5 pot lights that are not insulated, the owner intends to use LED type lamps but the fixture has a rating for a 75 watt par type lamp that could potentially cause a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Charleston-6.png | file://x:/photopub/docs/0000000383/77e45067-55b6-48e9-bc1a-736b30f19daa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0d965c1_e982_4174_ad03_3cb1cc28bae0
BPVOP-516624-2016 | 4881033 | 1/26/2016 8:43:48 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Found a machine mounted vertical air receiver (1.5m long and .51m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure-boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | SAFETY_VALVE_EXCEEDED_SERVICING__INTERVAL.png | file://x:/photopub/docs/0000000383/781ef230-128c-4293-9e75-09d665477951.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3281cd1a_71d4_43a9_9a32_dacecf589ce9
BPVOP-516644-2016 | 4881041 | 1/26/2016 8:43:36 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 2 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 240*Fahrenheit, it is determined that there is no pressure or altitude gauge on the boiler. There is no way to detect and take subsequent corrective action in the event of pressure rise above operating range or even MAWP, caused by malfunction of controls , which may lead to incident | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | HWH_BOILER_1.png | file://x:/photopub/docs/0000000383/480e3692-f87e-4253-859f-b7f8aac22a34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35d4a5b0_c58e_4597_8403_0adb9dc7e54f
BPVOP-516649-2016 | 4881040 | 1/26/2016 8:43:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment of hot water boiler with Allowable Working Pressure (AWP) of 50psig and Maximum Allowable Working Temperature (MAWT) of 240*Fahrenheit,it is determined that low water fuel cutout device is not within boiler main and flow switch is on boiler inlet. Boiler operation without protection against low water and/or low flow condition (low water fuel cutout device is isolable and flow switch on boiler inlet does not accurately reflect flow through boiler tube) is possible which may lead to tube failure and incident. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | HWH_BOILER_2.png | file://x:/photopub/docs/0000000383/41a1459b-d7a0-4861-b112-c041d25836b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4734f550_a989_44f7_b586_7ba6234c7341
ELIN-485552-2015 | EL-280274-2015 | 12/2/2015 7:37:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | A new storage garage 100amp 120/240volt panel is installed not using the correct installation methods. The pinched wire of the feeder on the connector could lead to a short circuit condition. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Service.png | file://x:/photopub/docs/0000000361/91dfa677-af42-46fe-be6e-68a50eecb72a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4802e2bd_bbea_41eb_948f_59ca0030206c
ELIN-484572-2015 | EL-315380-2015 | 12/3/2015 10:16:51 AM | ASSESS: EL: Service Connection | png | #asFound |  |  | 4 | 4 | A 200amp 120/240volt new residential service has the system ground installed into the incorrect location. It is installed into the meterbase bond terminal and not into the electrical distribution panel as required. This is a potential thermal hazard. |  |  | Ground_on_bond_lug.png | file://x:/photopub/docs/0000000361/b5267f73-ab0a-412f-9ba8-5e9de57ee1ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42dc18ce_10a5_4148_a87f_54b4fadf1393
ELIN-484394-2015 | UW-314228-2015 | 11/25/2015 3:35:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Splices for branch circuit wiring are required to be made inside of an approved box and fitted with a cover plate. This is required to prevent accidental contact with energized conductors and connections, to mechanically protect conductors and connections, and to contain thermal energy in the event that conductor connections or insulation fail. This installation in the secondary suite of a house has open conductors and connections above a dropped ceiling in the bathroom. The connections are on a 15A, 120V circuit for the splice to the bathroom fan and light fixture. Left uncorrected this installation poses a potential fire hazard if the connections, or conductor insulation fail and the circuit over heats. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Bathroom_ceiling_in_suite.png | file://x:/photopub/docs/0000000357/9c899b11-3b0c-40d6-afdf-b9e8e4889792.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6a723fe_e3ba_4218_8eed_d7facc7179b3
ELIN-484394-2015 | UW-314228-2015 | 11/25/2015 3:35:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Splices for branch circuit wiring are required to be made inside of an approved box and fitted with a cover plate. This is required to prevent accidental contact with energized conductors and connections, to mechanically protect conductors and connections, and to contain thermal energy in the event that conductor connections or insulation fail. This installation in the secondary suite of a house has open conductors and connections above a dropped ceiling in the bathroom. The connections are on a 15A, 120V circuit for the splice to the bathroom fan and light fixture. Left uncorrected this installation poses a potential fire hazard if the connections, or conductor insulation fail and the circuit over heats. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Open_splice_above_bathroom_ceiling_in_suite.png | file://x:/photopub/docs/0000000357/a855d9d7-d872-4d7a-a2b9-048c6b548634.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6a723fe_e3ba_4218_8eed_d7facc7179b3
ELIN-496143-2015 | UW-326537-2015 | 12/14/2015 10:12:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The service conduit is not bonded with a bond bushing. This could make a high resistance connection in the fault current circuit, resulting in a possible shock hazard during a fault in the electrical system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Service_no_bond_bush.png | file://x:/photopub/docs/0000000368/55e06064-05fd-47eb-b882-4cc2223305df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6465d6b9_3537_40e5_9bb6_bb83e2ecc151
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_9.png | file://x:/photopub/docs/0000000368/74b8262e-0001-436b-8ee2-15889a4d9eaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_4.png | file://x:/photopub/docs/0000000368/97990808-1cdf-4fcf-9d8f-c66041920fcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom2.png | file://x:/photopub/docs/0000000368/02cd076a-5fbe-4b20-98fd-cafd6220b790.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-498638-2015 | EL-320528-2015 | 12/21/2015 3:51:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 14/2 nmsc is used to connect construction heaters and protected by a 60A breaker. This is a mechanical and thermal hazard, possibly resulting in shock or fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Open_splice_to_14_2_nmsc.png | file://x:/photopub/docs/0000000369/2988a7cd-1f39-40a8-905b-58c734c1d48c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__023e3efb_dfa6_4e6e_8612_61a311bc3da2
ELIN-498638-2015 | EL-320528-2015 | 12/21/2015 3:51:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 14/2 nmsc is used to connect construction heaters and protected by a 60A breaker. This is a mechanical and thermal hazard, possibly resulting in shock or fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | _12_Cabtyre_connected_to_60A_breaker.png | file://x:/photopub/docs/0000000369/f71bf84a-79ac-421e-84c3-ed4b61bdd643.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__023e3efb_dfa6_4e6e_8612_61a311bc3da2
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Branch_circuits_have_been_wired_to_bus_and_are_hanging_out_of_panel.png | file://x:/photopub/docs/0000000378/aa5d154a-17e4-4cc8-bfa7-5af06872ddd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
ELIN-484572-2015 | EL-315380-2015 | 12/3/2015 10:16:51 AM | ASSESS: EL: Service Connection | png | #asFound |  |  | 4 | 4 | A 200amp 120/240volt new residential service has the system ground installed into the incorrect location. It is installed into the meterbase bond terminal and not into the electrical distribution panel as required. This is a potential thermal hazard. |  |  | Ground_entering_meterbase.png | file://x:/photopub/docs/0000000361/904fde73-a602-432a-a917-6580b911071f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42dc18ce_10a5_4148_a87f_54b4fadf1393
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_8.png | file://x:/photopub/docs/0000000368/3edc2ecc-1d31-4de5-92f5-3ad7e66a51a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_10.png | file://x:/photopub/docs/0000000368/e1cf5d18-90c0-4971-9735-5583a48ffd7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_7.png | file://x:/photopub/docs/0000000368/7798a4bc-6da7-4020-b6d2-dfd0c4c4de6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_5.png | file://x:/photopub/docs/0000000368/0fe2b184-b787-49d6-8441-abdfb7b39370.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_1.png | file://x:/photopub/docs/0000000368/8a403f78-af42-4543-83fd-a578796e0f01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom_6.png | file://x:/photopub/docs/0000000368/03e55a43-cd18-4883-8558-864ea968752e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-497175-2015 | UW-327231-2015 | 12/16/2015 11:21:32 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Found a feeder sub-panel installed in a bathroom which according to code is an undesirable location for a panel-board. When a panel-board is installed in a bathroom the electrical equipment may become wet and be subjected to humidity or adverse environmental conditions which may damage electrical equipment or will not allow proper operation of electrical equipment as required by approved use of electrical equipment. This could pose a possible electrical shock or fire hazard to people and property. | 3 | General Equipment is not approved for the specific use | Panel_in_bathroom3.png | file://x:/photopub/docs/0000000368/0fcded46-55b5-40d6-8db8-b37df161eb2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27f0e3b4_0398_4cd0_b2d1_cc0b37ea666f
ELIN-498638-2015 | EL-320528-2015 | 12/21/2015 3:51:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | 14/2 nmsc is used to connect construction heaters and protected by a 60A breaker. This is a mechanical and thermal hazard, possibly resulting in shock or fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Construction_heater.png | file://x:/photopub/docs/0000000369/642bc80e-39a9-4e12-80ab-8d0d3abc51f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__023e3efb_dfa6_4e6e_8612_61a311bc3da2
ELIN-505576-2016 | EL-250628-2015 | 1/27/2016 6:52:22 AM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Label.png | file://x:/photopub/docs/0000000383/05397558-21d0-4218-b143-bdb74ae7657b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__974e14bb_6eec_4aae_8ffa_fd65bb5ecfb5
ELIN-485341-2015 | EL-316568-2015 | 12/16/2015 9:19:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Cable connectors installed for equipment located outdoors are required to be installed so that water will not enter electrical equipment. This installation has a service cable connector at a 200A, 120\240V meter base that is not preventing water from entering the equipment. The connector is either not tightened properly or is the wrong size and is not providing a weather proof seal. Left uncorrected, over time moisture inside the electrical equipment may cause condensation, rust, and corrosion, to the equipment and conductor terminations. Long term this is a potential fire hazard if the equipment fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Water_entering_pull_elbow_fitting.png | file://x:/photopub/docs/0000000367/790a99ce-05a0-43cb-9866-374e33f66a0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f815c654_3b43_40d6_ab78_020742365eb7
ELIN-485341-2015 | EL-316568-2015 | 12/16/2015 9:19:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Cable connectors installed for equipment located outdoors are required to be installed so that water will not enter electrical equipment. This installation has a service cable connector at a 200A, 120\240V meter base that is not preventing water from entering the equipment. The connector is either not tightened properly or is the wrong size and is not providing a weather proof seal. Left uncorrected, over time moisture inside the electrical equipment may cause condensation, rust, and corrosion, to the equipment and conductor terminations. Long term this is a potential fire hazard if the equipment fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Water_entering_meter_base.png | file://x:/photopub/docs/0000000367/2fc5120c-7612-4455-82fa-9f0fac508812.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f815c654_3b43_40d6_ab78_020742365eb7
ELIN-485341-2015 | EL-316568-2015 | 12/16/2015 9:19:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Cable connectors installed for equipment located outdoors are required to be installed so that water will not enter electrical equipment. This installation has a service cable connector at a 200A, 120\240V meter base that is not preventing water from entering the equipment. The connector is either not tightened properly or is the wrong size and is not providing a weather proof seal. Left uncorrected, over time moisture inside the electrical equipment may cause condensation, rust, and corrosion, to the equipment and conductor terminations. Long term this is a potential fire hazard if the equipment fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_cable_and_meter_base.png | file://x:/photopub/docs/0000000367/1a57ef79-4aba-488b-bc1a-31420e85a82f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f815c654_3b43_40d6_ab78_020742365eb7
ELIN-485341-2015 | EL-316568-2015 | 12/16/2015 9:19:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Cable connectors installed for equipment located outdoors are required to be installed so that water will not enter electrical equipment. This installation has a service cable connector at a 200A, 120\240V meter base that is not preventing water from entering the equipment. The connector is either not tightened properly or is the wrong size and is not providing a weather proof seal. Left uncorrected, over time moisture inside the electrical equipment may cause condensation, rust, and corrosion, to the equipment and conductor terminations. Long term this is a potential fire hazard if the equipment fails. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_cable_connector_not_properly_tightened_or_the_wrong_size_to_prevent_water_from_entering_equipment.png | file://x:/photopub/docs/0000000367/3d968a26-66f0-44af-9c00-0a8c72dd72da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f815c654_3b43_40d6_ab78_020742365eb7
ELIN-523552-2016 | EL-324576-2015 | 2/15/2016 3:50:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The electrical system is required to be grounded. This is achieved by terminating the grounding conductor to the system neutral. This assessment found the grounding conductor to be terminated to the equipment instead of the required system neutral. In a fault situation there is a risk of shock with energized equipment as the system may not see the fault to trip the breaker. | 4 | Installation Grounding; conductor is not continuous. | Grounding.png | file://x:/photopub/docs/0000000391/f1665300-75fb-4c65-b6db-087f569857a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5e5d129_6659_41a0_9328_ee247e620811
ELIN-525411-2016 | EL-326997-2015 | 2/15/2016 2:05:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | The electrical system is required to be grounded. This is achieved by terminating the grounding conductor to the system neutral. This assessment found the grounding conductor to be terminated to the equipment instead of the required system neutral. In a fault situation there is a risk of shock with energized equipment as the system may not see the fault to trip the breaker. | 4 | Installation Grounding; conductor is not continuous. | Grounding_in_meter.png | file://x:/photopub/docs/0000000391/0e34c951-3d78-44f3-b99c-dfad0d97a531.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07439351_1a6c_4d8d_a5b4_266589dd54b5
ELIN-527547-2016 | EL-345904-2016 | 2/16/2016 3:44:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 200 amp, 120/240 volt main distribution panel has service conductors terminated outside of service conductor compartment. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Service_conductors_terminated_outside_of_service_conductor_compartment.png | file://x:/photopub/docs/0000000392/27fd1280-703e-4832-9343-9e7790104c84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76a56394_f8af_43d8_aec4_57912c427397
ELIN-488169-2015 | EL-319911-2015 | 12/4/2015 2:37:15 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The system has re-bonded the feeder identified conductor to the panel bonding system by not removing the bonding strap in the trailer service panel and connecting the feeder bond cable to the neutral connection point creating a secondary flow of current through the existing bonding conductor back to the main service that can cause a thermal issue on the feeder cable | 3 | Continuity Bonding; method for equipment is not adequate. | Panel_bond.png | file://x:/photopub/docs/0000000361/7a554937-d6ab-448d-9075-ed5e25e8c926.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64149f60_bc66_44b5_95d2_0dd9fd7fd0c2
ELIN-488169-2015 | EL-319911-2015 | 12/4/2015 2:37:15 PM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The system has re-bonded the feeder identified conductor to the panel bonding system by not removing the bonding strap in the trailer service panel and connecting the feeder bond cable to the neutral connection point creating a secondary flow of current through the existing bonding conductor back to the main service that can cause a thermal issue on the feeder cable | 3 | Continuity Bonding; method for equipment is not adequate. | trailer_service_panel.png | file://x:/photopub/docs/0000000361/c7a1485f-a2ed-454d-bdc2-f4adf734b5a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64149f60_bc66_44b5_95d2_0dd9fd7fd0c2
BPVOP-492760-2015 | 4090833 | 12/10/2015 12:57:18 PM | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000365/e941f52c-2664-4a1e-87e6-44c5d1486c02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3caa5ecd_ef25_49bb_b633_66e4992d7df7
ELIN-513868-2016 | EL-248282-2015 | 1/27/2016 3:27:58 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 20 amp 120v tamper resistant receptacle located at the end of a kitchen counter is within 1.5 meters of a sink and is not adequately protected to prevent accidental prolonged electrical shock. Installation of a ground fault circuit interrupt protected receptacle is required to minimize the danger of prolonged electrical shock. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_adjacent_to_sink.png | file://x:/photopub/docs/0000000383/5a42640c-8dea-4db8-9e18-ab136e6c57a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee285035_a2fa_423e_a859_810fa04d78af
GAUP-510802-2016 | UW-335066-2016 | 1/15/2016 12:54:45 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | The as found hazard was a furnace and water heater which had been installed within a closet with no provisions to supply combustion air to the space. This is a hazard because without adequate combustion air there is a risk of improper combustion and/or depressurization of the space which will prevent proper appliance venting potentially allowing the products of combustion to enter the home. | 4 | Combustion air supply missing | Water_Heater.png | file://x:/photopub/docs/0000000378/7d798894-dc5a-4ca3-9b14-108981e6db5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6277601_8bb4_4261_83e5_f76cab59de72
GAUP-510802-2016 | UW-335066-2016 | 1/15/2016 12:54:45 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | The as found hazard was a furnace and water heater which had been installed within a closet with no provisions to supply combustion air to the space. This is a hazard because without adequate combustion air there is a risk of improper combustion and/or depressurization of the space which will prevent proper appliance venting potentially allowing the products of combustion to enter the home. | 4 | Combustion air supply missing | furnace.png | file://x:/photopub/docs/0000000378/ae3e5acf-75fc-4b99-96c5-da547eb69dd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6277601_8bb4_4261_83e5_f76cab59de72
BPVIN-503105-2015 | BPV-306891-2015 | 1/15/2016 3:17:41 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP017 | 1.0.2 Clearances/Maintenance - No start up or commissioning report | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - No start up or commissioning report | Boiler_switch_not_lockable.png | file://x:/photopub/docs/0000000378/75e4fae2-9cda-4927-ab16-ddaadbca1a1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7309414e_0c8b_4fcc_ae46_b7dd97e7709b
ELIN-487371-2015 | EL-294297-2015 | 12/2/2015 12:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Faults can occur between an insulated service conductor and its metal raceway or metal cable armour, or between an insulated service conductor and the metal enclosure of service electrical equipment, at a point ahead of the service overcurrent device (circuit breaker or fuse). As a result of such faults, a relatively large current can flow through the bonding conductors for a considerable time for the supply authority’s overcurrent protection to clear the fault. During an inspection, it was discovered that the metal service raceway was not adequately bonded to ground. Should a fault occur, sections of this metal raceway could fail resulting in a risk to persons and property. In addition, limiting the Utilities’ ability to clear the fault. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Supply_Service_Raceway_.png | file://x:/photopub/docs/0000000360/05e17f04-8952-450f-8293-aac3bf96f5cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfb8bd35_171a_4742_8c84_5a27f7254bb1
ELIN-487371-2015 | EL-294297-2015 | 12/2/2015 12:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Faults can occur between an insulated service conductor and its metal raceway or metal cable armour, or between an insulated service conductor and the metal enclosure of service electrical equipment, at a point ahead of the service overcurrent device (circuit breaker or fuse). As a result of such faults, a relatively large current can flow through the bonding conductors for a considerable time for the supply authority’s overcurrent protection to clear the fault. During an inspection, it was discovered that the metal service raceway was not adequately bonded to ground. Should a fault occur, sections of this metal raceway could fail resulting in a risk to persons and property. In addition, limiting the Utilities’ ability to clear the fault. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Close_nipple_not_bonded_.png | file://x:/photopub/docs/0000000360/d1b7ccf8-4bfb-42aa-83b0-0e50cc3a8803.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfb8bd35_171a_4742_8c84_5a27f7254bb1
GAOP-187384-2014 | 3852569 | 11/5/2015 8:09:30 AM | ASSESS: GA OP: Periodic | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | Bella_Bulk_plant.png | file://x:/photopub/docs/0000000359/f1ed613e-30e2-4a26-bbdf-7b35facc1975.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41d6af6e_0435_4f74_baad_1448e7d16dfb
BPVOP-496851-2015 | 4814039 | 12/16/2015 3:40:15 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Horizontal_pressure_relief_device_.png | file://x:/photopub/docs/0000000367/fa4f7ef7-b13d-46cf-8200-14de218299d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44401eaf_202c_4145_a6bc_05ffce423092
ELIN-517024-2016 | EL-334942-2016 | 1/26/2016 10:14:48 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | The 15 amp 120 volt energized circuit is accessible to persons, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Switch_at_basement_exit_.png | file://x:/photopub/docs/0000000384/afbe9997-fb1d-4d3d-901e-f778da8c51ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4a8b63c_6dd6_4072_b186_91a5decc43cd
ELIN-494003-2015 | EL-323805-2015 | 12/16/2015 2:11:16 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed in locations where they will not become damaged. This is required to prevent damage to the cable sheath and conductor insulation to prevent potential shock and fire hazards. This installation has energized NMSC and an outlet box that have been removed from a section of wall and are laying on the floor. The installation is related to a bathroom renovation and the cable and outlet box are in a location where they may get damaged during construction. Left uncorrected this is a potential fire and shock hazard if the cable sheath and conductor insulation get damaged and conductive parts come in contact with each other or with a person. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Energized_branch_circuit_wiring_and_outlet_box_removed_from_the_wall_during_bath_room_renovation.png | file://x:/photopub/docs/0000000368/7f64d6ce-217d-4160-bcf8-1fa48916e99b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57230d82_961b_4c9c_bfca_bd71bead6829
ELIN-512751-2016 | EL-279282-2015 | 1/20/2016 6:27:24 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Mobile home feeder cable is posing a tripping hazard and will cause strain on the box cable connector under pulling force because it is not strapped near the box. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Service_cable.png | file://x:/photopub/docs/0000000380/8fe2bda0-47cd-428a-be60-981aa7bd2d0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60a165c8_c386_4418_b7ad_48a1ed328b46
ELIN-503278-2015 | EL-330205-2015 | 1/5/2016 7:37:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Washer cord supplied by an extension cord. Receptacle supplying extension cord is installed on an exterior wall which requires extension cord to run across exposed floor space. The extension cord is subject to mechanical damage in its current location. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Extension_cord_connection_to_washer_plug.png | file://x:/photopub/docs/0000000374/4c89e3bb-7cc9-41e4-b782-b61a1d606546.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13373577_7cb0_45be_9b8f_a8ed27ea3410
ELIN-503278-2015 | EL-330205-2015 | 1/5/2016 7:37:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | Washer cord supplied by an extension cord. Receptacle supplying extension cord is installed on an exterior wall which requires extension cord to run across exposed floor space. The extension cord is subject to mechanical damage in its current location. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Extension_supply_to_washer.png | file://x:/photopub/docs/0000000374/88e80616-29ef-4db1-8fbc-b187023d371b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13373577_7cb0_45be_9b8f_a8ed27ea3410
GAIN-495418-2015 | GA-304203-2015 | 12/17/2015 11:58:25 AM | ASSESS: GA: Final | png | #asFound | GA028 | Meter set /regulatory assembly undersized for connected load | 3 | 3 | Gas Contractor did not contact Fortis BC before connecting standby generator to existing gas meter and if there is an electrical power failure the gas meter is too small to adequately supply gas to all the connected appliances causing straight on the gas meter and premature gas meter failure. | 3 | Meter set /regulatory assembly undersized for connected load | 3830_200_str_.png | file://x:/photopub/docs/0000000368/6dd30e2a-69e7-49bc-8915-32db6ff7eb75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7cd5aa16_6c2b_4c90_9104_280919e421b1
GAIN-495412-2015 | GA-304207-2015 | 12/17/2015 11:57:38 AM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | New installation of a stand by generator installed to close to the relief opening of a gas regulator and if gas escapes from the relief opening it could be ignited causing a fire or explosion | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3830_200_street.png | file://x:/photopub/docs/0000000368/e3de1fdd-4abb-4d56-8b2d-db6120e1e30e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bca3427d_e36f_4420_9d33_f5ad129d1880
ELIN-505639-2016 | EL-320109-2015 | 1/6/2016 3:49:45 PM | ASSESS: EL: Service Connection | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | Recirculating currents in the bonding path can be created if the neutral conductor is connected to bonding system at more than one location in a circuit. These currents can create a high impedance path to ground which could limit the over current device operation in the event of a ground fault. During a residential service inspection, the service neutral was connected to the bonding system at three locations. | 3 | Continuity Multiple grounded systems are not interconnected. | Bonding_jumper_not_removed.png | file://x:/photopub/docs/0000000374/ac5545cd-8f4d-46ca-9b9e-dc1f84141e31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__276cba69_6ab3_43ba_ab69_1a94497ce97f
ELIN-525183-2016 | EL-253923-2015 | 2/12/2016 4:25:36 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Cables installed in panel without connectors, holes in panel are sharp and abrasive, repeated movement of cables may cause cable sheath failure and would allow energized conductors to come in contact with panel enclosure. Risk of shock or fire to persons or property | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Cables_installed_without_connectors.png | file://x:/photopub/docs/0000000390/70c931f4-df7c-4096-a038-40cd413f7039.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39273c73_7aa5_4c2a_8563_f1450aa35d73
ELIN-526488-2016 | EL-299055-2015 | 2/15/2016 7:01:15 AM | ASSESS: EL: Final | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | 15A 230V 12/3 armoured cable is not properly terminated to the connector which could result in a shock hazard or cable failure. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Teck.png | file://x:/photopub/docs/0000000391/2f823ca8-4e16-46f4-8acf-072f0a30ae71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a5a5a2c_d00d_49f3_b4ea_1adb7d870f1b
ELIN-485660-2015 | EL-247268-2015 | 12/1/2015 12:06:10 PM | ASSESS: EL: Final | png | #asFound | EL150 | Installation of electrical equipment Fixtures without suitable support. | 4 | 4 | Mounting hardware for lamps in exterior mounted recessed lighting fixtures not properly installed. Lamps are hanging free below recessed fixtures, exposing the lamps and hardware to mechanical damage. This poses a risk of personal injury (shock) or property damage (thermal event). | 4 | Installation of electrical equipment Fixtures without suitable support. | View01_exterior_fixtures_A.png | file://x:/photopub/docs/0000000360/aeaf2aa2-70e0-414d-b7b4-4f1426921c0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b52f339a_f55d_48e0_b415_0beba7943736
ELIN-484878-2015 | EL-091276-2014 | 12/1/2015 12:06:54 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Exterior receptacles have been provided with covers that are not suitable for use in a wet location if a utilization vice is inserted into the receptacle. This poses a risk of personal injury (shock) or equipment damage due to the effects of exposure to weather. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | View01_exterior_receptacle_A.png | file://x:/photopub/docs/0000000360/560e94dc-4302-4677-81a9-865f362da064.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bcdde84_0d68_43ef_afff_dd5c660c9c2e
ELIN-491738-2015 | EL-301784-2015 | 12/11/2015 7:53:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | No mechanical protection provided on building exterior allowing the risk of nails to be driven through conduit (and feeder cable) when finishing is installed. This is an equipment/property damage risk and can include shock and thermal | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Exterior_wall.png | file://x:/photopub/docs/0000000366/fd013f94-bcad-4461-8e29-f673d9d1a35b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238253aa_0d49_4b6a_b093_ba8df661334d
ELIN-491738-2015 | EL-301784-2015 | 12/11/2015 7:53:55 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | No mechanical protection provided on building exterior allowing the risk of nails to be driven through conduit (and feeder cable) when finishing is installed. This is an equipment/property damage risk and can include shock and thermal | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Garage_feeder_cable_.png | file://x:/photopub/docs/0000000366/3ebfc8a0-d4db-4008-a2dd-f19380e8cacd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__238253aa_0d49_4b6a_b093_ba8df661334d
ELIN-499722-2015 | EL-328506-2015 | 12/22/2015 4:22:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | A 3” rigid PVC service conduit is connected to a 200 amp 120/240 volt meter/disconnect switch combination enclosure. An Expansion joint has not been installed in the raceway. Movement in the conduits from frost or settlement will cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Underground_service_raceway.png | file://x:/photopub/docs/0000000370/05a8a00f-542b-43f0-967a-e3d9ad577671.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c64ace7e_a5bc_4bba_a4b7_f65ae131173f
GAIN-524156-2016 | GA-248278-2015 | 2/17/2016 8:47:47 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Boiler has been left in service with exhaust vent terminating to close to soffit, when boilers is operating the exhaust gases are condensing on the soffit and will cause water damage and to the soffit area | 2 | Side wall vent termination not compliant with installation instructions | 2_20621_44.png | file://x:/photopub/docs/0000000392/6704dd47-88a9-4242-99a4-35e8751d4418.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92416eb3_1866_4c0d_a646_9ecfef01e0ab
GAIN-524156-2016 | GA-248278-2015 | 2/17/2016 8:47:47 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Boiler has been left in service with exhaust vent terminating to close to soffit, when boilers is operating the exhaust gases are condensing on the soffit and will cause water damage and to the soffit area | 2 | Side wall vent termination not compliant with installation instructions | 3_20621_44.png | file://x:/photopub/docs/0000000392/24334554-f62e-4cca-a103-ae458984ea02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92416eb3_1866_4c0d_a646_9ecfef01e0ab
GAIN-524156-2016 | GA-248278-2015 | 2/17/2016 8:47:47 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Boiler has been left in service with exhaust vent terminating to close to soffit, when boilers is operating the exhaust gases are condensing on the soffit and will cause water damage and to the soffit area | 2 | Side wall vent termination not compliant with installation instructions | 1__20621_44.png | file://x:/photopub/docs/0000000392/4d9bebe9-4b3b-455c-8062-3cadb3409b3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92416eb3_1866_4c0d_a646_9ecfef01e0ab
BPVOP-528168-2016 | 4171393 | 2/16/2016 1:16:39 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP009 | 1.0.1 Temp/Pressure ratings not met - Operating pressures above Maximum Allowable Working Pressure | 3 | 3 | Upon assessment it is determined that expansion tank Maximum Allowable Working Pressure (MAWP) of 45psig is less than Safety relief valve set pressure (75psig). If system operating pressure reaches above MAWP of expansion tank, pressure boundary of vessel may fail and can lead to incident. | 3 | 1.0.1 Temp/Pressure ratings not met - Operating pressures above Maximum Allowable Working Pressure | NAMEPLATE_SHOWING_MAWP.png | file://x:/photopub/docs/0000000391/4fcea9de-e916-41f6-b859-a1691cf0e558.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4514f451_250a_4952_8b9a_7292b8cd8d02
BPVOP-528180-2016 | 4171395 | 2/16/2016 12:55:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 5.68 square meters, Maximus Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_B2.png | file://x:/photopub/docs/0000000391/4dfc8dd9-14ec-4481-bfab-9404b7f1a16a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45aa1d71_379f_4287_a5c4_12b7313ae557
BPVOP-528190-2016 | 4171394 | 2/16/2016 12:29:54 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 5.68 square meters, Maximus Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE_B1.png | file://x:/photopub/docs/0000000391/1f757e34-0c82-42e1-8719-a2584d12900c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc880182_9046_4f24_8392_c7a795acaa66
GAIN-499882-2015 | GA-319323-2015 | 1/14/2016 4:46:42 PM | ASSESS: GA: Final | png | #asFound | GA148 | Over fired equipment | 4 | 4 | Over fired propane appliance. A propane fueled kitchen range designed to operate at 11 inches water column pressure (0.4 pounds per square inch pressure) was connected to a Propane supply system delivering 2 pounds per square inch pressure, roughly 4 times the allowable. This is a hazard as it exceeds the maximum allowable pressure as set out by the manufacturer and could lead to a “Overfired” condition, which can lead to incomplete combustion and Carbon Monoxide as well as delayed ignition, which can create an explosion and fire hazard. | 4 | Over fired equipment | 10120_tsaykum_1.png | file://x:/photopub/docs/0000000378/6f1a86b1-9c63-42b8-a843-2be3159d1e57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6614ff7c_b861_4f1b_99dc_eea01a3e2b4e
GAIN-499882-2015 | GA-319323-2015 | 1/14/2016 4:46:42 PM | ASSESS: GA: Final | png | #asFound | GA148 | Over fired equipment | 4 | 4 | Over fired propane appliance. A propane fueled kitchen range designed to operate at 11 inches water column pressure (0.4 pounds per square inch pressure) was connected to a Propane supply system delivering 2 pounds per square inch pressure, roughly 4 times the allowable. This is a hazard as it exceeds the maximum allowable pressure as set out by the manufacturer and could lead to a “Overfired” condition, which can lead to incomplete combustion and Carbon Monoxide as well as delayed ignition, which can create an explosion and fire hazard. | 4 | Over fired equipment | 10120_tsaykum_2.png | file://x:/photopub/docs/0000000378/3486e743-f1e3-4177-9675-57dade2f57be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6614ff7c_b861_4f1b_99dc_eea01a3e2b4e
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Lighting_boxes_missing_covers_and_no_connectors.png | file://x:/photopub/docs/0000000378/7eb1f55f-7623-42a8-ab94-e10af24cf379.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Address.png | file://x:/photopub/docs/0000000378/8c43aba2-67d0-4e33-8855-de4b0331b49e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Branch_circuit_not_terminated_using_manufactured_connection__wire_is_twisted_to_terminal.png | file://x:/photopub/docs/0000000378/4887a880-d2e6-4456-8234-412378aee92b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
ELIN-510193-2016 | UW-334791-2016 | 1/14/2016 4:32:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | There is no main disconnect for the main panel to protect panel from fault current generated on load side of panel. Connection is direct to BC Hydro using Hydro transformer primary protection against main panel fault currents. The panel cover is missing and branch circuits, tapped directly off the main bus, are hanging outside the panel with a circuit breaker not compatible with the panel. The conductors supplying this breaker do not have local disconnect or over current protection and are exposed for shock and subject to create fire. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Main_panel_not_equiped_with_main_disconnect__direct_connect_to_BCHydro.png | file://x:/photopub/docs/0000000378/a059455c-5292-43dd-ab08-19a55d76b5ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__224d16db_4d50_4ff2_8282_66eb84720ab0
ELIN-498750-2015 | EL-328023-2015 | 12/23/2015 1:40:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 | A 120/240v - 400A multi-Meterbase position shall be clearly identified as to what consumer service for future disconnection/ re-connection purposes. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Duplex_meterbase.png | file://x:/photopub/docs/0000000370/0a00931a-be5f-4fb3-b0f5-95645a8e5af4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2255d05c_adba_4d9d_a0d2_144db382b35b
ELOP-301465-2015 | 3261 | 2/9/2016 12:53:43 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 2 | Doors, when closed, are 2inches or less in front of transformer, in electrical closet. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Electrical_room_transformer_and_closet_door.png | file://x:/photopub/docs/0000000388/2c16ad58-33c9-4cba-8eff-209f9b6be806.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6adaf071_268e_46a0_bfe6_1862df77a249
PROP-465954-2015 | 2224183 | 2/10/2016 2:19:32 PM | ASSESS: PR OP: RAP | png | #asFound | PR025 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | Containment barriers that are placed along side the towpath which are intended to stop and control a detached secondary carrier (tube) are not securely anchored to ground. They are very easily moved by hand and would not function as intended. There is a probability that a detached carrier with a rider would not be stopped or controlled. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Containment_barrier_not_anchored_to_ground.png | file://x:/photopub/docs/0000000389/59cffd7e-2dc4-4ea2-8f26-84b040677ee5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4720F2E3_02B5_42E3_BFAF_CFAB3A937AF6
ELOP-196136-2014 | 1222 | 12/2/2015 8:45:26 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are for use with portable appliances and to reduce the effects of vibration. In this installation flexible cord has been installed as a replacement for permanent wiring and with unapproved splices. | 4 | Conductors, Misuse of flexible cords. | Behind_genset.png | file://x:/photopub/docs/0000000360/de268527-7ee5-46ad-883d-a9d5025efd4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd391b3e_406a_4384_9460_d3896f58fa65
ELOP-195653-2014 | 1223 | 12/2/2015 8:45:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are for use with portable equipment and to reduce the effects of vibration. In this installation flexible cords had been introduced into conduit and run from an attic space to a SCADA server enclosure. | 4 | Conductors, Misuse of flexible cords. | Server_feeder.png | file://x:/photopub/docs/0000000360/74e2772c-a1ee-40ef-9134-0e0f3b3726ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a335343a_0d6d_46fc_9923_60828fb69cad
ELOP-196136-2014 | 1222 | 12/2/2015 8:45:26 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are for use with portable appliances and to reduce the effects of vibration. In this installation flexible cord has been installed as a replacement for permanent wiring and with unapproved splices. | 4 | Conductors, Misuse of flexible cords. | Splices.png | file://x:/photopub/docs/0000000360/c2e26987-1ba0-498a-ba44-48514fcb8098.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd391b3e_406a_4384_9460_d3896f58fa65
ELOP-226700-2014 | 4020457 | 12/2/2015 8:44:53 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Conductors must be protected by overcurrent devices each time they are reduced in size. In this installation a feeder was observed undersized for the load it supplied. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Dist_with_no_oc_protection.png | file://x:/photopub/docs/0000000360/cd55a59a-1d40-4f76-8551-0d9a92a9490e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__716c02d6_7873_48b1_b4a0_8dac40f683e4
ELOP-196124-2014 | 1221 | 12/2/2015 8:45:45 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL103 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | 3 | 3 | Conductors from different systems and with different voltages may not be contained intent same raceway or splitter unless approved for such use. In this installation extra low voltage conductors are installed with low voltage conductors in the same raceway. | 3 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | Mixed_voltages_in_splitter.png | file://x:/photopub/docs/0000000360/867fa408-6672-42a0-a345-304d5c876aea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f8fcced_1e03_4352_b123_07077f984d97
ELIN-526589-2016 | EL-343941-2016 | 2/17/2016 11:57:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Screw in style point of attachment. This is a fire hazard as these types of knobs have been found to pull out over time. This can stress the electrical splices and cause hot spots or fire. Minimum 38mm bolts are required to extend through the wood blocking with adequate washers. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | A.png | file://x:/photopub/docs/0000000392/ed875b09-e6be-4f21-8741-cf4511a489d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5606a461_caa8_4ac2_ba1b_0f74bdd9868b
BPVOP-508561-2016 | 3215140 | 12/21/2015 3:28:59 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | Eight to ten leaks were found on a steam boiler operating with a Maximum Allowable Working Pressure of 150 psi. Cracks in the boiler tubes and tube sheet was the source of the leaks. Steam boilers store large amounts of energy, a potential rupture may result in an explosion. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Boiler_tube_sheet.png | file://x:/photopub/docs/0000000377/7bde1150-f8b8-4764-9c36-1a8de44e0c46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4430b3f_61e3_487a_a1cc_365315333f31
ELIN-503831-2016 | EL-222795-2015 | 1/5/2016 8:33:05 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 2 | Missing cover on junction box. Should arcing ever occur due to a bad splice or fault condition the sparks can escape from the junction box. The missing required cover contains any arcing within the box. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | missing_cover.png | file://x:/photopub/docs/0000000374/35dadde7-a4e6-4ff6-b70f-0e2569a95179.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b69514dc_ee34_4fba_a83e_9bc1b21813ec
GAIN-494970-2015 | GA-305100-2015 | 2/5/2016 11:42:14 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Fresh_air_term.png | file://x:/photopub/docs/0000000391/f1447f76-0dcf-4299-9f70-b322c1268b97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6669341f_142b_4aee_8c20_3cc7e869710c
ELIN-486356-2015 | EL-291409-2015 | 12/1/2015 5:24:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed a minimum of 25mm from metal heating ducts or they need to have thermal insulation installed between heating ducts and wiring. This is required to prevent the cable sheath from thermal or mechanical damage. This installation of wiring for a new house has NMSC installed in contact with metal heating ducts. Left uncorrected this is a potential fire hazard if the cable sheath and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_ducts_.png | file://x:/photopub/docs/0000000360/32426030-645c-4c78-a7e0-8fafd7495f82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6881b2f5_8585_40b1_aaa8_19aca2b66e66
ELIN-486356-2015 | EL-291409-2015 | 12/1/2015 5:24:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed a minimum of 25mm from metal heating ducts or they need to have thermal insulation installed between heating ducts and wiring. This is required to prevent the cable sheath from thermal or mechanical damage. This installation of wiring for a new house has NMSC installed in contact with metal heating ducts. Left uncorrected this is a potential fire hazard if the cable sheath and conductor insulation is damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_ducts.png | file://x:/photopub/docs/0000000360/87ed0d15-fdf7-446e-ab95-96477d681e96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6881b2f5_8585_40b1_aaa8_19aca2b66e66
ELIN-527628-2016 | EL-335824-2016 | 2/16/2016 11:24:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | The overcurrent protection for the service cable is oversized. This could result in overheating and a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 100A_main_breaker_in_panel_fed_with_3c_6_acwu.png | file://x:/photopub/docs/0000000391/5d420e8c-1250-4b5d-892b-b766bed30b13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__604f2760_5e19_431b_b994_e2134f3ffefe
GAIN-520888-2016 | GA-247079-2015 | 2/9/2016 12:50:46 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | To industrial gas boiler were left in operation with uncertified vent material extending through the combustible roof. During normal operation of the boilers the combustible roof will be subject to excessive stack temperatures potentially causing a roof fire. | 3 | Unapproved venting material | 5292_272nd.png | file://x:/photopub/docs/0000000388/3a7521ee-e8f0-4669-a108-8462e87a8c98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d02d315b_a324_4a1c_8d26_db67d06fedf6
GAIN-520888-2016 | GA-247079-2015 | 2/9/2016 12:50:46 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | To industrial gas boiler were left in operation with uncertified vent material extending through the combustible roof. During normal operation of the boilers the combustible roof will be subject to excessive stack temperatures potentially causing a roof fire. | 3 | Unapproved venting material | 5292_272_inside.png | file://x:/photopub/docs/0000000388/dcd23756-c348-486e-b753-2b87978f8613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d02d315b_a324_4a1c_8d26_db67d06fedf6
GAIN-520888-2016 | GA-247079-2015 | 2/9/2016 12:50:46 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | To industrial gas boiler were left in operation with uncertified vent material extending through the combustible roof. During normal operation of the boilers the combustible roof will be subject to excessive stack temperatures potentially causing a roof fire. | 3 | Unapproved venting material | 5292_272_boilers.png | file://x:/photopub/docs/0000000388/04d18306-1dff-45ae-9aae-aaf269a1bdd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d02d315b_a324_4a1c_8d26_db67d06fedf6
GAIN-529118-2016 | GA-322499-2015 | 2/17/2016 3:23:26 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | Cat 4 appliance air inlet is located to close to regulator relief device. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Cat_4_air_inlet__.png | file://x:/photopub/docs/0000000394/994bca1f-6d2d-466b-95d6-55971cf9346a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a70ef1f9_0b86_4a3c_8f88_7bbe08093474
GAIN-529119-2016 | GA-295951-2015 | 2/17/2016 10:42:03 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 4 | Gas fitter did not use correct assembly and glue procedure for high eff. furnace exhaust plastic venting. Joints were found leaking vent gas condensate water. | 5 | Special venting system not glued or connected as per certified instructions | Incorrect_glue_of_venting.png | file://x:/photopub/docs/0000000394/dde15f3d-dd2f-4676-9798-55c2490efdd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5a1ac9e_b8ca_4a33_83d7_d2327447733b
GAIN-529119-2016 | GA-295951-2015 | 2/17/2016 10:42:03 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 4 | Gas fitter did not use correct assembly and glue procedure for high eff. furnace exhaust plastic venting. Joints were found leaking vent gas condensate water. | 5 | Special venting system not glued or connected as per certified instructions | Furnace_vent_water_leak_.png | file://x:/photopub/docs/0000000394/15f5318e-64dd-4dc2-9820-ad12a5d09f70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5a1ac9e_b8ca_4a33_83d7_d2327447733b
GAIN-529119-2016 | GA-295951-2015 | 2/17/2016 10:42:03 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 4 | Gas fitter did not use correct assembly and glue procedure for high eff. furnace exhaust plastic venting. Joints were found leaking vent gas condensate water. | 5 | Special venting system not glued or connected as per certified instructions | Incorrect_furnace_vent_joint_install.png | file://x:/photopub/docs/0000000394/9f9d8190-7a7d-462b-a138-b962a260b996.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5a1ac9e_b8ca_4a33_83d7_d2327447733b
GAUP-528156-2016 | UW-346274-2016 | 2/16/2016 11:44:04 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | Improper venting material and atmospheric water heater installed in a negative airspace of commercial kitchen where products of combustion are spilling into occupied space which could cause serious illness. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Water_heater.png | file://x:/photopub/docs/0000000392/1e126053-f9cc-4281-ab26-73a886025cc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49ae2ef6_e473_4f20_b3a7_f4b9b3a455cf
GAIN-524455-2016 | GA-335308-2016 | 2/16/2016 11:15:43 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_.png | file://x:/photopub/docs/0000000392/52af89c6-29ea-4a16-9163-f5d00cc3e5e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02d27873_0142_42e1_99bd_49c402f65385
GAUP-528156-2016 | UW-346274-2016 | 2/16/2016 11:44:04 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | Improper venting material and atmospheric water heater installed in a negative airspace of commercial kitchen where products of combustion are spilling into occupied space which could cause serious illness. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Venting.png | file://x:/photopub/docs/0000000392/7a49cf92-1821-4616-94c3-47ef290d17af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49ae2ef6_e473_4f20_b3a7_f4b9b3a455cf
ELIN-525631-2016 | EL-303701-2015 | 2/11/2016 9:55:48 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Energized_outlet1.png | file://x:/photopub/docs/0000000389/0bb15994-b523-4a58-83ad-7e55640696e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c94d509_db9b_4227_baf7_112742382213
ELIN-458366-2015 | EL-299222-2015 | 11/24/2015 8:40:58 AM | ASSESS: EL: Final | png | #asFound | EL118 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | The identified conductor of multi conductor cables has been used for line voltage for both 3 phase and single phase 208 volt circuit conductors on circuits rated up to 40 amps. A worker servicing equipment may mistake the conductor as a neutral or identified conductor and make contact with that conductor in equipment and junction boxes, which could lead to injury for worker | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Identified_conductor_used_line_voltafe_throught_installation_no_tape.png | file://x:/photopub/docs/0000000357/5049eb5a-607f-4628-b91f-d971b4b76e57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9af7d6f_59f9_4fbc_9ceb_1e0d45d49fd4
ELIN-483674-2015 | EL-279494-2015 | 11/24/2015 8:41:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | An aluminum bonding conductor is installed using a copper only lug. The service cable is feeding a 125 amp 240 volt single phase service panel in a dwelling. Aluminum can react adversely to copper only lugs and leave the equipment without an effective bond. This can result in the failure of an overcurrent device to react when required if there is a fault in the cable or equipment with a potential for damage to persons or property | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Copper_lug_used_for_aluminum__no_anti_oxidant.png | file://x:/photopub/docs/0000000357/01f2ecce-a983-4ae2-8b56-ee3e8a1f256b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5338dbe_4824_4bd3_a74d_089839276134
ELOP-226736-2014 | 1002 | 2/10/2016 10:07:00 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings in electrical enclosures must be closed off to prevent accidental contact with live parts and to contain a blast in the enclosure. In this school installation a panel filler had fallen out of a large distribution centre. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Missing_panel_filler.png | file://x:/photopub/docs/0000000389/58939282-39d5-4db6-b8be-fedf2e834569.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2e094cd_08bb_437f_917e_a58e88dbe290
ELIN-525636-2016 | 5435035 | 2/11/2016 9:18:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Temp_recep.png | file://x:/photopub/docs/0000000389/9325761c-8e16-45c9-8606-ed87fb178005.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__717c39c4_f85b_4bb1_b72b_b6ba1401d922
ELIN-523170-2016 | EL-343349-2016 | 2/11/2016 11:03:05 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Grd_lug.png | file://x:/photopub/docs/0000000389/5ae10754-3619-4f19-95af-705183081b9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edcd6cb8_1566_4f05_b0ea_78691f99ddb6
ELIN-522346-2016 | EL-312376-2015 | 2/11/2016 10:12:54 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | PVC.png | file://x:/photopub/docs/0000000389/f2c0d7de-0986-4a3a-b394-5a5c1aee7644.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf4baa49_6dbd_46a2_812e_3266e19a8569
ELIN-525631-2016 | EL-303701-2015 | 2/11/2016 9:55:48 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Energized_outlet.png | file://x:/photopub/docs/0000000389/ac6278cf-ea1a-4018-8dc9-c02cd4ba90cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c94d509_db9b_4227_baf7_112742382213
ELIN-525631-2016 | EL-303701-2015 | 2/11/2016 9:55:48 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Perm_panel.png | file://x:/photopub/docs/0000000389/9e7d97d6-57bd-46e2-b431-ab4fc6324597.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c94d509_db9b_4227_baf7_112742382213
ELIN-525636-2016 | 5435035 | 2/11/2016 9:18:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Unapproved_splices.png | file://x:/photopub/docs/0000000389/3c45e01a-a12b-4db3-ab52-d54be8f42f57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__717c39c4_f85b_4bb1_b72b_b6ba1401d922
ELIN-525636-2016 | 5435035 | 2/11/2016 9:18:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | TCS_cables.png | file://x:/photopub/docs/0000000389/6cedba86-6726-44cb-9d69-0e9e4d63c785.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__717c39c4_f85b_4bb1_b72b_b6ba1401d922
ELIN-525636-2016 | 5435035 | 2/11/2016 9:18:19 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Panel_openings.png | file://x:/photopub/docs/0000000389/aa3e1af8-24b5-41a4-b4e2-6515b9bfefd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__717c39c4_f85b_4bb1_b72b_b6ba1401d922
BPVOP-531939-2016 | 2296936 | 2/23/2016 10:19:33 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 5.0 square meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it is determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000394/10e3ae4a-79ce-477c-810b-2f60edad4de5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ec35e77_202b_40bd_b3bd_aa611ce486d6
BPVOP-531931-2016 | 2296937 | 2/23/2016 11:25:28 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 5.0 square meters, Maximus Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it is determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000394/2dfa1a1f-8f40-4631-bb35-7d5736e8f72e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d407881_df24_49f2_868b_67e9c283902e
ELIN-525542-2016 | EL-179972-2014 | 2/12/2016 1:37:44 PM | ASSESS: EL: Final | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Outdoor 120/208V 100A Panel enclosure has not been provided with mechanical protection from vehicle traffic in parking area and has already been struck, this poses a shock risk and permanent mechanical damage and failure of equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Panel_enclosure.png | file://x:/photopub/docs/0000000390/da9f6c6c-7431-4c4c-95df-f74d67c74b02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b3beb9_1b42_4b37_9090_d35c959a240d
ELIN-525712-2016 | EL-279446-2015 | 2/12/2016 2:09:01 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | No evidence of approval on LED sign fed from a 15A 120V branch circuit. Without evidence of approval there is no assurance the product has been assembled or wired in a safe fashion, resulting in product failure. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Sign.png | file://x:/photopub/docs/0000000390/c45c5737-58e8-4d93-83c9-1b25f8923342.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97de51a1_a0da_419e_a10e_c7f57191a521
ELIN-528731-2016 | EL-339347-2016 | 2/17/2016 10:38:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The new bare #6 cu ground cable is run across the upper surface across a sidewalk (in expansion joint) and is not mechanically protected. This is subject to equipment damage and will become a tripping hazard for individuals | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_wire_in_crack_of_sidewalk.png | file://x:/photopub/docs/0000000393/7a35adc3-768d-4fa4-8ae5-f4ed1952694a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10d43b27_a032_4a52_ac9a_555185403732
ELIN-529532-2016 | EL-274061-2015 | 2/19/2016 10:59:53 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | The basement suite kitchen counters are short in quantity for the required 20 amp GFCI receptacles, this could create a thermal affect on the remaining circuits | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Suite_Kitchen__1.png | file://x:/photopub/docs/0000000393/e9ad2aaa-2cfe-413d-8db6-d41895cd7854.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48327975_aed4_4fdc_a3e0_753921cff637
ELIN-529532-2016 | EL-274061-2015 | 2/19/2016 10:59:53 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | The basement suite kitchen counters are short in quantity for the required 20 amp GFCI receptacles, this could create a thermal affect on the remaining circuits | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Suite_kitchen__2.png | file://x:/photopub/docs/0000000393/d3547112-e682-4f82-ab6d-4446390619e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48327975_aed4_4fdc_a3e0_753921cff637
BPVOP-531678-2016 | 4434714 | 2/19/2016 8:31:27 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Heat Exchanger with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 257*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject heat exchanger to pressure above MAWP if control fails or heat exchanger is operated inadvertently with valve on heat receiving side shut. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000394/9e32a1aa-e2d6-405a-ba0b-0d598ef963de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8cf392eb_f55a_4a1e_94de_e8712ad4292d
BPVOP-531681-2016 | 4434721 | 2/19/2016 9:22:57 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Heat Exchanger with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 257*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject heat exchanger to pressure above MAWP if control fails or heat exchanger is operated inadvertently with valve on heat receiving side shut. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000394/ae04b1c6-98f7-4fce-b7f0-b607a7be8638.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7ab3f65_67e4_4de4_9aa1_85c183a3cd4d
ELIN-518549-2016 | EL-335016-2016 | 2/1/2016 6:53:32 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | SO discovered a energized conductor at the elevation of the hood fan. The new cupboards were not installed at time of inspection. Owner stated he was responsible for the conductor being energized. If the wire cap was hit or fell off there would be a possibility of electric shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_conductor_totem_cres.png | file://x:/photopub/docs/0000000385/8ec553be-56ff-46ca-a63a-8a8ac75d5254.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bfaabad_93d8_423f_8046_fdd431a05543
GAIN-521971-2016 | GA-209969-2015 | 2/3/2016 9:35:42 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Pipe fittings into first stage regulator are not rated for tank pressure. Fittings could rupture causing gas leak and possible fire. | 3 | Non-compliant material/fittings installed | Fittings_.png | file://x:/photopub/docs/0000000389/3b41404a-4fa5-42ec-800f-f94e13f1cdd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__064a1708_746d_418b_9dc1_c4fcfe5536af
ELIN-481468-2015 | EL-203319-2015 | 11/30/2015 9:58:39 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL228 | All Classes, All Zones Area is classified: Guards, or shields are not observed. | 4 | 4 | Light fixtures in hangars must be guarded so accidental damage to a bulb or fixture cannot result in sparks or hot embers falling onto aircraft where fuel or fumes may be present. In this installation an unguarded type of fixture was installed throughout the hangar area. | 4 | All Classes, All Zones Area is classified: Guards, or shields are not observed. | Light_in_hangar.png | file://x:/photopub/docs/0000000359/fd3edcd4-d5a0-42c4-b6c6-8eb7534f715e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f562327_15f1_4e41_84a6_5b9b0bf60550
BPVOP-532143-2016 | 3113704 | 2/23/2016 1:50:21 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Heat Exchanger with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 230*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject heat exchanger to pressure above MAWP if control fails or heat exchanger is operated inadvertently with valve on heat receiving side shut. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve.png | file://x:/photopub/docs/0000000394/fd38f79e-dec9-460b-9196-79a72d5ea1cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3466797e_5cb1_4f49_81f7_0cfebc134ecb
ELIN-490845-2015 | EL-237534-2015 | 12/8/2015 1:30:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 240 v 30 a subdistribution panel supplying two 120 v gfci receptacles not protected from weather including receptacle covers | 3 | General Equipment is not approved for the specific use | Subdistribution.png | file://x:/photopub/docs/0000000363/e85dd164-e537-4487-9802-1f3a53b72712.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dcc4bd1_5381_45e7_bd7f_5616c4a843a9
ELIN-508319-2016 | EL-304507-2015 | 1/20/2016 9:31:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected portion of consumer service conductors exceeds 1.5m of total length inside structure exposing that portion of installation to an increased risk of mechanical damage. This portion of the consumer service is not protected by an overcurrent device and any resulting mechanical damage could result in serious personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View02_consumer_service_conductors.png | file://x:/photopub/docs/0000000381/0b8dc1b7-6f86-4126-bca7-e0c8badca3c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dccc7981_1266_4e74_8445_12f7d76c28e2
ELIN-513828-2016 | UW-336948-2016 | 1/20/2016 9:30:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Building electrical systems subject to catastrophic damage resulting from thermal event. The integrity of the installation has been severely compromised due to water and heat exposure. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | View04_302_entrance.png | file://x:/photopub/docs/0000000381/8ea2b71e-5bb4-48e3-a5b9-6c61e6eb1023.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2562f5af_cda0_4d64_816c_521356a10fe5
ELIN-513828-2016 | UW-336948-2016 | 1/20/2016 9:30:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Building electrical systems subject to catastrophic damage resulting from thermal event. The integrity of the installation has been severely compromised due to water and heat exposure. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | View03_second_floor_stairway.png | file://x:/photopub/docs/0000000381/714d4c8f-fe91-404f-acc7-8e150ec1c761.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2562f5af_cda0_4d64_816c_521356a10fe5
ELIN-513828-2016 | UW-336948-2016 | 1/20/2016 9:30:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Building electrical systems subject to catastrophic damage resulting from thermal event. The integrity of the installation has been severely compromised due to water and heat exposure. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | View02_302_branch_circuitry.png | file://x:/photopub/docs/0000000381/553c17d4-dfb5-4c4d-8e54-524d24ccb9b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2562f5af_cda0_4d64_816c_521356a10fe5
ELIN-513828-2016 | UW-336948-2016 | 1/20/2016 9:30:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Building electrical systems subject to catastrophic damage resulting from thermal event. The integrity of the installation has been severely compromised due to water and heat exposure. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | View01_302_distribution.png | file://x:/photopub/docs/0000000381/9cae6495-52a5-417c-aa56-64a6b37bf038.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2562f5af_cda0_4d64_816c_521356a10fe5
ELIN-508319-2016 | EL-304507-2015 | 1/20/2016 9:31:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected portion of consumer service conductors exceeds 1.5m of total length inside structure exposing that portion of installation to an increased risk of mechanical damage. This portion of the consumer service is not protected by an overcurrent device and any resulting mechanical damage could result in serious personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_consumer_service_conductors.png | file://x:/photopub/docs/0000000381/cd82dc14-2af7-43bf-a833-f37f283758d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dccc7981_1266_4e74_8445_12f7d76c28e2
ELIN-508319-2016 | EL-304507-2015 | 1/20/2016 9:31:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected portion of consumer service conductors exceeds 1.5m of total length inside structure exposing that portion of installation to an increased risk of mechanical damage. This portion of the consumer service is not protected by an overcurrent device and any resulting mechanical damage could result in serious personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View03_consumer_service_conductors.png | file://x:/photopub/docs/0000000381/37af236f-15dd-4a36-98f5-6a6d9aed7a07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dccc7981_1266_4e74_8445_12f7d76c28e2
ELIN-510598-2016 | EL-322472-2015 | 1/20/2016 9:31:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | Rigid type DB2 conduit installed above grade in an insulated wall and subject to mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. | View01_wireway.png | file://x:/photopub/docs/0000000381/46db6f4c-7e19-4f6d-84c3-ac1336770784.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b84b53dd_813b_4f42_9713_176adf1560a3
ELIN-528022-2016 | EL-346165-2016 | 2/18/2016 12:44:19 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | A meter enclosure operating in a 3 phase 100 amp 208 volt system was energized and fitted with makeshift flattened copper pipe jumpers. The meter enclosure was then covered with only the rain cover supplied by manufacturer to exclude rain prior to energization. This system was in a public access area and could have resulted in injury or worse to persons. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Jumpers_not_approved_and_energized.png | file://x:/photopub/docs/0000000394/8f386048-9c93-4aef-87b2-8124443661df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ea4e2c3_423b_4a96_b311_08147a675c72
ELIN-520996-2016 | EL-340346-2016 | 2/10/2016 10:54:36 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Non energized, exposed 120/240 volt 40 amp non-metallic sheathed cable conductors not normally accessible to persons. Over current device not locked out. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Exposed_hot_tub_conductors_.png | file://x:/photopub/docs/0000000389/8681e19c-8751-495d-b95d-d8886c6c39f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ae3b250_a42e_4391_b484_99470199a810
GAIN-497612-2015 | GA-326396-2015 | 1/12/2016 1:55:28 PM | ASSESS: GA: Final | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | Gas line is run under foundation and under slab. If building should settle, gas line crushed or damaged causing a gas leak which could result in fire or explosion | 3 | Underground piping entering a building below grade (unapproved) | Gas_lines.png | file://x:/photopub/docs/0000000377/bc4c4c6b-fd58-4d25-9bfb-e8861502045e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3203dc2_d50c_48e0_b1b1_bc7e2df043f9
GAIN-481906-2015 | GA-314016-2015 | 1/12/2016 1:55:24 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearances from regulator to ignition source not met. If the regulator should start to relieve and the generator started, the gas would more than likely ignite, causing an uncontrolled fire which could start nearby structures on fire | 3 | Clearance to combustible not met | Generator.png | file://x:/photopub/docs/0000000377/3b051c35-0884-4400-ad01-3064c14bac87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee385a3c_191e_477f_b7b6_bdc1a6fc947f
ELIN-530433-2016 | EL-269163-2015 | 2/22/2016 1:35:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The energized 15 amp 120 volt receptacles and lighting switches not include cover plates, this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_outlets.png | file://x:/photopub/docs/0000000394/14a97cd2-89b8-49ce-bad4-4acd3054c731.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff95adb2_68a6_4433_950a_74e3c3cee8ca
ELIN-487269-2015 | UW-319807-2015 | 11/30/2015 8:50:30 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | NMD90 cabling protruding from underneath baseboard heater exposed to mechanical damage directly beside the bath tub. Accidental contact with while stepping out of the bath tub could create both a shock and a thermal hazard to persons. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | NMD_cable_connection_to_baseboard_heater.png | file://x:/photopub/docs/0000000364/ba62b3e1-8b5b-461c-868a-2e13d32d6ddb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1116b314_1e20_442c_bffd_c1437006c910
ELIN-487269-2015 | UW-319807-2015 | 11/30/2015 8:50:30 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | NMD90 cabling protruding from underneath baseboard heater exposed to mechanical damage directly beside the bath tub. Accidental contact with while stepping out of the bath tub could create both a shock and a thermal hazard to persons. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Baseboard_heater_in_bathroom.png | file://x:/photopub/docs/0000000364/9947cf26-3a85-4ba8-822d-f5cddb1aa502.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1116b314_1e20_442c_bffd_c1437006c910
ELIN-489920-2015 | EL-321110-2015 | 12/9/2015 4:23:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The bonding conductor pulled from duplex meterbase was undersized and terminated in a service pullbox rather than extended through to panelboard and disconnect. No bonding bushings installed. This can create a shock hazard due to poor mechanical connections. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding_conductor_terminates_only_in_jb.png | file://x:/photopub/docs/0000000364/4451d290-3dff-4d9c-8964-8ce31dce2a07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe461e2f_ee86_49ee_a745_fa4fef27732a
ELIN-498301-2015 | EL-312175-2015 | 12/21/2015 2:51:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | Boxes over 4 inches require support on two sides. This assessment found the dryer box to be supported on only one side. The dryer receptacle will be subject to damage due to the force required to insert the dryer cord. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Dryer_receptacle.png | file://x:/photopub/docs/0000000369/192f6a0f-cabd-40e0-976c-6bea62b25647.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55a25322_508a_4016_ab57_1971b497f989
ELIN-498301-2015 | EL-312175-2015 | 12/21/2015 2:51:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | Boxes over 4 inches require support on two sides. This assessment found the dryer box to be supported on only one side. The dryer receptacle will be subject to damage due to the force required to insert the dryer cord. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | gas_receptacle.png | file://x:/photopub/docs/0000000369/bd945256-c110-49b2-9bc5-db3ee3a94c75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55a25322_508a_4016_ab57_1971b497f989
530378-2016 | EL-326386-2015 | 2/19/2016 9:48:33 AM | ASSESS: EL: Final | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables run where they will be walked on during attic access, no connector used is panel | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Cables_attic.png | file://x:/photopub/docs/0000000393/bce18e03-4f2e-4b76-be8f-90eb681b91a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55e75f2f_4728_4dc3_ac9a_89f45cfef832
530378-2016 | EL-326386-2015 | 2/19/2016 9:48:33 AM | ASSESS: EL: Final | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Cables run where they will be walked on during attic access, no connector used is panel | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | No_connector.png | file://x:/photopub/docs/0000000393/2f9b326c-85e8-49f8-9245-6c030eff3a2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55e75f2f_4728_4dc3_ac9a_89f45cfef832
ELIN-525421-2016 | EL-338964-2016 | 2/18/2016 2:29:42 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | A gas furnace operating on a 120 volt 15 amp circuit has not been provided a disconnect switch in a location that is not too close to furnace. When the furnace switch is located too close to the furnace persons can be injured when trying to turn off power in an emergency. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | Furnace_switch_over_top_of_furnace.png | file://x:/photopub/docs/0000000394/a28d8132-7081-40b7-b566-073377760c03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__425f23e4_e2f0_4cce_b48b_996a3b376351
BPVOP-504717-2016 | 3938392 | 1/5/2016 1:34:07 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP222 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | 3 | 2 | Upon assessment of Domestic hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 240*Fahrenheit I did not find a shut of valve on boiler outlet of a single boiler system. Flushing of hot water in the long length of pipe may cause burning of personnel carrying out maintenance when boiler is shutdown for maintenance and not given enough time for water in piping system to cool off. | 3 | 1.2.3 Boiler construction - Code required drain or blow off not provided. | No_shutoff_valve_on_boiler_outlet.png | file://x:/photopub/docs/0000000374/b6715c52-f371-4389-842c-411e6a6e7c3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9861031e_2258_4803_b6a3_d19f0e499f9d
ELOP-268654-2014 | EL-057352-2013 | 12/7/2015 7:36:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Open box covers with energized controls and wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Feeder-loose.png | file://x:/photopub/docs/0000000363/b66a3c8c-4e2c-40a9-8b11-ef54981f87bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b851ff76_d64d_4291_bf57_a56ccf2596f1
ELOP-268654-2014 | EL-057352-2013 | 12/7/2015 7:36:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Open box covers with energized controls and wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Loose_box.png | file://x:/photopub/docs/0000000363/c7a53f2b-78c0-4850-b5fe-38c19e1358cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b851ff76_d64d_4291_bf57_a56ccf2596f1
ELOP-268654-2014 | EL-057352-2013 | 12/7/2015 7:36:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Open box covers with energized controls and wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Box-1.png | file://x:/photopub/docs/0000000363/385657a3-6698-4c61-a4a9-977911673a89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b851ff76_d64d_4291_bf57_a56ccf2596f1
ELOP-268654-2014 | EL-057352-2013 | 12/7/2015 7:36:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Open box covers with energized controls and wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Loose-BX.png | file://x:/photopub/docs/0000000363/7732b36a-82a0-46fa-8667-a2205fd22801.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b851ff76_d64d_4291_bf57_a56ccf2596f1
ELIN-487655-2015 | EL-299767-2015 | 12/4/2015 10:02:17 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized electrical parts are required to be mechanically protected to prevent shock and equipment damage should energized parts be contacted by persons and or conductive material. During a rough wire inspection, 240volt temporary construction electrical panels were discovered with unused openings. As a result, energized parts were exposed. One panel was located outside of the building and was wet at time of inspection. This creates a risk to both persons and property should contact be made with energized parts. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Interior_of_satellite_panel__Exposed_energized_buss.png | file://x:/photopub/docs/0000000361/44d899d4-7b4a-4db3-ac2e-ea452c0b2818.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf610513_b567_409c_988b_0b6d93f38444
ELIN-487655-2015 | EL-299767-2015 | 12/4/2015 10:02:17 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized electrical parts are required to be mechanically protected to prevent shock and equipment damage should energized parts be contacted by persons and or conductive material. During a rough wire inspection, 240volt temporary construction electrical panels were discovered with unused openings. As a result, energized parts were exposed. One panel was located outside of the building and was wet at time of inspection. This creates a risk to both persons and property should contact be made with energized parts. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exterior_of_satellite_panel.png | file://x:/photopub/docs/0000000361/df8c130c-ce17-4d2f-b50b-ef0d7d2042eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf610513_b567_409c_988b_0b6d93f38444
BPVOP-526587-2016 | 2277970 | 2/23/2016 12:27:56 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion_.png | file://x:/photopub/docs/0000000394/7b9768ae-b24b-4862-9ec9-3f6e9a18259a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8b78a93_695d_419e_b42f_18c35bf5d0c3
BPVOP-517448-2016 | 2250758 | 2/23/2016 10:13:09 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | Boiler must be watertight in order to hold pressure. I found a crack in the bottom of the tubesheet of this low pressure steam boiler, which is about 5 inches long and leaking water. Potential exists for an incident due to this crack. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Crack_.png | file://x:/photopub/docs/0000000394/fbe21513-c1e8-4b36-8565-fcd59933d4a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23a417d8_f33e_429a_81d2_e709b55731b7
ELIN-512129-2016 | EL-333022-2016 | 1/19/2016 7:11:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | 120/240 volt 100 amp new service has ground conductor not terminated on identified conductor. This thermal hazard. | 4 | Installation Grounding; conductor is not continuous. | Ground_conductor_not_terminated_identified_conductor.png | file://x:/photopub/docs/0000000380/b66d2121-9378-44b8-abe5-d4cfb68d490b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d35c978c_7915_47b2_86e3_840916c536c0
ELIN-530657-2016 | EL-318456-2015 | 2/22/2016 9:14:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 200 amp, 120/240 volt de-energized main distribution panel has cover removed. Bus bars accessible to persons. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel_cover_not_installed.png | file://x:/photopub/docs/0000000394/7dff18eb-01d7-4a8b-93e0-ddda86516c41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c682261_0b10_4d21_aa55_fc0ec77a28c5
ELIN-484960-2015 | UW-318151-2015 | 11/27/2015 3:44:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found 120 volt receptacle outlet with damaged electrical equipment and exposed energized conductors that were unsafe and non-compliant behind kitchen range. When electrical equipment is energized and is damaged, unsafe and non-compliant then the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Damaged_exposed_conductors_unsafe_and_non-compliant_behind_range_3.png | file://x:/photopub/docs/0000000358/7efb4378-e132-4582-92c3-2bf675f66a61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c514d810_ad21_413e_aae2_d009b0b7931a
ELIN-484960-2015 | UW-318151-2015 | 11/27/2015 3:44:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found 120 volt receptacle outlet with damaged electrical equipment and exposed energized conductors that were unsafe and non-compliant behind kitchen range. When electrical equipment is energized and is damaged, unsafe and non-compliant then the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Damaged_exposed_conductors_unsafe_and_non-compliant_behind_range1.png | file://x:/photopub/docs/0000000358/86581eab-28ca-4ab4-8f5c-492d8f88fa98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c514d810_ad21_413e_aae2_d009b0b7931a
ELIN-484960-2015 | UW-318151-2015 | 11/27/2015 3:44:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found 120 volt receptacle outlet with damaged electrical equipment and exposed energized conductors that were unsafe and non-compliant behind kitchen range. When electrical equipment is energized and is damaged, unsafe and non-compliant then the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Damaged_exposed_conductors_unsafe_and_non-compliant_behind_range_4.png | file://x:/photopub/docs/0000000358/2818cf75-d22a-4449-ae2d-2e05cb56551e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c514d810_ad21_413e_aae2_d009b0b7931a
ELIN-484960-2015 | UW-318151-2015 | 11/27/2015 3:44:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found 120 volt receptacle outlet with damaged electrical equipment and exposed energized conductors that were unsafe and non-compliant behind kitchen range. When electrical equipment is energized and is damaged, unsafe and non-compliant then the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Damaged_exposed_conductors_unsafe_and_non-compliant_behind_range_2.png | file://x:/photopub/docs/0000000358/1414e881-7229-4b6d-814c-0a254d166d98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c514d810_ad21_413e_aae2_d009b0b7931a
BPVIN-527428-2016 | UW-345843-2016 | 2/15/2016 12:13:26 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | Upon assessment of expansion tank (dimensions: length-1.50meter and diameter-0.46meter) with Maximum Allowable Working Pressure of 125psig it is determined that vessel is not firmly anchored to floor or braced. In the event of earthquake of significant scale vessel may trip or move and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | EXPANSION_TANK_WITHOUT_ANCHOR_BOLT_OR_BRACE.png | file://x:/photopub/docs/0000000391/eef0980a-f0a8-4547-9bbd-e5263f7bd5ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a697457d_60a3_4197_91b7_a4916304d465
BPVOP-527395-2016 | 2297541 | 2/15/2016 1:59:49 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment of Hot Water Boiler with Heating surface area of 5square meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it was determined that flow switch is installed on boiler inlet. If there is no flow switch installed on boiler outlet piping, there would be no way to detect minimum flow as required to prevent overheating of coil or fin-tube and consequently failure of coil or fin-tube may result. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | FLOW_SWITCH_ON_BOILER_INLET_SIDE.png | file://x:/photopub/docs/0000000391/3fb803a4-7c43-47ea-9377-387d74902e33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68a4b7d3_ff4f_4a82_9b39_d61b7cf0370f
BPVOP-527393-2016 | 2297546 | 2/15/2016 12:59:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment of Hot Water Boiler with Heating surface area of 5 square meters, Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it was determined that flow switch is installed on boiler inlet. If there is no flow switch installed on boiler outlet piping, there would be no way to detect minimum flow as required to prevent overheating of coil or fin-tube and consequently failure of coil or fin-tube may result. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | FLOW_SWITCH_ON_BOILER_INLET.png | file://x:/photopub/docs/0000000391/0b0507d2-cf20-4e1d-ad92-a4454fd819f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dbd01e5_e376_44e6_b375_924e6f90a53f
ELIN-501064-2015 | EL-325400-2015 | 12/30/2015 1:16:05 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 100A 240V main neutral has not been grounded in the main panel, without proper grounding the breakers may fail to operate posing a shock and fire hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding.png | file://x:/photopub/docs/0000000372/994b4d53-7059-4f7c-a103-b6fcc2eb2fc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc95260b_0ac7_4374_be2d_4e9769dfbe1d
ELOP-195672-2014 | 1214 | 12/11/2015 3:08:52 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Elecrical cables must be approved for use. In this installation cables not approved for use outdoors and which pass through metal soffits without protection were observed. | 3 | Conductors Equipment is not approved for the specific use. | NMS_through_soffit.png | file://x:/photopub/docs/0000000365/59263b0d-c562-4133-933e-d7dd83bcad2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9627151f_78ab_4ba1_88b7_c90c67b88800
ELOP-195927-2014 | 1209 | 12/11/2015 3:08:54 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 3 | Elecrical equipment must be maintained in good working order. Here the high level warning light on top of a sewage lift kiosk is broken. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | North_side.png | file://x:/photopub/docs/0000000365/504c851c-d8cb-4b28-b686-5a0783ba0fb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ee8f429_bebb_49c9_abca_6693d650457c
ELIN-529436-2016 | EL-300736-2015 | 2/22/2016 8:25:27 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | The bonding conductor installed was not insulated. This could cause a fire if a lightning strike was to occur due to the bonding conductor not being insulated. The bonding conductor without insulation could heat up enough to cause combustible material to catch fire. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding_conductor.png | file://x:/photopub/docs/0000000394/be2fefb4-054f-46a6-9ab6-113a7a8e1f33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2fb8cf5_9ede_4c59_a68e_14a0d15e181c
ELIN-485029-2015 | EL-311800-2015 | 12/3/2015 10:56:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | A new 200amp 1phase 120/240 service brought into an older relocatable structure has the existing system ground conductor attached to the new grounding conductor with a copper split bolt. This is a thermal hazard. | 4 | Installation Grounding; conductor is not continuous. | Ground_splice.png | file://x:/photopub/docs/0000000363/8e44d072-f1b7-43fc-8c1f-e96caba068b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00f6402f_c75a_42af_963c_4636671d0f88
ELIN-531573-2016 | UW-349365-2016 | 2/22/2016 9:29:10 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Main electrical panel is exposed with circuits not connected correctly and circuit breakers hanging out of panel. Exposed to shock. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_main_panel.png | file://x:/photopub/docs/0000000394/078022c4-6f36-406b-9069-dbcacfb7eb86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4b74510_9e75_4c03_a5d0_f7b2ccced480
ELIN-531295-2016 | UW-349094-2016 | 2/22/2016 11:21:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Un-used openings in energized electrical panels are required to have approved fillers and or plugs installed. This is to ensure persons and or conductive material does not come into contact with energized parts. During an inspection of a greenhouse, the attending safety officer discovered a 600 volt, 400 amp electrical panel which was missing a filler in one of the breaker positions. As such, energized buss was exposed. This poses a shock hazard should a person come into contact with the energized parts of this panel. In addition, should conductive material come into contact with the energized parts a fault condition could occur. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | front_of_panel.png | file://x:/photopub/docs/0000000394/c55a136d-d09b-4258-806a-4bebd9882d93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f04f68cf_ce8c_493c_a599_7b82c05f47a0
ELIN-531295-2016 | UW-349094-2016 | 2/22/2016 11:21:00 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Un-used openings in energized electrical panels are required to have approved fillers and or plugs installed. This is to ensure persons and or conductive material does not come into contact with energized parts. During an inspection of a greenhouse, the attending safety officer discovered a 600 volt, 400 amp electrical panel which was missing a filler in one of the breaker positions. As such, energized buss was exposed. This poses a shock hazard should a person come into contact with the energized parts of this panel. In addition, should conductive material come into contact with the energized parts a fault condition could occur. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Missing_filler_exposed_buss.png | file://x:/photopub/docs/0000000394/04ea0919-50c4-4675-9ac0-45c7dcecb78c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f04f68cf_ce8c_493c_a599_7b82c05f47a0
ELIN-520347-2016 | EL-292353-2015 | 2/4/2016 12:42:45 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Walls were completed before a assessment was performed. | 0 | No Created Hazard Identified | Finished_wall_-2.png | file://x:/photopub/docs/0000000389/4c392ac0-cd50-4013-a9c8-0a7e83f21ac1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__335095c9_668e_45fb_82b8_66c78e4a5517
ELIN-520347-2016 | EL-292353-2015 | 2/4/2016 12:42:45 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Walls were completed before a assessment was performed. | 0 | No Created Hazard Identified | Panel_with_finished_wall.png | file://x:/photopub/docs/0000000389/fb66b8e8-f101-40de-b611-2aee850bd349.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__335095c9_668e_45fb_82b8_66c78e4a5517
BPVOP-525671-2016 | BPV-041265-2013 | 2/2/2016 10:08:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | The boiler casing is a gas-tight structure surrounding the components of the boiler. I found water leaking by on the right side boiler case panel. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 5.1.0 In service proc/process - Casing leakage | Boiler_leaking_.png | file://x:/photopub/docs/0000000389/57c216e5-4eaa-4721-ac44-257dac0e07bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d17eeb61_4448_4e98_9b54_f221f91c48f2
BPVOP-525671-2016 | BPV-041265-2013 | 2/2/2016 10:08:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | The boiler casing is a gas-tight structure surrounding the components of the boiler. I found water leaking by on the right side boiler case panel. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 5.1.0 In service proc/process - Casing leakage | Boiler_data_plate_.png | file://x:/photopub/docs/0000000389/44f2ad46-76a1-475c-9071-06245b6789ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d17eeb61_4448_4e98_9b54_f221f91c48f2
BPVOP-525671-2016 | BPV-041265-2013 | 2/2/2016 10:08:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | The boiler casing is a gas-tight structure surrounding the components of the boiler. I found water leaking by on the right side boiler case panel. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 5.1.0 In service proc/process - Casing leakage | Boiler_leakage_.png | file://x:/photopub/docs/0000000389/6f68dc12-c3d2-4248-8416-d1d96964576f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d17eeb61_4448_4e98_9b54_f221f91c48f2
BPVOP-525671-2016 | BPV-041265-2013 | 2/2/2016 10:08:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP189 | 5.1.0 In service proc/process - Casing leakage | 4 | 4 | The boiler casing is a gas-tight structure surrounding the components of the boiler. I found water leaking by on the right side boiler case panel. This can lead to degradation of the boiler that could interfere from proper operation. | 4 | 5.1.0 In service proc/process - Casing leakage | Cleaver_Brooks_boiler_.png | file://x:/photopub/docs/0000000389/91709d3a-b4fa-4ec9-b640-f78915354770.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d17eeb61_4448_4e98_9b54_f221f91c48f2
ELIN-531385-2016 | EL-335824-2016 | 2/23/2016 2:24:11 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 2 | Service acwu inside house is more than 1.5m without concrete encasement. This increases risk of conductor damage and overheating. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Cables_below_meterbase.png | file://x:/photopub/docs/0000000394/0ade486b-5e6c-46f4-bb64-131db7c2805a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdbf30ae_8933_4540_b735_3960784d4d46
GAIN-530524-2016 | GA-301779-2015 | 2/23/2016 2:23:15 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Water heater installed in an alcove with a closing door. When the door is closed the appliance does not meet its 6" clearance to combustibles to the font of the appliance. Reduced clearances to combustibles may result in fire. | 3 | Clearance to combustible not met | Water_heater.png | file://x:/photopub/docs/0000000394/640e59cb-3a60-4b4e-a759-bc98a3eb420d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8193f46b_f4c7_4650_8d70_d4bd83bae863
ELIN-519071-2016 | EL-282504-2015 | 2/22/2016 9:40:29 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | 208 volt outlet box is missing cover plate. This is a thermal hazard should conductors receive damage. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Outlet_box_missing_cover_plate.png | file://x:/photopub/docs/0000000394/9141df94-0ac1-49d8-a739-4021c598973d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5057201_f665_4cc2_8dc3_3f5e97be01d7
ELIN-530355-2016 | EL-287520-2015 | 2/22/2016 11:54:56 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Energized 120 volt, 15 amp switch outlet box without cover plate installed located in an area it is not accessible to the public. This is a shock hazard should someone make accidental contact with the exposed terminals. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Exposed_terminals_outlet_box.png | file://x:/photopub/docs/0000000394/544d254a-1025-4d36-825b-a6b2c0b9e8d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30210712_f209_4da2_92a9_319e5450817f
ELIN-530665-2016 | EL-348540-2016 | 2/22/2016 1:35:18 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 120 volt multi-gang outlet boxes protected by 15 amp overcurrent devices are installed with support on one side only. This is a thermal issue. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Multi-gang_outlet_boxes.png | file://x:/photopub/docs/0000000394/5bc9dd72-0240-4d58-b0db-e765a3c18b58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c02afc1_29e6_42f0_8246_60a434452869
ELIN-505710-2016 | EL-331644-2016 | 1/11/2016 8:39:18 AM | ASSESS: EL: Final | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 120 V 15 amp receptacle located at living rm floor level is damaged exposing bare parts. There is a shock hazard given there is small children playing near the receptacle. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Damaged_receptacle.png | file://x:/photopub/docs/0000000376/a49eeaf3-33d6-45c4-91db-c9d407ebe8c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff7d57c1_1348_4a10_9404_edd971214b99
ELIN-505710-2016 | EL-331644-2016 | 1/11/2016 8:39:18 AM | ASSESS: EL: Final | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The 120 V 15 amp receptacle located at living rm floor level is damaged exposing bare parts. There is a shock hazard given there is small children playing near the receptacle. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Panel.png | file://x:/photopub/docs/0000000376/e5da13f4-e88c-4cb3-ab2a-c224c05c40d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff7d57c1_1348_4a10_9404_edd971214b99
ELIN-529062-2016 | EL-346562-2016 | 2/22/2016 9:18:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | Underground consumer service raceway is installed without adequate protection from mechanical damage for portion above grade. This poses a serious risk of personal injury (shock) or property damage (thermal event) as this portion of the consumer service is not protected by a main disconnecting means that would de-energize the system during a fault condition. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Detail02_consumer_service_raceway.png | file://x:/photopub/docs/0000000394/922d4de5-871b-4bba-afc6-954138a21925.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e4d76c8_7ba5_41ed_b89a_5b9a3ca73b26
ELIN-529062-2016 | EL-346562-2016 | 2/22/2016 9:18:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | Underground consumer service raceway is installed without adequate protection from mechanical damage for portion above grade. This poses a serious risk of personal injury (shock) or property damage (thermal event) as this portion of the consumer service is not protected by a main disconnecting means that would de-energize the system during a fault condition. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | View01_consumer_service_equipment.png | file://x:/photopub/docs/0000000394/41ff1370-abe7-4ec8-85cb-d7659cc7eddd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e4d76c8_7ba5_41ed_b89a_5b9a3ca73b26
ELIN-489703-2015 | EL-319739-2015 | 12/7/2015 5:52:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | Energized panel with cover missing and with 40A breaker back feeding new service, installer is unknown. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Energized_panel.png | file://x:/photopub/docs/0000000363/b8c8b9f7-a81b-4341-8e9d-df52e4ce0c81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f79a8d8_3a8e_4a2b_8013_573e512d9227
ELIN-529731-2016 | EL-347249-2016 | 2/22/2016 2:51:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 2 | Enclosure is required to be weathertight, as per CEC 76-008 2012 | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | TCS_Enclosure.png | file://x:/photopub/docs/0000000394/3cf558d1-4c4b-46c9-85f3-4fde4a7d4185.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3c4fa55_0505_420e_83c3_b9ce742d077e
ELOP-226766-2014 | EL-084132-2014 | 2/3/2016 5:40:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused openings were observed in 600 volt equipment. These must be closed to avoid accidental introduction of conducting materials into the cabinet works. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Distribution_600_volt.png | file://x:/photopub/docs/0000000386/d881d0ec-20b4-4e14-858c-f48e0c7a9746.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b620eb3_950c_461c_9668_2f984db91374
ELOP-191129-2014 | 3915713 | 2/3/2016 5:39:23 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | This installation includes a coin-operated electrical control for a public shower. The bond conductor to the metal actuator was omitted. Metal boxes must be bonded to ground to avoid shock hazards. This part of the installation was installed perhaps 15 years ago and was not easily seen during normal inspection. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Actuator.png | file://x:/photopub/docs/0000000386/36257a04-43ce-4a2d-a187-299b941a4067.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9edf3a_efd5_462a_a0e3_cbad8b2a4c3b
ELOP-191129-2014 | 3915713 | 2/3/2016 5:39:23 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | This installation includes a coin-operated electrical control for a public shower. The bond conductor to the metal actuator was omitted. Metal boxes must be bonded to ground to avoid shock hazards. This part of the installation was installed perhaps 15 years ago and was not easily seen during normal inspection. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Power_supply_above_electric_valve.png | file://x:/photopub/docs/0000000386/8ca34d5b-0117-45f4-be67-d895d2456584.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df9edf3a_efd5_462a_a0e3_cbad8b2a4c3b
GAUP-505590-2016 | UW-331962-2016 | 1/6/2016 8:55:56 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA116 | Supports/termination present, but not in compliance with mfg instructions | 1 | 1 | When in operation for gas fumes from the furnace vent termination were being drawn in through the make up air into the building | 1 | Supports/termination present, but not in compliance with mfg instructions | 20378_88.png | file://x:/photopub/docs/0000000374/bf79e3a3-f55a-4e0a-bc91-0a20a7db6403.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d5c9b0c_228a_4702_8ce7_a21c22cbe562
GAUP-505590-2016 | UW-331962-2016 | 1/6/2016 8:55:56 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA116 | Supports/termination present, but not in compliance with mfg instructions | 1 | 1 | When in operation for gas fumes from the furnace vent termination were being drawn in through the make up air into the building | 1 | Supports/termination present, but not in compliance with mfg instructions | 20378_88_after_picture.png | file://x:/photopub/docs/0000000374/7be4e6d3-e69b-41ff-9526-7dabf9a1e213.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d5c9b0c_228a_4702_8ce7_a21c22cbe562
ELIN-520403-2016 | UW-341775-2016 | 2/1/2016 7:52:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found unapproved, damaged, unsafe and non-compliant temporary construction 120/240volt 100a panelboard in wooden enclosure which had energized exposed bus bars due to covers missing on bus bars. When temporary electrical equipment is unapproved, damaged, unsafe and non-compliant this electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Energized_exposed_bus_bars_and_damaged_equipment_2.png | file://x:/photopub/docs/0000000385/2b0b0be2-85b6-46fc-ad80-ad537f6e4a4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bee25fa_465e_441a_97f7_00652304f8ba
ELIN-520403-2016 | UW-341775-2016 | 2/1/2016 7:52:34 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found unapproved, damaged, unsafe and non-compliant temporary construction 120/240volt 100a panelboard in wooden enclosure which had energized exposed bus bars due to covers missing on bus bars. When temporary electrical equipment is unapproved, damaged, unsafe and non-compliant this electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Energized_exposed_bus_bars_1.png | file://x:/photopub/docs/0000000385/f809eba6-6541-4263-9498-07c39a9895ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bee25fa_465e_441a_97f7_00652304f8ba
ELIN-489802-2015 | EL-319600-2015 | 12/10/2015 4:01:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | The 100 amp, 120/240 volt connection termination box for the mobile home is not securely supported to allow for safe clearance for access. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Trailer_connection_box_.png | file://x:/photopub/docs/0000000365/0cd31d25-28bd-4692-b749-fe06cea4ff46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1307ec0_c000_4760_9d5a_60ec52c742b8
ELIN-491022-2015 | EL-322238-2015 | 12/10/2015 4:00:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | 3 “ DBII Residential Service Entry Conduit is installed above grade. No mechanical protection has been provided. Conduit is subject to damage and breakage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | DB_2_raceway_above_grade.png | file://x:/photopub/docs/0000000365/0c4e0a8f-cd43-4867-a181-350bf25633c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1085783_e092_4522_8e7b_450239705b03
GAIN-530071-2016 | GA-329361-2015 | 2/22/2016 11:34:18 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Rinnai_Term.png | file://x:/photopub/docs/0000000394/9822573a-0ef7-4017-8ad4-408ee645b590.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__638a5ea4_8b19_4b59_9e7e_cdd43592d4ac
ELIN-500538-2015 | EL-279371-2015 | 12/23/2015 12:54:45 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | The backside mounting holes of the NEMA 1 disconnect are exposed to weather and open to insects (bees) to build nests within enclosure, this is both a shock hazard and can lead to equipment damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | EV_charger_disconnect.png | file://x:/photopub/docs/0000000372/d0f50026-5cef-48cb-9213-c4c00bbbb8b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__619eb2a9_6de3_4cdc_95af_585545d3704d
ELIN-500538-2015 | EL-279371-2015 | 12/23/2015 12:54:45 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | The backside mounting holes of the NEMA 1 disconnect are exposed to weather and open to insects (bees) to build nests within enclosure, this is both a shock hazard and can lead to equipment damage. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Exterior_view_EV_disconnect.png | file://x:/photopub/docs/0000000372/f85e0e74-6a4f-4182-bb98-a5e604c7210b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__619eb2a9_6de3_4cdc_95af_585545d3704d
ELIN-531216-2016 | EL-309410-2015 | 2/23/2016 12:42:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | 120/240 volt unfused Armored cables have been installed less than the required minimum clearance distances to ensure no mechanical damage could occur. Left unprotected the cables could be damaged at the time of concealment therefore creating a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Suite_supply_cable.png | file://x:/photopub/docs/0000000394/8311ff61-1528-4a70-a3c2-57c5fa3b6c1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02abeeb4_3f3c_4780_821a_a0d295d3fa9f
ELIN-531216-2016 | EL-309410-2015 | 2/23/2016 12:42:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | 120/240 volt unfused Armored cables have been installed less than the required minimum clearance distances to ensure no mechanical damage could occur. Left unprotected the cables could be damaged at the time of concealment therefore creating a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Main_house_supply_cable.png | file://x:/photopub/docs/0000000394/8fd0c63e-10f7-4aab-8f2d-d9a575ce0e2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02abeeb4_3f3c_4780_821a_a0d295d3fa9f
ELIN-530457-2016 | EL-307444-2015 | 2/23/2016 1:09:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Magnetic material has been used to protect the main system ground wire and under a fault condition this creates potential encircling magnetic fields which increases the inductive voltage drop, thus increasing conductor impedance. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Bond_bushings_missing_.png | file://x:/photopub/docs/0000000394/ebece6db-47f9-4b6c-ba67-8081cc82cb96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a89fe7ae_de00_400b_916a_05b13771c757
ELIN-495396-2015 | UW-325848-2015 | 12/10/2015 1:51:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | The 200 amp main service panel cover was removed and this exposed the energized bus. The area is accessible to persons and the exposed bus is a potential shock hazard to anyone in the area. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Main_Panel.png | file://x:/photopub/docs/0000000367/05c7ef76-05ac-43e5-bfd0-1b7283ddf5c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22df5320_bef3_47c9_94b7_a388723e1952
ELIN-495396-2015 | UW-325848-2015 | 12/10/2015 1:51:01 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | The 200 amp main service panel cover was removed and this exposed the energized bus. The area is accessible to persons and the exposed bus is a potential shock hazard to anyone in the area. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Existing_feed_to_Heater.png | file://x:/photopub/docs/0000000367/4981cbe7-0754-4284-91eb-659ca5280bfd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22df5320_bef3_47c9_94b7_a388723e1952
ELIN-512746-2016 | UW-336286-2016 | 1/27/2016 4:45:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | A 120volt 15amp receptacle, in a residential basement suite, is installed so that it sticks out of the wall greater than 6mm. This is an equipment damage hazard. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Fireplace_outlet.png | file://x:/photopub/docs/0000000383/e08ddff4-d9aa-4b3a-bb42-82ceda9a5dc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9a89939_4ecf_42f2_8db8_5a11de175d75
ELIN-512746-2016 | UW-336286-2016 | 1/27/2016 4:45:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | A 120volt 15amp receptacle, in a residential basement suite, is installed so that it sticks out of the wall greater than 6mm. This is an equipment damage hazard. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | No_mechanical_protection.png | file://x:/photopub/docs/0000000383/148ce60c-9a32-49af-ae15-d22e68a051b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9a89939_4ecf_42f2_8db8_5a11de175d75
ELIN-512746-2016 | UW-336286-2016 | 1/27/2016 4:45:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | A 120volt 15amp receptacle, in a residential basement suite, is installed so that it sticks out of the wall greater than 6mm. This is an equipment damage hazard. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Take_your_pick.png | file://x:/photopub/docs/0000000383/9fa8c582-e4ae-4314-91b5-ca8c5025110c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9a89939_4ecf_42f2_8db8_5a11de175d75
ELIN-512746-2016 | UW-336286-2016 | 1/27/2016 4:45:43 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL144 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | 4 | 4 | A 120volt 15amp receptacle, in a residential basement suite, is installed so that it sticks out of the wall greater than 6mm. This is an equipment damage hazard. | 4 | Installation of electrical equipment Boxes in walls or ceilings are not flush (or within 6 mm of finished surface); | Counter_circuit.png | file://x:/photopub/docs/0000000383/69105a66-451e-47a1-9472-f76ec7f42f9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9a89939_4ecf_42f2_8db8_5a11de175d75
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 1.png | file://x:/photopub/docs/0000000379/9daa5541-e26b-44d6-920f-7ec6c89d7d19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 2.png | file://x:/photopub/docs/0000000379/b7d66a8f-7725-400a-913e-ec83c6a8b1d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 5.png | file://x:/photopub/docs/0000000379/efe0c348-003f-415e-9bb4-11474805ab9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 6.png | file://x:/photopub/docs/0000000379/55dff9ea-fe41-4b53-a96e-5e11093339b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 4.png | file://x:/photopub/docs/0000000379/5879a1d4-c018-4209-9f4e-7da3cd64da6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-480165-2015 | EL-243828-2015 | 1/18/2016 4:17:17 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Found 2 sets of parallel feeder conductors size 250 KCM AWG copper run from its termination on 600volt 600 amp rated 3 phase breaker which feeds 450 KVAR rated 3 phase capacitor bank. The conductor rating of parallel feeders run is too small size of conductors and are not properly sized for 75 degree Celsius rated breaker and equipment. When equipment is not adequately sized and rated as required by code, then electrical equipment could become overloaded, overheat and possibly cause an electrical fire. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3.png | file://x:/photopub/docs/0000000379/91f353e4-d3e3-4831-bea7-b24686e2303e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc65adcb_d929_4e4b_9a49_f8a0d00ebb4b
ELIN-518830-2016 | UW-337447-2016 | 2/1/2016 7:42:42 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 3 | The exposed splice is a shock hazard. The cables are not supported and the marrets can work loose and fall off. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Splice_for_furnace_feed.png | file://x:/photopub/docs/0000000385/1039edee-2460-4247-8d2a-9e13e99ff193.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__556f2e4f_b0be_4495_a6a0_c622c8f669ab
ELIN-528438-2016 | EL-338013-2016 | 2/16/2016 6:43:41 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found branch circuit conductors and receptacle devices hanging out exposed from outlet boxes and have no covers installed on receptacles outlet boxes as required for final completion of all electrical work and equipment. When electrical equipment is not fully installed and fully completed (with receptacle devices bolted into outlet boxes and with covers on the branch circuit conductors) are not safe to connect to energized power supply system because this would be an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 2.png | file://x:/photopub/docs/0000000392/aaee63b7-1e29-4489-910e-4f13a0725459.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8922b6_08fb_4bd9_b599_ef12d2d7372e
ELIN-528438-2016 | EL-338013-2016 | 2/16/2016 6:43:41 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found branch circuit conductors and receptacle devices hanging out exposed from outlet boxes and have no covers installed on receptacles outlet boxes as required for final completion of all electrical work and equipment. When electrical equipment is not fully installed and fully completed (with receptacle devices bolted into outlet boxes and with covers on the branch circuit conductors) are not safe to connect to energized power supply system because this would be an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 1.png | file://x:/photopub/docs/0000000392/78a339ec-e436-4057-bfbf-70ed1cfdaf3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8922b6_08fb_4bd9_b599_ef12d2d7372e
ELIN-528438-2016 | EL-338013-2016 | 2/16/2016 6:43:41 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found branch circuit conductors and receptacle devices hanging out exposed from outlet boxes and have no covers installed on receptacles outlet boxes as required for final completion of all electrical work and equipment. When electrical equipment is not fully installed and fully completed (with receptacle devices bolted into outlet boxes and with covers on the branch circuit conductors) are not safe to connect to energized power supply system because this would be an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 3.png | file://x:/photopub/docs/0000000392/bf30d73e-32ff-4a81-97c8-7318433daa95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8922b6_08fb_4bd9_b599_ef12d2d7372e
ELIN-528438-2016 | EL-338013-2016 | 2/16/2016 6:43:41 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found branch circuit conductors and receptacle devices hanging out exposed from outlet boxes and have no covers installed on receptacles outlet boxes as required for final completion of all electrical work and equipment. When electrical equipment is not fully installed and fully completed (with receptacle devices bolted into outlet boxes and with covers on the branch circuit conductors) are not safe to connect to energized power supply system because this would be an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 4.png | file://x:/photopub/docs/0000000392/229bfdd8-0581-4c23-9d09-12fc37654976.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8922b6_08fb_4bd9_b599_ef12d2d7372e
ELIN-532027-2016 | UW-349737-2016 | 2/22/2016 11:37:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | This is unsafe condition because the service pole is rotten/broken and is no longer accepted for use to secure electrical equipment. This pole also supports the electrical supply wires. Regulations require equipment to be kept in good safe working order. There is a shock and fire hazard to persons and property if the pole falls with energized wires. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Rotten_broken_pole_2.png | file://x:/photopub/docs/0000000394/5f58d03a-6313-4bed-9d10-9165e6cc1413.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c28e3d7_84e8_4aa9_8e28_0d66aa3cfcda
ELIN-532027-2016 | UW-349737-2016 | 2/22/2016 11:37:47 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | This is unsafe condition because the service pole is rotten/broken and is no longer accepted for use to secure electrical equipment. This pole also supports the electrical supply wires. Regulations require equipment to be kept in good safe working order. There is a shock and fire hazard to persons and property if the pole falls with energized wires. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Rotten_broken_pole_1.png | file://x:/photopub/docs/0000000394/587fcd83-3295-4289-a26f-aa6c754098f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c28e3d7_84e8_4aa9_8e28_0d66aa3cfcda
ELIN-504991-2016 | EL-315214-2015 | 1/7/2016 2:34:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Service conductor installed inside dwelling. These conductors pose a hazard as the fuses are normally oversized by the utility provider. This could result in a fire if the conductor became damaged because the over-current device will not trip or open. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | A.png | file://x:/photopub/docs/0000000375/a76b2800-53b8-46d4-8d7c-5058337fcda8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60edc8f3_256a_4bba_8077_b269c2a2f280
ELIN-505913-2016 | EL-168402-2014 | 2/19/2016 12:56:00 PM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 2 | At Final Inspection, a homeowner had not installed three exterior lights. The conductors were connected to energized switches which, if turned on, could produce a shock hazard at the bared ends of these conductors. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Exterior_light_not_installed.png | file://x:/photopub/docs/0000000394/86c47795-704f-4167-a536-489ab856b523.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2887b2ef_1f78_42c0_99b5_cb464b773dc4
ELIN-508737-2016 | UW-333773-2016 | 1/14/2016 4:09:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors. This is a shock hazard as someone could come into contact with the exposed wires. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | C.png | file://x:/photopub/docs/0000000377/42a60805-9d86-41c2-8fa7-e7904cf52197.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2eba7f9_e2a9_4964_abba_e4608a0c2f63
ELIN-508737-2016 | UW-333773-2016 | 1/14/2016 4:09:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors. This is a shock hazard as someone could come into contact with the exposed wires. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | E.png | file://x:/photopub/docs/0000000377/5d78de6e-1b58-47be-b96b-b2ef104af882.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2eba7f9_e2a9_4964_abba_e4608a0c2f63
ELIN-508737-2016 | UW-333773-2016 | 1/14/2016 4:09:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors. This is a shock hazard as someone could come into contact with the exposed wires. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | D.png | file://x:/photopub/docs/0000000377/989c4054-996b-49c3-945c-9965a5f1e221.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2eba7f9_e2a9_4964_abba_e4608a0c2f63
ELIN-508737-2016 | UW-333773-2016 | 1/14/2016 4:09:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors. This is a shock hazard as someone could come into contact with the exposed wires. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000377/82e87e97-82ee-42a3-9824-13f06ef828ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2eba7f9_e2a9_4964_abba_e4608a0c2f63
ELIN-508737-2016 | UW-333773-2016 | 1/14/2016 4:09:04 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed conductors. This is a shock hazard as someone could come into contact with the exposed wires. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | B.png | file://x:/photopub/docs/0000000377/52c7e9ab-73dd-4ea1-b424-2517edec6e9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2eba7f9_e2a9_4964_abba_e4608a0c2f63
BPVIN-493522-2015 | UW-324169-2015 | 12/9/2015 1:40:41 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s). Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000365/a55aa274-cbee-4d51-b29d-93ed77e2a56d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4174b5fa_3199_4ebf_a1a2_3e15f59c399a
ELIN-527763-2016 | EL-346092-2016 | 2/19/2016 12:52:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Damage.png | file://x:/photopub/docs/0000000393/e6379427-72e1-49c0-a106-4f233e28177b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45b152c5_ff1b_4c20_aace_35207495e59e
ELIN-527763-2016 | EL-346092-2016 | 2/19/2016 12:52:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Clearances_2.png | file://x:/photopub/docs/0000000393/2744ebbd-02c5-488a-8821-050229244648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45b152c5_ff1b_4c20_aace_35207495e59e
ELIN-527763-2016 | EL-346092-2016 | 2/19/2016 12:52:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Clearances.png | file://x:/photopub/docs/0000000393/5f2c246a-ce61-4e75-b5ac-116d8347edf7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45b152c5_ff1b_4c20_aace_35207495e59e
ELIN-527763-2016 | EL-346092-2016 | 2/19/2016 12:52:29 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Clearances_1.png | file://x:/photopub/docs/0000000393/713985b8-1003-4c19-8be8-30cadf0776f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45b152c5_ff1b_4c20_aace_35207495e59e
ELIN-501164-2015 | EL-321968-2015 | 1/12/2016 7:00:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | This installation was discussed a month ago with contractor and in an attempt at education I directed him to BCSA diagram on webpage, discussed multiple non-compliances. New declaration was submitted and access provided, revealing further non-compliances in addition to remaining previously discussed non-compliances. Troubling lack of common installation requirements and principles of electrical safety. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Temp_service_1.png | file://x:/photopub/docs/0000000377/c0ee5e3a-ea6a-44d7-8d70-c5f6aa0a9042.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d057d6c_e841_4a9f_bf90_993d8c6aff56
ELIN-501164-2015 | EL-321968-2015 | 1/12/2016 7:00:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 4 | This installation was discussed a month ago with contractor and in an attempt at education I directed him to BCSA diagram on webpage, discussed multiple non-compliances. New declaration was submitted and access provided, revealing further non-compliances in addition to remaining previously discussed non-compliances. Troubling lack of common installation requirements and principles of electrical safety. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Temp_service_2.png | file://x:/photopub/docs/0000000377/b5ee6621-faa9-4aba-b13a-ee70d8548095.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d057d6c_e841_4a9f_bf90_993d8c6aff56
BPVOP-479989-2015 | 2250687 | 12/21/2015 4:44:23 PM | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Pressure retaining vessels must maintain minimal required shell thickness in order to contain maximum rated working pressure. I found that this liquid ammonia vessel is not fit for service because of an active general corrosion and pitting, which exceeds the allowable amount. Potential exists for an incident such as ammonia release due to deteriorated condition of the pressure vessel. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Pitting_on_the_surface.png | file://x:/photopub/docs/0000000369/8a81fa7c-b455-443e-b147-aedeb314d0b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd720293_4a5d_481e_befe_0090c7733fc6
BPVOP-479989-2015 | 2250687 | 12/21/2015 4:44:23 PM | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Pressure retaining vessels must maintain minimal required shell thickness in order to contain maximum rated working pressure. I found that this liquid ammonia vessel is not fit for service because of an active general corrosion and pitting, which exceeds the allowable amount. Potential exists for an incident such as ammonia release due to deteriorated condition of the pressure vessel. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Deepest_pit_on_the_surface.png | file://x:/photopub/docs/0000000369/702e16ae-e3ff-4570-9f5c-f83902b09ceb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd720293_4a5d_481e_befe_0090c7733fc6
ELIN-526362-2016 | EL-337749-2016 | 2/15/2016 1:07:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | The entry 240V 400A service conduit has not been properly bonded which could result in a shock hazard. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Service_conduit.png | file://x:/photopub/docs/0000000391/b36a1b58-9ee6-4834-93e1-343e2880827e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f089e63_b41b_4d13_8081_6bbede83aa73
ELIN-508239-2016 | EL-090808-2014 | 2/2/2016 4:41:49 PM | ASSESS: EL: Final | png | #asFound | EL130 | Installation of electrical equipment Arc producing electrical equipment within 1 meter of gas relief device or vent | 2 | 1 |  | 2 | Installation of electrical equipment Arc producing electrical equipment within 1 meter of gas relief device or vent | View01_exterior_deenergized_receptacle.png | file://x:/photopub/docs/0000000385/582046e1-71be-4f6f-ad45-84797615a481.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9702673_cac6_46c5_8948_ba1daa00eeea
ELIN-502514-2015 | EL-270999-2015 | 12/30/2015 4:27:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | 4 deficiencies: 1 - lamp cord used for temp lighting poses a shock hazard as there is no bond wire and open spices without boxes. 2-range receptacle too high creates strain on connections when the ranges back is pushed against it. 3- attic junction box was inaccessible and could pose a shock hazard if connections become loose. 4- 3- gang boxes were not supported on two sides could create a strain on connections. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Attic_junction_box.png | file://x:/photopub/docs/0000000372/a5c59826-e63b-40df-9be1-f3d45a4db44a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de8b66f_2665_40df_89df_5f50cb974010
ELIN-502514-2015 | EL-270999-2015 | 12/30/2015 4:27:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | 4 deficiencies: 1 - lamp cord used for temp lighting poses a shock hazard as there is no bond wire and open spices without boxes. 2-range receptacle too high creates strain on connections when the ranges back is pushed against it. 3- attic junction box was inaccessible and could pose a shock hazard if connections become loose. 4- 3- gang boxes were not supported on two sides could create a strain on connections. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Range_box.png | file://x:/photopub/docs/0000000372/d51586c2-504f-436a-8e80-303c5884ffa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de8b66f_2665_40df_89df_5f50cb974010
ELIN-502514-2015 | EL-270999-2015 | 12/30/2015 4:27:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | 4 deficiencies: 1 - lamp cord used for temp lighting poses a shock hazard as there is no bond wire and open spices without boxes. 2-range receptacle too high creates strain on connections when the ranges back is pushed against it. 3- attic junction box was inaccessible and could pose a shock hazard if connections become loose. 4- 3- gang boxes were not supported on two sides could create a strain on connections. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Box_support.png | file://x:/photopub/docs/0000000372/d0e12733-abd3-4705-803f-e5b0dfb91623.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de8b66f_2665_40df_89df_5f50cb974010
ELOP-314695-2015 | EL-084231-2014 | 2/17/2016 11:40:24 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Where marinas and wharfs are served with electrical installations a copper equipment bond conductor is required. In this installation an aluminum bond was used to a junction box at the head of the dock ramp. The environment is quite corrosive (salty). | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Junction_box_to_dock.png | file://x:/photopub/docs/0000000392/8ffb1075-9267-468f-b140-0cbdca0e8dde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d460948_7987_4fe1_b383_c9b0684a88ba
ELOP-226530-2014 | EL-087111-2014 | 2/17/2016 2:24:08 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized electrical components must be guarded to avoid accidental contact. In this installation a cover had been left off a compressor control panel and a fitting had broken exposing energized wiring. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Open_conductors.png | file://x:/photopub/docs/0000000392/5feee0de-e5ce-42ce-ab1e-479f53fcf3db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0fa29f58_15d1_4b04_8e08_06ba169aa598
ELIN-482900-2015 | EL-316574-2015 | 11/25/2015 10:33:10 PM | ASSESS: EL: Final | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | Found one kitchen outlet receptacle fed 120 volt 1phase on 15 amp breaker has reversed polarity between hot and neutral conductors on receptacle. This is a possible electrical shock or fire hazard in the event that receptacle feeds current supply on identified conductor of electrical equipment. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Incorrect_polarity_on_kitchen_receptacle.png | file://x:/photopub/docs/0000000357/a4c05d81-9686-4f43-8c3f-8f9cc813c5ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fea6e4d_7b72_48f1_9234_50e23610be47
ELIN-509311-2016 | EL-332407-2016 | 1/21/2016 10:08:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Electrical service equipment installed without outdoors without weatherproof enclosure | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | WP_ENCLOSURE.png | file://x:/photopub/docs/0000000383/3189700f-98cb-44fa-aaa9-53c12154ae7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc9b23d4_d95b_426e_8c10_4a0ca5388b56
BPVIN-508096-2016 | UW-303177-2015 | 1/12/2016 2:13:24 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 248*Fahrenheit, it was determined that low water fuel cutout device is not installed within boiler main and isolable from boiler. There is no way to detect low water level in the boiler in the event of boiler operation with shut off valves closed and operation of boiler with low water level will cause over heating and failure of tube with consequent severe incident. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | LOW_WATER_FUEL_CUTOUT_DEVICES_LOCATION.png | file://x:/photopub/docs/0000000376/d8c34d2b-483d-4b5d-b68d-6f54514ad58b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95fd511e_09e2_45f7_bae0_0d6dd83bf6d9
BPVIN-508095-2016 | UW-303181-2015 | 1/12/2016 2:14:13 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 248*Fahrenheit, it was determined that low water fuel cutout device is not installed within boiler main and isolable from boiler. There is no way to detect low water level in the boiler in the event of boiler operation with shut off valves closed and operation of boiler with low water level will cause over heating and failure of tube with consequent severe incident. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | LOW_WATER_FUEL_CUTOUT_DEVICE_LOCATION.png | file://x:/photopub/docs/0000000376/993e3944-b3e1-4f1c-a4cd-44b5f271d436.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a40f211_0f0e_4fae_8921_e5da3bd6d743
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 6.png | file://x:/photopub/docs/0000000387/d93ad1d6-69fc-41ad-8b02-04e30e97d2e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 9.png | file://x:/photopub/docs/0000000387/3f43398b-7639-400c-93d6-70943e3317c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 8.png | file://x:/photopub/docs/0000000387/9cf21647-318b-4dda-a3a3-5166fd76a8ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 7.png | file://x:/photopub/docs/0000000387/508323c0-e6ca-47e7-ac7d-643187a61908.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 10.png | file://x:/photopub/docs/0000000387/0677fc9c-00ab-4832-9087-122e9908b0f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 5.png | file://x:/photopub/docs/0000000387/1866de94-5c43-42cd-883a-4121c24fd63b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000387/7ba06aa8-c879-4d46-b516-bbe80b3c0bf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 11.png | file://x:/photopub/docs/0000000387/b617a229-f864-4b86-8c75-973537f40cb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000387/399a5483-058c-48db-a240-5d86b9e3c1e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000387/0c22188e-b588-42c8-ab83-6f290faf5fd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-520405-2016 | EL-313970-2015 | 2/1/2016 11:03:34 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found 120/240 volt 100 amp relocatable temporary construction wooden enclosure which houses temporary panel-board, branch circuit outlet receptacles and has armoured cable feeder which is all an unapproved, unsafe non-compliant and hazardous electrical equipment assembly. Found energized exposed conductors and bus bars and badly damaged armoured feeder cables. When temporary construction relocatable electrical equipment is relocated from site to site and is unapproved, unsafe and non-compliant the electrical equipment is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000387/a4792206-ef30-4998-900a-1e5938c95a10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28666836_da71_4750_a49a_947eca5f9061
ELIN-487350-2015 | UW-319752-2015 | 1/27/2016 2:25:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | A hazard notification was submitted to BCSA detailing electrical concerns regarding a single family dwelling. This notification was forwarded to the area safety officer. The safety officer initiated an investigation and was able to contact the owner of the property and arranged to meet on site to perform a safety audit of the electrical system. During the inspection, the safety officer identified an energized, 240 volt, 60 amp electrical distribution panel located in an area under the rear deck. This panel did not have a panel cover installed, was located such that an individual had to stand in approx 1 inch of water to access, and in an area with no lighting. This posed an immediate shock hazard should an individual come into contact with the energized bussing of this panel. In addition, the area was accessible via an unlocked access door. The safety officer reviewed the hazard with the owner then de-energized the feeder supplying the panel and applied a red (do no operate) tag. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_location_under_deck.png | file://x:/photopub/docs/0000000383/5ee2ec5b-0e6c-481f-a095-d983c2a21073.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8bd6a34_fb84_4ac4_9987_0c292ae195ac
ELIN-487350-2015 | UW-319752-2015 | 1/27/2016 2:25:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | A hazard notification was submitted to BCSA detailing electrical concerns regarding a single family dwelling. This notification was forwarded to the area safety officer. The safety officer initiated an investigation and was able to contact the owner of the property and arranged to meet on site to perform a safety audit of the electrical system. During the inspection, the safety officer identified an energized, 240 volt, 60 amp electrical distribution panel located in an area under the rear deck. This panel did not have a panel cover installed, was located such that an individual had to stand in approx 1 inch of water to access, and in an area with no lighting. This posed an immediate shock hazard should an individual come into contact with the energized bussing of this panel. In addition, the area was accessible via an unlocked access door. The safety officer reviewed the hazard with the owner then de-energized the feeder supplying the panel and applied a red (do no operate) tag. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Area_Under_Deck_Photo_1.png | file://x:/photopub/docs/0000000383/e20226f4-2a89-4f8e-a59d-c7818ea7f9c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8bd6a34_fb84_4ac4_9987_0c292ae195ac
ELIN-487350-2015 | UW-319752-2015 | 1/27/2016 2:25:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | A hazard notification was submitted to BCSA detailing electrical concerns regarding a single family dwelling. This notification was forwarded to the area safety officer. The safety officer initiated an investigation and was able to contact the owner of the property and arranged to meet on site to perform a safety audit of the electrical system. During the inspection, the safety officer identified an energized, 240 volt, 60 amp electrical distribution panel located in an area under the rear deck. This panel did not have a panel cover installed, was located such that an individual had to stand in approx 1 inch of water to access, and in an area with no lighting. This posed an immediate shock hazard should an individual come into contact with the energized bussing of this panel. In addition, the area was accessible via an unlocked access door. The safety officer reviewed the hazard with the owner then de-energized the feeder supplying the panel and applied a red (do no operate) tag. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Entrance_To_Area_Under_Deck.png | file://x:/photopub/docs/0000000383/43838ecd-fe33-4bcb-9cfa-66b931e56b1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8bd6a34_fb84_4ac4_9987_0c292ae195ac
ELIN-487350-2015 | UW-319752-2015 | 1/27/2016 2:25:47 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | A hazard notification was submitted to BCSA detailing electrical concerns regarding a single family dwelling. This notification was forwarded to the area safety officer. The safety officer initiated an investigation and was able to contact the owner of the property and arranged to meet on site to perform a safety audit of the electrical system. During the inspection, the safety officer identified an energized, 240 volt, 60 amp electrical distribution panel located in an area under the rear deck. This panel did not have a panel cover installed, was located such that an individual had to stand in approx 1 inch of water to access, and in an area with no lighting. This posed an immediate shock hazard should an individual come into contact with the energized bussing of this panel. In addition, the area was accessible via an unlocked access door. The safety officer reviewed the hazard with the owner then de-energized the feeder supplying the panel and applied a red (do no operate) tag. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_without_cover.png | file://x:/photopub/docs/0000000383/a7a877f4-4b2d-42ea-9cde-6b6fccac28ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8bd6a34_fb84_4ac4_9987_0c292ae195ac
ELIN-483612-2015 | EL-315352-2015 | 11/30/2015 4:29:27 PM | ASSESS: EL: Final | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Access to the 60A 120/240V sub-panel is partially blocked, creating a hazard to operate any of the breakers or to service the panel. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Sub_panel.png | file://x:/photopub/docs/0000000359/5327a0ad-d941-41f2-8d9e-a163d4ea3c41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac437858_3888_48df_ae03_5b7d636f08c7
ELIN-513648-2016 | EL-331175-2016 | 2/3/2016 4:34:48 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | At the rough wire inspection, the dryer and range boxes were found to be secured on only one side. Larger dimension boxes such as these, with a dimension greater than 100mm, require additional support to ensure they remain secure in the wall through years of use. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Dryer_outlet_box.png | file://x:/photopub/docs/0000000386/e9c01915-805c-423e-87e3-a8ecb7a48716.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f141bd3d_2d15_4d2c_81bc_77abce4c3e22
ELIN-513648-2016 | EL-331175-2016 | 2/3/2016 4:34:48 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | At the rough wire inspection, the dryer and range boxes were found to be secured on only one side. Larger dimension boxes such as these, with a dimension greater than 100mm, require additional support to ensure they remain secure in the wall through years of use. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Range_outlet_box.png | file://x:/photopub/docs/0000000386/26049dd7-9b13-413b-92ad-94f92753e66e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f141bd3d_2d15_4d2c_81bc_77abce4c3e22
ELIN-487639-2015 | UW-070197-2013 | 12/1/2015 1:06:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Electrical panel covers are required to be in place at all times when electrical equipment is energized. This is required in part to prevent accidental contact with energized parts of the equipment. This installation had a 200 Amp, 120/240 Volt rated breaker panel that is energized and is missing the cover. Left uncorrected this a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_electrical_panel.png | file://x:/photopub/docs/0000000360/9e528aad-d0de-4d53-a863-c25a55d8890b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7423ef_f321_4486_937e_d385c03b0f99
ELIN-487639-2015 | UW-070197-2013 | 12/1/2015 1:06:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Electrical panel covers are required to be in place at all times when electrical equipment is energized. This is required in part to prevent accidental contact with energized parts of the equipment. This installation had a 200 Amp, 120/240 Volt rated breaker panel that is energized and is missing the cover. Left uncorrected this a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | I_installed_the_panel_cover.png | file://x:/photopub/docs/0000000360/4afd8c0c-0629-462a-9f55-a426f89ee0f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf7423ef_f321_4486_937e_d385c03b0f99
ELIN-508004-2016 | EL-311950-2015 | 1/13/2016 2:15:52 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Temporary heater connection at 240 volt dryer and range outlets are exposed and have potential and shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Temp_heater_connection_range.png | file://x:/photopub/docs/0000000377/27ae0840-7841-4d4e-9122-b8200d6e6d81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df955d3c_f2ca_401b_954c_7f94a15f1222
ELIN-508004-2016 | EL-311950-2015 | 1/13/2016 2:15:52 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Temporary heater connection at 240 volt dryer and range outlets are exposed and have potential and shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Temp_heater_connection.png | file://x:/photopub/docs/0000000377/1dbd053b-52c1-4c4c-a1a7-c756112bb99d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df955d3c_f2ca_401b_954c_7f94a15f1222
GAIN-484127-2015 | GA-276412-2015 | 11/25/2015 12:58:04 PM | ASSESS: GA: Rough-In | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Incorrect_grade1.png | file://x:/photopub/docs/0000000357/3663a760-5699-4e1e-98bf-dff71587dcaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ba62c72_8d49_4693_ab98_760f246e0506
GAIN-484127-2015 | GA-276412-2015 | 11/25/2015 12:58:04 PM | ASSESS: GA: Rough-In | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Incorrect_termination.png | file://x:/photopub/docs/0000000357/a31241cb-67cc-4420-a11f-a4725ec0a418.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ba62c72_8d49_4693_ab98_760f246e0506
GAIN-484127-2015 | GA-276412-2015 | 11/25/2015 12:58:04 PM | ASSESS: GA: Rough-In | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Incorrect_grade2.png | file://x:/photopub/docs/0000000357/947ca372-9358-4add-9e59-b2aefd4102d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ba62c72_8d49_4693_ab98_760f246e0506
BPVOP-505962-2016 | 4073413 | 1/7/2016 2:03:19 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of liquid refrigerant (R-22) receiver (3.6m long and .4m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 300psig, it is determined that vessel has relief valves those exceeded 5 year interval for servicing or replacement. Failure to have relief valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of refrigerant and shooting/rocketing effect of flying object (caused by uncontrolled release of refrigerant) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | RELIEF_VALVE.png | file://x:/photopub/docs/0000000375/8757455f-2073-4940-8654-764425328fcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6acc0a5_6acc_4bda_abc2_7bfef61c8df2
ELIN-484851-2015 | EL-291126-2015 | 11/26/2015 3:23:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | 2x Panel boards in basement are missing the covers allowing personnel to be exposed to energized wiring creating the possibility of a shock hazard. The area is only accessible to contractors on site | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Old_sub-panel.png | file://x:/photopub/docs/0000000358/cb34f3ab-6669-43fe-9365-d91e0b258ded.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a85e5b9_ed12_4f1d_824b_c8260a395769
ELIN-481768-2015 | EL-306821-2015 | 11/26/2015 3:23:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The use of a mast insulator mounted onto EMT conduit on the pole for support creates a safety hazard for the equipment once energized to be subject to being pulled off from the pole. Equipment damage could lead to shock and thermal hazards. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Dip_service_pole_point_of_attachment.png | file://x:/photopub/docs/0000000358/7bd1d912-26e9-4aa9-8ad9-f2c73740818e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5968ad7c_4229_45fe_9144_7d6b1df62ec2
ELIN-484851-2015 | EL-291126-2015 | 11/26/2015 3:23:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | 2x Panel boards in basement are missing the covers allowing personnel to be exposed to energized wiring creating the possibility of a shock hazard. The area is only accessible to contractors on site | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Main_150amp_sub-panel.png | file://x:/photopub/docs/0000000358/f9f8c83b-b293-4e06-a987-3428b8e4acf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a85e5b9_ed12_4f1d_824b_c8260a395769
ELIN-496553-2015 | EL-326542-2015 | 12/15/2015 8:06:11 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 4 | The installation of new replacement LED lighting requires a qualified person for the regulated electrical work. Circuits for lighting are on timers and photocells and require proper lockout to avoid shock hazards.. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Site_overview.png | file://x:/photopub/docs/0000000367/b4243282-6438-42b6-abaf-db581ce9e5d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1cac229_9283_4285_b723_e72b69469a3d
ELIN-496553-2015 | EL-326542-2015 | 12/15/2015 8:06:11 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 4 | The installation of new replacement LED lighting requires a qualified person for the regulated electrical work. Circuits for lighting are on timers and photocells and require proper lockout to avoid shock hazards.. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Regulated_work_being_performed.png | file://x:/photopub/docs/0000000367/78bd745a-d79e-46b1-acf8-e9d24cd6190c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1cac229_9283_4285_b723_e72b69469a3d
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 34.png | file://x:/photopub/docs/0000000391/292679e5-2539-45dd-9897-87fffebb62df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 47.png | file://x:/photopub/docs/0000000391/b46aa057-c25a-4340-a7ef-ad56e2d852bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 48.png | file://x:/photopub/docs/0000000391/3ad10246-6609-4131-9ed2-340f9bb3bdac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 39.png | file://x:/photopub/docs/0000000391/e8fa08db-09eb-4f47-89d8-dff4b68bd6be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 41.png | file://x:/photopub/docs/0000000391/bf394822-e195-4540-8f98-58c2e58006b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 43.png | file://x:/photopub/docs/0000000391/3ce757a0-81ee-427d-849e-0da38bcaf504.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 32.png | file://x:/photopub/docs/0000000391/d57d52e8-8c53-493e-9832-d5213bb77a94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 37.png | file://x:/photopub/docs/0000000391/93c8ff64-95e7-4a23-b790-f845a0d88f06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 36.png | file://x:/photopub/docs/0000000391/70846ebb-c771-4564-b81a-e74e9dce78fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 44.png | file://x:/photopub/docs/0000000391/a10018b6-7cc7-4253-983e-74fd81b770d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 45.png | file://x:/photopub/docs/0000000391/97dbe8ec-37d1-401c-87f0-dec96a09852e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 31.png | file://x:/photopub/docs/0000000391/6e70f98f-a7fa-46c3-8a81-10a1b47827a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 49.png | file://x:/photopub/docs/0000000391/d282c5e6-bf21-4570-8da5-44ce44242721.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 38.png | file://x:/photopub/docs/0000000391/011b7fdd-aafb-4fdb-97fc-deb3f471261a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 51.png | file://x:/photopub/docs/0000000391/0269d854-6edd-4ab1-a350-b379d98d8ec2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 42.png | file://x:/photopub/docs/0000000391/cbae5814-fd90-432c-8f42-78f053989d24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 35.png | file://x:/photopub/docs/0000000391/13b6e9fa-df3e-4ef7-bab6-f9a37d10f709.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 53.png | file://x:/photopub/docs/0000000391/f9fd6bb9-b911-4477-8c78-1af489706fc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 40.png | file://x:/photopub/docs/0000000391/85c4f6c5-a383-4807-8140-7b4d8c228294.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 52.png | file://x:/photopub/docs/0000000391/5082734b-b506-47ca-b325-fb62f21a6a61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 33.png | file://x:/photopub/docs/0000000391/df161545-70de-4a9e-b1c1-384931190473.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 50.png | file://x:/photopub/docs/0000000391/5451fc98-4ad0-49ed-b906-c39f34335a95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-527533-2016 | EL-304457-2015 | 2/15/2016 1:11:45 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found exposed, non-compliant, unsafe and unapproved electrical equipment which could become 120volt energized and which had flexible #16AWG flexible cord used as permanent wiring and entered into energized receptacle outlet box. This flexible cord fed with exposed terminations to a luminaire inside a clothes closet wiring was not fully and permanently disconnected and removed as required from previous inspection done. When electrical equipment such as undersized flexible extension cords are not fully disconnected and removed from becoming energized, the electrical equipment is an electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | 46.png | file://x:/photopub/docs/0000000391/ac25fc5b-8305-4902-ab76-61016786ed26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ec3d4f_b8e8_4e80_9e2b_2912f6690775
ELIN-507880-2016 | UW-333299-2016 | 1/7/2016 2:49:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Unqualified persons performing regulated work. Energized panel without covers. Non metallic sheathed cable exposed to mechanical injury. These are shock hazards because the cable could easily become damage and the live bus bars on the panel are exposed. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | A.png | file://x:/photopub/docs/0000000377/a2bd23c1-a43c-454a-827b-19a8615739f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d6e0738_7414_4ea5_80ce_c072fc48ffe3
ELIN-507880-2016 | UW-333299-2016 | 1/7/2016 2:49:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Unqualified persons performing regulated work. Energized panel without covers. Non metallic sheathed cable exposed to mechanical injury. These are shock hazards because the cable could easily become damage and the live bus bars on the panel are exposed. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | C.png | file://x:/photopub/docs/0000000377/585a2f7d-0925-4802-b020-415cad64ad00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d6e0738_7414_4ea5_80ce_c072fc48ffe3
ELIN-507880-2016 | UW-333299-2016 | 1/7/2016 2:49:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Unqualified persons performing regulated work. Energized panel without covers. Non metallic sheathed cable exposed to mechanical injury. These are shock hazards because the cable could easily become damage and the live bus bars on the panel are exposed. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | B.png | file://x:/photopub/docs/0000000377/b4b40da4-aac2-4df0-885c-c8b894ce91a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d6e0738_7414_4ea5_80ce_c072fc48ffe3
ELIN-507880-2016 | UW-333299-2016 | 1/7/2016 2:49:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Unqualified persons performing regulated work. Energized panel without covers. Non metallic sheathed cable exposed to mechanical injury. These are shock hazards because the cable could easily become damage and the live bus bars on the panel are exposed. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | D.png | file://x:/photopub/docs/0000000377/d655cf43-7ace-44b5-b3c4-70a3492f0a70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d6e0738_7414_4ea5_80ce_c072fc48ffe3
ELIN-507880-2016 | UW-333299-2016 | 1/7/2016 2:49:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Unqualified persons performing regulated work. Energized panel without covers. Non metallic sheathed cable exposed to mechanical injury. These are shock hazards because the cable could easily become damage and the live bus bars on the panel are exposed. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | E.png | file://x:/photopub/docs/0000000377/80285842-34f7-4727-9e83-99a43cbedee9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d6e0738_7414_4ea5_80ce_c072fc48ffe3
ELIN-496012-2015 | EL-161721-2014 | 1/8/2016 8:44:40 AM | ASSESS: EL: Final | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The transformer secondary neutral X0 connection is not bonded to the transformer case. A fault in the circuits that are fed from this transformer may not open the over current devices resulting in the metal parts of electrical equipment being energized, creating a shock hazard. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Transformer_X0.png | file://x:/photopub/docs/0000000376/57f2ca60-1f23-4f9a-9342-a322f506fe36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b32c7d1_0f59_4b80_bcd5_9b8ab6c9277b
ELIN-486210-2015 | EL-278694-2015 | 12/1/2015 9:40:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles installed for temporary construction power use are energized and do not include cover plates. The accidental contact of live conductors can create a shock hazard to persons | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cabling_in_truss_space_2.png | file://x:/photopub/docs/0000000360/25638f2e-e88b-42e9-b863-9d29f2a04c64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeffca74_9a92_4453_b8e3_5507dc0df666
ELIN-486210-2015 | EL-278694-2015 | 12/1/2015 9:40:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles installed for temporary construction power use are energized and do not include cover plates. The accidental contact of live conductors can create a shock hazard to persons | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_receptacle__1.png | file://x:/photopub/docs/0000000360/ed05030f-d3c6-45e7-b0e7-aa1097d58391.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeffca74_9a92_4453_b8e3_5507dc0df666
ELIN-486210-2015 | EL-278694-2015 | 12/1/2015 9:40:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles installed for temporary construction power use are energized and do not include cover plates. The accidental contact of live conductors can create a shock hazard to persons | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cable_n_trusses_1.png | file://x:/photopub/docs/0000000360/d9012078-a8be-488d-ab9a-1aa40da0f3c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeffca74_9a92_4453_b8e3_5507dc0df666
ELIN-484838-2015 | 4231252 | 11/27/2015 4:16:41 PM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The metal sheath of an armoured cable must be bonded. In this installation unapproved connectors has been used to connect cables to PVC boxes. Failure to bond cable sheaths could result in a shock hazard. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | TECK_into_PVC_box.png | file://x:/photopub/docs/0000000358/2392c3d6-2df6-431e-b0ee-640579c8ca23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d6c5f60_639d_4c8c_b17b_fb7a4353aa9b
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Conductors_not_identified.png | file://x:/photopub/docs/0000000389/7313921a-6e28-4469-b37c-77a6ee0f708c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Connector_not_making_contact.png | file://x:/photopub/docs/0000000389/44fbc497-a9d2-43fc-9a19-79c4ea2ea90a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | sub-panel_bond_to_neutral.png | file://x:/photopub/docs/0000000389/e230277e-3bf7-470e-84d3-3f436a8c95ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Neutrals_not_identified.png | file://x:/photopub/docs/0000000389/fbf45dc8-f013-46f2-9b00-ad6f6b44c231.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Cable_not_straped.png | file://x:/photopub/docs/0000000389/30016053-8e98-47c9-8f51-f8c060aa247f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_mechanical_protection.png | file://x:/photopub/docs/0000000389/a0da5b0f-6473-4546-b796-8ebd59410c50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-514881-2016 | EL-336708-2016 | 2/11/2016 4:25:20 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | An existing commercial outbuilding with an existing 400amp 120/208volt 3phase distribution feeding a new 200amp 120/240volt sub-distribution panel installed in outbuilding #1, does not have the bonding of equipment effectively connected together. This is a shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bond_and_neutral_coupled_togeter.png | file://x:/photopub/docs/0000000389/b7bb90e1-ad2a-4f30-9e7c-64d68eaa957c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__369cc81e_4e87_4ba2_9233_38b771c6cf26
ELIN-524744-2016 | EL-311450-2015 | 2/11/2016 5:33:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 120/240 volt, 200 Amp sub distribution panel has a second ground electrode installed. This could cause equipment damage and is a thermal hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | House_distribution_panel_grounding.png | file://x:/photopub/docs/0000000389/7e46c84c-4fea-4874-bb4f-6f200dcae433.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9021f27_c7e3_4d54_b85a_c25833aba44b
GAIN-526231-2016 | GA-329363-2015 | 2/18/2016 11:29:33 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_.png | file://x:/photopub/docs/0000000393/f062728f-cf7e-4cbf-94a3-371e6f003d9f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e9a3e9b_87c9_411e_9fe2_ba4ceeb62067
EDOP-504577-2016 | 3467853 | 1/4/2016 12:13:09 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If the car is stopped/stuck outside of the landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside unlocking zone (landing) is restricted to 4 inches. It was found that the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports of fatalities due to this condition. The picture is for reference only and is not the actual site photo. | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000375/e3bea8c3-02e0-4f5c-8433-fbc8cf33b306.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cde0f1b_af7c_4fdb_98a7_d483780bdc81
BPVOP-484705-2015 | 2285298 | 11/30/2015 4:02:50 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Pressure retaining components must be fit for service and maintain minimal required shell thickness in order to contain maximum rated working pressure. I found that some firetubes of this hot water boiler were not fit for service because of an active general corrosion, which exceeded the allowable amount where tubes started to leak. Potential exists for an incident like a tube rupture due to deteriorated condition of pressure retaining parts. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Failed_boiler_tubes.png | file://x:/photopub/docs/0000000359/6a18cc02-eda2-43b3-9b8f-e746fe3aa042.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2bd175df_1e26_48f8_b354_d513e647516f
BPVOP-484903-2015 | 3597592 | 11/30/2015 4:01:58 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | Safety valve pressure setting must be governed by a piece of equipment protected maximum pressure rating. I found that the rating of this safety valve located on a hot water boiler was higher than the maximum pressure rating of the boiler by almost 30%. Potential exists for a boiler rupture due to a higher than required pressure setting of the safety valve. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | Boiler_data_.png | file://x:/photopub/docs/0000000359/3e1358ac-8218-4737-a38f-f117a15b1580.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33c5f0a6_a9d2_40c2_8dcf_8d467253642d
BPVOP-484705-2015 | 2285298 | 11/30/2015 4:02:50 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP047 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | 5 | 5 | Pressure retaining components must be fit for service and maintain minimal required shell thickness in order to contain maximum rated working pressure. I found that some firetubes of this hot water boiler were not fit for service because of an active general corrosion, which exceeded the allowable amount where tubes started to leak. Potential exists for an incident like a tube rupture due to deteriorated condition of pressure retaining parts. | 5 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component to the extent that a vessel, pipe or component fails a fitness for service evaluation and is inadequate for operating conditions | Old_boiler_tubes.png | file://x:/photopub/docs/0000000359/3cdd4c9f-917c-44c3-aec3-117495621aa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2bd175df_1e26_48f8_b354_d513e647516f
BPVOP-484903-2015 | 3597592 | 11/30/2015 4:01:58 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | Safety valve pressure setting must be governed by a piece of equipment protected maximum pressure rating. I found that the rating of this safety valve located on a hot water boiler was higher than the maximum pressure rating of the boiler by almost 30%. Potential exists for a boiler rupture due to a higher than required pressure setting of the safety valve. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | Relief_valve_data.png | file://x:/photopub/docs/0000000359/5d5dda73-218f-4646-b221-bf24a19738be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33c5f0a6_a9d2_40c2_8dcf_8d467253642d
ELIN-498644-2015 | EL-319228-2015 | 1/12/2016 7:51:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Construction heaters were found connected to the dryer outlet and a kitchen counter outlet with open splices, no strain relief, using cables that are highly susceptible to mechanical damage that were laying on the floor. the only support was the wire nuts holding the cables to the outlet conductors. During construction improperly installed cabling can lead to potential fire or injury to workers. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Construction_heater_connection_to_wall_outlet.png | file://x:/photopub/docs/0000000377/2cb016fa-ca68-4029-bb60-b1adecb9d5e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a61b0a97_13c1_4bb8_bb70_b6831179f928
ELIN-498644-2015 | EL-319228-2015 | 1/12/2016 7:51:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Construction heaters were found connected to the dryer outlet and a kitchen counter outlet with open splices, no strain relief, using cables that are highly susceptible to mechanical damage that were laying on the floor. the only support was the wire nuts holding the cables to the outlet conductors. During construction improperly installed cabling can lead to potential fire or injury to workers. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Construction_heater_connected_to_dryer_outlet.png | file://x:/photopub/docs/0000000377/de551ab1-8c6e-45f6-b86a-5125d80dd217.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a61b0a97_13c1_4bb8_bb70_b6831179f928
ELIN-498644-2015 | EL-319228-2015 | 1/12/2016 7:51:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Construction heaters were found connected to the dryer outlet and a kitchen counter outlet with open splices, no strain relief, using cables that are highly susceptible to mechanical damage that were laying on the floor. the only support was the wire nuts holding the cables to the outlet conductors. During construction improperly installed cabling can lead to potential fire or injury to workers. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Open_splices_in_6locations.png | file://x:/photopub/docs/0000000377/e7cafa8f-a56e-42b2-ae46-d32a93e13fff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a61b0a97_13c1_4bb8_bb70_b6831179f928
ELIN-503323-2015 | UW-330732-2015 | 12/30/2015 3:30:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | Temporary generator (rated more than 400amps at 208 volts) and its temporary feeder cables/conductors run from generator to building service/distribution system were installed, connected and energized while the flexible cords have cam locks on cords which are not approved electrical equipment. The cord cam locks could become disconnected for any reason and at any time while under load and feed building main electrical system. When unapproved electrical equipment is not approved for the use and is not compliant with code for safe proper operation of flexible power cord connections, the conductors could cause an electrical fire or shock hazard to people and property. This cam lock cord connection could become disconnected under load whether it is done intentionally or by accident. | 4 | Damage to equipment may result in overheating. | 1.png | file://x:/photopub/docs/0000000372/91a7e553-b9c2-4533-a25a-2028a163d962.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fc2bbef_c128_4edc_9124_fcf6b7c84372
ELIN-503323-2015 | UW-330732-2015 | 12/30/2015 3:30:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | Temporary generator (rated more than 400amps at 208 volts) and its temporary feeder cables/conductors run from generator to building service/distribution system were installed, connected and energized while the flexible cords have cam locks on cords which are not approved electrical equipment. The cord cam locks could become disconnected for any reason and at any time while under load and feed building main electrical system. When unapproved electrical equipment is not approved for the use and is not compliant with code for safe proper operation of flexible power cord connections, the conductors could cause an electrical fire or shock hazard to people and property. This cam lock cord connection could become disconnected under load whether it is done intentionally or by accident. | 4 | Damage to equipment may result in overheating. | 3.png | file://x:/photopub/docs/0000000372/4528db81-cfb7-423a-8973-ef1e93a09a52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fc2bbef_c128_4edc_9124_fcf6b7c84372
ELIN-503323-2015 | UW-330732-2015 | 12/30/2015 3:30:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | Temporary generator (rated more than 400amps at 208 volts) and its temporary feeder cables/conductors run from generator to building service/distribution system were installed, connected and energized while the flexible cords have cam locks on cords which are not approved electrical equipment. The cord cam locks could become disconnected for any reason and at any time while under load and feed building main electrical system. When unapproved electrical equipment is not approved for the use and is not compliant with code for safe proper operation of flexible power cord connections, the conductors could cause an electrical fire or shock hazard to people and property. This cam lock cord connection could become disconnected under load whether it is done intentionally or by accident. | 4 | Damage to equipment may result in overheating. | 5.png | file://x:/photopub/docs/0000000372/b7e4b52f-1101-4588-a638-bf9f81228331.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fc2bbef_c128_4edc_9124_fcf6b7c84372
ELIN-503323-2015 | UW-330732-2015 | 12/30/2015 3:30:54 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL020 | Damage to equipment may result in overheating. | 4 | 4 | Temporary generator (rated more than 400amps at 208 volts) and its temporary feeder cables/conductors run from generator to building service/distribution system were installed, connected and energized while the flexible cords have cam locks on cords which are not approved electrical equipment. The cord cam locks could become disconnected for any reason and at any time while under load and feed building main electrical system. When unapproved electrical equipment is not approved for the use and is not compliant with code for safe proper operation of flexible power cord connections, the conductors could cause an electrical fire or shock hazard to people and property. This cam lock cord connection could become disconnected under load whether it is done intentionally or by accident. | 4 | Damage to equipment may result in overheating. | 2.png | file://x:/photopub/docs/0000000372/6a9b59b3-1f58-4826-a847-a60109f3dd11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fc2bbef_c128_4edc_9124_fcf6b7c84372
ELOP-495506-2015 | 553 | 12/17/2015 10:38:08 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Adequate mechanical protection is required to ensure energized components of a panel board do not come into contact with persons and or objects. During an electrical operating permit inspection, it was determined that the main distribution panel board was missing several fillers. As a result, exposed 600volt, 1200amp, three phase energized parts were exposed to contact. This presents a shock hazard, should an individual come into contact with the energized parts. In addition, equipment failure is possible should an object come into contact with the energized parts. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Front_of_energized_CDP.png | file://x:/photopub/docs/0000000368/3152ca01-4821-4764-bc5b-e46fd5e51e8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e9c0074_fd5f_4fff_b774_b6f5ae0abe0b
ELOP-495506-2015 | 553 | 12/17/2015 10:38:08 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Adequate mechanical protection is required to ensure energized components of a panel board do not come into contact with persons and or objects. During an electrical operating permit inspection, it was determined that the main distribution panel board was missing several fillers. As a result, exposed 600volt, 1200amp, three phase energized parts were exposed to contact. This presents a shock hazard, should an individual come into contact with the energized parts. In addition, equipment failure is possible should an object come into contact with the energized parts. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Close_up_of_missing_fillers_in_CDP.png | file://x:/photopub/docs/0000000368/d3a63673-46d1-4aec-9012-45d274e6bce7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e9c0074_fd5f_4fff_b774_b6f5ae0abe0b
GAIN-505421-2016 | GA-331820-2016 | 1/12/2016 8:13:49 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Had 2 pound gas feeding a low pressure appliance. The appliance is designed to a maximum of 14 inches water column. 2 pound gas is measured at 56 inches water column There is a possibility of a gas release or explosion due to the exceeding pressure | 3 | Appliance not installed according to installation instructions | Shut_off_valve.png | file://x:/photopub/docs/0000000378/c2393201-3ec8-4baf-9e8e-9daf558023ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbea0cc3_b0e7_46b1_8aa3_6e6bf5017452
GAIN-505421-2016 | GA-331820-2016 | 1/12/2016 8:13:49 AM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Had 2 pound gas feeding a low pressure appliance. The appliance is designed to a maximum of 14 inches water column. 2 pound gas is measured at 56 inches water column There is a possibility of a gas release or explosion due to the exceeding pressure | 3 | Appliance not installed according to installation instructions | Shut_off_valve_on_riser.png | file://x:/photopub/docs/0000000378/330ed4fd-ea0c-4d91-b8e3-b1161b6bae98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbea0cc3_b0e7_46b1_8aa3_6e6bf5017452
ELIN-516338-2016 | EL-289838-2015 | 1/27/2016 3:12:14 PM | ASSESS: EL: Final | png | #asFound | EL158 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | 3 | 3 | The 15amp 120volt receptacle for the microwave is located inside a cupboard with closing doors and no wiring interlock to prevent operation of appliance when doors are closed. This is a thermal hazard | 3 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | Microwave_receptacle_in_cupboard.png | file://x:/photopub/docs/0000000383/f9453681-92a0-45d1-8e62-b58bc9064c27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19397aad_2562_4e5c_a0ac_62571aabf57a
ELIN-516339-2016 | EL-285473-2015 | 1/27/2016 3:12:04 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 15 amp 120 volt NMSC is in contact with the heating ducts causing the potential of overheating of the cables, this is a thermal hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_on_heating_duct_1.png | file://x:/photopub/docs/0000000383/f7d36e04-f7fb-4ac6-b60b-6da4732e4659.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e63762e_e023_40bb_b562_61c2f1d9db55
ELIN-516339-2016 | EL-285473-2015 | 1/27/2016 3:12:04 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 15 amp 120 volt NMSC is in contact with the heating ducts causing the potential of overheating of the cables, this is a thermal hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMSC_on_return_air_duct.png | file://x:/photopub/docs/0000000383/ac861ad7-7d48-4bc6-9372-af3a95abaafe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e63762e_e023_40bb_b562_61c2f1d9db55
ELIN-516543-2016 | EL-338013-2016 | 1/27/2016 12:13:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found 240 volt branch circuit cable TYPE NMD90 non-metallic sheathed cable was connected to power supply system breaker while cable has exposed insulated conductors laying on the floor and subject to possible mechanical damage and contact with energized and connected conductors. When conductors are connected to an energized power supply system breaker and the breaker is not locked off and may be switched on at any time while conductors are laying on the floor and subjected to possible mechanical damage, this electrical equipment could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Baseboard_heater_240_volt_connected_conductor_laying_on_the_floor.png | file://x:/photopub/docs/0000000383/5b8c51d3-b1b7-4ccf-852a-50541d63d5ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6754d7_2655_4f99_9f01_1a6a0e389049
ELIN-516543-2016 | EL-338013-2016 | 1/27/2016 12:13:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found 240 volt branch circuit cable TYPE NMD90 non-metallic sheathed cable was connected to power supply system breaker while cable has exposed insulated conductors laying on the floor and subject to possible mechanical damage and contact with energized and connected conductors. When conductors are connected to an energized power supply system breaker and the breaker is not locked off and may be switched on at any time while conductors are laying on the floor and subjected to possible mechanical damage, this electrical equipment could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | BBH_cct_240_volt_connected_while_not_safe4.png | file://x:/photopub/docs/0000000383/84f38701-1636-4a79-8468-b909dd9246db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6754d7_2655_4f99_9f01_1a6a0e389049
ELIN-516543-2016 | EL-338013-2016 | 1/27/2016 12:13:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found 240 volt branch circuit cable TYPE NMD90 non-metallic sheathed cable was connected to power supply system breaker while cable has exposed insulated conductors laying on the floor and subject to possible mechanical damage and contact with energized and connected conductors. When conductors are connected to an energized power supply system breaker and the breaker is not locked off and may be switched on at any time while conductors are laying on the floor and subjected to possible mechanical damage, this electrical equipment could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | BBH_cct_240_volt_connected_while_not_safe5.png | file://x:/photopub/docs/0000000383/8e9d0016-1ae8-4859-a2b6-b0ac538595aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6754d7_2655_4f99_9f01_1a6a0e389049
ELIN-516543-2016 | EL-338013-2016 | 1/27/2016 12:13:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found 240 volt branch circuit cable TYPE NMD90 non-metallic sheathed cable was connected to power supply system breaker while cable has exposed insulated conductors laying on the floor and subject to possible mechanical damage and contact with energized and connected conductors. When conductors are connected to an energized power supply system breaker and the breaker is not locked off and may be switched on at any time while conductors are laying on the floor and subjected to possible mechanical damage, this electrical equipment could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | BBH_cct_240_volt_connected_while_not_safe_1.png | file://x:/photopub/docs/0000000383/eeb267ab-a54c-4c28-912b-7430161261ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6754d7_2655_4f99_9f01_1a6a0e389049
ELIN-516543-2016 | EL-338013-2016 | 1/27/2016 12:13:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found 240 volt branch circuit cable TYPE NMD90 non-metallic sheathed cable was connected to power supply system breaker while cable has exposed insulated conductors laying on the floor and subject to possible mechanical damage and contact with energized and connected conductors. When conductors are connected to an energized power supply system breaker and the breaker is not locked off and may be switched on at any time while conductors are laying on the floor and subjected to possible mechanical damage, this electrical equipment could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | BBH_cct_240_volt_connected_while_not_safe_6.png | file://x:/photopub/docs/0000000383/cc12b1d5-84d8-4a6a-bb11-f96073e2fd46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6754d7_2655_4f99_9f01_1a6a0e389049
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 35.png | file://x:/photopub/docs/0000000388/62a778aa-a619-4a4a-a221-2d48ea628365.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 30.png | file://x:/photopub/docs/0000000388/4cf1e860-3e88-407c-85ec-719533d2ea65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 76.png | file://x:/photopub/docs/0000000388/2606f579-8007-4171-a1c3-fe9d38c1727b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 68.png | file://x:/photopub/docs/0000000388/afc5c620-8fb1-4c7d-9d47-02d88148b05f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 65.png | file://x:/photopub/docs/0000000388/ab0ef604-6ffd-42af-a6cd-8fa1b2f157a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 33.png | file://x:/photopub/docs/0000000388/e15a38af-d3c0-43d1-a518-c0a69769ba84.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 70.png | file://x:/photopub/docs/0000000388/88bac61f-cc4a-4d66-88bd-46c124b4fd01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 36.png | file://x:/photopub/docs/0000000388/718e98d2-3491-4e40-b598-d4f7982e6b7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 40_.png | file://x:/photopub/docs/0000000388/f44539ed-f4d7-48af-96ef-e51ae64343ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 34.png | file://x:/photopub/docs/0000000388/465fb41f-8ea8-4539-84cc-5e9f7bebde7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 61.png | file://x:/photopub/docs/0000000388/a8bcbe53-a4f6-455b-83c8-81c343fd2bb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 74.png | file://x:/photopub/docs/0000000388/60d216cc-9b87-4c9c-8a6d-944433191bcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 41.png | file://x:/photopub/docs/0000000388/a9e54919-7ee1-490b-b9c9-6d061c4225e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 77.png | file://x:/photopub/docs/0000000388/37e22b57-9324-4b38-97cd-8d0a8ee21d00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 67.png | file://x:/photopub/docs/0000000388/5bc690f9-6553-41d9-bf99-fcbe2e9a44df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 31.png | file://x:/photopub/docs/0000000388/9c0aad62-6cd1-4527-a1e3-e9ab316b98fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 38.png | file://x:/photopub/docs/0000000388/764e57c8-f1f1-47ec-9402-a57ac8f97712.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 39.png | file://x:/photopub/docs/0000000388/64e6839a-0723-4b03-bddf-e0965408d745.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 32.png | file://x:/photopub/docs/0000000388/04e160da-b101-4f3f-9016-9a59172684c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-518898-2016 | EL-338026-2016 | 2/4/2016 7:43:44 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found contractor had requested a roughwire inspection and had left all load end electrical equipment with exposed conductors while branch circuit conductors are connected to branch circuit breakers. When branch circuit conductors are not fully completed and safe and connected to power supply system | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 37.png | file://x:/photopub/docs/0000000388/d6c411ab-5048-458f-9943-e5ea4cf5ae29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d6e0e9_84cf_47f5_baf3_7596929e47ea
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 73.png | file://x:/photopub/docs/0000000388/ecf75c94-be51-4fca-bb40-f6164348d3fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-527132-2016 | EL-335424-2016 | 2/16/2016 9:32:10 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The 200 amp 120/240 volt main service panel does not have approved weather proof protection installed, the roof is in progress but not weather tight, this can lead to as shock hazard and equipment damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Mai_panelboard.png | file://x:/photopub/docs/0000000391/411248bf-7028-43c6-8168-590ffe3244b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f408e062_6355_455d_9b50_b55670139966
ELIN-516543-2016 | EL-338013-2016 | 1/27/2016 12:13:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found 240 volt branch circuit cable TYPE NMD90 non-metallic sheathed cable was connected to power supply system breaker while cable has exposed insulated conductors laying on the floor and subject to possible mechanical damage and contact with energized and connected conductors. When conductors are connected to an energized power supply system breaker and the breaker is not locked off and may be switched on at any time while conductors are laying on the floor and subjected to possible mechanical damage, this electrical equipment could become an electrical fire or shock hazard to people and property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Baseboard_heater_240_volt_connected_to_power.png | file://x:/photopub/docs/0000000383/6d8915b9-dd53-444a-a8b5-aeaaead6eb8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6754d7_2655_4f99_9f01_1a6a0e389049
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 69.png | file://x:/photopub/docs/0000000388/46d0e259-ea56-4868-a1d1-3c452c1e4d7b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 72.png | file://x:/photopub/docs/0000000388/788acd3d-2a80-4bfe-9e6e-18a5ace502bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 71.png | file://x:/photopub/docs/0000000388/6d2e105f-99ef-41c1-bf63-e05caa84226d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 60.png | file://x:/photopub/docs/0000000388/d7f50158-c69e-433c-a729-26bce77735de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 63.png | file://x:/photopub/docs/0000000388/a2be391c-2327-480f-9784-27696d9d0468.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 66.png | file://x:/photopub/docs/0000000388/c0ad48a7-0dd7-492c-bea9-37433f2d3c21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 78.png | file://x:/photopub/docs/0000000388/d0b30e41-dc40-4714-906e-00d9f11f8f83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 62.png | file://x:/photopub/docs/0000000388/7325a302-0ff3-44ff-a0c9-eed978a6b9eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 64.png | file://x:/photopub/docs/0000000388/639c8faf-8db0-47bd-9688-e6bcb3c983d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-519166-2016 | EL-338026-2016 | 2/4/2016 9:29:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found that contractor submitted inspection request for service connection and authorized the garage consumer's service equipment for connection to power supply system while the electrical equipment and its distribution is unsafe, non-compliant, unapproved wiring and there would be exposed bus bars and conductors that will be energized if connection above is made. If electrical equipment such as service and distribution bus bars and conductors are energized while exposed to possible contact with people and property, the electrical equipment becomes a very hazardous electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 75.png | file://x:/photopub/docs/0000000388/4d3ac77f-ed15-45fc-85ce-17ea007c89c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7dea3ce_c57c_405b_b61e_7ea1f4dd85a1
ELIN-488503-2015 | EL-305599-2015 | 12/3/2015 3:27:42 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | The system previously used the water line as the main ground and has since been replaced with plastic leaving the service without a grounded system creating the potential of a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_clamp.png | file://x:/photopub/docs/0000000361/881ab790-10ff-442b-96f1-92fed05702b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c64d23f_3445_4e23_b5e3_c70c6b877a62
ELIN-488503-2015 | EL-305599-2015 | 12/3/2015 3:27:42 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | The system previously used the water line as the main ground and has since been replaced with plastic leaving the service without a grounded system creating the potential of a shock hazard. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_missing.png | file://x:/photopub/docs/0000000361/7dfddcc6-1af5-4ff1-89e6-9c0ab2ce4832.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c64d23f_3445_4e23_b5e3_c70c6b877a62
ELIN-507769-2016 | EL-274388-2015 | 1/18/2016 5:28:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | In a commercial building containing a new 400amp 3phase 120/208volt service in an isolated electrical room, a 120/208volt 100amp service panel was found energized with covers not installed and no electrician on site. This is a shock hazard. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Open_panel.png | file://x:/photopub/docs/0000000379/36d6e316-b92d-4a3b-9b9c-1b521e1404da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45c69bf1_cc62_4dc0_97c6_7f65d4b579b1
ELIN-528319-2016 | EL-346345-2016 | 2/17/2016 11:46:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 100 amp, 120/208 volt armoured cable is within 32mm of outer member of wall edge. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | ACWU_cable_extends_past_outer_of_wall.png | file://x:/photopub/docs/0000000392/b7c190ff-5b7b-422f-bec7-0e93cf359e58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3bcf92f_4d8d_47df_9123_2f75bdac8a39
ELIN-498204-2015 | EL-262201-2015 | 2/17/2016 2:06:41 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 15 amp 120/240 volt non metallic sheathed cable below 1.5 meters has no mechanical protection. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMDU90_below_1_5m_no_mechanical_protection.png | file://x:/photopub/docs/0000000392/db51b6c0-deb0-4473-9c51-a51fdea7fa92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6931a51_5081_4e3c_bced_f217fcfeb301
ELIN-526269-2016 | EL-317487-2015 | 2/16/2016 12:36:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #8 stranded aluminum conductor installed under wire binding screw. Code permits stranded conductors up to #10 to be terminated in this way. #8 being larger there is possibility of having not all of the stranded conductors under the wire binding screw. Possibility exists of having insufficient bonding Shock to persons or damage to property could exist in a fault situation. | 3 | Continuity Bonding; method for equipment is not adequate. | 8awg_stranded_terminated_to_wire_binding_screw.png | file://x:/photopub/docs/0000000391/e5ac438f-ae6b-4d05-85c2-420c96c1e2e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d8ff7b1_1da9_4dc4_937f_9aa46c765443
ELIN-523365-2016 | EL-224062-2015 | 2/16/2016 8:08:29 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | In a single family residence, a 15amp 120volt outlet was was found installed and energized but not the approved type of equipment. This could lead to a thermal effect. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non-TR_GFCI.png | file://x:/photopub/docs/0000000392/827e1e06-b40e-41dc-9d08-a10516e405fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db8b1ea0_16b2_4eef_8291_a096ea96d716
ELIN-523365-2016 | EL-224062-2015 | 2/16/2016 8:08:29 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | In a single family residence, a 15amp 120volt outlet was was found installed and energized but not the approved type of equipment. This could lead to a thermal effect. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Non-TR_GENERAL_USE_RECEPTACLE.png | file://x:/photopub/docs/0000000392/9fb9dbfc-e65e-49c8-8f63-bd994dcfad3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db8b1ea0_16b2_4eef_8291_a096ea96d716
ELIN-507450-2016 | EL-331722-2016 | 2/17/2016 11:44:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Some junction boxes had exposed conductors that were energized. The main panel was not properly terminated and covered. This would allow a person to come in contact with the exposed energized conductor,and possibly injure the person. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | main_panel.png | file://x:/photopub/docs/0000000392/5b6092a1-122f-48ea-a70b-8f5bb7388c97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d10e5001_4339_4be4_ac1d_f2c3a37abd4a
ELIN-507450-2016 | EL-331722-2016 | 2/17/2016 11:44:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Some junction boxes had exposed conductors that were energized. The main panel was not properly terminated and covered. This would allow a person to come in contact with the exposed energized conductor,and possibly injure the person. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Receptacle_power.png | file://x:/photopub/docs/0000000392/2abbdfa1-eb16-40d9-a179-5b89a791889f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d10e5001_4339_4be4_ac1d_f2c3a37abd4a
ELIN-496291-2015 | EL-326618-2015 | 2/10/2016 9:54:38 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Standard receptacle installed in bathroom beside sink, receptacles installed within 1.5 meters of a sink are required to be ground fault protected, ground fault protection detects current flow along unintended paths, current is to be in the supply and return paths only, water may cause these currents to stray and cause shock to persons in contact, or damage to property. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Non_gfci_receptacle_beside_sink.png | file://x:/photopub/docs/0000000389/d9c32e02-3533-4a1e-8de8-6436d4196a7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85a17d4e_91cb_4998_b53d_6b6f2b204da8
ELIN-527249-2016 | EL-344790-2016 | 2/18/2016 3:14:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Plastic_cover.png | file://x:/photopub/docs/0000000393/3acef667-8292-4a1b-ad05-407178f37ad4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d5e9b27_6d4b_4614_9fe4_572831cf2d6b
ELIN-482604-2015 | EL-315861-2015 | 12/8/2015 1:47:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Covers off the main and two subpanels. The exposed main bus of the panels, once energized, could pose a shock hazard to workers. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Sub100.png | file://x:/photopub/docs/0000000363/d5c849b1-dcf1-45a1-85df-80b4447c188f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a6348ff_be3e_41a2_85aa_2bcc159a2f54
ELIN-482604-2015 | EL-315861-2015 | 12/8/2015 1:47:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Covers off the main and two subpanels. The exposed main bus of the panels, once energized, could pose a shock hazard to workers. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Mobile_Sub.png | file://x:/photopub/docs/0000000363/5b209289-36be-4a78-aea0-2d6233c7a13b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1a6348ff_be3e_41a2_85aa_2bcc159a2f54
GAIN-525487-2016 | GA-329477-2015 | 2/16/2016 11:51:06 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | The as found hazard was a mechanical room which did not have any provisions for ventilation air installed. This creates a risk of excessive ambient temperatures potentially resulting in equipment damage. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Combustion_air_opening_only.png | file://x:/photopub/docs/0000000392/54564148-9b30-4792-b725-056cd409ccc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfd0b300_5b91_4522_a34f_f59b1b9ed3f8
GAIN-521989-2016 | GA-323348-2015 | 2/16/2016 3:41:02 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a gas fireplace which had been removed for repairs and when re-installed the units vent assembly connections integral to the fireplace were not reassembled or sealed correctly. This configuration created a risk of the products of combustion being able to escape the appliance and enter the home. | 3 | Appliance not installed according to installation instructions | missing_insulation.png | file://x:/photopub/docs/0000000392/ebd1a5a2-e834-4daa-b854-0340c4f9282c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d4b08fc_4950_4750_ae5e_8872f9efb677
GAIN-521989-2016 | GA-323348-2015 | 2/16/2016 3:41:02 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a gas fireplace which had been removed for repairs and when re-installed the units vent assembly connections integral to the fireplace were not reassembled or sealed correctly. This configuration created a risk of the products of combustion being able to escape the appliance and enter the home. | 3 | Appliance not installed according to installation instructions | missing_insulation_2.png | file://x:/photopub/docs/0000000392/1a59470a-d43c-42c5-8efa-57ac5c1d9f1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d4b08fc_4950_4750_ae5e_8872f9efb677
GAIN-521989-2016 | GA-323348-2015 | 2/16/2016 3:41:02 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a gas fireplace which had been removed for repairs and when re-installed the units vent assembly connections integral to the fireplace were not reassembled or sealed correctly. This configuration created a risk of the products of combustion being able to escape the appliance and enter the home. | 3 | Appliance not installed according to installation instructions | Gap_at_connection_2.png | file://x:/photopub/docs/0000000392/57f43eb1-2493-434e-acf9-fdc000d60142.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d4b08fc_4950_4750_ae5e_8872f9efb677
GAIN-521989-2016 | GA-323348-2015 | 2/16/2016 3:41:02 PM | ASSESS: GA: Final | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | The as found hazard was a gas fireplace which had been removed for repairs and when re-installed the units vent assembly connections integral to the fireplace were not reassembled or sealed correctly. This configuration created a risk of the products of combustion being able to escape the appliance and enter the home. | 3 | Appliance not installed according to installation instructions | Gap_at_connection.png | file://x:/photopub/docs/0000000392/c50d6bb7-617c-4994-ac0b-a0dc746370ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d4b08fc_4950_4750_ae5e_8872f9efb677
BPVOP-495844-2015 | 4135158 | 12/14/2015 9:35:34 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that machine mounted vertical air receiver (1.12m long and .45m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure-boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVES.png | file://x:/photopub/docs/0000000366/4f3a5fcb-2f9c-4937-8f08-d07adbc8ed93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__640835d4_0704_40d2_9532_dbb6662c38ba
BPVIN-495174-2015 | BPV-207987-2015 | 12/14/2015 7:11:27 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 60psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | HOT_WATER_BOILER.png | file://x:/photopub/docs/0000000366/b079162c-b166-445d-a4f7-f56b84688eec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47d3774f_8827_4b92_90a4_cfaf3eb58830
BPVIN-491285-2015 | UW-322501-2015 | 12/7/2015 9:23:47 PM | ASSESS: BPV IN: Installation REF/PV | png | #asFound | BP027 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | 3 | 2 | During assessment of expansion tank (dimensions: length-2meter and diameter-1meter) with Maximum Allowable Working Pressure of 125psig it is determined that vessel is not firmly anchored to foundation. In the event of earthquake of significant scale vessel may trip or shift and can lead to incident. | 3 | 1.0.2 Clearances/Maintenance - Anchor bolts not correctly torque | NO_ANCHOR_BOLT.png | file://x:/photopub/docs/0000000364/9bf2b645-3b1e-4015-a83f-9a5b72c3971c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53c5e717_4dd3_44cd_8131_0bc54863afc5
BPVOP-507034-2016 | 2250760 | 1/11/2016 2:02:55 PM | ASSESS: BPV OP: Incident REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | CORROSION_UNDER_INSULATION.png | file://x:/photopub/docs/0000000376/b9be8e2c-5c68-492f-9f4b-455aeef70fda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__867e84c9_e38e_4c2f_892a_bf310fd0f381
GAIN-504726-2016 | GA-284731-2015 | 1/20/2016 8:46:24 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | No low water cut-off installed on boilers or primary loop, This could create a hazard as the heating pipes run to the first floor, and boilers on second floor, if a water heating pipe breaks, the boiler could run without water. | 4 | Missing mandatory safety controls | Ibc.png | file://x:/photopub/docs/0000000380/3ee6d1fb-b929-4f79-ac52-e13fa8a613e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62c91ffa_1f6f_48e6_bde3_94b81c7c034c
ELIN-524818-2016 | EL-342924-2016 | 2/11/2016 2:58:54 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Cover plates missing off of energized 120 volt 15 amp duplex receptacles and light switch could result in electrical shock if energized device terminals are contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_missing_off_switch.png | file://x:/photopub/docs/0000000389/1be5c3ed-fe69-45d6-8a5d-1163f0429f02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fced393_fc01_4299_83fd_297deac29bfc
ELIN-524818-2016 | EL-342924-2016 | 2/11/2016 2:58:54 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Cover plates missing off of energized 120 volt 15 amp duplex receptacles and light switch could result in electrical shock if energized device terminals are contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_missing_in_bedroom.png | file://x:/photopub/docs/0000000389/ca8b03d2-3338-4c5b-8911-c87915c9eb1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fced393_fc01_4299_83fd_297deac29bfc
ELIN-524818-2016 | EL-342924-2016 | 2/11/2016 2:58:54 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Cover plates missing off of energized 120 volt 15 amp duplex receptacles and light switch could result in electrical shock if energized device terminals are contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Light_fixture_not_attached_to_outlet_box.png | file://x:/photopub/docs/0000000389/dbc68b78-b9a6-4558-a9b4-8cc57c120636.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fced393_fc01_4299_83fd_297deac29bfc
ELIN-524818-2016 | EL-342924-2016 | 2/11/2016 2:58:54 PM | ASSESS: EL: Final | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Cover plates missing off of energized 120 volt 15 amp duplex receptacles and light switch could result in electrical shock if energized device terminals are contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_missing_off_outlet_box.png | file://x:/photopub/docs/0000000389/38d98f08-497d-4b11-a186-d7fa033c36d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fced393_fc01_4299_83fd_297deac29bfc
ELIN-492058-2015 | EL-322341-2015 | 12/9/2015 11:24:48 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | And addition was added to the house. The weatherhead service conductors and triplex are now resting on the new roof of the addition. The insulation on the service conductors me where down and short circuit against the house there by possibly causing a fire. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 4398_48a_street.png | file://x:/photopub/docs/0000000364/44e3d38d-84b2-48df-8ed9-4b7229aaa1eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2d5d1d2_0565_46fa_8be8_6ac95337c9a7
ELIN-519897-2016 | UW-340966-2016 | 2/1/2016 7:26:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Energized 40' pole | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Existing_pole.png | file://x:/photopub/docs/0000000385/c29df201-493f-4219-81d1-d991a6b8dab7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d53c0a7_d15c_4ec5_b724_9dc54a46d8e0
ELIN-519897-2016 | UW-340966-2016 | 2/1/2016 7:26:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Energized 40' pole | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Existing_pole_Cert.png | file://x:/photopub/docs/0000000385/f9e22c7e-bdfd-4895-bc5a-679848497165.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d53c0a7_d15c_4ec5_b724_9dc54a46d8e0
ELIN-519897-2016 | UW-340966-2016 | 2/1/2016 7:26:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Energized 40' pole | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Existing_serv.png | file://x:/photopub/docs/0000000385/18824cb6-3614-489d-bcf2-ff2b211da8b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d53c0a7_d15c_4ec5_b724_9dc54a46d8e0
ELIN-519897-2016 | UW-340966-2016 | 2/1/2016 7:26:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Energized 40' pole | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Burnt_pole.png | file://x:/photopub/docs/0000000385/344c15c7-ba7b-4546-928d-f979b4b1ab25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d53c0a7_d15c_4ec5_b724_9dc54a46d8e0
ELIN-497993-2015 | EL-297479-2015 | 12/22/2015 4:50:04 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the service conductors emerge from the service head on the service conduit or cable. This is required to prevent water from entering the service equipment and causing rust or corrosion on conductor terminations and service equipment. This installation has the point of attachment for the over head service conductors approximately 300mm above where the service conductors emerge from the service head. Left uncorrected over time water damage to conductor terminations and equipment may cause high resistance connections on the service cable terminations in the meter base. This is a potential fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Point_of_attachment_above_service_head.png | file://x:/photopub/docs/0000000370/f6dc966c-bb72-4a58-9277-dccfe502b885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f9b8247_8910_46ee_882e_5ae7593ad90b
ELIN-497993-2015 | EL-297479-2015 | 12/22/2015 4:50:04 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the service conductors emerge from the service head on the service conduit or cable. This is required to prevent water from entering the service equipment and causing rust or corrosion on conductor terminations and service equipment. This installation has the point of attachment for the over head service conductors approximately 300mm above where the service conductors emerge from the service head. Left uncorrected over time water damage to conductor terminations and equipment may cause high resistance connections on the service cable terminations in the meter base. This is a potential fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Over_head_service_equipment_mounted_to_exterior_of_house.png | file://x:/photopub/docs/0000000370/b2b8e8e2-3621-4a0f-9b16-bda0949f4723.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f9b8247_8910_46ee_882e_5ae7593ad90b
ELIN-497993-2015 | EL-297479-2015 | 12/22/2015 4:50:04 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the service conductors emerge from the service head on the service conduit or cable. This is required to prevent water from entering the service equipment and causing rust or corrosion on conductor terminations and service equipment. This installation has the point of attachment for the over head service conductors approximately 300mm above where the service conductors emerge from the service head. Left uncorrected over time water damage to conductor terminations and equipment may cause high resistance connections on the service cable terminations in the meter base. This is a potential fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Front_of_house_.png | file://x:/photopub/docs/0000000370/81f2efe8-4413-4595-9a4a-613b8966068b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f9b8247_8910_46ee_882e_5ae7593ad90b
ELIN-497993-2015 | EL-297479-2015 | 12/22/2015 4:50:04 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | The point of attachment for over head service conductors is required to be between 150mm - 300mm below the point where the service conductors emerge from the service head on the service conduit or cable. This is required to prevent water from entering the service equipment and causing rust or corrosion on conductor terminations and service equipment. This installation has the point of attachment for the over head service conductors approximately 300mm above where the service conductors emerge from the service head. Left uncorrected over time water damage to conductor terminations and equipment may cause high resistance connections on the service cable terminations in the meter base. This is a potential fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Point_of_attachment_for_over_jean_service_supply_conductors_is_above_the_service_head.png | file://x:/photopub/docs/0000000370/ff7196d3-7f11-447c-a74b-c9f3841aeadb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f9b8247_8910_46ee_882e_5ae7593ad90b
BPVIN-490827-2015 | BPV-314141-2015 | 12/7/2015 9:23:48 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 3 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | HOT_WATER_HEATING_BOILER_4.png | file://x:/photopub/docs/0000000364/71d55fe2-f024-4813-8e2e-808632f17728.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8055cb60_097d_4001_9ddd_51f16f9d18f6
EDOP-504579-2016 | 3467854 | 1/4/2016 3:04:00 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED008 | Defects that are: Not detected by maintenance program Likely to progress | 3 | 3 | If the car is stopped/stuck outside at the landing, the passengers are not to open the car door and try to exit the elevator. They will be exposed to the open hoistway and may fall resulting in a fatality, the car may also move also exposing them to shearing/pinching hazards. For rider safety the manual opening of the elevator car doors when an elevator car is outside the unlocking zone (landing) is restricted to 4 inches. It was found at the car door restrictor was not adjusted correctly and therefore would allow the door to open fully. There have been many reports fatalities due to this condition. The picture is for reference only and is not the actual site photo | 3 | Defects that are: Not detected by maintenance program Likely to progress | Car_door_restrictor.png | file://x:/photopub/docs/0000000375/89808f37-f051-4338-bdb3-1c287bebf416.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ce613b7_a02e_4241_bdac_9bb8b2120a22
BPVOP-523263-2016 | 2284158 | 2/5/2016 6:47:29 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | HW79261.png | file://x:/photopub/docs/0000000388/a501cb1f-8a17-42e1-b037-098b0571d77b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__719ef90d_114a_4fa1_ab0b_2724c8d95edc
ELIN-500866-2015 | EL-263967-2015 | 12/23/2015 12:46:00 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Additional 120volt receptacle required for usable wall space as no receptacle in that area may lead to unapproved use of flex cords or other shock and fire hazards. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Wall_space.png | file://x:/photopub/docs/0000000370/d76c3e8e-2245-4c42-9e7e-9f3d9e4dc085.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85d4ff8a_9e1d_4776_82d0_1c637233034c
ELIN-493093-2015 | EL-288908-2015 | 12/10/2015 4:17:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Cable is not adequately protected from overcurrent. This could result in overheating and failure of cable/fire risk. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Cables_to__from_transformer.png | file://x:/photopub/docs/0000000365/e21a55ed-0867-44e0-a585-6239a8e7b365.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1eadb30b_3b2a_448d_bf30_ae9bcae3872a
ELIN-423793-2015 | UW-277463-2015 | 12/10/2015 7:27:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | Used mobile homes must bear evidence of certification before they are sold or offered for sale. In this case a mobile home had been recently transferred without the benefit of recertification. The park electrician disconnected the unit from its source of supply. | 3 | General Equipment is not approved for the specific use | Street_view.png | file://x:/photopub/docs/0000000366/feb0ba44-dfb7-40cf-b60f-9e33a6afd37b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2fd49df_1808_4858_b428_72db90595018
ELIN-423793-2015 | UW-277463-2015 | 12/10/2015 7:27:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | Used mobile homes must bear evidence of certification before they are sold or offered for sale. In this case a mobile home had been recently transferred without the benefit of recertification. The park electrician disconnected the unit from its source of supply. | 3 | General Equipment is not approved for the specific use | Trailer_box.png | file://x:/photopub/docs/0000000366/687aa2f7-f429-4e32-be30-5014a0c6c88e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2fd49df_1808_4858_b428_72db90595018
ELIN-545167-2016 | EL-321025-2015 | 3/21/2016 5:28:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The armoured cabling is improperly terminated in a manner that isolates the metallic armour from the system bonding and provides no means of mechanical support, resulting in strain placed on the connection at the terminals. This poses a risk of personal injury (shock) or property damage (thermal event) if the amour of the cabling is placed into an energized state or the terminations are subjected to mechanical strain. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | View01_main_distribution.png | file://x:/photopub/docs/0000000406/672df628-f203-4b32-9db3-334a4c8ee11e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__029cbe3f_556c_463b_acd2_7bee6de72fd1
ELIN-542920-2016 | EL-227870-2015 | 3/21/2016 3:24:18 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Armoured cabling in location accessible to general public not adequately protected from effects of mechanical damage where it rises from grade. This presents a serious risk of personal injury (shock) or property damage (thermal event) from contact and exposure with energized portions of the cabling. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_feeder-junction_box.png | file://x:/photopub/docs/0000000406/9ec417d4-6894-4099-b432-30c8f7754284.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28491065_db4e_4b12_9a85_3609bf4d35f4
BPVOP-535159-2016 | 2285313 | 3/11/2016 12:51:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Every pressure retaining component of a regulated equipment must be provided with a pressure relief device in order to protect from over pressurization and possible rupture. I found a shutoff valve (opened) installed between the hot water boiler and safety relief valve. Potential exists for an incident due to safety valve being compromised and isolated from the boiler. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Safety_valve_data_.png | file://x:/photopub/docs/0000000405/449dccbd-6da9-43d2-b557-209b05d4ffb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab093248_3b58_4da8_8d00_f1e948c5d500
BPVOP-535159-2016 | 2285313 | 3/11/2016 12:51:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Every pressure retaining component of a regulated equipment must be provided with a pressure relief device in order to protect from over pressurization and possible rupture. I found a shutoff valve (opened) installed between the hot water boiler and safety relief valve. Potential exists for an incident due to safety valve being compromised and isolated from the boiler. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Safety_valve_with_shuttoff_valve.png | file://x:/photopub/docs/0000000405/422e477f-f57c-4416-a8d8-494cc235aa3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab093248_3b58_4da8_8d00_f1e948c5d500
BPVOP-535159-2016 | 2285313 | 3/11/2016 12:51:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | Every pressure retaining component of a regulated equipment must be provided with a pressure relief device in order to protect from over pressurization and possible rupture. I found a shutoff valve (opened) installed between the hot water boiler and safety relief valve. Potential exists for an incident due to safety valve being compromised and isolated from the boiler. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Saskatoon_boiler.png | file://x:/photopub/docs/0000000405/eb66ca52-aa1b-4d93-8676-4140c752b43a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab093248_3b58_4da8_8d00_f1e948c5d500
ELIN-537429-2016 | UW-355742-2016 | 3/2/2016 3:09:41 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | An unlicensed individual wired a detached garage for a customer. To provide temporary power, he spliced several circuits together inside the panel in the garage and installed a cord end which was then connected to an extension cord plugged in at the existing home. This could lead to an overloading of the supply circuit and thermal damage to it. | 3 | Protection and control Loading of distribution equipment exceeded | Multiple_branch_circuits_spliced_and_supplied_by_an_evtension_cord_.png | file://x:/photopub/docs/0000000400/feb0c661-e868-4274-a54e-3c669aeba1d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3aa4f89b_f934_4224_8c2e_3ed5b1daa661
ELIN-539220-2016 | EL-320575-2015 | 3/7/2016 2:53:48 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | The 120/240 volt service conductors, 3 conductor 1/0 armoured cables, are closer than 32 mm to the surface framing. The cables could be damaged, which would cause equipment damage, and be a shock and thermal hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Service_conductors.png | file://x:/photopub/docs/0000000401/22ff51e0-dad4-4e62-815d-97a316872c21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2f2fa22_f681_4959_9962_b0b63b0176d4
ELIN-536275-2016 | EL-199567-2015 | 3/9/2016 11:21:49 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | 120 volt 15 amp ceiling outlet boxes has unused openings. This is a thermal hazard should a fault occur in the outlet box when the circuit is energized. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Ceiling_outlet_box__.png | file://x:/photopub/docs/0000000402/493c012e-7e36-4721-9391-267fbdd78e51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f08e9cb_ee11_44c2_b56e_a65f34b6e0a8
ELOP-229671-2014 | 6036 | 3/10/2016 4:36:32 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | In sewage lift stations and kiosks it is important to seal off the wet well from electrical equipment to prohibit the transfer of corrosive and potentially explosive gases into an area where a spark could be produced. In this installation the conduits from the wet well were installed without seals in the base of the kiosk. Everything below 12" high including electrical equipment and the kiosk itself were damaged and require replacement. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | No_seal.png | file://x:/photopub/docs/0000000403/3320732e-3667-4f9d-a7a6-8f681000aab8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4f7ed14_e688_4321_b3fe_e8bc142233ce
ELOP-229670-2014 | 6044 | 3/11/2016 6:06:29 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not intended to be used as a replacement for permanent wiring. In this lounge an extension cord had been woven through the ceiling to plug into a festive lighting display. | 4 | Conductors, Misuse of flexible cords. | Extension_above_bar.png | file://x:/photopub/docs/0000000403/6ed654cd-32f0-4f3a-9107-8acc9796f748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d29fb4a_eb86_44c2_9905_8e8425f9484e
ELOP-229665-2014 | 6045 | 3/10/2016 5:22:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment must be approved for use as installed. In this fire hall unapproved equipment was installed and utilized. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Lighting_controller.png | file://x:/photopub/docs/0000000403/930f5455-da66-4570-b48b-1a3cff4ec57f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cedaf071_a39a_470d_a8b6_9c16fdaeb299
ELOP-229675-2014 | 6035 | 3/10/2016 4:59:36 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Electrical equipment must be installed so energized parts are not accessible to accidental touch. In this sewage treatment plant a fixture had been removed above an entrance door and the wiring was left hanging without being contained in some sort of approved enclosure. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Screen_room_equipment.png | file://x:/photopub/docs/0000000403/2058a5e3-ca41-4ea1-a50a-e4b4d6da091e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__467f0018_876a_4cf8_8aa8_5a8e4ba3e976
ELOP-229678-2014 | 1991 | 3/10/2016 9:49:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are intended for temporary or portable uses and not as a substitute for permanent wiring. In this school several flexible cords are in use inappropriately. | 4 | Conductors, Misuse of flexible cords. | Do_not_unplug.png | file://x:/photopub/docs/0000000403/2108405d-87fc-47b8-950c-bb7e483f5d73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96364c47_c315_48a9_9c8e_6c55e60e3da0
ELOP-229679-2014 | 6037 | 3/10/2016 6:31:46 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Unused openings in electrical cabinets must be closed to avoid inadvertent shock. In this installation a meter had been removed from a cabinet but not filled. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hole_in_the_wall.png | file://x:/photopub/docs/0000000403/0c47b335-d830-4692-8806-e2cf03441716.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59374f88_6c64_4541_981a_34c9d68073ff
ELOP-229664-2014 | 6041 | 3/10/2016 6:01:49 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Unused openings in electrical boxes must be closed to ensure objects or fingers are not accidentally inserted. In this installation fillers were omitted when alterations were made to a portion of the site. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | KO_missing.png | file://x:/photopub/docs/0000000403/56794b66-b89f-4b6e-9089-250d6e44b549.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19ed2aa2_e60f_4a43_b40c_e8d069e40362
ELOP-229667-2014 | 6042 | 3/10/2016 5:39:26 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | Electrical equipment and conductors must be protected from overcurrent with fuses or other current limiting devices. In this installation emergency radio equipment was observed installed without approved protection. | 3 | Protection and control Low voltage protection damaged or not provided. | Open_under_desk.png | file://x:/photopub/docs/0000000403/05da4984-b6f2-4a89-be98-16708663f78c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6a005_6d49_4b1b_83a4_5f8bcb5bfa3c
GAIN-532281-2016 | GA-322102-2015 | 2/29/2016 12:39:02 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Contractor piped 10psi propane into single family residence into a 2psi regulator. Could cause pressure control issues and possible over-firing of appliance which in turn could cause a fire. | 3 | Code prohibited practices or materials | 10psi_tank_reg.png | file://x:/photopub/docs/0000000399/0769f524-3aac-42aa-bddf-b5a2c22e491d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8848c40e_01fa_4ab8_9b88_1d82484d8f3d
GAIN-532281-2016 | GA-322102-2015 | 2/29/2016 12:39:02 PM | ASSESS: GA: Final | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Contractor piped 10psi propane into single family residence into a 2psi regulator. Could cause pressure control issues and possible over-firing of appliance which in turn could cause a fire. | 3 | Code prohibited practices or materials | 2psi_reg.png | file://x:/photopub/docs/0000000399/71573a80-1ff0-4df5-b1b7-c1e5c8e005b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8848c40e_01fa_4ab8_9b88_1d82484d8f3d
ELIN-530608-2016 | EL-229601-2015 | 2/24/2016 10:42:28 AM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Unused branch breaker openings in the 100A 120/240V Subpanel have not been filled, a shock hazard exists as possible contact with energized equipment inside the panel through the openings could happen. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Panel_openings.png | file://x:/photopub/docs/0000000395/2e26b973-e699-4d0f-a70d-c63d10f980bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77a9e0b6_e49d_4adc_9747_7eb78082f879
ELIN-353869-2015 | EL-232658-2015 | 4/11/2016 4:11:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | 8540_Alaska_Rd_sub-distribution_.png | file://x:/photopub/docs/0000000415/7b40589d-60a3-499c-ba2a-8c3b50c94efe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e44ddd1_214e_4df7_a6c1_40ee78e5ff16
ELIN-559976-2016 | EL-344761-2016 | 4/15/2016 9:45:25 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 |  | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | fire_alarm_wiring_in_ent.png | file://x:/photopub/docs/0000000417/44b5c988-a35c-4c98-b386-b183952d7245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bce14ba6_e8fc_4e53_8cc0_63a1cbe7fe92
ELIN-540202-2016 | EL-345557-2016 | 3/23/2016 4:37:11 PM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Newly installed outdoor overhead consumer's service raceway is installed within walls of house and are not located outside of the house as required by code. When a consumer's service raceway is installed within walls of a building there may be overheating and is not safe because there are no over current devices on supply side of consumer's service panel where the utility connection is made. This could become a fire or shock hazard because there are no over current devices that will open the circuit in the event there is a short circuit or fault condition on service conductors within the raceway located within walls of wood structure of house. A fault condition on service conductors would not be readily visible inside walls of house as would a raceway installed on surface of outside of the house. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 201.png | file://x:/photopub/docs/0000000417/29554102-6e32-4ce2-ac3f-b1a5427f3b44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c564339_628e_48f4_8a5e_459a3e6b8829
ELIN-540202-2016 | EL-345557-2016 | 3/23/2016 4:37:11 PM | ASSESS: EL: Final | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | Newly installed outdoor overhead consumer's service raceway is installed within walls of house and are not located outside of the house as required by code. When a consumer's service raceway is installed within walls of a building there may be overheating and is not safe because there are no over current devices on supply side of consumer's service panel where the utility connection is made. This could become a fire or shock hazard because there are no over current devices that will open the circuit in the event there is a short circuit or fault condition on service conductors within the raceway located within walls of wood structure of house. A fault condition on service conductors would not be readily visible inside walls of house as would a raceway installed on surface of outside of the house. | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 200.png | file://x:/photopub/docs/0000000417/10d49821-96f8-4e75-b579-2c919ed9a6b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c564339_628e_48f4_8a5e_459a3e6b8829
ELOP-229672-2014 | 6043 | 3/10/2016 6:36:13 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Electrical connections must be made up in approved enclosures to a ad accidental contact. In this installation a portion of a raceway system had been removed and the energized wires left open to touch. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Air_splice_in_back_room.png | file://x:/photopub/docs/0000000403/1e86bd8f-b924-485b-8015-9dcfd363b24f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52771614_daaa_4ee1_8df3_44a3b92d677c
ELOP-229667-2014 | 6042 | 3/10/2016 5:39:26 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL122 | Protection and control Low voltage protection damaged or not provided. | 3 | 3 | Electrical equipment and conductors must be protected from overcurrent with fuses or other current limiting devices. In this installation emergency radio equipment was observed installed without approved protection. | 3 | Protection and control Low voltage protection damaged or not provided. | White_cable_not_protected.png | file://x:/photopub/docs/0000000403/40175c87-69db-4095-8feb-6922a9329877.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85f6a005_6d49_4b1b_83a4_5f8bcb5bfa3c
ELOP-229675-2014 | 6035 | 3/10/2016 4:59:36 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Electrical equipment must be installed so energized parts are not accessible to accidental touch. In this sewage treatment plant a fixture had been removed above an entrance door and the wiring was left hanging without being contained in some sort of approved enclosure. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Meter_base_gone.png | file://x:/photopub/docs/0000000403/1c5a5ec2-f487-45a7-aa08-3efc6f0119c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__467f0018_876a_4cf8_8aa8_5a8e4ba3e976
ELOP-229665-2014 | 6045 | 3/10/2016 5:22:25 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment must be approved for use as installed. In this fire hall unapproved equipment was installed and utilized. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Dart_board_light.png | file://x:/photopub/docs/0000000403/a35072c5-d63c-48e2-a316-78f029b022a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cedaf071_a39a_470d_a8b6_9c16fdaeb299
ELOP-229671-2014 | 6036 | 3/10/2016 4:36:32 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | In sewage lift stations and kiosks it is important to seal off the wet well from electrical equipment to prohibit the transfer of corrosive and potentially explosive gases into an area where a spark could be produced. In this installation the conduits from the wet well were installed without seals in the base of the kiosk. Everything below 12" high including electrical equipment and the kiosk itself were damaged and require replacement. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Effects_of_corrosion.png | file://x:/photopub/docs/0000000403/4a8fb5f1-767c-422b-b8c1-3c3e96840210.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4f7ed14_e688_4321_b3fe_e8bc142233ce
ELOP-229680-2014 | 6046 | 3/10/2016 5:53:02 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Electrical service equipment cannot be used as a junction box or a raceway for conductors. In this installation a fan controller had been installed at the side of a panel with wiring going through the panel to the load. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Switch_leg_through_panel.png | file://x:/photopub/docs/0000000403/c287ce5c-4c2a-40d1-b5ce-32394a0f797e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38b7ae64_dbc5_4276_a636_e23a69d78f58
ELOP-229666-2014 | 6033 | 3/10/2016 6:18:21 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL254 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical equipment which is not in service must be made servicable or permanently disconnected. In this installation an old sewage lift station which was temporarily connected to a replacement system was never removed from service. | 4 | Category 2 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Disconnect_me.png | file://x:/photopub/docs/0000000403/4afba891-c82e-44fb-bf0c-6ff7f64e65db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed93323f_33c0_488a_a040_04a110cd0ee6
ELIN-530226-2016 | EL-307064-2015 | 2/25/2016 12:53:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling exceeds maximum allowable length inside structure for unprotected portion of cabling. This exposes the unprotected portion of unfused consumer service cabling to mechanical damage resulting in personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_suite_distribution.png | file://x:/photopub/docs/0000000396/aa9e7ea6-ddb2-4f99-b71a-c3f7eb5869e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dc68862_cc16_4926_9c28_8da5dc2f8b18
ELIN-530226-2016 | EL-307064-2015 | 2/25/2016 12:53:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service cabling exceeds maximum allowable length inside structure for unprotected portion of cabling. This exposes the unprotected portion of unfused consumer service cabling to mechanical damage resulting in personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View02_service_cabling.png | file://x:/photopub/docs/0000000396/3c83a4cc-ce9c-4403-aac7-e97899e6f4f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dc68862_cc16_4926_9c28_8da5dc2f8b18
ELIN-539541-2016 | EL-302409-2015 | 3/7/2016 3:34:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The improper termination of the grounded circuit conductor can create a shock hazard during a fault condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_ground.png | file://x:/photopub/docs/0000000401/a030b20c-982c-4335-b076-bb8b49087592.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07cc5734_19c0_41b1_b829_ab2919b2e545
ELIN-557457-2016 | UW-374697-2016 | 4/11/2016 9:20:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | Energized and exposed unapproved branch circuit wiring and open splicing of circuitry throughout multiple structures at property designated as single family occupancy only. | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | unapproved_installation_method.png | file://x:/photopub/docs/0000000415/ce0663bb-8889-4a88-92cd-239ce5b5a820.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f25e842b_057b_44b4_a255_261a60cdc2a5
ELIN-550913-2016 | EL-352918-2016 | 3/30/2016 12:57:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 200 amp, 120/240 volt duplex meter base has ground conductor terminated to enclosure bond point. Identified conductor has not been grounded. This is a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_not_terminated_on_identified_conductor.png | file://x:/photopub/docs/0000000409/37c4ed33-7655-4639-a805-6e78aa6705bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5d6b57f_9ff3_4076_9c19_f18bab922200
BPVOP-538685-2016 | 3235332 | 4/1/2016 12:12:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP080 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | 4 | 4 | Refractory is required in order to contain high temperature flame that is inside the boiler due to gas combustion. I found that refractory on the back cover of this high pressure steam boiler was severely eroded possible from water and steam leaks from cracked firetubes and tubesheet. Potential exists for an incident because of missing parts and bad condition of this refractory. | 4 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | Refractory_eroded.png | file://x:/photopub/docs/0000000410/7e903728-39b7-4a69-9cc4-0f44a6a7b9db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8028932c_41c6_4a39_ae41_8000c3bedc20
BPVOP-538685-2016 | 3235332 | 4/1/2016 12:12:24 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP080 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | 4 | 4 | Refractory is required in order to contain high temperature flame that is inside the boiler due to gas combustion. I found that refractory on the back cover of this high pressure steam boiler was severely eroded possible from water and steam leaks from cracked firetubes and tubesheet. Potential exists for an incident because of missing parts and bad condition of this refractory. | 4 | 1.2.3 Boiler construction - Damaged refractory and underlining base metal is deteriorating or shows inductions of overheating. | Overheating_bottom.png | file://x:/photopub/docs/0000000410/f7b28315-4ff4-4701-8b59-e28d55a36ada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8028932c_41c6_4a39_ae41_8000c3bedc20
ELIN-560193-2016 | EL-249378-2015 | 4/15/2016 11:56:04 AM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Box2.png | file://x:/photopub/docs/0000000417/c3fda675-2963-4ac6-b6ce-5b847b92f417.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d095eab_3c65_4ec4_81a8_1e345c8ba7d4
ELIN-560193-2016 | EL-249378-2015 | 4/15/2016 11:56:04 AM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Clearance.png | file://x:/photopub/docs/0000000417/fbdf2b5f-a353-45e5-92a8-f608c2b4b79e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d095eab_3c65_4ec4_81a8_1e345c8ba7d4
ELIN-560193-2016 | EL-249378-2015 | 4/15/2016 11:56:04 AM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Openings.png | file://x:/photopub/docs/0000000417/83778e60-6842-4100-9007-a06dc3493581.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d095eab_3c65_4ec4_81a8_1e345c8ba7d4
ELIN-560193-2016 | EL-249378-2015 | 4/15/2016 11:56:04 AM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Box1.png | file://x:/photopub/docs/0000000417/3d0aab85-7cbf-4628-aaa3-9d331b556b72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d095eab_3c65_4ec4_81a8_1e345c8ba7d4
ELIN-560193-2016 | EL-249378-2015 | 4/15/2016 11:56:04 AM | ASSESS: EL: Final | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Cables1.png | file://x:/photopub/docs/0000000417/6248bc21-c543-4e0a-94f2-40434c9312e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d095eab_3c65_4ec4_81a8_1e345c8ba7d4
ELIN-563403-2016 | UW-378539-2016 | 4/20/2016 12:52:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | An electrical system in a commercial suite with a 100 amp 240 volt feed has had a majority of the lighting and power circuits altered leaving loose electrical equipment and incomplete circuits. The panel is accessible to unauthorized operation. Altered circuits can be easily re energized leaving hazards to both persons and property | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel_ffeding_altered_circuits_all_connected_to_breakers_in_accessible_area_to_unqualified_persons.png | file://x:/photopub/docs/0000000419/b885e609-b470-4e0a-8491-bb6d5f5d1d5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4e52f60_52a5_4dc3_badf_955a7be712a4
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_lighting_and_power_in_garage.png | file://x:/photopub/docs/0000000403/5fd88a15-449b-488f-ae01-5290f7b304f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_wiring_of_light_on_the_exterior_of_the_garage_.png | file://x:/photopub/docs/0000000403/241b64b8-a354-4d21-af01-adf26dcb0951.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_lighting_and_receptacles_in_garage_.png | file://x:/photopub/docs/0000000403/d851951d-8782-4d72-867e-8fd633df7d32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_a_substitute_for_permanent_wiring_in_the_garage.png | file://x:/photopub/docs/0000000403/6f24fe42-6bc1-48b9-a793-1fac19dfefbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Front_of_the_house.png | file://x:/photopub/docs/0000000403/ea5c902c-3fc5-4c82-8563-e81e9c45ea3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_a_s_a_substitute_for_permanent_wiring_in_the_garage.png | file://x:/photopub/docs/0000000403/48a7c7ae-5226-47d5-8be0-5c494d39ea2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_for_lighting_and_receptacles_in_garage.png | file://x:/photopub/docs/0000000403/7536742b-1c24-4533-b6b8-c6d5882da8f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_a_substitute_off_permanent_wiring_method_in_garage.png | file://x:/photopub/docs/0000000403/87e9d11d-2e94-4aff-af10-776e75678d24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-539878-2016 | UW-351335-2016 | 3/11/2016 12:22:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords, extensions cords, splitter cords, and power bars are not permitted to be used as a substitute for permanent wiring. They are not permitted to be fastened to structures or run through walls, ceilings, windows, or door ways. This is not permitted because this type of wiring is not designed or approved to be fastened to structural members or used for extended periods of time in place of permanent wiring methods. Used in this manner this type of equipment may become mechanically damaged, overloaded, and lacks proper fire rating for use as a permanent wiring method. The electrical system in this house has extensive use of flexible cords (extension cords), splitter cords, power bars, and temporary lighting in the garage that is being used as a permanent wiring method due to a lack of permanent wiring in this area. Left uncorrected this poses a fire and shock hazard should this equipment become damaged or overloaded. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_fastened_to_walls_and_ceilings_in_garage.png | file://x:/photopub/docs/0000000403/f6f073c2-c8bf-42e6-ba22-f2c0cdd60fea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b294a5a_d780_43a4_a91a_3daafaa9374b
ELIN-545246-2016 | EL-319361-2015 | 3/22/2016 12:40:33 PM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | Plywood has been used to mount a new 200 amp 240 volt service equipment to an outdoor pole. Plywood and wooden supports have an indeterminable life span and can delaminate unpredictably leaving service equipment loose on a service pole. This condition can lead to a potential for equipment damage and potential injury to persons | 3 | General Equipment is not approved for the specific use | Plywood_and_lumber_used_to_mount_new_service_equipment_to_pole.png | file://x:/photopub/docs/0000000407/e47d5a05-1900-4c18-b84a-745650d4953e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9da2e23d_a239_4623_bc6e_6bd0e957a681
ELIN-544946-2016 | EL-337450-2016 | 3/18/2016 12:20:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | The homeowner did not instal a number six bonding conductor from the electrical panel to the telephone and cable D Mark point. Lightning protection has not been provided for the incoming communications cable | 3 | Continuity Bonding conductor is not observed or broken | Photo_one__Photo_one_no_bonding_conductor_at_the_communications_point.png | file://x:/photopub/docs/0000000405/8497bcfe-0eda-4d3e-9b95-46857ffc46d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1ff4c42_2e96_4876_a84b_1f3d5393ede3
ELIN-544946-2016 | EL-337450-2016 | 3/18/2016 12:20:44 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | The homeowner did not instal a number six bonding conductor from the electrical panel to the telephone and cable D Mark point. Lightning protection has not been provided for the incoming communications cable | 3 | Continuity Bonding conductor is not observed or broken | Photo_number__Photo_number_two_no_bonding_conductor_at_the_communication_point.png | file://x:/photopub/docs/0000000405/06efccda-672b-4d1c-9041-853333bdba51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1ff4c42_2e96_4876_a84b_1f3d5393ede3
ELIN-544472-2016 | UW-367131-2016 | 3/15/2016 10:18:53 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Veterinary electo-medical equipment (X-ray, operation light, autoclave, etc) does not bear evidence of recognized electrical approval by a certification agency Electrical equipment that does not bear evidence of an approval mark by a recognized electrical certification agency may present a fire/shock hazard and therefore is unapproved for use, sale, or display | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | X-ray_.png | file://x:/photopub/docs/0000000405/e7b3f56a-ce6b-4019-9699-6604644bc96f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98253efb_37fd_4472_85ac_cbf5c3259942
ELIN-544472-2016 | UW-367131-2016 | 3/15/2016 10:18:53 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Veterinary electo-medical equipment (X-ray, operation light, autoclave, etc) does not bear evidence of recognized electrical approval by a certification agency Electrical equipment that does not bear evidence of an approval mark by a recognized electrical certification agency may present a fire/shock hazard and therefore is unapproved for use, sale, or display | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Fixt.png | file://x:/photopub/docs/0000000405/581472a7-0ba0-4b05-83a7-383421ad9348.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98253efb_37fd_4472_85ac_cbf5c3259942
ELIN-554703-2016 | EL-331722-2016 | 4/19/2016 3:28:04 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles beside sink are not GFCI protected. This could result in a shock hazard to persons using the sink. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_beside_sink.png | file://x:/photopub/docs/0000000418/c3f130c1-3d52-45fb-86f8-61e538119d90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85b609e6_1ec8_4277_9a66_06766eae932f
ELIN-538572-2016 | UW-356328-2016 | 3/4/2016 3:24:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Houle_1.png | file://x:/photopub/docs/0000000400/db36737e-6ade-41d4-a03e-e5f7f4903860.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef14628_d3e0_4f90_bbb0_5404ce690f5a
ELIN-538572-2016 | UW-356328-2016 | 3/4/2016 3:24:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Houle_2.png | file://x:/photopub/docs/0000000400/14e6e91f-5865-4ec9-bbaf-42708b4a4d94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef14628_d3e0_4f90_bbb0_5404ce690f5a
ELIN-538572-2016 | UW-356328-2016 | 3/4/2016 3:24:53 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Houle_3.png | file://x:/photopub/docs/0000000400/dde8dedb-3214-4aec-aac7-f664c93c1442.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef14628_d3e0_4f90_bbb0_5404ce690f5a
ELIN-554911-2016 | EL-340404-2016 | 4/8/2016 11:22:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Residential construction sites are often equipped with temporary power by energizing what will eventually become the main distribution. However, while the building is open to the elements the distribution must be protected with a lockable enclosure. In this installation a sheet of plastic was used as a barrier. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Not_protected.png | file://x:/photopub/docs/0000000414/20a5739f-12a4-4599-a1f0-61380ba42371.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9aec5ab_3f80_4747_ac5b_01ebe6f23e69
ELIN-551591-2016 | EL-367135-2016 | 4/8/2016 1:55:53 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Generators and sub-feeder cables must be sized to properly and safety handle the loads connected to them. This is required to ensure the system works properly, breakers do not trip and most importantly electrical equipment and components do not become overloaded and thermally damaged. This installation of a back up generator for a house has a connected load and calculated load that exceeds the rating of the feeder cable and the generator. Left uncorrected this is a potential fire hazard if equipment repeatedly becomes over loaded causing it to malfunction. | 3 | Protection and control Loading of distribution equipment exceeded | New_generator_.png | file://x:/photopub/docs/0000000414/e1be00ec-cf5a-4632-8419-1f648a589e16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92cca72f_12df_4ce3_922f_a2f898ca0644
ELIN-551591-2016 | EL-367135-2016 | 4/8/2016 1:55:53 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Generators and sub-feeder cables must be sized to properly and safety handle the loads connected to them. This is required to ensure the system works properly, breakers do not trip and most importantly electrical equipment and components do not become overloaded and thermally damaged. This installation of a back up generator for a house has a connected load and calculated load that exceeds the rating of the feeder cable and the generator. Left uncorrected this is a potential fire hazard if equipment repeatedly becomes over loaded causing it to malfunction. | 3 | Protection and control Loading of distribution equipment exceeded | Panel_directory_for_connected_loads_on_generator.png | file://x:/photopub/docs/0000000414/58e29cfd-fd4d-4e57-9d75-a4181bc90e14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92cca72f_12df_4ce3_922f_a2f898ca0644
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Lowest_venting_is_from_mezzanine_above_shop_floor.png | file://x:/photopub/docs/0000000416/ddc06bc0-c106-4b12-aad0-3db8c129a991.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Receptacles_in_pit.png | file://x:/photopub/docs/0000000416/dca97dd2-89d5-4f2e-a0f6-dc0e51ad2448.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Oil_tanks_in_pit.png | file://x:/photopub/docs/0000000416/9715df74-08a0-4625-8c7f-bc5e88cd723c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Stairs_down_to_pit.png | file://x:/photopub/docs/0000000416/65caa8d7-e041-4f13-b160-75d5c438744f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Pit.png | file://x:/photopub/docs/0000000416/7b6016f0-837e-413f-8f00-78534de2f80d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | View_of_stairs_from_pit_level.png | file://x:/photopub/docs/0000000416/fa3b0413-6912-4812-9b2b-e7635de31cf0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Another_vent_in_ceiling_of_shop.png | file://x:/photopub/docs/0000000416/e946ab19-f2fc-43d1-ba00-c1452ef4c91d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Lighting_and_receptacles_in_pit.png | file://x:/photopub/docs/0000000416/4c96a3b2-e5d3-49ac-bf21-5ef5a29d9471.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-559265-2016 | EL-291547-2015 | 4/14/2016 11:26:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in a hazardous location. This could result in an explosion and serious injuries. | 3 | Conductors Equipment is not approved for the specific use. | Lighting_and_receptacle_on_pit_ceiling.png | file://x:/photopub/docs/0000000416/3ca4d3b0-a84f-434f-a378-b6fec3a55e36.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68830532_1ede_4ee5_a43a_689cde0234ce
ELIN-552734-2016 | UW-371712-2016 | 3/31/2016 11:26:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | NMD 90 used in various locations is damaged. This could be an eventual fire/shock hazard due to the damaged nylon sheathing. This could eventually cause a short circuit or small arcing fault that will either cause a fire or eventually shock a person. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_NMD_90_2.png | file://x:/photopub/docs/0000000410/fe8feaf9-d5e6-4b81-a992-cbbfffaf2613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0befd22b_9ca6_4017_b7b8_4d2ae525d702
ELIN-552734-2016 | UW-371712-2016 | 3/31/2016 11:26:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | NMD 90 used in various locations is damaged. This could be an eventual fire/shock hazard due to the damaged nylon sheathing. This could eventually cause a short circuit or small arcing fault that will either cause a fire or eventually shock a person. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Exposed_NMD_90.png | file://x:/photopub/docs/0000000410/4cf0da9f-5857-4a7c-8c88-a94672d0a59c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0befd22b_9ca6_4017_b7b8_4d2ae525d702
ELIN-551591-2016 | EL-367135-2016 | 4/8/2016 1:55:53 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Generators and sub-feeder cables must be sized to properly and safety handle the loads connected to them. This is required to ensure the system works properly, breakers do not trip and most importantly electrical equipment and components do not become overloaded and thermally damaged. This installation of a back up generator for a house has a connected load and calculated load that exceeds the rating of the feeder cable and the generator. Left uncorrected this is a potential fire hazard if equipment repeatedly becomes over loaded causing it to malfunction. | 3 | Protection and control Loading of distribution equipment exceeded | Interior_of_generator_panel.png | file://x:/photopub/docs/0000000414/11a2bc97-033c-417d-b085-e0d287b06ece.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92cca72f_12df_4ce3_922f_a2f898ca0644
ELIN-551591-2016 | EL-367135-2016 | 4/8/2016 1:55:53 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Generators and sub-feeder cables must be sized to properly and safety handle the loads connected to them. This is required to ensure the system works properly, breakers do not trip and most importantly electrical equipment and components do not become overloaded and thermally damaged. This installation of a back up generator for a house has a connected load and calculated load that exceeds the rating of the feeder cable and the generator. Left uncorrected this is a potential fire hazard if equipment repeatedly becomes over loaded causing it to malfunction. | 3 | Protection and control Loading of distribution equipment exceeded | Rating_label_on_generator.png | file://x:/photopub/docs/0000000414/ba0b045a-c864-4b0d-9a31-c59561a2083c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92cca72f_12df_4ce3_922f_a2f898ca0644
ELIN-551591-2016 | EL-367135-2016 | 4/8/2016 1:55:53 PM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | Generators and sub-feeder cables must be sized to properly and safety handle the loads connected to them. This is required to ensure the system works properly, breakers do not trip and most importantly electrical equipment and components do not become overloaded and thermally damaged. This installation of a back up generator for a house has a connected load and calculated load that exceeds the rating of the feeder cable and the generator. Left uncorrected this is a potential fire hazard if equipment repeatedly becomes over loaded causing it to malfunction. | 3 | Protection and control Loading of distribution equipment exceeded | 50A_main_breaker_on_generator.png | file://x:/photopub/docs/0000000414/06badedc-fb94-4e3e-8834-7a6893c20b75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92cca72f_12df_4ce3_922f_a2f898ca0644
ELIN-538544-2016 | EL-353096-2016 | 3/8/2016 10:22:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The temporary construction receptacles do not provide protection from energized terminals, this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Temp_recept__2.png | file://x:/photopub/docs/0000000401/faa1188e-98aa-427b-9f69-735a1e038528.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a5c0371_16f2_4c3a_af06_5f9b9b2a8160
ELIN-538544-2016 | EL-353096-2016 | 3/8/2016 10:22:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The temporary construction receptacles do not provide protection from energized terminals, this is a shock hazard | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Temp_receptacle.png | file://x:/photopub/docs/0000000401/17cd6c1a-a947-4e61-8dd8-2380840e271f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a5c0371_16f2_4c3a_af06_5f9b9b2a8160
ELIN-560222-2016 | EL-106889-2014 | 4/22/2016 10:35:01 AM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Service switches come from the factory with termination lugs that have been installed, tested, and approved for that particular piece of equipment. Modifying or removing the original lugs and replacing them with lugs that have not been confirmed as approved for that particular piece of equipment may cause the terminations to over heat and fail. This installation has a 200A, 120/240V service switch that has had the original lugs on the load side of the switch removed and replaced with lugs that that were not originally supplied with the equipment and not confirmed as compatible or approved for use with this particular switch. Left uncorrected this is a potential fire hazard if the conductor terminations fail and over heat. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Service_switch_on_pole.png | file://x:/photopub/docs/0000000420/243dfba5-5c6f-4e38-b0c6-2a309ca56f71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e268b7c8_87e4_4bbc_ab7c_fcccd2e7d374
ELIN-560222-2016 | EL-106889-2014 | 4/22/2016 10:35:01 AM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Service switches come from the factory with termination lugs that have been installed, tested, and approved for that particular piece of equipment. Modifying or removing the original lugs and replacing them with lugs that have not been confirmed as approved for that particular piece of equipment may cause the terminations to over heat and fail. This installation has a 200A, 120/240V service switch that has had the original lugs on the load side of the switch removed and replaced with lugs that that were not originally supplied with the equipment and not confirmed as compatible or approved for use with this particular switch. Left uncorrected this is a potential fire hazard if the conductor terminations fail and over heat. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Lugs_on_load_side_of_switch_modified_to_connect_two_cables.png | file://x:/photopub/docs/0000000420/c292f1c6-46e7-41c0-bc95-147a3a1112a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e268b7c8_87e4_4bbc_ab7c_fcccd2e7d374
ELIN-560222-2016 | EL-106889-2014 | 4/22/2016 10:35:01 AM | ASSESS: EL: Final | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Service switches come from the factory with termination lugs that have been installed, tested, and approved for that particular piece of equipment. Modifying or removing the original lugs and replacing them with lugs that have not been confirmed as approved for that particular piece of equipment may cause the terminations to over heat and fail. This installation has a 200A, 120/240V service switch that has had the original lugs on the load side of the switch removed and replaced with lugs that that were not originally supplied with the equipment and not confirmed as compatible or approved for use with this particular switch. Left uncorrected this is a potential fire hazard if the conductor terminations fail and over heat. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Lugs_on_load_side_of_switch_modified_to_connect_two_service_cables.png | file://x:/photopub/docs/0000000420/eeab39b2-bd8b-4bf7-81f8-94a837cd60ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e268b7c8_87e4_4bbc_ab7c_fcccd2e7d374
BPVOP-567879-2016 | 2290227 | 4/28/2016 12:11:26 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | HORIZONTAL_RELIEF_VALVE.png | file://x:/photopub/docs/0000000422/42f766fa-f8d0-4bcd-980d-c1a28d5cdab7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1e151fc_771d_481e_97b3_2e4ba2ab8cd9
ELOP-548121-2016 | 5194147 | 3/29/2016 4:23:55 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 15 amp, 120 volt receptacle, is installed within 1.5 meters of a sink without GFCI protection provided in a commercial kitchen application. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_within_1_5_meters_of_sink.png | file://x:/photopub/docs/0000000409/e939920d-0fd9-4e95-acec-5bfd3731f09b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82e2b244_04c8_49ba_83eb_8f21a7f124ba
ELIN-545135-2016 | EL-291032-2015 | 3/21/2016 1:27:08 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found exposed conductors and bus bars on panelboards that are connected to power supply system which could easily become energized and hazardous and non-compliant once service is connected as contractor had declared and requested for service connection. When electrical conductors are exposed and energized with all panelboard covers missing and energized conductors could come in contact with people or property, the electrical system is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 1.png | file://x:/photopub/docs/0000000408/5f54c93d-e5b0-4dc6-9ccc-7189c7dfc56f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54e5ada0_c434_455e_ba82_3ebd634044dd
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_duct_.png | file://x:/photopub/docs/0000000409/d4d3b88e-dc22-4f4d-91af-c2c349b98eb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_loser_than_32mm_from_face_of_stud.png | file://x:/photopub/docs/0000000409/181120fd-48fe-4f7b-a4fa-fc31fc413d4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_on_top_of_trusses_.png | file://x:/photopub/docs/0000000409/46a9f33b-f510-4774-b806-5f6fefff0415.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
ELIN-547392-2016 | EL-228289-2015 | 3/30/2016 3:50:55 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles are required to be protected by over-current devices that do not exceed the ampacity of the receptacle. This is required so that the receptacle does not get thermally damaged from an over current or over load condition. This installation has eight 30A, 120/240V dryer receptacles connected to 40A branch circuit conductors and 40A breakers. Left uncorrected this is a potential fire hazard if the receptacles become overloaded or if there is a fault causing an over current condition at the receptacles. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Panel_directory.png | file://x:/photopub/docs/0000000409/666f2db1-8881-4f9a-a244-30a367681d48.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__062216c0_fc3f_4301_934d_d7d1ae32993a
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_on_top_of_trusses.png | file://x:/photopub/docs/0000000409/5d5d512e-aa92-4832-9403-3dce0cc6fe30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
ELIN-547392-2016 | EL-228289-2015 | 3/30/2016 3:50:55 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles are required to be protected by over-current devices that do not exceed the ampacity of the receptacle. This is required so that the receptacle does not get thermally damaged from an over current or over load condition. This installation has eight 30A, 120/240V dryer receptacles connected to 40A branch circuit conductors and 40A breakers. Left uncorrected this is a potential fire hazard if the receptacles become overloaded or if there is a fault causing an over current condition at the receptacles. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Circuit_2_4_6_8_10_12_14_16_are_40A_breakers_protecting_30A_receptacles.png | file://x:/photopub/docs/0000000409/dbd0b44c-b96f-4777-b70b-16ea94a2b457.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__062216c0_fc3f_4301_934d_d7d1ae32993a
ELIN-559591-2016 | EL-347473-2016-1 | 4/15/2016 8:03:34 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A three conductor armoured cable service conductor exceeds 1.5 meters in a framed area. This is a thermal hazard should a fault occur in the service conductor. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_conductors_exceed_1_5_meters_inside_building_.png | file://x:/photopub/docs/0000000417/18888d07-c018-4c1d-ba51-0c59859654da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2bfd1fa4_8a23_4ab9_b85f_c7aaea5539a4
ELIN-559551-2016 | UW-376322-2016 | 4/15/2016 12:25:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 volt branch wiring in a commercial establishment is not terminated in an acceptable method. Branch wiring is exposed for accidental contact. This building is currently locked and the general public does not have access. This is a shock hazard should the branch wiring be energized. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Branch_wiring_without_approved_terminations_or_outlet_boxes.png | file://x:/photopub/docs/0000000417/b6d930ea-c23d-45fb-97a8-d60cbc981726.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30a3603f_3d1f_42d6_ae7d_f7d86aa88b39
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Front_of_new_house_under_construction.png | file://x:/photopub/docs/0000000409/621c2eb0-9fa0-4b1c-b5dc-6a4ac1811605.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_duct.png | file://x:/photopub/docs/0000000409/9a7d98b5-6fba-4a90-9468-e014ffb5312a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
ELIN-547392-2016 | EL-228289-2015 | 3/30/2016 3:50:55 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles are required to be protected by over-current devices that do not exceed the ampacity of the receptacle. This is required so that the receptacle does not get thermally damaged from an over current or over load condition. This installation has eight 30A, 120/240V dryer receptacles connected to 40A branch circuit conductors and 40A breakers. Left uncorrected this is a potential fire hazard if the receptacles become overloaded or if there is a fault causing an over current condition at the receptacles. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Laundry_room_panel.png | file://x:/photopub/docs/0000000409/0edb150c-a77c-4162-a5e8-9f2081297593.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__062216c0_fc3f_4301_934d_d7d1ae32993a
BPVIN-539436-2016 | UW-356804-2016 | 3/7/2016 3:42:46 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP134 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Safety devices bypassed or failed but the back up corresponding safety devices operational | 4 | 4 | Upon the assessment of an Electric High Pressure Boiler with a working pressure of 100 psi, I found the gauge glass broken and the valves were shut for the last 2 years. Potential exists for a low water condition, and if the backup devices will not function, can result in equipment or personnel damage. | 4 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Safety devices bypassed or failed but the back up corresponding safety devices operational | Broken_gauge_glass.png | file://x:/photopub/docs/0000000401/e444b257-073e-4e60-b6d7-7081e7096554.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d51d3328_597b_4e13_a4c9_8bb6be8b0a76
ELIN-539923-2016 | EL-358043-2016 | 3/9/2016 8:56:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The grounding conductor was terminated on the wrong portion of the electrical panel. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Ground_conductor__ground_conductor_terminated_at_wrong_spot.png | file://x:/photopub/docs/0000000402/671a722a-d9ad-489b-af36-457be37c2a30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__940c240c_7f74_4def_be0c_d0a1ed8fc6f0
BPVOP-534968-2016 | 5294676 | 3/2/2016 1:49:17 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP060 | 1.2.2 Boiler leakage: procedure - Minor leaks from flanges or hand whole covers. | 3 | 3 | Boiler fittings and piping are required to hold the contents of the fluid medium under pressure. I found heavy leakage at flanged and union joints of a 2006 hot water boilers outlet operating at 30psi.This can lead to environmental and mechanical damage to the boiler and surrounding equipment. | 3 | 1.2.2 Boiler leakage: procedure - Minor leaks from flanges or hand whole covers. | Boiler_outlet_leakage.png | file://x:/photopub/docs/0000000402/a4ceb372-e331-4ab7-b524-08c22a9af04e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4afd036_0f20_4024_8464_6d532d13af6c
BPVOP-534968-2016 | 5294676 | 3/2/2016 1:49:17 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP060 | 1.2.2 Boiler leakage: procedure - Minor leaks from flanges or hand whole covers. | 3 | 3 | Boiler fittings and piping are required to hold the contents of the fluid medium under pressure. I found heavy leakage at flanged and union joints of a 2006 hot water boilers outlet operating at 30psi.This can lead to environmental and mechanical damage to the boiler and surrounding equipment. | 3 | 1.2.2 Boiler leakage: procedure - Minor leaks from flanges or hand whole covers. | Boiler_with_leak_evidence.png | file://x:/photopub/docs/0000000402/a1464ef5-f263-420b-8b4f-b9bea1a9eea9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4afd036_0f20_4024_8464_6d532d13af6c
ELIN-568139-2016 | UW-381449-2016 | 4/29/2016 12:13:42 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Old manually operated knife switch. Oxidation of conductors from dissimilar metals. These switches are dangerous to open under load as they can arc. The oxidation of the conductors is a fire hazard as it impedes the flow of current which can cause excessive heat. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | A.png | file://x:/photopub/docs/0000000422/f6cf918d-e2f1-4362-b992-f371b014c5a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d42ae314_c737_434f_b7c4_5eba7541d01d
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Actuator_motor.png | file://x:/photopub/docs/0000000410/2883e4c9-1be1-4a54-9dbc-91cef056aee6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Unapproved_gate_controller___.png | file://x:/photopub/docs/0000000410/3fa3a13b-91df-4cb1-8d8f-736a69cfb77e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Gates_at_end_of_drive_way.png | file://x:/photopub/docs/0000000410/0c3ab770-5d75-4209-af1c-60fb2641c13d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Water_in_box_on_gate_post.png | file://x:/photopub/docs/0000000410/925103a6-91ab-4e0f-956a-9b876b3a97ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Water_in_junction_box.png | file://x:/photopub/docs/0000000410/7b042942-dc0f-42df-814f-a98c9d00b222.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Unapproved_gate_controller_.png | file://x:/photopub/docs/0000000410/2e26191a-38d8-4c9e-af2a-10380b2ef362.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Label_on_gate_controller_.png | file://x:/photopub/docs/0000000410/6917aae8-37a7-47e9-86a5-fa7d8006c165.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Unapproved_wiring_and_equipment.png | file://x:/photopub/docs/0000000410/7f5dfd96-11bd-4323-80d4-654efb8f87f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Label_on_gate_controller.png | file://x:/photopub/docs/0000000410/0a892c2a-8b13-4169-91e0-ae6bf9814d5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
AMOP-564591-2016 | 2042450 | 4/22/2016 10:56:01 AM | ASSESS: AM OP: Periodic | png | #asFound | AM037 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Flaking and chipping in noted in the fibreglass slide surface present a laceration injury hazard to riders sliding on the slide. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Chipping_and_flaking_in_slide_surface.png | file://x:/photopub/docs/0000000423/456d39f6-7f07-404a-a819-d250a93f6dc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f7f0954_acb8_4f2f_a3fb_f2f160b2e39e
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Actuator_motor_label.png | file://x:/photopub/docs/0000000410/54a2a10a-2f30-43b9-b2cc-b2e931cf69e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Junction_box_and_connections_submerged_in_water.png | file://x:/photopub/docs/0000000410/120f0b5e-6bc7-4a29-9e24-cbb4c207ce81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-552101-2016 | UW-371352-2016 | 3/31/2016 5:04:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Under ground and outdoor locations are considered wet locations. Wiring methods and equipment installed in outdoor locations must be installed correctly and approved for the locations where they are installed. This is required to prevent equipment from getting wet and corroded there by damaging the it. This installation has wiring installed to and connections for automatic gate operators and their associated equipment that is not approved for the location and is not installed correctly. Water is entering the equipment conduits and enclosures wetting connections and equipment. Left uncorrected this will cause damage to the equipment and eventual failure potentially creating a shock and fire hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Unapproved_gate_controller__.png | file://x:/photopub/docs/0000000410/adce582e-4a17-4b2e-974b-e172b5b83a07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e0fc726_7ce8_458a_9f83_a6b7e88212d9
ELIN-551402-2016 | EL-353575-2016 | 3/31/2016 9:34:21 PM | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | During a used mobile home inspection! two outlet boxes were found to be loose in the wall cavity. This presents a possible shock hazard for anyone trying to insert or remove a plug from the outlet. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Outlet_box_not_secured_in_wall_.png | file://x:/photopub/docs/0000000410/1e40454e-cc3a-423f-a471-3b79fefe10bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9aa1f5c8_43d0_4d44_b949_8ea281a5e961
ELIN-552254-2016 | EL-367777-2016 | 4/1/2016 10:33:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2_inch_rigTo__2_inch_rigid_conduit_complete_with_coupling_above_roofline.png | file://x:/photopub/docs/0000000410/43cb60a7-ec81-4e06-be90-a3ff72c83031.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__baeee55a_81ef_4e58_bf8c_fbdef70459f5
ELIN-539374-2016 | EL-356721-2016 | 3/9/2016 10:52:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The energized 250? Amp 120/208 volt 3 phase 4 wire panelboard does not have the cover installed. No electricians on site. This is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Sylvania_panelboard_4.png | file://x:/photopub/docs/0000000402/2278aca0-792f-4f2a-89b6-5da159eaa813.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf8e17c9_a8c0_440d_821f_0163b43049c2
ELIN-539374-2016 | EL-356721-2016 | 3/9/2016 10:52:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The energized 250? Amp 120/208 volt 3 phase 4 wire panelboard does not have the cover installed. No electricians on site. This is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Sylvania_panelboard_1.png | file://x:/photopub/docs/0000000402/942a4c05-7d69-4bfd-adde-fa3c82d24c57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf8e17c9_a8c0_440d_821f_0163b43049c2
ELIN-539374-2016 | EL-356721-2016 | 3/9/2016 10:52:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The energized 250? Amp 120/208 volt 3 phase 4 wire panelboard does not have the cover installed. No electricians on site. This is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Sylvania_panelboard_3.png | file://x:/photopub/docs/0000000402/3e598f0f-18d3-4100-8952-5de7d905c263.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf8e17c9_a8c0_440d_821f_0163b43049c2
ELIN-528326-2016 | EL-222409-2015 | 3/9/2016 12:55:16 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt exterior wall light is not mounted or approved for the location, this is a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Back_half_of_shop_ceiling.png | file://x:/photopub/docs/0000000402/58c5e04f-ccbe-40c2-8065-be3f81f08359.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d67c391_5902_4dd7_a94f_b8e22f8e0301
ELIN-539374-2016 | EL-356721-2016 | 3/9/2016 10:52:20 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The energized 250? Amp 120/208 volt 3 phase 4 wire panelboard does not have the cover installed. No electricians on site. This is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Sylvania_panelboard_2.png | file://x:/photopub/docs/0000000402/738e2a86-7cb7-4ba7-9291-195056bf0dcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf8e17c9_a8c0_440d_821f_0163b43049c2
ELIN-528326-2016 | EL-222409-2015 | 3/9/2016 12:55:16 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt exterior wall light is not mounted or approved for the location, this is a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_light.png | file://x:/photopub/docs/0000000402/a627a52d-5788-4873-9126-578506042822.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d67c391_5902_4dd7_a94f_b8e22f8e0301
ELIN-528326-2016 | EL-222409-2015 | 3/9/2016 12:55:16 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt exterior wall light is not mounted or approved for the location, this is a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Front_half_of_shop_ceiling.png | file://x:/photopub/docs/0000000402/d95ce5d3-f5fe-4e7c-bdcc-8282a5d4ba29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d67c391_5902_4dd7_a94f_b8e22f8e0301
ELIN-551351-2016 | EL-338026-2016 | 3/30/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found dual lug 120/240 volt 200amp consumer's service meter-base which feeds 2 sets of consumer's service disconnects that have a 100amp breaker in each of these service disconnects. The load end of the above 100amp service breakers have feeder conductors terminated onto the above 100amp breakers while the other end of these feeder cable conductors are hanging mid-air and are not terminated in an enclosure and have bare exposed aluminum conductor ends. If the consumer's service is connected by the utility (as contractor authorized service connection) and any of the above 100 amp service breakers are turned on, then there would be the potential of exposed energized bare conductors on load ends which could be an electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | 34.png | file://x:/photopub/docs/0000000410/02162cce-859c-442f-9fc0-9f6ea667df68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba87fe60_9e90_4723_b0e4_3574e303414b
ELIN-551351-2016 | EL-338026-2016 | 3/30/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found dual lug 120/240 volt 200amp consumer's service meter-base which feeds 2 sets of consumer's service disconnects that have a 100amp breaker in each of these service disconnects. The load end of the above 100amp service breakers have feeder conductors terminated onto the above 100amp breakers while the other end of these feeder cable conductors are hanging mid-air and are not terminated in an enclosure and have bare exposed aluminum conductor ends. If the consumer's service is connected by the utility (as contractor authorized service connection) and any of the above 100 amp service breakers are turned on, then there would be the potential of exposed energized bare conductors on load ends which could be an electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | 30.png | file://x:/photopub/docs/0000000410/e8dd35ec-b8a9-4f27-a91d-0b0cdb9a5113.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba87fe60_9e90_4723_b0e4_3574e303414b
ELIN-551351-2016 | EL-338026-2016 | 3/30/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found dual lug 120/240 volt 200amp consumer's service meter-base which feeds 2 sets of consumer's service disconnects that have a 100amp breaker in each of these service disconnects. The load end of the above 100amp service breakers have feeder conductors terminated onto the above 100amp breakers while the other end of these feeder cable conductors are hanging mid-air and are not terminated in an enclosure and have bare exposed aluminum conductor ends. If the consumer's service is connected by the utility (as contractor authorized service connection) and any of the above 100 amp service breakers are turned on, then there would be the potential of exposed energized bare conductors on load ends which could be an electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | 32.png | file://x:/photopub/docs/0000000410/883313b1-0d25-49d9-8e0b-e437eb2d3ded.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba87fe60_9e90_4723_b0e4_3574e303414b
ELIN-551351-2016 | EL-338026-2016 | 3/30/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found dual lug 120/240 volt 200amp consumer's service meter-base which feeds 2 sets of consumer's service disconnects that have a 100amp breaker in each of these service disconnects. The load end of the above 100amp service breakers have feeder conductors terminated onto the above 100amp breakers while the other end of these feeder cable conductors are hanging mid-air and are not terminated in an enclosure and have bare exposed aluminum conductor ends. If the consumer's service is connected by the utility (as contractor authorized service connection) and any of the above 100 amp service breakers are turned on, then there would be the potential of exposed energized bare conductors on load ends which could be an electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | 33.png | file://x:/photopub/docs/0000000410/936deba0-b1bc-4801-bddb-e9200afedc3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba87fe60_9e90_4723_b0e4_3574e303414b
ELIN-551351-2016 | EL-338026-2016 | 3/30/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found dual lug 120/240 volt 200amp consumer's service meter-base which feeds 2 sets of consumer's service disconnects that have a 100amp breaker in each of these service disconnects. The load end of the above 100amp service breakers have feeder conductors terminated onto the above 100amp breakers while the other end of these feeder cable conductors are hanging mid-air and are not terminated in an enclosure and have bare exposed aluminum conductor ends. If the consumer's service is connected by the utility (as contractor authorized service connection) and any of the above 100 amp service breakers are turned on, then there would be the potential of exposed energized bare conductors on load ends which could be an electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | 31.png | file://x:/photopub/docs/0000000410/eecea586-c054-4841-b0d6-a28b9a7b3cd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba87fe60_9e90_4723_b0e4_3574e303414b
ELIN-551351-2016 | EL-338026-2016 | 3/30/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL051 | Protection and control Switching is not done in an ungrounded conductor | 4 | 4 | Found dual lug 120/240 volt 200amp consumer's service meter-base which feeds 2 sets of consumer's service disconnects that have a 100amp breaker in each of these service disconnects. The load end of the above 100amp service breakers have feeder conductors terminated onto the above 100amp breakers while the other end of these feeder cable conductors are hanging mid-air and are not terminated in an enclosure and have bare exposed aluminum conductor ends. If the consumer's service is connected by the utility (as contractor authorized service connection) and any of the above 100 amp service breakers are turned on, then there would be the potential of exposed energized bare conductors on load ends which could be an electrical fire or shock hazard to people and property. | 4 | Protection and control Switching is not done in an ungrounded conductor | 35.png | file://x:/photopub/docs/0000000410/0eb96da9-c0b3-44b5-898c-4939b7659bdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba87fe60_9e90_4723_b0e4_3574e303414b
ELOP-195321-2014 | 7062 | 4/14/2016 4:30:18 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 3 | Separately derived electrical system, the secondary of the transformer, was not grounded creating a potential shock hazard during a fault condition. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Transformer_nameplate_XO_not_grounded_.png | file://x:/photopub/docs/0000000418/fb50961e-c796-4062-a983-fcd16d7d0869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__656f3d86_89a7_41fc_836d_7d1c2428cd51
ELIN-570318-2016 | UW-382399-2016 | 5/2/2016 8:02:53 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The panel cover is off exposing the panel bus to accidental contact which can cause serious injury due to arc flash. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel.png | file://x:/photopub/docs/0000000424/92db3144-f99f-46a3-aa06-8a587d093d0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e098b23_2f74_45ab_b6a3_e986facb250b
ELIN-570318-2016 | UW-382399-2016 | 5/2/2016 8:02:53 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The panel cover is off exposing the panel bus to accidental contact which can cause serious injury due to arc flash. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Teck__teleduct.png | file://x:/photopub/docs/0000000424/a5f9f7de-7eb6-40cf-9ff1-4c3f1ced8274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e098b23_2f74_45ab_b6a3_e986facb250b
GAUP-564677-2016 | UW-379310-2016 | 4/20/2016 11:34:56 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA015 | Clearance to combustibles not maintained imminent hazard during operation | 4 | 4 | At time of inspection found a non secured 100 LB cylinder with regulator and rubber hose beside the generator exhaust. This could create a hazard as when the generator is running the exhaust could melt the rubber hose or over heat the cylinder and relief valve could release raw propane gas. | 4 | Clearance to combustibles not maintained imminent hazard during operation | Gen1.png | file://x:/photopub/docs/0000000420/3660e670-0025-49dc-9f37-5fc0bb8250f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ed6e97_7488_4e8e_ba51_f09e0a6261ef
GAUP-564677-2016 | UW-379310-2016 | 4/20/2016 11:34:56 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA015 | Clearance to combustibles not maintained imminent hazard during operation | 4 | 4 | At time of inspection found a non secured 100 LB cylinder with regulator and rubber hose beside the generator exhaust. This could create a hazard as when the generator is running the exhaust could melt the rubber hose or over heat the cylinder and relief valve could release raw propane gas. | 4 | Clearance to combustibles not maintained imminent hazard during operation | Gen2.png | file://x:/photopub/docs/0000000420/77f854b2-2d40-47fd-8718-632d78bea8fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ed6e97_7488_4e8e_ba51_f09e0a6261ef
ELIN-545221-2016 | EL-313105-2015 | 3/18/2016 10:20:06 AM | ASSESS: EL: Final | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Equipment is labeled for use in US but not Canada. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Approval_label.png | file://x:/photopub/docs/0000000405/745b26bd-c7cf-4e95-8968-a37095153f44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8430f3cd_e956_4db0_a801_48fe51c1c57f
ELIN-556595-2016 | EL-251591-2015 | 4/11/2016 11:53:16 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 40 amp, 120/240 volt non metallic sheathed cable located with in 1.5 meters of floor not mechanically protected. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_with_no_mechanical_protection.png | file://x:/photopub/docs/0000000415/add78cf8-1b2f-4739-b399-818483c6588d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d95f830_60c0_4530_917d_4d5b7b630900
ELIN-555658-2016 | EL-371336-2016 | 4/7/2016 2:14:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 15 amp, 120 volt approved recessed incandescent fixture modified to have LED driver and fixture installed within it. This is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Incandescent_housing_used_as_a_retro_housing.png | file://x:/photopub/docs/0000000413/dc9f1128-80b7-429a-8938-bf8892a8e981.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55e59650_06e1_40c5_b534_cab8d4d0d0d8
ELIN-542456-2016 | EL-358259-2016 | 3/24/2016 10:38:08 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | 15A GFCI outlet has been connected with the wrong polarity, this could cause the outlet not to function and trip as designed posing a shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | GFCI.png | file://x:/photopub/docs/0000000408/cf777f01-f6ca-43df-85c8-7cab7ec61762.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__035008cc_8c77_42a3_96ac_e54457003d1a
ELIN-551801-2016 | EL-367727-2016 | 4/1/2016 10:17:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | 100 amp, 120/240 volt overhead service has a unapproved mast assembly installed to support overhead utility service conductors. This is a shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Mast_not_approved_for_installation.png | file://x:/photopub/docs/0000000411/0e27225e-a33b-40ca-8a43-464e6a146921.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__45deba15_d022_4283_be23_592b499a2b42
ELIN-545164-2016 | EL-321025-2015 | 3/21/2016 4:41:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The armoured cabling is improperly terminated in a manner that isolates the metallic armour from the system bonding. This poses a risk of personal injury (shock) or property damage (thermal event) if the amour of the cabling is placed into an energized state. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | View01_feeder_cabling.png | file://x:/photopub/docs/0000000406/c73fc292-3778-44b2-a530-faae990600f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f83c67d6_f7e6_4b66_bea2_69a473c6ba13
ELIN-545167-2016 | EL-321025-2015 | 3/21/2016 5:28:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The armoured cabling is improperly terminated in a manner that isolates the metallic armour from the system bonding and provides no means of mechanical support, resulting in strain placed on the connection at the terminals. This poses a risk of personal injury (shock) or property damage (thermal event) if the amour of the cabling is placed into an energized state or the terminations are subjected to mechanical strain. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Detail02_service_cabling-meter_base.png | file://x:/photopub/docs/0000000406/eb1b986c-b701-4e28-a121-e32b1e4c9cd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__029cbe3f_556c_463b_acd2_7bee6de72fd1
ELIN-542919-2016 | EL-307034-2015 | 3/21/2016 6:03:07 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Service raceway, accessible to general public, is improperly installed and subjected to the effects of mechanical damage caused by movement of service pole independent of that of the service equipment enclosure. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | View01_service_conduit.png | file://x:/photopub/docs/0000000406/a427490b-8e0e-4083-bb28-30b8c0947f2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bbb8b07_18f0_4912_811a_9135ebd49b1f
ELIN-543840-2016 | 5216286 | 3/16/2016 10:55:57 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Suite 401 is being renovated at time of final inspection. Switch and receptacle devices are hanging out of boxes or are not installed and are energized resulting in exposure to electric shock. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Range_receptacle_not_installed.png | file://x:/photopub/docs/0000000405/aa3dece9-8087-483e-99f6-6546c1a74dff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0dc13313_25f5_4f72_a659_058e4418d9bc
ELIN-546548-2016 | EL-237247-2015 | 3/21/2016 5:23:22 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | 15A 120V Ceiling outlet box is energized but missing a cover or device, this poses a shock hazard to persons. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Smoke_Alarm.png | file://x:/photopub/docs/0000000406/499c43b7-bf98-46ec-b08b-c8480630059d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56b2678c_546f_4ac3_a807_e77496891a0b
ELIN-562339-2016 | UW-377894-2016 | 4/20/2016 2:33:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Kitchen_receptacle.png | file://x:/photopub/docs/0000000418/d99a1ccd-46a6-470c-aaac-ec5942e0d223.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12893085_e10a_4ad1_90fc_95875eb335b7
ELIN-562339-2016 | UW-377894-2016 | 4/20/2016 2:33:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Outdoor_wiring.png | file://x:/photopub/docs/0000000418/a04b74e8-94e0-4f98-90a9-1aa5f2bc2fe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12893085_e10a_4ad1_90fc_95875eb335b7
ELIN-562339-2016 | UW-377894-2016 | 4/20/2016 2:33:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pete.png | file://x:/photopub/docs/0000000418/7acc46c0-f19d-4937-9bcc-4fd51cd4a869.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12893085_e10a_4ad1_90fc_95875eb335b7
ELIN-562339-2016 | UW-377894-2016 | 4/20/2016 2:33:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Boxes.png | file://x:/photopub/docs/0000000418/0e552018-37a8-46ed-807b-2009040c7549.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12893085_e10a_4ad1_90fc_95875eb335b7
ELIN-562339-2016 | UW-377894-2016 | 4/20/2016 2:33:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Damaged_service.png | file://x:/photopub/docs/0000000418/e784453f-a03a-43e0-84b2-c57d244a99ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12893085_e10a_4ad1_90fc_95875eb335b7
ELIN-550174-2016 | EL-234505-2015 | 4/14/2016 9:48:32 PM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Consumer service conductors are not adequately protected from mechanical damage (impact; strain) where rising from grade. This presents a risk of serious personal injury (shock) or property damage (thermal event/ interface fire) as a result of fault conditions. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_service_cabling.png | file://x:/photopub/docs/0000000417/70da4ee2-a0b9-4fc0-8aef-ba0be60be424.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92668506_bda0_4ea7_b51e_c18c858b35c6
ELIN-536284-2016 | EL-296510-2015 | 3/3/2016 3:07:16 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The grounded conductor was terminated onto the bond bus. The improper termination of the ground conductor can create a shock hazard during fault conditions. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor.png | file://x:/photopub/docs/0000000400/ad26fdd8-bc52-4caf-926e-1c385600ae16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__530aaa8e_637a_4be5_bd4b_7a42f9ee8175
GAIN-520676-2016 | GA-334534-2016 | 2/24/2016 12:34:58 PM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Vent_clearance.png | file://x:/photopub/docs/0000000395/2cea3524-dd87-4e91-a3c4-64c299f7a134.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99860051_b00b_4acf_803e_ab18f3c3a08c
ELIN-518611-2016 | EL-339029-2016 | 3/14/2016 12:55:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In marina installations a hard usage cable is required together with a copper bond conductor. In this installation both had been omitted. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Triplex_to_boathouse.png | file://x:/photopub/docs/0000000403/f107980f-cb9f-47a3-bf9e-839862c28c99.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__356bcd5f_6107_4830_af41_5229b9ce86c4
ELIN-544582-2016 | EL-367188-2016 | 3/17/2016 2:58:03 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 2 | Transformer secondary conductors are too small. This could possibly lead to overheating. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 300_K_CM__300_K_CM_ECW_feeding_400_amp_panel_from_75_kVA_transformer.png | file://x:/photopub/docs/0000000405/89f84a3d-40a6-44e4-b837-bf756779f37a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02ad59bb_bea4_403e_ae99_723715a77a08
ELIN-532407-2016 | EL-336732-2016 | 2/25/2016 5:21:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding electrode was not buried to the proper depth, and not connected with proper fittings. This is fire and shock hazard. Proper grounding is a necessary to protect persons and property from short circuits and lightning strikes. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | A.png | file://x:/photopub/docs/0000000396/5db38843-7b0a-44b8-afc5-6ea9dc096c2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__204e1fb4_0cf9_44f6_8022_d04b97197f99
ELIN-531391-2016 | EL-236503-2015 | 2/24/2016 4:57:07 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized receptacle outlet boxes are required to be fitted with a receptacle and cover plate, or blank cover plate. If left open the circuit must be left in a de-energized state. This electrical installation for a new house has an energized open 15A, 120V receptacle outlet box. The house is occupied and four young children have access to this outlet box. Left uncorrected this is a potential shock hazard if a person contacts the energized wiring in this outlet box. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Front_of_house_.png | file://x:/photopub/docs/0000000395/724f99c2-d3a5-4484-8e53-30a07203f4de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0994163_b042_4f59_a7f0_8ac593dd4e7a
ELIN-531391-2016 | EL-236503-2015 | 2/24/2016 4:57:07 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized receptacle outlet boxes are required to be fitted with a receptacle and cover plate, or blank cover plate. If left open the circuit must be left in a de-energized state. This electrical installation for a new house has an energized open 15A, 120V receptacle outlet box. The house is occupied and four young children have access to this outlet box. Left uncorrected this is a potential shock hazard if a person contacts the energized wiring in this outlet box. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_box_with_energized_wiring.png | file://x:/photopub/docs/0000000395/c2484c2f-02a8-4fcc-a910-835cd870585a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0994163_b042_4f59_a7f0_8ac593dd4e7a
ELIN-554502-2016 | UW-372624-2016 | 3/30/2016 11:47:37 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | The main consumer disconnect switch is inoperable due to condensation over time which has created a potential failure of operational function. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Main_disconnect.png | file://x:/photopub/docs/0000000412/c10f81ca-31bd-4abb-a91f-0c5d132fba7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__565f1814_ffc2_4f65_a11b_ce46b831ecab
ELIN-561106-2016 | EL-298761-2015 | 4/19/2016 10:16:31 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Non-ic rated fixtures in contact with combustible material. This is a fire hazard as these fixtures can produce a sufficient amount of heat to start a fire. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | B.png | file://x:/photopub/docs/0000000418/5cfe68dc-413f-4112-a1ef-ae4a5185a918.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1cbc2e02_51a8_492d_bf04_5bbaf47b4499
ELIN-561106-2016 | EL-298761-2015 | 4/19/2016 10:16:31 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | Non-ic rated fixtures in contact with combustible material. This is a fire hazard as these fixtures can produce a sufficient amount of heat to start a fire. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | A.png | file://x:/photopub/docs/0000000418/fe436577-baa9-4b7f-8a88-3d901b5d5d17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1cbc2e02_51a8_492d_bf04_5bbaf47b4499
ELIN-531072-2016 | EL-332967-2016 | 2/24/2016 2:53:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Screw in type point of attachement in use, a bolt through type is required to comply with code requirements. Screw type points of attachement are at risk of pulling out,due to the tension and weight of the overhead conductors. If attachement were to pull out,service conductors may come in contact with persons or vehicles below, causing shock or fire. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Screw_in_type_point_of_attachement_in_use.png | file://x:/photopub/docs/0000000395/5ae7d4fd-8b7b-4976-b805-609b5661b80d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61dbe9cf_7e07_4c0c_af3f_1339789ac019
ELIN-544277-2016 | EL-366525-2016 | 3/17/2016 12:34:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Poi.png | file://x:/photopub/docs/0000000405/fdbbe02c-ec76-49af-9b98-6d276b00c229.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68382d1d_60a7_4796_a1b4_9ff43a66abc4
ELIN-544277-2016 | EL-366525-2016 | 3/17/2016 12:34:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Enclosure.png | file://x:/photopub/docs/0000000405/1c37b041-9add-4619-ac36-5aca2bad5d8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68382d1d_60a7_4796_a1b4_9ff43a66abc4
ELIN-539976-2016 | EL-356685-2016 | 3/17/2016 12:53:52 PM | ASSESS: EL: Final | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 |  | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Breaker.png | file://x:/photopub/docs/0000000405/99637e69-d03c-419e-9781-a98d10829de4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24b6826b_6acc_45b0_8daa_c061b483ec24
AMOP-551938-2016 | AM-206958-2015 | 3/31/2016 12:41:26 PM | ASSESS: AM OP: Periodic | png | #asFound | AM008 | Small misalignments that are: Reasonably detectable by maintenance program Unlikely to result in rapid wear or deropement | 1 | 1 | An adjustable vertical support of a mini roller coaster track is set low (excessive of a 1/4"). Adjustable vertical supports are to be adjusted so as to provide even support of the track structure. It is suspected, that when vertical supports jacks are not supporting the track evenly, that this condition could cause excessive stresses to the track structure. This, over a period of time, would result in a risk of a track structure failure. It is also suspected, that when vertical support are not evenly loaded that the track structure could start to move sideways over the ground. | 1 | Small misalignments that are: Reasonably detectable by maintenance program Unlikely to result in rapid wear or deropement | Track_support_jack_under_height.png | file://x:/photopub/docs/0000000426/ae3358a1-9657-49f9-b577-d668a45f9ebc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d5c5cc8_0fba_48d3_aadc_5c5022136f22
AMOP-563317-2016 | 2053226 | 4/20/2016 4:35:20 PM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | It was observed that a certain portion of a passenger carrier unit (PCU) on an Eyerly Aircraft, Spider II was making contact with the sweep arm when the the PCU was rotated. It is suspected that this condition was due to a worn PCU spindle configuration. It is not known with any certainty, but it may be possible that during the ride cycle this condition may result in a hazard in which a rotating PCU could come to a sudden jarring stop which could cause damage to the PCU and injure the rider. Also, wear in the spindle configuration may indicated that the structural strength of the spindle configuration is suspect and therefore over a period of operating there is a risk that the PCU could become detached from the sweep arm with it being occupied by a rider. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Witness_mark_of_PCU_making_contact_with_sweep_arm.png | file://x:/photopub/docs/0000000426/50f0d619-91ef-401f-870a-5aa79224944c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5026e2f8_9229_4231_ac0b_746e5910799b
AMOP-563311-2016 | 7238-0 | 4/21/2016 2:11:19 PM | ASSESS: AM OP: Periodic | png | #asFound | AM034 | Required operational strength does not exist. | 5 | 4 | A mechanical brake actuated by the raising of the passenger carrier unit (PCU) lap bar was not functional because the mechanical PCU brake had come out of adjustment on the majority of the PCUs on this ride. This results in a condition in which a brake that restricts the rotation of the PCU during the loading and unload is not functional. There is however a redundant mechanical/electric brake on each PCU that provides the same function and is was confirmed that all these brake where operational. There is a hazard, that in the event that the mechanical/electric PCU brake does not operate, that a person could be injured as they enter or exit the PCU because of sudden movement of the PCU. | 5 | Required operational strength does not exist. | Lap_bar_functions_as_actuator_of_mechanical_PCU_brake.png | file://x:/photopub/docs/0000000426/e3861633-3863-4420-9a6d-59d7e8bafde7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48863f82_24d8_4931_aebe_576b3755c0df
ELIN-531391-2016 | EL-236503-2015 | 2/24/2016 4:57:07 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized receptacle outlet boxes are required to be fitted with a receptacle and cover plate, or blank cover plate. If left open the circuit must be left in a de-energized state. This electrical installation for a new house has an energized open 15A, 120V receptacle outlet box. The house is occupied and four young children have access to this outlet box. Left uncorrected this is a potential shock hazard if a person contacts the energized wiring in this outlet box. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Basement_room_where_open_box_was_observed.png | file://x:/photopub/docs/0000000395/0cb2a3b9-8364-4dbe-ae09-6b31763bd27e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0994163_b042_4f59_a7f0_8ac593dd4e7a
ELIN-539706-2016 | EL-298518-2015 | 3/8/2016 2:00:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | Indoor panel installed outdoors and protected with polyethylene. Plastic is not a suitable weather proofing material for such an installation. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | A.png | file://x:/photopub/docs/0000000401/9d9a79ff-fd4e-4451-ae39-51fbfa08191c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13a0767d_33ca_42bc_9c9b_d1708d22579d
ELIN-556242-2016 | EL-374165-2016 | 4/8/2016 12:23:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | 400A 120/240 volt rated equipment has conductor ampacity rating less than ampacity rating of equipment. This is a thermal issue. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Conductor_size_for_400A_rated_equipment.png | file://x:/photopub/docs/0000000414/911b7c9f-9264-470a-b31b-095fcf5e9742.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4684edbb_a702_46c3_bd33_e56f637babca
ELIN-542804-2016 | EL-360829-2016 | 3/16/2016 12:20:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | 240 volt/ 60 amp temporary service pole not adequately supported and may be subject to damage which can lead to potential electrical shock or fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Temp_service_.png | file://x:/photopub/docs/0000000404/e29b34a2-bc98-4372-ad95-089de1267f43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7c8836a_b2cd_44c0_95f3_53ff9ebd74ad
BPVIN-544576-2016 | UW-367213-2016 | 3/16/2016 8:06:27 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve(s) on a Hot Water Boiler with MAWP 160 PSI and MAWT 250 F. Potential exists for a safety valve not functioning properly in a critical situation and if if the back up devices fail it can lead to an overpressure or explosion. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000404/a9f00212-cf5c-4298-a626-34a5babe39ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__811557b8_25f4_4a9b_8a0f_bacc841a7747
ELIN-562827-2016 | EL-369722-2016 | 4/25/2016 9:03:45 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 3 | The lighting and outlet junction boxes are not bonded, this can create a shock hazard | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Missing_box_bonding.png | file://x:/photopub/docs/0000000420/2f77ea22-5d2e-42a4-aff7-e7224fbed00b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f6ee997_dfac_4996_9e98_b9cbcc9f9896
ELIN-563123-2016 | EL-376403-2016 | 4/25/2016 12:28:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Panel replacement installation/alteration has ground conductor cut short and not connected to panelboard, this can create a potential difference between any metal to ground and is a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | Panelboard.png | file://x:/photopub/docs/0000000420/cad799e6-fda8-4065-b976-a2ce49eb832c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__081ea6e6_66bc_4363_afc8_d733de928144
ELIN-540187-2016 | EL-248567-2015 | 3/10/2016 3:04:11 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 15 amp, 120 volt receptacle is within 1.5 meters of a sink without ground fault protection provided. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_within_1_5m_of_sink.png | file://x:/photopub/docs/0000000402/86ca7da6-a88a-4e21-837b-92a5b86eef98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46250fb0_f79c_4d13_bc90_80ced616970a
BPVIN-561940-2016 | BPV-093580-2014 | 5/10/2016 2:07:03 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of a hot water heating boiler with a maximum allowable working pressure of 160 psig and a maximum allowable water temperature of 250F it was determined that the remote shutdown switch for the boiler was not installed. As the name implies the remote shutdown switch allows a person to shutoff the boilers from a remote location should an emergency situation arise such as hot water escape or a fire situation that would prevent the person from shutting off the boiler from its local control panel. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000428/992eba3e-67e0-4325-9026-fede52c865c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dc8e997_5969_4845_b2a6_e131d98f821f
ELIN-556360-2016 | EL-356702-2016 | 4/8/2016 9:52:24 AM | ASSESS: EL: Service Connection | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | 200 amp, 120/240 volt service has a service conductor installed which has a ampacity rating less then the service size rating. This is a thermal effect. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Conductor_ampacity_rating_not_rated_for_service_rating.png | file://x:/photopub/docs/0000000414/bf57c6e8-ca78-43c6-86d5-2652f74a20e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7837ce58_a4c5_496e_be9a_3944e88092bd
ELIN-543637-2016 | 5219481 | 3/14/2016 6:03:53 PM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Consumers service conductors must not be within reach of an opening window. In this installation the service conductors were installed within 1 m of an opening window. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service_conductors_beside_window.png | file://x:/photopub/docs/0000000404/8ed7496a-a489-4acb-a1bd-632d4cfe08e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76f8596c_8945_4f92_a80b_c1c3d588d083
ELIN-553586-2016 | EL-331754-2016 | 4/18/2016 1:30:32 PM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | The service conduit was not bonded correctly. This could create a high resistance to the fault current path resulting in a shock hazard during a fault condition. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Service_panels.png | file://x:/photopub/docs/0000000417/c1762bc8-3e4e-4d8a-b9a2-1551dbba72dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9e898ec_1178_4b54_bcd5_6016ed88ee4b
ELIN-558515-2016 | EL-369423-2016 | 4/18/2016 10:42:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a new irrigation pumphouse, the 200amp 600volt main switch was observed with the system ground not installed to the correct location. This could lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_installation.png | file://x:/photopub/docs/0000000418/2865400c-ae6f-45dd-8783-63f620c9a0d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac75b394_1907_4bfc_9bf3_6d0e16c451df
ELIN-565162-2016 | EL-377131-2016 | 4/25/2016 3:57:37 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 2 | Consumer service raceways bedded in large angular material posing risk of mechanical damage resulting in failure of conduit system. This could result in potential personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_service_conduits.png | file://x:/photopub/docs/0000000420/b5187717-551d-4a9d-86e7-577e6a186b4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e472a0e2_920c_4ead_ae17_7760a46407fd
ELIN-565959-2016 | EL-352944-2016 | 4/26/2016 2:04:12 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles intended for construction purposes did not have protective cover plates installed, exposing occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Receptacles_in_kitchen_.png | file://x:/photopub/docs/0000000421/90f8933f-79f8-4ebe-810b-64a53722d0e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b562f17c_f727_4c4a_a963_8ec94f17f5ab
ELIN-548904-2016 | EL-369213-2016 | 3/29/2016 4:41:43 PM | ASSESS: EL: Final | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | A sump pump was fed with extension cord that was damaged and worn. The extension cord damage could result in a person receiving a shock if they were to pick the cord up at the damaged section. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Sump-pump.png | file://x:/photopub/docs/0000000409/279350ba-93cf-4d30-a1ce-6d1ce72edbd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b83f111_07c3_4a5a_96de_ea7c8fd47933
GAIN-561954-2016 | GA-377733-2016 | 5/3/2016 8:19:53 AM | ASSESS: GA: Rough-In | png | #asFound | GA038 | Pipe supports not compliant but in place | 1 | 1 |  | 1 | Pipe supports not compliant but in place | Piping_support.png | file://x:/photopub/docs/0000000424/ead8083b-4369-4f5d-8b23-e6e29483cfde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__defb396e_3b5a_48e3_9bfb_3606f0d6b845
ELIN-544080-2016 | EL-161492-2014 | 3/17/2016 9:37:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | The system grounding conductor was found to be undersized. This conductor would not have sufficient ampacity to carry the maximum transformer fault current. A loss of the grounding conductor presents a shock hazard | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 3_0_ground.png | file://x:/photopub/docs/0000000405/e61009af-4830-4f66-ab91-f496bfa66a85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cca9526f_83eb_4d77_81df_00ccdb79dc4e
BPVOP-551336-2016 | 3059237 | 3/30/2016 11:45:54 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Upon assessment it is determined that machine mounted horizontal air receiver (1.4m long and .51m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Safety_valve.png | file://x:/photopub/docs/0000000409/7372dd82-87fa-4df4-96ab-c4d6ef4569d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4cef9f1_5539_45ca_80ac_b20bb950e4c9
BPVOP-551326-2016 | 3059963 | 3/30/2016 2:45:30 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Domestic hot water storage tank (2.4m long and 0.91m wide) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that temperature and pressure relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject storage tank to pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_and_P_RELIEF_VALVE.png | file://x:/photopub/docs/0000000409/af9750a2-dd11-48c5-8915-0b8e6c413284.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__786160a3_ed47_48b7_8a7d_b0ae0793313b
BPVOP-551331-2016 | 3059968 | 3/30/2016 1:58:59 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Domestic hot water storage tank (2.4m long and 0.91m wide) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that temperature and pressure relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject storage tank to pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_AND_P_RELIEF_VALVE.png | file://x:/photopub/docs/0000000409/8026c27a-835a-41cf-a69f-7d2790f76801.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8977662d_f67e_4d43_a017_27339fc2a193
ELIN-534031-2016 | EL-350842-2016 | 2/29/2016 12:26:43 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Overhead electrical services must be adequately supported to avoid the lateral pull of the utility conductors damaging the service equipment. In this installation the length of utility conductor exceeds that allowed by CSA standards. The mast is bent and the service cap has fallen off allowing water to accumulate in a meter base below the mast. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Open_cap.png | file://x:/photopub/docs/0000000397/5f2c5b7d-5886-4961-b107-ad80152e3aff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77a09efa_f071_4556_9942_e7c2131b2022
ELIN-534031-2016 | EL-350842-2016 | 2/29/2016 12:26:43 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Overhead electrical services must be adequately supported to avoid the lateral pull of the utility conductors damaging the service equipment. In this installation the length of utility conductor exceeds that allowed by CSA standards. The mast is bent and the service cap has fallen off allowing water to accumulate in a meter base below the mast. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Bent_mast.png | file://x:/photopub/docs/0000000397/c655a111-3096-42ba-9656-ba4aab125195.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77a09efa_f071_4556_9942_e7c2131b2022
ELIN-528942-2016 | EL-214060-2015 | 2/29/2016 11:44:00 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Overhead electrical service equipment must be adequately supported to avoid utility conductors pulling consumer services from their installations. In this installation the support member for a residential overhead service had deteriorated badly and an unknown individual had attempted to extend the life of the support member by roping it to a service mast not designed to take the pull of overhead conductors. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Mast_roped_to_post.png | file://x:/photopub/docs/0000000397/70be70c9-f4db-457e-945c-b0d7b730b972.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0811ca09_b886_424c_8c6a_1c589a489dea
ELIN-570626-2016 | EL-376494-2016 | 5/3/2016 1:53:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 240V energized cable accessible to general public | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Service_cable_exposed_and_accessible.png | file://x:/photopub/docs/0000000424/a3a10432-0ce8-4f71-b53f-ada23ec0055e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74b267b5_ff80_4e9a_a86d_d002e6307bfb
EDMA-573022-2016 | ED-258719-2015 | 5/11/2016 2:38:35 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED033 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | 3 | 3 | Electrical control circuits are protected with fuses. Fuses will trip if there is a short or ground fault in the circuit. During testing, a short was introduced in the door lock circuit to test the functionality of the fusing. The fuse did not trip. This resulted in the door frame being energized, and the circuit overloading. This could of resulted in persons being electrocuted and also an electrical fire. | 3 | Operating control installed contrary to the manufacturer instructions and/ or applicable Standards Contractor is not aware Risk Reg ED-02 | Fuses.png | file://x:/photopub/docs/0000000429/97eb4bf8-5471-40c0-a00a-69f7f3c3dec2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5a3005e_520f_4c0a_9d37_f1a53c423435
BPVIN-575843-2016 | UW-386607-2016 | 5/12/2016 11:31:44 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP018 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | 2 | 2 |  | 2 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | Missing_amchor_bolt.png | file://x:/photopub/docs/0000000429/f33215aa-ec17-4e57-8d60-258b70edd53d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c37dc08_c1e1_4810_837a_bc3a105664c9
BPVIN-575843-2016 | UW-386607-2016 | 5/12/2016 11:31:44 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP018 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | 2 | 2 |  | 2 | 1.0.2 Clearances/Maintenance - Pipe supports not compliant but in place | Nameplate_1.png | file://x:/photopub/docs/0000000429/b2ed4eed-3a8f-4ab1-b7d8-ffe367c02637.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c37dc08_c1e1_4810_837a_bc3a105664c9
ELIN-574994-2016 | EL-382964-2016 | 5/12/2016 4:16:40 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | 200 amp, 120/240 volt main distribution has bond strap removed. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bond_strap_at_main_distribution_removed.png | file://x:/photopub/docs/0000000429/d4db7a6b-0dd3-4be4-a460-4d5477f5a60d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__503cda35_4de6_4663_988b_c2cae6ed8055
ELIN-560585-2016 | UW-376961-2016 | 4/22/2016 7:33:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unused openings in live electrical panels must be closed to avoid accidental contact. In this installation two subdistributions had been altered and the panels were left open so the live parts inside were accessible to touch. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_bus_no_directory.png | file://x:/photopub/docs/0000000421/3922c91b-784e-4365-852b-1569893e302a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__361a3cec_38bf_40f5_a767_6825bbaae840
ELIN-523668-2016 | UW-136403-2014 | 3/23/2016 10:14:19 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | Elecrical installations are required to have a continuous grounding conductor connected to a system neutral and metallic parts. In this installation the ground conductor had been spliced with a connector not approved for that use. | 4 | Installation Grounding; conductor is not continuous. | Joint_in_system_ground.png | file://x:/photopub/docs/0000000407/a3a5ddf8-4c36-438e-b7d1-dda06bcf6a6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__494bc12b_03d5_444d_afb1_187d745ce6a2
ELIN-547915-2016 | UW-369002-2016 | 3/22/2016 12:19:18 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | 120/240 volt, single phase 60 amp fused disconnects feeding mobile homes are in poor condition due to exposure to the weather. Failure of this equipment could cause equipment damage and be a shock and thermal hazard. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Mobile_Home_fused_disconnect.png | file://x:/photopub/docs/0000000407/e341d9d0-3805-4ef6-9c50-eb77a7c1b33f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__968ae44a_ccb5_4cea_8be6_bc7c123fec79
ELIN-544367-2016 | EL-298692-2015 | 3/31/2016 1:07:38 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | This assessment found an exterior receptacle to be inaccessible due to snow. The cable supplying the receptacle was not approved for wet a location yet it was exposed to wet conditions. The receptacle had an extension cord plugged in to service a snow plough. There is a fire and shock hazard if the wiring becomes wet and deteriorated. The same hazard exists with the extension cords end being inaccessible, in the event it needed to be unplugged. | 3 | Conductors Equipment is not approved for the specific use. | Receptacle-snow.png | file://x:/photopub/docs/0000000410/f28f8698-c723-4f35-993b-d40e32252c3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75b82dc5_ef62_4382_bedb_a8c036336054
ELIN-547855-2016 | UW-368934-2016 | 3/18/2016 11:02:38 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Rooftop_unit.png | file://x:/photopub/docs/0000000406/0c5c7cb3-60f6-4675-97d1-9d5265315948.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff14e683_24c7_4120_a86d_e536ee021508
ELIN-547855-2016 | UW-368934-2016 | 3/18/2016 11:02:38 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Van_on_site.png | file://x:/photopub/docs/0000000406/f26bd35f-dfdb-46d9-8669-d43d279f7652.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff14e683_24c7_4120_a86d_e536ee021508
ELIN-547855-2016 | UW-368934-2016 | 3/18/2016 11:02:38 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Disconnect.png | file://x:/photopub/docs/0000000406/84d273a3-b997-4fe3-b294-8fd3f53f051b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff14e683_24c7_4120_a86d_e536ee021508
ELIN-569363-2016 | EL-379703-2016 | 5/4/2016 2:50:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | 200 amp, 120/240 volt service has service conductor bond terminated on neutral buss. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Bond_terminated_on_neutral.png | file://x:/photopub/docs/0000000425/d032514c-624b-4c19-a7c2-f8fe44ebb30f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df06ddf4_7b9c_483e_9ab9_2c4595a7df49
GAIN-504133-2016 | GA-322574-2015 | 2/26/2016 1:06:48 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | The exhaust portion of the furnace vent is not secured at the furnace, and is leaking exhaust condensate. | 3 | Leaking or failing special venting system (Minor) | _air_filter_opening.png | file://x:/photopub/docs/0000000399/34fc65a9-e365-4ef3-8947-0c75d84355a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f63600a_5cf4_4075_b483_6b2d16337e9d
GAIN-504133-2016 | GA-322574-2015 | 2/26/2016 1:06:48 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | The exhaust portion of the furnace vent is not secured at the furnace, and is leaking exhaust condensate. | 3 | Leaking or failing special venting system (Minor) | Plastic_vent_at_furnace_leaking.png | file://x:/photopub/docs/0000000399/e3deb815-e276-4efe-9836-844a185de3a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f63600a_5cf4_4075_b483_6b2d16337e9d
GAIN-504133-2016 | GA-322574-2015 | 2/26/2016 1:06:48 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | The exhaust portion of the furnace vent is not secured at the furnace, and is leaking exhaust condensate. | 3 | Leaking or failing special venting system (Minor) | No_vent_suport.png | file://x:/photopub/docs/0000000399/3b550d97-548d-44d1-92fb-53d81aef1b37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f63600a_5cf4_4075_b483_6b2d16337e9d
GAIN-504133-2016 | GA-322574-2015 | 2/26/2016 1:06:48 PM | ASSESS: GA: Final | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | The exhaust portion of the furnace vent is not secured at the furnace, and is leaking exhaust condensate. | 3 | Leaking or failing special venting system (Minor) | Vent_termination_.png | file://x:/photopub/docs/0000000399/702657d7-9134-49c8-b275-3f241ad1d104.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f63600a_5cf4_4075_b483_6b2d16337e9d
ELIN-541893-2016 | EL-358056-2016 | 3/18/2016 10:29:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead service conductors on pole to low over grade where there will likely be vehicular and machinery heavy equipment traffic going underneath overhead conductors. When overhead service conductors are too low over grade where vehicle and heavy construction equipment traffic goes there could be an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000406/5cb4ec10-5fdf-4b4a-9c5a-eb5cf11451b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6d905ea_593c_4eca_9217_79b551503ceb
ELIN-541893-2016 | EL-358056-2016 | 3/18/2016 10:29:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead service conductors on pole to low over grade where there will likely be vehicular and machinery heavy equipment traffic going underneath overhead conductors. When overhead service conductors are too low over grade where vehicle and heavy construction equipment traffic goes there could be an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000406/9f59647f-f5fe-4bde-9088-9f671f258161.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6d905ea_593c_4eca_9217_79b551503ceb
ELIN-541893-2016 | EL-358056-2016 | 3/18/2016 10:29:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead service conductors on pole to low over grade where there will likely be vehicular and machinery heavy equipment traffic going underneath overhead conductors. When overhead service conductors are too low over grade where vehicle and heavy construction equipment traffic goes there could be an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000406/756b19e3-ccdd-458c-93ee-fa2a21244c5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6d905ea_593c_4eca_9217_79b551503ceb
ELIN-557353-2016 | EL-370107-2016 | 4/12/2016 11:45:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The # 6 copper, main ground conductor has not been installed at the dual meter base location. The service is rated 200 amps 120/240 volts single phase. This is a shock and thermal hazard should a fault condition occur. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Dual_meter_base_without_ground_connection_.png | file://x:/photopub/docs/0000000415/de1659dd-8a34-4bb3-8ea1-3ad86fae8f64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__835c9a63_0676_45e2_9880_dd0185cf6b44
GAIN-552952-2016 | GA-317568-2015 | 4/25/2016 4:34:40 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | All appliances require combustion air. No combustion air found on site. Upset flame conditions. Possible creating high levels of carbon monoxide. | 4 | Combustion air supply missing | Venting_2.png | file://x:/photopub/docs/0000000422/77f5d4de-18d6-4c3a-b184-25b710352432.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac5e0b9_7e96_4f62_8872_cf760c16d1d9
GAIN-552952-2016 | GA-317568-2015 | 4/25/2016 4:34:40 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | All appliances require combustion air. No combustion air found on site. Upset flame conditions. Possible creating high levels of carbon monoxide. | 4 | Combustion air supply missing | Venting_1.png | file://x:/photopub/docs/0000000422/f14676e5-1f0a-40df-b53c-d7f9a4188f1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac5e0b9_7e96_4f62_8872_cf760c16d1d9
BPVOP-536720-2016 | 3505973 | 3/2/2016 1:01:41 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 | Upon assessment it is determined that Tridicator pressure and temperature range is below code requirement but within operating range. There is no way to verify abnormal operation beyond normal operating condition. | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Tridicator_.png | file://x:/photopub/docs/0000000399/28531092-bee2-4099-9606-04bbd0f71fa4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79f2ee25_a146_4fb0_bc48_5bc24bd8b458
BPVIN-536798-2016 | UW-355444-2016 | 3/2/2016 2:12:26 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 2 | Upon assessment of Heat Exchanger with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 248*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject heat exchanger to pressure above MAWP if control fails or heat exchanger is operated inadvertently with valve on heat receiving side shut. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Heat_exchanger_safety_relief_valve.png | file://x:/photopub/docs/0000000399/840be3ae-8d43-4598-b1b9-16f6a85ab17d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__013fbe72_bade_4485_9a5f_11a85df2a521
BPVOP-536744-2016 | 3505978 | 3/2/2016 1:40:37 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 | Upon assessment it is determined that Tridicator pressure and temperature range is below code requirement but within operating range. With Tridicator at its present range, there is no way to verify abnormal operation beyond normal operating range. | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | TRIDICATOR.png | file://x:/photopub/docs/0000000399/37a00f1f-e9a7-4afa-8e3b-c4cb28e2775b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f79b3e29_e414_49ae_ac92_5434635bb504
ELIN-533478-2016 | EL-351218-2016 | 3/1/2016 2:27:55 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | During a used mobile home Silver Label inspection, the bath fan motor was found to have been removed. The conductors for the fan motor remained stuffed into the housing along with thermal insulation. The fan was switched with the bathroom light so the conductors were energized whenever the light was on. This creates a potential fire hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Bath_fan_motor_removed__but_conductors_remain_and_are_connected_to_switch.png | file://x:/photopub/docs/0000000399/c56ca6fe-602a-4cc7-8507-530e45bd68e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14389857_0bab_48f4_a71d_2f64243fb648
ELIN-546568-2016 | EL-323583-2015 | 3/21/2016 10:19:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 | The supply wire to the furnace safety control circuit is a 3 wire circuit. The neutral is common with another circuit. | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | Furnace_switch.png | file://x:/photopub/docs/0000000406/a16e87e3-7f9f-48ca-982f-b9c731c0462a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b24f2d12_6872_453c_a192_b9e6dc33d877
ELIN-541893-2016 | EL-358056-2016 | 3/18/2016 10:29:23 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found overhead service conductors on pole to low over grade where there will likely be vehicular and machinery heavy equipment traffic going underneath overhead conductors. When overhead service conductors are too low over grade where vehicle and heavy construction equipment traffic goes there could be an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000406/fcbcffe0-25cf-4b7b-bcb3-bfd828381878.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6d905ea_593c_4eca_9217_79b551503ceb
BPVOP-573322-2016 | 2250692 | 5/9/2016 12:14:12 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP118 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | 4 | 4 | A pressure relief device shall be connected to a main discharge header in order to direct ammonia refrigerant outside in case of leak. I found the pressure relief device not connected to that header so ammonia may enter the building in case of leak. | 4 | 3.0.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 Ammonia Pressure Relief Device discharge location does not meet CSA B-52 code requirements and is likely to cause risk to personnel if overpressure and discharge occurs. | Pressure_relief_device_not_connected_.png | file://x:/photopub/docs/0000000427/05a0f2df-f83c-4d8e-a789-fedade9b5db3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67f359ee_4f41_4d29_b935_1b7f495651e9
ELIN-547276-2016 | EL-345761-2016 | 3/22/2016 1:29:31 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | In a new outdoor wood mill facility, a 600volt 400amp service is installed using the main cables that are sized smaller than required. This is a potential thermal hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 0000_aluminum_RW90.png | file://x:/photopub/docs/0000000407/5ee80aa9-dcfc-42d0-8d87-fe91efbd523a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4c43d64_b089_4fc1_9074_03be2f8388a2
ELIN-547276-2016 | EL-345761-2016 | 3/22/2016 1:29:31 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | In a new outdoor wood mill facility, a 600volt 400amp service is installed using the main cables that are sized smaller than required. This is a potential thermal hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 400amp_fuses.png | file://x:/photopub/docs/0000000407/c5954d8f-0ccf-4196-ac01-03402fc14a7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4c43d64_b089_4fc1_9074_03be2f8388a2
ELIN-536071-2016 | EL-296493-2015 | 3/7/2016 2:52:23 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles are close to sink. This greatly increases the potential for counter equipment to fall into a sink filled with water causing a shock hazard to user. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 656_murelet.png | file://x:/photopub/docs/0000000401/27323e54-c05f-4382-813e-b8fe5dd9b813.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a852a6e5_bcc4_477b_9a1b_c9ea72b55699
ELIN-553607-2016 | EL-371914-2016 | 4/18/2016 3:33:58 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cables that rise from an under ground location to an above ground location to terminate at electrical equipment are required to be mechanically protected from the below ground location to 2 meters above finished grade. This is required to protect the cable from mechanical damage. This installation has an existing under ground service cable that was re-installed onto a new service pole after the new pole was installed to replace a rotten pole. The service cable is not mechanically protected and it is installed beside a drive way in a location where it may be subject to mechanical damage. Left uncorrected this is a potential shock and fire hazard should this service cable become damaged. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | new_secondary_pole_installed_to_replace_existing_pole_that_was_rotten.png | file://x:/photopub/docs/0000000417/1fc838b9-2f61-43ea-b925-664ae302cfd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41d21a83_54ba_4037_82eb_7f514ad406c9
ELIN-553607-2016 | EL-371914-2016 | 4/18/2016 3:33:58 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cables that rise from an under ground location to an above ground location to terminate at electrical equipment are required to be mechanically protected from the below ground location to 2 meters above finished grade. This is required to protect the cable from mechanical damage. This installation has an existing under ground service cable that was re-installed onto a new service pole after the new pole was installed to replace a rotten pole. The service cable is not mechanically protected and it is installed beside a drive way in a location where it may be subject to mechanical damage. Left uncorrected this is a potential shock and fire hazard should this service cable become damaged. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Existing_service_cable_is_not__mechanically_protected_on_newly_installed_pole.png | file://x:/photopub/docs/0000000417/1527b669-93e5-471e-a5c5-62eef0a1a596.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41d21a83_54ba_4037_82eb_7f514ad406c9
BPVIN-539255-2016 | UW-356661-2016 | 3/7/2016 2:55:16 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Heavenly corroded hot water piping with pits more than 25% nominal thickness. This can cause leakage or rupture with the possibility of scalding attendants. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Very_corroded_piping.png | file://x:/photopub/docs/0000000401/25a5d2ae-063f-4a63-b3e4-5272156c08df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c7873ad4_a6e9_4ed4_b6cb_71367507c294
ELIN-566061-2016 | EL-351777-2016 | 4/28/2016 10:23:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Indoor panel installed outdoors and not sealed properly from weather. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | A.png | file://x:/photopub/docs/0000000422/c129101f-e0ed-445c-a91f-0a0a099a952d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f62ccd65_8d70_48a2_a814_11a5ba531769
ELIN-566061-2016 | EL-351777-2016 | 4/28/2016 10:23:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Indoor panel installed outdoors and not sealed properly from weather. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | B.png | file://x:/photopub/docs/0000000422/72a5bfaa-736f-41a8-8be0-c58427e33e47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f62ccd65_8d70_48a2_a814_11a5ba531769
ELIN-566061-2016 | EL-351777-2016 | 4/28/2016 10:23:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Indoor panel installed outdoors and not sealed properly from weather. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | C.png | file://x:/photopub/docs/0000000422/72c394d6-6ecb-4be8-bb37-0feda7e6ffb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f62ccd65_8d70_48a2_a814_11a5ba531769
ELIN-567125-2016 | EL-270604-2015 | 4/28/2016 3:52:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Potential fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-534br.png | file://x:/photopub/docs/0000000422/2386820c-ce35-4b92-9102-8ec4d2f19f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fbb17f6_4bf9_4c9d_a39e_fbb33821ce45
BPVOP-527758-2016 | BPV-007866-2013 | 4/4/2016 10:02:01 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment of document supplied for the valve it is determined that flow passage in valve does not meet intent of the code but has appropriate pressure and temperature rating. Sediment can collect in valve making it difficult to close or even plug the passage if valve is not used for a while. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Slow_opening_blow_off_valve.png | file://x:/photopub/docs/0000000412/8b12e6d2-c040-4d71-ba59-61d0124996fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6ed938b_70a5_47bf_b002_e08ae2bdb460
GAIN-537424-2016 | GA-343955-2016 | 3/4/2016 12:57:06 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Regulator relief must be piped to the outdoors. When not piped outdoors and within close proximity to source of ignition it is possible to release gas into the building and most certainly cause a fire or explosion | 3 | Regulator vent not terminated as per manufacturers instruction | Relief_reg.png | file://x:/photopub/docs/0000000401/d7af329c-6738-4c68-a1b6-580271b5e0d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e3d385b_ab08_4024_8f44_2e99feca2e9e
GAIN-537424-2016 | GA-343955-2016 | 3/4/2016 12:57:06 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Regulator relief must be piped to the outdoors. When not piped outdoors and within close proximity to source of ignition it is possible to release gas into the building and most certainly cause a fire or explosion | 3 | Regulator vent not terminated as per manufacturers instruction | Fire_valve.png | file://x:/photopub/docs/0000000401/c20311fc-f6d4-42fe-bef9-fb0f71003d61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e3d385b_ab08_4024_8f44_2e99feca2e9e
ELIN-544875-2016 | EL-298636-2015 | 3/24/2016 9:44:39 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found energized exposed conductors on main consumer's service combination panelboard distribution where there are empty breaker spaces and filler plates missing. When covers and filler plates are missing on exposed energized electrical equipment the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | Main_service_panel_energized_and_has_energized_exposed_conductors_1.png | file://x:/photopub/docs/0000000408/44ad0836-52a5-433a-ad30-08b80196cbce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9909a711_b133_4fd4_aecf_305f8d15565a
ELIN-544875-2016 | EL-298636-2015 | 3/24/2016 9:44:39 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found energized exposed conductors on main consumer's service combination panelboard distribution where there are empty breaker spaces and filler plates missing. When covers and filler plates are missing on exposed energized electrical equipment the electrical equipment is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. | Main_service_panel_energized_and_has_energized_exposed_conductors_2.png | file://x:/photopub/docs/0000000408/011a10e2-6b78-4154-b353-34de0dcf109d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9909a711_b133_4fd4_aecf_305f8d15565a
ELIN-566224-2016 | EL-380126-2016 | 5/2/2016 4:06:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The grounding conductor of the 200 amp 120/208 volt 3-phase temporary service passes through non-approved "neutral" identified conductor termination point in the fusible disconnect and connects to service conduit bonding bushing only- no bonding screw/strap or conductor installed to metal enclosure at point of grounded conductor, only points of connection are through bonding bushing and metal connector where grounding cable enters enclosure. This is a shock hazard | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Unapproved_neutral_kit.png | file://x:/photopub/docs/0000000423/c77d8aae-f680-4412-b91a-ef3f347a4a06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ad3691d_6392_4536_80d9_a1121f85c15e
ELIN-566224-2016 | EL-380126-2016 | 5/2/2016 4:06:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | The grounding conductor of the 200 amp 120/208 volt 3-phase temporary service passes through non-approved "neutral" identified conductor termination point in the fusible disconnect and connects to service conduit bonding bushing only- no bonding screw/strap or conductor installed to metal enclosure at point of grounded conductor, only points of connection are through bonding bushing and metal connector where grounding cable enters enclosure. This is a shock hazard | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Main_switch.png | file://x:/photopub/docs/0000000423/8a3c8198-86e6-4a33-8711-d9f201fc5b78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ad3691d_6392_4536_80d9_a1121f85c15e
BPVOP-510079-2016 | 2299600 | 5/3/2016 10:54:30 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP077 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | 3 | 3 | During the Inspection of a High Pressure Steam Boiler with a MAWP of 150 psig, I found overheating of the shell and heavy corrosion, signs of leaking of the handhold covers. The Safety Valve was from 2004 also, and in case of the safeties failure it can lead to an explosion. | 3 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | Overheated_casing.png | file://x:/photopub/docs/0000000424/cd86478d-d686-4ed0-a305-2d1645012ddd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da19be75_7f6c_4085_bb7e_82c41d0e9e2b
BPVOP-510079-2016 | 2299600 | 5/3/2016 10:54:30 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP077 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | 3 | 3 | During the Inspection of a High Pressure Steam Boiler with a MAWP of 150 psig, I found overheating of the shell and heavy corrosion, signs of leaking of the handhold covers. The Safety Valve was from 2004 also, and in case of the safeties failure it can lead to an explosion. | 3 | 1.2.3 Boiler construction - Indications of overheating caused by scale or deposits on heat exchange surfaces. | Rust_and_Scale.png | file://x:/photopub/docs/0000000424/3bb6de6b-9376-4552-9250-a4dec79db513.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da19be75_7f6c_4085_bb7e_82c41d0e9e2b
ELIN-570430-2016 | UW-382484-2016 | 5/3/2016 9:22:59 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Commercial electric steam boiler does not display evidence of electrical electrical approval Electrical equipment which does not display evidence of recognized approval (testing) by a recognized certification agency may present a fire or shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Name_plate.png | file://x:/photopub/docs/0000000424/c416faaa-08dc-4a13-8126-d2efd0a294be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d1b69e_6419_429e_a45f_9e3e9b5f338d
ELIN-570430-2016 | UW-382484-2016 | 5/3/2016 9:22:59 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 3 | Commercial electric steam boiler does not display evidence of electrical electrical approval Electrical equipment which does not display evidence of recognized approval (testing) by a recognized certification agency may present a fire or shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Model.png | file://x:/photopub/docs/0000000424/0fc84c51-5b96-4515-ab86-974e8e937a6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78d1b69e_6419_429e_a45f_9e3e9b5f338d
ELIN-576366-2016 | EL-238841-2015 | 5/13/2016 7:14:41 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 1.png | file://x:/photopub/docs/0000000430/c8d91159-bf28-492a-aad5-e35a6c20213a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90501e0_5b44_47e7_96e1_1a35fde24da2
ELIN-576366-2016 | EL-238841-2015 | 5/13/2016 7:14:41 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 4.png | file://x:/photopub/docs/0000000430/45423907-af05-48f3-a602-2801bba196e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90501e0_5b44_47e7_96e1_1a35fde24da2
ELIN-576366-2016 | EL-238841-2015 | 5/13/2016 7:14:41 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 6.png | file://x:/photopub/docs/0000000430/7e0d8d14-fdab-4bd1-a3a6-eae85ffd0d78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90501e0_5b44_47e7_96e1_1a35fde24da2
ELIN-576366-2016 | EL-238841-2015 | 5/13/2016 7:14:41 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 3.png | file://x:/photopub/docs/0000000430/f5e98dd8-a99b-4238-9f0a-b7d6f74d7c34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90501e0_5b44_47e7_96e1_1a35fde24da2
ELIN-576366-2016 | EL-238841-2015 | 5/13/2016 7:14:41 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2.png | file://x:/photopub/docs/0000000430/93496f91-dbbc-4c58-b7ec-d81270c16932.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90501e0_5b44_47e7_96e1_1a35fde24da2
ELIN-576366-2016 | EL-238841-2015 | 5/13/2016 7:14:41 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 5.png | file://x:/photopub/docs/0000000430/bde83634-1fcb-47ba-9302-c5e41bdc8b22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90501e0_5b44_47e7_96e1_1a35fde24da2
BPVOP-535087-2016 | 3173116 | 3/15/2016 10:22:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this hot water heating boiler for the last 15 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Boiler_2_.png | file://x:/photopub/docs/0000000407/c2069720-b696-41fb-b670-29b5834f04b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__033767d8_f095_415e_a5e0_796c80733d12
ELIN-547334-2016 | EL-367552-2016 | 3/23/2016 12:35:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL258 | Medical Bonding is not adequate. | 4 | 4 | 15 amp, 120 volt # 12 awg armoured branch wiring in a patient care area does not have an insulated bond conductor. This is a shock hazard. | 4 | Medical Bonding is not adequate. | Bare_bonding_conductor__.png | file://x:/photopub/docs/0000000407/122e67bd-f1ac-4352-a059-bdd8538455c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d0b2ceb_724e_4f57_89b6_6f498e3e1611
ELIN-543661-2016 | EL-243146-2015 | 3/23/2016 1:36:03 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp, 120 volt branch wiring, in residential bedroom areas do not have arc fault protection provided. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Suite_panel_without_arc_fault.png | file://x:/photopub/docs/0000000407/48a6aa47-1707-43b5-908a-7582b0f10238.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c76278ef_9580_4b99_b623_d965a70c4506
ELIN-546932-2016 | EL-286473-2015 | 3/31/2016 2:13:45 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 2 | It is preferable to bond metallic gas lines which could become energized to ground. Propane system vents must be located 3 m or more from electrical equipment. In this installation neither precaution was observed. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_bond_at_tanks_or_equipment.png | file://x:/photopub/docs/0000000410/bbc15635-8259-4124-bde9-e99e499027a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c9af034_668a_483b_ba94_c2f0808579c6
BPVOP-561751-2016 | 4151551 | 4/18/2016 5:21:57 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment of pressurized expansion tank installed in Domestic Hot Water system with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it is determined that tank is non ASME. Non-ASME tank may fail due to lack of quality control and flashing hot water can lead to incident. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | EXPANSION_TANK_LOCATION_IN_THE_SYSTEM.png | file://x:/photopub/docs/0000000419/e6768b64-d9fd-41c0-aeaa-a62a8b356835.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf5dfa02_a815_49e5_9486_66fdf3e4d8b0
ELIN-566292-2016 | EL-380145-2016 | 4/26/2016 1:27:50 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | A 120 volt flexible cord feeding a heat tape below the mobile home skirting is being utilized for permanent branch wiring. This is a thermal hazard. | 4 | Conductors, Misuse of flexible cords. | Flexible_Cord.png | file://x:/photopub/docs/0000000421/8756dff5-ac4b-41f7-adce-2c965ecd4d58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d5c7c75_214d_455a_b64c_353b631c9b8c
ELOP-461760-2015 | 1204 | 3/7/2016 1:37:28 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL247 | Protection and control, all locations Method of protection has been compromised. | 4 | 4 | Sewage lift stations can produce a combination of conditions which require specialized care be taken in electrical installations. One means of protecting rooms and enclosures from intrusion of sewage and waste gases is to pressurize the room or enclosure. In this installation the pressure fan had failed and the electrical installation was subjected to corrosive and potentially explosive gas. | 4 | Protection and control, all locations Method of protection has been compromised. | To_wet_well.png | file://x:/photopub/docs/0000000401/2a0048d9-0c6c-4967-8298-c4f4895e004a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02fa4385_0efa_4542_ad7a_62325e9540a7
ELOP-461760-2015 | 1204 | 3/7/2016 1:37:28 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL247 | Protection and control, all locations Method of protection has been compromised. | 4 | 4 | Sewage lift stations can produce a combination of conditions which require specialized care be taken in electrical installations. One means of protecting rooms and enclosures from intrusion of sewage and waste gases is to pressurize the room or enclosure. In this installation the pressure fan had failed and the electrical installation was subjected to corrosive and potentially explosive gas. | 4 | Protection and control, all locations Method of protection has been compromised. | Pressure_and_no_seal.png | file://x:/photopub/docs/0000000401/22ac9d73-3b8d-4e8d-91b2-74ca91d51dd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02fa4385_0efa_4542_ad7a_62325e9540a7
BPVIN-556140-2016 | UW-374037-2016 | 4/7/2016 2:40:39 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 |  | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | BOILER_ADJUSTABLE_HIGH_TEMPERATURE_LIMIT.png | file://x:/photopub/docs/0000000414/90363392-d6f3-43cb-be41-8de57cf4bd3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__032667cd_b2e5_463b_8c1f_ab85d0d5df41
ELIN-546932-2016 | EL-286473-2015 | 3/31/2016 2:13:45 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 2 | It is preferable to bond metallic gas lines which could become energized to ground. Propane system vents must be located 3 m or more from electrical equipment. In this installation neither precaution was observed. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Vent_in_compound.png | file://x:/photopub/docs/0000000410/daef0aaf-2f78-465f-b0c6-99c207c725d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c9af034_668a_483b_ba94_c2f0808579c6
ELIN-556748-2016 | UW-374485-2016 | 4/8/2016 2:09:37 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | A 200 amp, 120/240 volt permanent pole service for a sewage lift station is in poor condition. The service is accessible to the general public. Failure of the pole could lead to electrical equipment damage. This is a shock and thermal hazard if left uncorrected. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Permanent_pole_service_in_poor_condition.png | file://x:/photopub/docs/0000000414/2f39e781-9939-476d-be67-176184b7d114.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ec5a666_36d9_4606_b43c_abfce9a18854
ELIN-556172-2016 | EL-295198-2015 | 4/11/2016 4:24:23 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Non metallic sheathed cables strapped on end. Cables strapped in this manner may push the bare bonding into the current carrying conductors insulation and compromise its insulation value. This may create an arcing or fire hazard to persons and property. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2_non_metallic_sheathed_cables_strapped_on_end.png | file://x:/photopub/docs/0000000415/208ba64f-40c9-4565-a565-3a2445d744bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__228f5316_b25c_4298_9047_510b2ad9e156
ELOP-226553-2014 | 3830385 | 3/9/2016 4:41:57 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not intended for use as a replacement for permanent wiring. In this hotel installation flexible cord was observed running through doorways above the door to a pop machine. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_through_doorway.png | file://x:/photopub/docs/0000000402/f137df43-8dff-4d42-81d5-8ac11d9fdec9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__094dd456_e7f5_45ee_8ad0_0f09ec13f46e
ELIN-544636-2016 | 5197030 | 3/16/2016 2:46:12 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL118 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | Cabling for 120 volt residential receptacle circuits is to be color coded black and white or red and white. In this installation the homeowner used a cable with one red and one black conductor between two receptacles. | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Heatex_feeding_receptacle.png | file://x:/photopub/docs/0000000404/fbf8b29a-8d4c-4c93-bf42-813845aa1a15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fef9f57d_92dc_455b_b323_257664b10480
ELIN-567720-2016 | EL-372870-2016 | 4/29/2016 5:15:24 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | Over head service supply conductors are required to be installed a minimum of 3.5M above grade level that is accessible to pedestrians. This is required to prevent contact between persons and energized conductors and to prevent damage to the conductors. This existing 200A, 120/240V over head service to a shop has service supply conductors that are approximately 1.5M from grade level adjacent to a detached shop on a residential property. The service supply conductors are energized and accessible to contact and damage from persons or objects. Left uncorrected this is a shock and fire hazard if the insulation on the energized conductors is damaged and a person or object contacts them. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Accessible_service_supply_conductors.png | file://x:/photopub/docs/0000000422/ebf143c0-fae7-4aca-a38f-fb4535047ada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293038da_bcd3_46d6_9793_a653356658ae
ELIN-567720-2016 | EL-372870-2016 | 4/29/2016 5:15:24 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | Over head service supply conductors are required to be installed a minimum of 3.5M above grade level that is accessible to pedestrians. This is required to prevent contact between persons and energized conductors and to prevent damage to the conductors. This existing 200A, 120/240V over head service to a shop has service supply conductors that are approximately 1.5M from grade level adjacent to a detached shop on a residential property. The service supply conductors are energized and accessible to contact and damage from persons or objects. Left uncorrected this is a shock and fire hazard if the insulation on the energized conductors is damaged and a person or object contacts them. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_supply_conductors_approx_1500mm_from_grade_level.png | file://x:/photopub/docs/0000000422/c0205b80-e5a8-4671-8d14-a3793de0ff46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293038da_bcd3_46d6_9793_a653356658ae
ELIN-567720-2016 | EL-372870-2016 | 4/29/2016 5:15:24 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | Over head service supply conductors are required to be installed a minimum of 3.5M above grade level that is accessible to pedestrians. This is required to prevent contact between persons and energized conductors and to prevent damage to the conductors. This existing 200A, 120/240V over head service to a shop has service supply conductors that are approximately 1.5M from grade level adjacent to a detached shop on a residential property. The service supply conductors are energized and accessible to contact and damage from persons or objects. Left uncorrected this is a shock and fire hazard if the insulation on the energized conductors is damaged and a person or object contacts them. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Service_supply_conductors_accessible_from_grade.png | file://x:/photopub/docs/0000000422/5144abbc-0f3c-43c6-8c9f-13f4881787ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__293038da_bcd3_46d6_9793_a653356658ae
BPVIN-575639-2016 | BPV-036080-2013 | 5/12/2016 4:13:41 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP160 | 5.0.1 Operator non-compliance - No operational procedure (e.g. lockout) | 2 | 2 |  | 2 | 5.0.1 Operator non-compliance - No operational procedure (e.g. lockout) | Remote_Shutdown_Switch.png | file://x:/photopub/docs/0000000429/fa509cef-5fff-4dd5-bec9-8d9e3eaf7405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65308dfc_a8bd_465a_9024_c177b387bceb
BPVIN-576153-2016 | UW-386802-2016 | 5/12/2016 5:02:07 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Pressure_temp_valve_installed_in_the_horizontal_direction.png | file://x:/photopub/docs/0000000429/90a49803-b6b6-4b25-b2e7-026b02795e2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa4f8d8f_a542_4576_9ea7_ea4efa249b62
BPVIN-576152-2016 | UW-386801-2016 | 5/12/2016 5:50:30 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Relief_valve_with_hv_stamping.png | file://x:/photopub/docs/0000000429/78c9bc0d-08d7-47ad-b20c-5b076160c23c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0a30f7b_1cdd_41ab_8524_7ec4dcabf81f
ELIN-540511-2016 | EL-358267-2016 | 3/10/2016 9:57:53 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | 200A 240V Main Panel does not have the cover installed. This poses a shock and possible fatal electrocution to persons who may come into contact with the exposed and energized bus. The cover also contains any possible short circuit or arc flash in the event of an overload or short circuit. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Main_Panel.png | file://x:/photopub/docs/0000000403/8b43f666-59fc-4e4e-bbc7-830507dbf713.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b684cbe5_d37e_429e_88ae_8e385771b026
ELIN-529870-2016 | EL-345147-2016 | 3/1/2016 7:11:04 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | A new 200 amp 240 volt single phase service was installed in a residential dwelling. The metal service raceway was not provided with a bonding bushing. Failure to provide a bonding bushing on a service raceway can lead to potential for shock or property damage | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Rigid_nipple_no_bond_bushing.png | file://x:/photopub/docs/0000000398/96ebaf19-50c6-4556-bb75-8029c2bfc575.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a43d2898_a25e_4f54_847d_01d979c51505
ELIN-530642-2016 | EL-327765-2015 | 2/29/2016 1:22:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | A new service of 125 amps 208 volts single phase has been fed with larger conductors due to voltage drop. Conductors have had strands removed to fit into the lugs provided by the equipment manufacturer. Additionally due to improper installation of the conductors undue strain has been placed on the main service breaker and consequently the main busbar in the panel. The combination of these two safety hazards can result in potential for fire and property damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Strands_removed_to_terminate_conductors_too_large_for_equipment.png | file://x:/photopub/docs/0000000398/0c984121-58fa-431e-84b1-0d2ffaa60c98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__708c9f94_c64e_4ebd_8095_b8d6cbbdf8ca
ELIN-530642-2016 | EL-327765-2015 | 2/29/2016 1:22:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | A new service of 125 amps 208 volts single phase has been fed with larger conductors due to voltage drop. Conductors have had strands removed to fit into the lugs provided by the equipment manufacturer. Additionally due to improper installation of the conductors undue strain has been placed on the main service breaker and consequently the main busbar in the panel. The combination of these two safety hazards can result in potential for fire and property damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Cable_armor_penetrates_past_throat_of_connector.png | file://x:/photopub/docs/0000000398/946020a3-6abc-4c91-8a71-8227fdb489ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__708c9f94_c64e_4ebd_8095_b8d6cbbdf8ca
BPVIN-576153-2016 | UW-386802-2016 | 5/12/2016 5:02:07 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Unsupported_relief_piping.png | file://x:/photopub/docs/0000000429/71aca771-7d5e-4280-9d86-2a2d8c2613e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa4f8d8f_a542_4576_9ea7_ea4efa249b62
BPVIN-576152-2016 | UW-386801-2016 | 5/12/2016 5:50:30 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Relief_valve_installation.png | file://x:/photopub/docs/0000000429/eeec3ad7-084f-46cc-a9d4-c9bebc28304d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0a30f7b_1cdd_41ab_8524_7ec4dcabf81f
BPVIN-576153-2016 | UW-386802-2016 | 5/12/2016 5:02:07 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP105 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Discharge piping not supported properly | Hc_stamping_on_valve.png | file://x:/photopub/docs/0000000429/538234b2-0a54-4b42-b613-40b1513f41f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa4f8d8f_a542_4576_9ea7_ea4efa249b62
AMOP-561417-2016 | 2780139 | 4/18/2016 11:24:17 AM | ASSESS: AM OP: Periodic | png | #asFound | AM033 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 | In the conveyor chain that is utilized in transporting occupied cars up the lift hill it was observed that the rolling bushing of the chain links were not of a consistent diameter. It is theorized, that because the bushing diameters are not consistent with each other, that there is a chance that the chain may not engage with the sprockets as designed. The chain may walk up onto the sprocket teeth, cause a sudden overloading condition of the chain which could then cause the chain to break. The risk level to passengers in the cars being transported by the conveyor chain is fairly low as there is a pawl and teeth system that would prevent cars from rolling backward in the event of a conveyor chain system failure. | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Not_consistent_sizes_rollers.png | file://x:/photopub/docs/0000000427/d8dafbb9-1369-48a3-9eb8-84d9219ac3d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__444ed925_119c_49ee_9a08_f801aaf503b4
AMOP-559176-2016 | 3730681 | 4/13/2016 3:04:01 PM | ASSESS: AM OP: Periodic | png | #asFound | AM046 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | In attempting to operate the main disconnecting breaker of the ride it was determined that it was not possible to switch the breaker into the "off" position (toggle would spring back into the "on" position). It therefore makes it not possible to isolate the rides electrical equipment in the event of requiring a lockout. It also raises the the question as to if the breaker where to operate in an over-current condition. This would result in a fire or shock hazard. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Main_Breaker.png | file://x:/photopub/docs/0000000427/f922aa5e-5452-4818-941e-703f45a81fbb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ed063d3_aa37_4021_a4a6_41acbbd75aa4
AMOP-551376-2016 | 2044008 | 3/29/2016 1:36:52 PM | ASSESS: AM OP: Periodic | png | #asFound | AM014 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | It was observed that the cover for the ring gear situated on the backside of the personal carrier unit (PCU) is not securely mounted (missing and broken rivets). There is a risk that if this cover where to become completely loose that it could become entangled with other moving equipment and be projected or flung out causing potential injury hazard to the passengers and other equipment. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Ring_gear_cover_broken_missing_rivets.png | file://x:/photopub/docs/0000000427/d1e47ccf-6aaf-4931-aa48-9679ae871a95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebdd595d_6d67_4316_b5cc_346e086eda8a
AMOP-548891-2016 | 3251949 | 3/23/2016 4:37:51 PM | ASSESS: AM OP: Periodic | png | #asFound | AM029 | Malfunction that results in loss of control yet additional means of detection and control are functional and unaffected | 4 | 4 | It was observed that the operating control panel functions were not operating as indicated in the labelling of the switches. 1) With the control power key switch in the "off" position it was possible to start the ride cycle. In this position the normal stop button was functional and the deadman switch only functioned intermittently. 2) With the control panel in the "on" position it was possible to start the ride cycle but it would not shut down with the normal stop button. It was only possible to shut down the ride cycle by pushing the emergency shunt trip button. These issues result in a hazard to the passengers and attendant due to the possibly of an inadvertent start of the ride cycle or being unable to stop the ride cycle in case of emergency. | 4 | Malfunction that results in loss of control yet additional means of detection and control are functional and unaffected | Operator_control_panel.png | file://x:/photopub/docs/0000000427/78bab1cc-e5e4-4141-be88-e96bd7a0a4b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94063cb8_9d16_422d_b1db_fe838218eddd
AMOP-563322-2016 | AM-101056-2014 | 4/20/2016 11:10:44 AM | ASSESS: AM OP: Periodic | png | #asFound | AM033 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | 1 | 1 | Fire suppression system not active and fire extinguisher at attendant station inspection certificate expired. | 1 | Suspected malfunction that is: reasonably detectable by maintenance program/operation unlikely to propagate | Fire_extinguisher_expired_inspection_certificate.png | file://x:/photopub/docs/0000000427/5f98b891-0155-4a57-8d90-b50bb933d074.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2435a6f1_465e_4080_b08b_e612a93c82f1
AMOP-567308-2016 | AM-011022-2013 | 4/28/2016 9:47:28 AM | ASSESS: AM OP: Periodic | png | #asFound | AM038 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | A missing grease zerk access cover to the personnel carrier unit (PCU) center hub dust cap creates an entrapment hazard for the riders appendages (eg open toes). i.e. If a persons toe was inside the aforementioned access cover it could be impacted by the grease zerk as the PCU rotates. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Open_grease_zerk_access_cover_missing.png | file://x:/photopub/docs/0000000427/f348caf6-55d7-4a38-9fa5-764448de4515.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23288f48_5e61_4ba0_acc9_731595aae335
AMOP-550612-2016 | 4341463 | 3/29/2016 3:56:21 PM | ASSESS: AM OP: Periodic | png | #asFound | AM038 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | The decorative outside panel is missing on a personal carrier unit (PCU) and is exposing the sharp rivet ends. This presents a laceration injury hazard to riders loading and unloading from the PCU. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | PCU_decorative_panel_missing.png | file://x:/photopub/docs/0000000427/b47da13c-5fa9-4311-a6b1-6bf9d8e07cae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ee3ea91_ddb2_4213_8e62_23c544ff96c7
AMOP-548070-2016 | 4732099 | 3/23/2016 1:42:05 PM | ASSESS: AM OP: Periodic | png | #asFound | AM038 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | During inspection it was noted that the nuts used to retain a bolt which is used to retain a head board (carpeted board) located above the riders head where missing at multiple locations. There is a risk that the nut less bolt could back out and the head board would no longer be retained. This would result in a hazard in which an unsecured head board could flung about during the ride cycle and cause injury to a rider. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Nut_missing_for_PCU_head_board.png | file://x:/photopub/docs/0000000427/64d1440b-8455-424a-90c1-8a12a45e7ce4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1497a315_ca8a_425e_aabf_a41c74166ee1
AMOP-555355-2016 | 2048342 | 4/6/2016 3:25:34 PM | ASSESS: AM OP: Periodic | png | #asFound | AM035 | Defects found where the required strength may no longer exist. | 4 | 4 | The restraint of a passenger carrier unit (PCU) is not engaging within the manufactures requirement of becoming fully locked (unable to lift restraint) with in 3 clips of the pawl. This results in a hazard in which the restraint may inadvertently open during the ride cycle and the passenger being ejected from the PCU. | 4 | Defects found where the required strength may no longer exist. | PCU_restrain.png | file://x:/photopub/docs/0000000427/23d6b3fd-97f5-40b1-966f-29839fb1af5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8f304bc_b1e4_499b_a8ad_78eeb070c291
AMOP-551372-2016 | 2053219 | 3/30/2016 1:20:45 PM | ASSESS: AM OP: Periodic | png | #asFound | AM029 | Malfunction that results in loss of control yet additional means of detection and control are functional and unaffected | 4 | 4 | Ride starts automatically when food peddle is depressed. No actuation of the start button is required. The stop button and start button on the control panel do not appear functional. Ride will however stop if the foot is lifted from the foot peddle switch. This results in a risk in which the ride could be inadvertently started causing injury hazard to riders and attendants. | 4 | Malfunction that results in loss of control yet additional means of detection and control are functional and unaffected | Attendant_controls.png | file://x:/photopub/docs/0000000427/8893628d-bb24-4f75-aab0-b508ac321466.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49e41090_8833_4b70_aa3e_911d382f10e1
AMOP-547864-2016 | 4490590 | 3/29/2016 10:33:06 AM | ASSESS: AM OP: Periodic | png | #asFound | AM037 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | On a personnel carrier unit (PCU) the nut retaining the bolt for a buckle which retains a lap restraint bar has come loose to a point were it could come completely off allowing the bolt to back out. At that point the buckle would no longer be retained. There is a risk that if the buckle were to become detached that the lap bar could potentially raise up during a ride cycle and would not provide retention to the rider. This could allow a rider to become elected from the PCU. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Loose_nut_used_to_retain_restraint.png | file://x:/photopub/docs/0000000427/d684bc33-3976-467d-b6b5-02ebb1f98d27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1629527b_bae6_4f60_89bc_2c1a9ef0aeef
AMOP-564116-2016 | 4708355 | 4/21/2016 1:14:40 PM | ASSESS: AM OP: Periodic | png | #asFound | AM038 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Car #1 and #2 front position push buttons mounted with excessive long screws and present a laceration injury hazard a riders legs. | 1 | Suspected wear or defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Excessive_long_screws_inside_carrier.png | file://x:/photopub/docs/0000000427/ec2398e7-4927-4f36-ab8a-0ae5729e150d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7744f9c1_9b02_4142_bd6a_35f046ae571d
ELIN-569629-2016 | EL-381615-2016 | 5/16/2016 4:16:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | In an existing single family dwelling, an electrical contractor installed a 200amp 120/240 volt service upgrade using 2012 rules. This could lead to a thermal effect. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | wire_size.png | file://x:/photopub/docs/0000000430/b727238b-5422-4a2e-a649-31cb4309f354.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b250aa66_3234_47e0_baba_c6bdd8fa263a
ELIN-558999-2016 | EL-369551-2016 | 5/16/2016 4:51:36 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | In a new outbuilding at a single family dwelling, a 40amp 120/240volt feeder cable has been connected to the main and the sub panels without having the rubber insulation of the teck cable removed. This could lead to a shock hazard. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Cable_connected.png | file://x:/photopub/docs/0000000430/93c9c762-8d19-4900-a655-85c2ef29433f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df541890_e883_4968_82db_9f909342f81f
ELOP-226665-2014 | 1985 | 5/18/2016 3:25:17 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | In child care areas receptacles must be tamper resistant so kids don't stick foreign objects into energized receptacles. In this school som classroom areas were converted to child care areas but the receptacles were not updated. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Kids_stuff.png | file://x:/photopub/docs/0000000431/7f9df307-4e27-4a20-9189-f59b09b4d083.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__161c6799_cce7_434c_82a7_9c73d6b0a2be
BPVIN-575648-2016 | BPV-345473-2016 | 5/18/2016 4:30:18 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP092 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | 3 | 3 | During the inspection of a HP Steam boiler with the MAWP of 150 psig I found that the gage glass was shut off. If the water level would drop and the back up safety devices would fail it could lead to overheating and an explosion. | 3 | 2.0.1 Control system may overrun - Operating Controls installed contrary to the manufacturer instructions and or applicable Standards and not providing intended control | Gage_glass_shut_off.png | file://x:/photopub/docs/0000000431/e773bf55-5447-41b0-a498-635172c49438.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__702ba228_ac09_4105_ae09_6191de907813
BPVOP-532351-2016 | UW-350013-2016 | 2/23/2016 9:24:05 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | I attended the site based on information from another Safety Officer regarding possible un-permitted boilers in operation. I met the site Maintenance person, introduced myself and explained why I was there. I asked to see his boilers and he led me to them. I observed no visible certification in the machinery space. I asked him if there was any certification for the boilers to which he replied, "no". After locating and inspecting a third boiler at the site I observed the noted non-compliances. I later determined that the two low pressure steam boilers had a combined heating surface 261 m2. This heating surface classifies this as a fifth class steam heating plant (30 - 300 m2). This means that the plant is running with no valid certification for either the plant size or for any of the machinery on the site. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | EXCESS_WIRE_SUPPORT.png | file://x:/photopub/docs/0000000395/855068c9-8af6-4b3a-8fd4-dd13ff5281bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260a3679_7913_4738_ad99_a0734c441860
BPVOP-532351-2016 | UW-350013-2016 | 2/23/2016 9:24:05 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | I attended the site based on information from another Safety Officer regarding possible un-permitted boilers in operation. I met the site Maintenance person, introduced myself and explained why I was there. I asked to see his boilers and he led me to them. I observed no visible certification in the machinery space. I asked him if there was any certification for the boilers to which he replied, "no". After locating and inspecting a third boiler at the site I observed the noted non-compliances. I later determined that the two low pressure steam boilers had a combined heating surface 261 m2. This heating surface classifies this as a fifth class steam heating plant (30 - 300 m2). This means that the plant is running with no valid certification for either the plant size or for any of the machinery on the site. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | INCORRECT_WIRING.png | file://x:/photopub/docs/0000000395/bf66e947-1fe5-4f2b-a39d-766c1f050f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260a3679_7913_4738_ad99_a0734c441860
BPVOP-532351-2016 | UW-350013-2016 | 2/23/2016 9:24:05 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | I attended the site based on information from another Safety Officer regarding possible un-permitted boilers in operation. I met the site Maintenance person, introduced myself and explained why I was there. I asked to see his boilers and he led me to them. I observed no visible certification in the machinery space. I asked him if there was any certification for the boilers to which he replied, "no". After locating and inspecting a third boiler at the site I observed the noted non-compliances. I later determined that the two low pressure steam boilers had a combined heating surface 261 m2. This heating surface classifies this as a fifth class steam heating plant (30 - 300 m2). This means that the plant is running with no valid certification for either the plant size or for any of the machinery on the site. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | NO_COVER_PLATES.png | file://x:/photopub/docs/0000000395/c61a981f-7ab6-4d9f-a873-8280c72de4db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260a3679_7913_4738_ad99_a0734c441860
BPVOP-532351-2016 | UW-350013-2016 | 2/23/2016 9:24:05 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | I attended the site based on information from another Safety Officer regarding possible un-permitted boilers in operation. I met the site Maintenance person, introduced myself and explained why I was there. I asked to see his boilers and he led me to them. I observed no visible certification in the machinery space. I asked him if there was any certification for the boilers to which he replied, "no". After locating and inspecting a third boiler at the site I observed the noted non-compliances. I later determined that the two low pressure steam boilers had a combined heating surface 261 m2. This heating surface classifies this as a fifth class steam heating plant (30 - 300 m2). This means that the plant is running with no valid certification for either the plant size or for any of the machinery on the site. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | EXPOSED_WIRING_1.png | file://x:/photopub/docs/0000000395/4e50fa9a-c49e-42e5-a684-197629e0bc14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260a3679_7913_4738_ad99_a0734c441860
BPVOP-532351-2016 | UW-350013-2016 | 2/23/2016 9:24:05 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | I attended the site based on information from another Safety Officer regarding possible un-permitted boilers in operation. I met the site Maintenance person, introduced myself and explained why I was there. I asked to see his boilers and he led me to them. I observed no visible certification in the machinery space. I asked him if there was any certification for the boilers to which he replied, "no". After locating and inspecting a third boiler at the site I observed the noted non-compliances. I later determined that the two low pressure steam boilers had a combined heating surface 261 m2. This heating surface classifies this as a fifth class steam heating plant (30 - 300 m2). This means that the plant is running with no valid certification for either the plant size or for any of the machinery on the site. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | THERMO_CORD.png | file://x:/photopub/docs/0000000395/b01ac7e2-4160-40e0-914d-bd42dc5a5817.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260a3679_7913_4738_ad99_a0734c441860
BPVOP-532351-2016 | UW-350013-2016 | 2/23/2016 9:24:05 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP169 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | 3 | 3 | I attended the site based on information from another Safety Officer regarding possible un-permitted boilers in operation. I met the site Maintenance person, introduced myself and explained why I was there. I asked to see his boilers and he led me to them. I observed no visible certification in the machinery space. I asked him if there was any certification for the boilers to which he replied, "no". After locating and inspecting a third boiler at the site I observed the noted non-compliances. I later determined that the two low pressure steam boilers had a combined heating surface 261 m2. This heating surface classifies this as a fifth class steam heating plant (30 - 300 m2). This means that the plant is running with no valid certification for either the plant size or for any of the machinery on the site. | 3 | 5.0.1 Operator non-compliance - Certified operator or licence holder performing regulated work beyond scope of certification or licence | EXPOSED_WIRING_2.png | file://x:/photopub/docs/0000000395/c26c78de-8fbd-4b8a-8662-69b4fa69d83a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__260a3679_7913_4738_ad99_a0734c441860
ELIN-543339-2016 | EL-359769-2016 | 3/15/2016 12:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The point of attachment for over head service supply conductors is required to be secure and installed in such a way as to prevent strain on the conductors and their terminations. This installation of an existing 100A over head service for a house has the point if attachment connected to a wood 2 x 4 nailed to the underside of the roof over hang. The 2 x 4 is deteriorating, and the point of connection for the service supply conductors is causing strain on the conductors and their terminations. Left uncorrected this is a potential shock and fire hazard if the point of attachment fails and the service supply conductors come into contact with the aluminum gutters or if the conductor terminations become loose or pull apart causing the connections to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Side_of_house.png | file://x:/photopub/docs/0000000404/611ce9f2-8334-48b6-b1b6-572b7f196303.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a095b68_9f6d_4003_9d03_6dac518a88f1
ELIN-543339-2016 | EL-359769-2016 | 3/15/2016 12:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The point of attachment for over head service supply conductors is required to be secure and installed in such a way as to prevent strain on the conductors and their terminations. This installation of an existing 100A over head service for a house has the point if attachment connected to a wood 2 x 4 nailed to the underside of the roof over hang. The 2 x 4 is deteriorating, and the point of connection for the service supply conductors is causing strain on the conductors and their terminations. Left uncorrected this is a potential shock and fire hazard if the point of attachment fails and the service supply conductors come into contact with the aluminum gutters or if the conductor terminations become loose or pull apart causing the connections to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_attachment_exposed_conductor.png | file://x:/photopub/docs/0000000404/f09885fd-a206-41cf-9423-a41ee92125e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a095b68_9f6d_4003_9d03_6dac518a88f1
ELIN-543339-2016 | EL-359769-2016 | 3/15/2016 12:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The point of attachment for over head service supply conductors is required to be secure and installed in such a way as to prevent strain on the conductors and their terminations. This installation of an existing 100A over head service for a house has the point if attachment connected to a wood 2 x 4 nailed to the underside of the roof over hang. The 2 x 4 is deteriorating, and the point of connection for the service supply conductors is causing strain on the conductors and their terminations. Left uncorrected this is a potential shock and fire hazard if the point of attachment fails and the service supply conductors come into contact with the aluminum gutters or if the conductor terminations become loose or pull apart causing the connections to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_attachment___.png | file://x:/photopub/docs/0000000404/d94880d8-20d0-4959-b004-a811c84381cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a095b68_9f6d_4003_9d03_6dac518a88f1
ELIN-543339-2016 | EL-359769-2016 | 3/15/2016 12:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The point of attachment for over head service supply conductors is required to be secure and installed in such a way as to prevent strain on the conductors and their terminations. This installation of an existing 100A over head service for a house has the point if attachment connected to a wood 2 x 4 nailed to the underside of the roof over hang. The 2 x 4 is deteriorating, and the point of connection for the service supply conductors is causing strain on the conductors and their terminations. Left uncorrected this is a potential shock and fire hazard if the point of attachment fails and the service supply conductors come into contact with the aluminum gutters or if the conductor terminations become loose or pull apart causing the connections to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_attachment_deteriorated_.png | file://x:/photopub/docs/0000000404/55876650-c697-4dd6-b4f9-d1473384684b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a095b68_9f6d_4003_9d03_6dac518a88f1
ELIN-543339-2016 | EL-359769-2016 | 3/15/2016 12:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The point of attachment for over head service supply conductors is required to be secure and installed in such a way as to prevent strain on the conductors and their terminations. This installation of an existing 100A over head service for a house has the point if attachment connected to a wood 2 x 4 nailed to the underside of the roof over hang. The 2 x 4 is deteriorating, and the point of connection for the service supply conductors is causing strain on the conductors and their terminations. Left uncorrected this is a potential shock and fire hazard if the point of attachment fails and the service supply conductors come into contact with the aluminum gutters or if the conductor terminations become loose or pull apart causing the connections to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_attachment_.png | file://x:/photopub/docs/0000000404/447971f4-e8e8-4f39-868b-2210eebf152f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a095b68_9f6d_4003_9d03_6dac518a88f1
BPVOP-526592-2016 | 2250769 | 3/11/2016 12:30:35 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP054 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | 2 | 2 |  | 2 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | Weeper_.png | file://x:/photopub/docs/0000000403/36badae2-2253-46d5-b087-7fe06b5dc77a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__632f0edd_9726_44c0_83df_a18e4eb61ec3
ELIN-550706-2016 | EL-369531-2016 | 3/30/2016 1:22:32 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15A 120V outlet for the washer is located within 1.5m of the tub and not GFCI protected, and is accessible for use for other items beside the washer. This poses a shock hazard and possible damage to equipment used in this outlet. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Washer_outlet.png | file://x:/photopub/docs/0000000409/ea71aeb0-117e-4589-b764-32538ba68978.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95f70b32_f8e1_472c_9ecc_5fbd223d6714
ELIN-552376-2016 | EL-371247-2016 | 4/1/2016 3:06:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Meter to high to read or service without a ladder. | 0 | No Created Hazard Identified | A.png | file://x:/photopub/docs/0000000410/680c358d-0da7-4f64-9511-75f95c4da924.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2340d478_2432_4e60_a8a5_3a0a43cb91aa
BPVOP-503721-2016 | 4916669 | 5/5/2016 3:34:02 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Scale_.png | file://x:/photopub/docs/0000000425/a745a5bb-121b-46cb-81b6-5884782ba5bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f63ccd92_d176_4fde_afe5_0e3a077bb670
ELIN-541824-2016 | EL-267253-2015 | 3/10/2016 2:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Service constructed in dangerous location, BC Hydro contacted to disconnect, previously waived | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Service2.png | file://x:/photopub/docs/0000000402/6317f194-af62-4153-bd97-93568b64e4e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__754913d5_ce80_4d4d_93cc_8bc950b4938d
ELIN-541824-2016 | EL-267253-2015 | 3/10/2016 2:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Service constructed in dangerous location, BC Hydro contacted to disconnect, previously waived | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Service_1.png | file://x:/photopub/docs/0000000402/960fd844-4c81-453b-a6d7-9e2fac9120f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__754913d5_ce80_4d4d_93cc_8bc950b4938d
ELIN-541824-2016 | EL-267253-2015 | 3/10/2016 2:07:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Service constructed in dangerous location, BC Hydro contacted to disconnect, previously waived | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Radii.png | file://x:/photopub/docs/0000000402/74eea169-8d73-4042-982a-41342dcbaf81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__754913d5_ce80_4d4d_93cc_8bc950b4938d
BPVOP-571218-2016 | 4006595 | 5/6/2016 12:29:41 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_PRD.png | file://x:/photopub/docs/0000000426/4016520e-1f7d-4526-ad2b-f448a86bc7cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6131e161_cd9e_44b3_b6dc_746dddb70485
BPVOP-571230-2016 | BPV-168587-2014 | 5/6/2016 11:28:42 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | During the inspection of a Domestic Hot Water Heating Boiler with a MAWP of 160 psig, I found that the Temperature&Pressure Relief Valve leaking. This can result in the T&P valve not to protect the boiler in case of overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leaking_T_and_P_valve.png | file://x:/photopub/docs/0000000426/f8b1ace4-9793-4dd6-8ecd-56dc86c32b00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85c88cb7_6489_436b_8914_753f73caf93c
BPVOP-571227-2016 | 3437068 | 5/6/2016 1:12:18 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of a machined mounted air receiver, I found a Pressure Relief Device not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_1.png | file://x:/photopub/docs/0000000426/4c1c4ee7-b295-477f-bef7-bbc162ae940b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f97ee5bf_cf0f_4e3d_ae8a_bdafece74822
BPVOP-572754-2016 | 2299600 | 5/6/2016 1:31:12 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP136 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | 4 | 4 | During the hydro test of a HP Steam boiler at 150 psi MAWP, the Safety Valve rated at 125psi did not pop when the test pressure was 150 psig. Safety devices protect equipment from dangerous conditions and damage. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 4 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000426/b049c4ca-4d5f-4ee3-9195-7e74d3e7acad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65333f6d_ca05_4854_b9ea_3733faa6f905
ELIN-543339-2016 | EL-359769-2016 | 3/15/2016 12:14:20 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The point of attachment for over head service supply conductors is required to be secure and installed in such a way as to prevent strain on the conductors and their terminations. This installation of an existing 100A over head service for a house has the point if attachment connected to a wood 2 x 4 nailed to the underside of the roof over hang. The 2 x 4 is deteriorating, and the point of connection for the service supply conductors is causing strain on the conductors and their terminations. Left uncorrected this is a potential shock and fire hazard if the point of attachment fails and the service supply conductors come into contact with the aluminum gutters or if the conductor terminations become loose or pull apart causing the connections to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Point_of_attachment__.png | file://x:/photopub/docs/0000000404/76e40d31-e76c-4560-b42e-186239dd1452.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a095b68_9f6d_4003_9d03_6dac518a88f1
ELIN-530353-2016 | EL-189833-2014 | 3/15/2016 2:38:22 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder for sub-distribution and branch circuitry inadequately protected from mechanical damage. This poses a serious risk of personal injury (shock) and property damage (thermal event/interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_sub-distribution_feeder.png | file://x:/photopub/docs/0000000404/6b0bae50-3c7e-47b2-b027-a4e5243446a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b8cf61c_3a5a_46a3_902e_ca84063bc7f3
ELIN-532428-2016 | EL-234501-2015 | 3/15/2016 2:47:55 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Multiple exterior branch circuits are not protected from the effects of weather or mechanical damage using approved methods. This poses a serious risk of personal injury (shock) or property damage (thermal event/interface fire) due to accidental contact by members of general public and deterioration from environmental factors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | View01_hot_tub_branch_circuit.png | file://x:/photopub/docs/0000000404/1b2b4b2b-e98f-40b7-893c-184f81e19a38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56c49625_71b5_4f97_a9f1_706cc6b48f24
ELIN-532428-2016 | EL-234501-2015 | 3/15/2016 2:47:55 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Multiple exterior branch circuits are not protected from the effects of weather or mechanical damage using approved methods. This poses a serious risk of personal injury (shock) or property damage (thermal event/interface fire) due to accidental contact by members of general public and deterioration from environmental factors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | View02_branch_circuit.png | file://x:/photopub/docs/0000000404/e617458f-f7d9-4180-a25a-4ba3f62b864b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56c49625_71b5_4f97_a9f1_706cc6b48f24
ELIN-534252-2016 | EL-344786-2016 | 3/1/2016 12:05:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15A 120V outlets have been connected for use but have not been mounted to the outlet boxes and no covers are present. A shock and fire hazard exists has no protection from contact to energized wiring or devices has been provided. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Washer_outlet.png | file://x:/photopub/docs/0000000398/355e864e-f751-408c-a0de-b3232931dc1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad1824d7_2460_4fba_82a6_4550fa3e6ae2
ELIN-534252-2016 | EL-344786-2016 | 3/1/2016 12:05:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15A 120V outlets have been connected for use but have not been mounted to the outlet boxes and no covers are present. A shock and fire hazard exists has no protection from contact to energized wiring or devices has been provided. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Livingroom_outlet.png | file://x:/photopub/docs/0000000398/589ab390-8d4c-433c-9b0c-58735697ff3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad1824d7_2460_4fba_82a6_4550fa3e6ae2
BPVOP-553308-2016 | 2258048 | 4/2/2016 12:47:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Arrived on site for annual inspection and was immediately informed by contractor that 5 tubes were leaking under pressure and would need to be replaced. This affects the pressure retaining ability of the boiler resulting in leakage and inefficient operation of the boiler. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 4_TUBES.png | file://x:/photopub/docs/0000000411/8051a91c-7f27-48fb-80d5-05e7f3c96b64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__791dbf41_554c_4f0d_8f4c_73dc350c20d9
BPVOP-553308-2016 | 2258048 | 4/2/2016 12:47:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Arrived on site for annual inspection and was immediately informed by contractor that 5 tubes were leaking under pressure and would need to be replaced. This affects the pressure retaining ability of the boiler resulting in leakage and inefficient operation of the boiler. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 1_TUBE.png | file://x:/photopub/docs/0000000411/deae7c0f-2f46-4dac-9803-a22b918b225c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__791dbf41_554c_4f0d_8f4c_73dc350c20d9
GAIN-533095-2016 | GA-342358-2016 | 5/3/2016 4:28:20 PM | ASSESS: GA: Final | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | The as found hazard was an outlet in the gas piping system with a shut off valve in the closed position which had not been capped. This is a hazard because is the valve were to leak or be opened gas would be allowed to discharge freely into the trailers. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_line.png | file://x:/photopub/docs/0000000425/54d5309a-ac00-4fad-a925-bc44322a99d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04f61d97_2e78_4b98_bbe9_bef266f8324a
GAIN-533089-2016 | GA-341105-2016 | 5/3/2016 4:46:15 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Rinnai.png | file://x:/photopub/docs/0000000425/c5469814-d1ed-44ed-979b-db307b808a05.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a15e5ff1_4d17_4fc3_b946_c5e5c0b08980
GAIN-533089-2016 | GA-341105-2016 | 5/3/2016 4:46:15 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | tubing_to_warming_table.png | file://x:/photopub/docs/0000000425/788eab68-63cf-4f54-a9be-80551268ffd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a15e5ff1_4d17_4fc3_b946_c5e5c0b08980
GAIN-533089-2016 | GA-341105-2016 | 5/3/2016 4:46:15 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | regulator_vent.png | file://x:/photopub/docs/0000000425/1e0b57ff-cdbf-4e7e-993f-04ebec5ea3d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a15e5ff1_4d17_4fc3_b946_c5e5c0b08980
ELIN-570480-2016 | EL-382274-2016 | 5/6/2016 10:59:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found possible exposed and energized bus bars and conductors if main service is connected by the utility to its utility power supply system while electrical equipment is not covered and is not safe for connection. When electrical equipment is connected to over-current devices that might become energized while covers are missing, the energized electrical equipment is an electrical fire or shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 1.png | file://x:/photopub/docs/0000000427/b3cc6808-9de1-4001-8ab9-15a86a5e46d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0867f6e4_83d0_4acb_8fc0_29187d4729ef
ELIN-570480-2016 | EL-382274-2016 | 5/6/2016 10:59:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found possible exposed and energized bus bars and conductors if main service is connected by the utility to its utility power supply system while electrical equipment is not covered and is not safe for connection. When electrical equipment is connected to over-current devices that might become energized while covers are missing, the energized electrical equipment is an electrical fire or shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 2possible_exposed_energized_bus_bars_conductors_in_garage_panel3.png | file://x:/photopub/docs/0000000427/db41ba00-ca9a-4a7e-8dcd-58ce7eba37a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0867f6e4_83d0_4acb_8fc0_29187d4729ef
ELIN-570480-2016 | EL-382274-2016 | 5/6/2016 10:59:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found possible exposed and energized bus bars and conductors if main service is connected by the utility to its utility power supply system while electrical equipment is not covered and is not safe for connection. When electrical equipment is connected to over-current devices that might become energized while covers are missing, the energized electrical equipment is an electrical fire or shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 2possible_exposed_energized_bus_bars_conductors_in_garage_panel.png | file://x:/photopub/docs/0000000427/63bc0283-d87f-4652-8d0c-6fa43174d675.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0867f6e4_83d0_4acb_8fc0_29187d4729ef
ELIN-570480-2016 | EL-382274-2016 | 5/6/2016 10:59:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found possible exposed and energized bus bars and conductors if main service is connected by the utility to its utility power supply system while electrical equipment is not covered and is not safe for connection. When electrical equipment is connected to over-current devices that might become energized while covers are missing, the energized electrical equipment is an electrical fire or shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 2possible_exposed_energized_bus_bars_conductors_in_garage_panel2.png | file://x:/photopub/docs/0000000427/12e20b40-222f-445a-b035-7ca6634d2292.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0867f6e4_83d0_4acb_8fc0_29187d4729ef
ELIN-565729-2016 | UW-379880-2016 | 4/25/2016 3:36:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Multiple #14AWG branch circuits terminated on a 50Amp GFCI 2P | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Multiple_circuits_terminated_to_15Amp_CB.png | file://x:/photopub/docs/0000000420/7e296561-c1cb-4e1b-94c4-61b3f97429b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3550a1_45d6_4409_848f_e848cc852e27
ELIN-561272-2016 | EL-352075-2016 | 4/20/2016 4:16:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | The 1/2 inch plastic staples were installed on two 14-3 and 3 14-2 conductors in a number of areas. This could damage the PVC jacket on the conductors and become a fire hazard in the future. | 3 | Conductors Equipment is not approved for the specific use. | Stapled_conductors.png | file://x:/photopub/docs/0000000418/1dbc94f3-c164-4598-89ed-510bcc88c00f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb82e792_18db_4841_b870_f98f6a726f3c
ELIN-561272-2016 | EL-352075-2016 | 4/20/2016 4:16:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | The 1/2 inch plastic staples were installed on two 14-3 and 3 14-2 conductors in a number of areas. This could damage the PVC jacket on the conductors and become a fire hazard in the future. | 3 | Conductors Equipment is not approved for the specific use. | Stapled_nmd.png | file://x:/photopub/docs/0000000418/279f57f2-1e6e-4789-8b7a-02e3a4650c5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb82e792_18db_4841_b870_f98f6a726f3c
ELIN-539942-2016 | EL-356115-2016 | 3/18/2016 2:45:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL014 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | 2 | 3 | High voltage installations on private property are required to have a switch and over current protection for the primary line conductor. This installation of an extension on an existing primary pole line to feed power to a newly sub-divided property does not have a switch or over current installed on the line. The switch is required to provide the property owner with a disconnecting means should there be an emergency involving the high voltage installation or should the installation require maintenance. Over current protection is required to protect the equipment from an over current and over load condition. Left uncorrected this will likely not become a problem as the existing line already has over current protection provided by BC Hydro's fuses at the road however it is a code requirement. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | Extension_to_primary_pole_line_on_private_property.png | file://x:/photopub/docs/0000000405/d7c26d2b-b6bd-4943-9587-85b53750d379.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6d0f985_90d0_43b6_8d8f_737b132aa49b
ELIN-539942-2016 | EL-356115-2016 | 3/18/2016 2:45:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL014 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | 2 | 3 | High voltage installations on private property are required to have a switch and over current protection for the primary line conductor. This installation of an extension on an existing primary pole line to feed power to a newly sub-divided property does not have a switch or over current installed on the line. The switch is required to provide the property owner with a disconnecting means should there be an emergency involving the high voltage installation or should the installation require maintenance. Over current protection is required to protect the equipment from an over current and over load condition. Left uncorrected this will likely not become a problem as the existing line already has over current protection provided by BC Hydro's fuses at the road however it is a code requirement. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | No_switch_on_the_first_pole_on_private_property.png | file://x:/photopub/docs/0000000405/77917db5-a5e5-445a-89ac-a587e629f9cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6d0f985_90d0_43b6_8d8f_737b132aa49b
ELIN-539942-2016 | EL-356115-2016 | 3/18/2016 2:45:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL014 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | 2 | 3 | High voltage installations on private property are required to have a switch and over current protection for the primary line conductor. This installation of an extension on an existing primary pole line to feed power to a newly sub-divided property does not have a switch or over current installed on the line. The switch is required to provide the property owner with a disconnecting means should there be an emergency involving the high voltage installation or should the installation require maintenance. Over current protection is required to protect the equipment from an over current and over load condition. Left uncorrected this will likely not become a problem as the existing line already has over current protection provided by BC Hydro's fuses at the road however it is a code requirement. | 2 | Placement of equipment does not allow for adequate access or egress. Illumination is not provided or adequate. | Photo_from_the_road.png | file://x:/photopub/docs/0000000405/c4051c9a-c212-44fe-984b-59ea15337e3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6d0f985_90d0_43b6_8d8f_737b132aa49b
ELIN-530353-2016 | EL-189833-2014 | 3/15/2016 2:38:22 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder for sub-distribution and branch circuitry inadequately protected from mechanical damage. This poses a serious risk of personal injury (shock) and property damage (thermal event/interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View_02_subdistribution.png | file://x:/photopub/docs/0000000404/077494d6-b342-4798-8d61-b9d13d82f885.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b8cf61c_3a5a_46a3_902e_ca84063bc7f3
ELIN-532428-2016 | EL-234501-2015 | 3/15/2016 2:47:55 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Multiple exterior branch circuits are not protected from the effects of weather or mechanical damage using approved methods. This poses a serious risk of personal injury (shock) or property damage (thermal event/interface fire) due to accidental contact by members of general public and deterioration from environmental factors. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Detail03_branch_circuit_under_deck.png | file://x:/photopub/docs/0000000404/9bd7384c-fe13-4ccd-8274-35abd05687ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56c49625_71b5_4f97_a9f1_706cc6b48f24
ELIN-530353-2016 | EL-189833-2014 | 3/15/2016 2:38:22 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Feeder for sub-distribution and branch circuitry inadequately protected from mechanical damage. This poses a serious risk of personal injury (shock) and property damage (thermal event/interface fire). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View_03_feeder-branch_circuitry.png | file://x:/photopub/docs/0000000404/deaa56ca-c6a9-439c-b370-138f76fdb6f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b8cf61c_3a5a_46a3_902e_ca84063bc7f3
BPVOP-578567-2016 | BPV-108342-2014 | 5/17/2016 9:36:43 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 |  | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Malleable_iron_fittings.png | file://x:/photopub/docs/0000000431/b06b8534-3ee7-4eb4-a170-3a62d8199316.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3e2c93f_9910_4be7_bc6b_1c9998c2bb39
BPVOP-578548-2016 | 3584162 | 5/17/2016 10:44:57 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP124 | 3.1.1 Safeties will not function - Refrigeration units (Non ammonia) - Inadequate servicing or testing records, servicing and testing to manufacturer recommended intervals being carried out. | 1 | 1 |  | 1 | 3.1.1 Safeties will not function - Refrigeration units (Non ammonia) - Inadequate servicing or testing records, servicing and testing to manufacturer recommended intervals being carried out. | Safety_Valve.png | file://x:/photopub/docs/0000000431/4a573e76-2dc8-4d37-ac6a-bfd767061971.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__929d7667_ed46_4d83_90ed_329ea0b1a5f3
ELIN-562921-2016 | EL-272536-2015 | 4/22/2016 9:16:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a new single family dwelling, a 200amp 120/240volt distribution panel was found with the system ground not terminated to the identified conductor. This could lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_panel.png | file://x:/photopub/docs/0000000419/a3503d96-ba34-463d-9411-77a0f1e8a5fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__445ec9a0_7442_44c7_b309_2b2a4fc2166b
ELIN-562979-2016 | EL-351636-2016 | 4/22/2016 7:06:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | In a new multi-family row housing development, a 400amp 120/240volt supply service conduit was found installed without having the expansion joint installed. This can lead to equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Supply_service.png | file://x:/photopub/docs/0000000419/65b13ede-d0a1-4b84-889e-c2afb31482ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b5dd15a_70e1_4f09_bf1a_061f9456b287
BPVOP-565294-2016 | 2285442 | 4/25/2016 10:38:01 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this hot water heating boiler for the last 9 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Pressure_relief_valve_data_.png | file://x:/photopub/docs/0000000420/b81fed64-55f9-44ba-9903-48b229171908.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e37da29_31d8_48e7_a1d8_a0ef4dee19ac
BPVOP-545603-2016 | 4457821 | 3/17/2016 7:23:46 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment it is determined that relief valve discharge is not installed 4.6m above accessible roof level. Accumulated refrigerant may deplete oxygen below that required for habitability in the event of popping up of relief valve and consequently can lead to severe incident. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Evaporator_relief_valve_discharge.png | file://x:/photopub/docs/0000000406/65343197-fde9-45c0-b4ba-dfcd236a8a29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b871c0b_3539_4130_ae22_2436e4c4c4a8
BPVOP-535087-2016 | 3173116 | 3/15/2016 10:22:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this hot water heating boiler for the last 15 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data_tag.png | file://x:/photopub/docs/0000000404/e626a845-1052-472c-882d-8a4f35991d27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__033767d8_f095_415e_a5e0_796c80733d12
BPVOP-564760-2016 | BPV-238927-2015 | 4/28/2016 8:13:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP044 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | 3 | 3 | Boiler tubes must have enough thickness in order to contain maximum allowable working pressure which the boiler is rated for. I found that a high pressure steam boiler tube was affected by corrosion and it's thickness has deteriorated to almost 50% from the original thickness. | 3 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which eliminates the corrosion allowance and is reducing the thickness below the minimum design thickness | Local_metal_loss_.png | file://x:/photopub/docs/0000000428/dcabad3b-80c1-40eb-9318-e59cf21b85ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__91612fb0_5b1e_4df5_b681_af813a6eaf70
BPVOP-505852-2016 | 3532197 | 5/10/2016 3:16:34 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Minor_scaling.png | file://x:/photopub/docs/0000000428/30daf949-1a44-4f77-b9b3-e4886d0e048b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df3abc9b_c8d1_4e00_96d0_b7fe3f922d49
ELIN-577477-2016 | EL-318297-2015 | 5/17/2016 12:39:46 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL103 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | 3 | 3 | Apartment suite feeder conductors have no cable separation between them. No cable separation between the cables will cause heat to transfer from one table to another. Heat will damage the cable insulation integrity which may result in a fire. | 3 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | Sweet_feeder__sweet_feeder_conductors_in_contact_with_each_other.png | file://x:/photopub/docs/0000000430/6e91df58-5d5d-4edc-a73f-804ae7fcf8e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccd50e14_efd2_490b_94aa_c50971114015
ELIN-577477-2016 | EL-318297-2015 | 5/17/2016 12:39:46 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL103 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | 3 | 3 | Apartment suite feeder conductors have no cable separation between them. No cable separation between the cables will cause heat to transfer from one table to another. Heat will damage the cable insulation integrity which may result in a fire. | 3 | Separation of circuits Conductors of different low voltage systems are not suitably separated from one and another. | Photo_to___Photo_too_sweet_feeder_conductors_in_contact_with_each_other.png | file://x:/photopub/docs/0000000430/9b46e66b-2e0f-4cd6-a784-d52112112e92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccd50e14_efd2_490b_94aa_c50971114015
ELOP-550417-2016 | 1271 | 3/30/2016 9:54:47 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp, 120 volt receptacle installed within 1.5 meters of a sink without GFCI protection. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_without_GFCI_protection_located_by_sink.png | file://x:/photopub/docs/0000000409/4c7cdcb8-3f87-40b2-a2bf-a670fa071412.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79a54046_5d89_4d30_8667_a788031f59e4
ELOP-550408-2016 | 1272 | 3/30/2016 9:31:32 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 120 volt, 15 amp receptacle located within 1.5 meters of a sink without GFCI protection. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_without_required_GFCI_protection.png | file://x:/photopub/docs/0000000409/65a77a73-2a27-40e9-9c72-3afeaa0c58d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d424282_06ed_4a53_b9b4_d6fb1470421a
GAIN-531920-2016 | GA-346344-2016 | 3/31/2016 11:13:23 AM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | Two pressure regulators with reliefs commonly vented together and terminal terminating under air intake louvers go electrical room. If the regulators vent, natural gas could enter the louvers into the electrical room potentially causing an explosion. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Vent_relief_location.png | file://x:/photopub/docs/0000000410/3e5595bc-ce4a-4246-b01f-f3bcf619abe4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__769f0852_c9e3_45b2_9481_af19b59086c2
GAIN-531920-2016 | GA-346344-2016 | 3/31/2016 11:13:23 AM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | Two pressure regulators with reliefs commonly vented together and terminal terminating under air intake louvers go electrical room. If the regulators vent, natural gas could enter the louvers into the electrical room potentially causing an explosion. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Regulator_vents.png | file://x:/photopub/docs/0000000410/05af1656-8c13-4c3f-afe8-8e58343653d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__769f0852_c9e3_45b2_9481_af19b59086c2
ELIN-547909-2016 | EL-323950-2015 | 3/31/2016 3:23:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In an agricultural pumphouse, a new 15amp 600volt transformer was found with the new system ground not connected to the existing system ground. This could lead to a thermal condition. | 4 | Installation Grounding; conductor is not continuous. | Ground_connection.png | file://x:/photopub/docs/0000000410/b92261bd-8734-4260-bb31-6df6d0404b1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25db3f89_3fcb_4fce_a45c_ced03fca4e46
ELIN-565280-2016 | EL-378342-2016 | 4/26/2016 9:00:35 AM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | 120/240 volt 70A circuit feeding the shop sub panel is installed in the main breaker compartment of the main distribution panel. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 70A_sub_feed_in_main_breaker_ompartment.png | file://x:/photopub/docs/0000000421/ed6cfc8e-bc82-42c2-8074-02fe05e528d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90afc1be_4c25_4fd4_9827_1f2047c00fd0
ELIN-572683-2016 | EL-382684-2016 | 5/9/2016 1:19:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Neutral not grounded. Ground conductor is bonded to disconnect enclosure. No effective neutral plane for grounded AC90, TECK90, NMD90, CAT5E, RG6, Heatex, LVT, plastic and metal device boxes system. Potential for shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Neutral_not_grounded_to_electrode.png | file://x:/photopub/docs/0000000427/a581cc06-97f4-46a5-b9d6-44bea112e2dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8bc9079_d8db_4e1b_9d7c_b2a00a1df800
ELIN-573843-2016 | UW-384718-2016 | 5/9/2016 4:50:02 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Electrical equipment enclosures must be sealed to prevent accidental contact. In this floating restaurant covers had been left off junction boxes, live wiring was observed on kitchen equipment, and panel fillers had been omitted during the renovation process just completed. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_to_bus.png | file://x:/photopub/docs/0000000427/da629bd0-21fd-4e9d-8b9d-ca8e4cddb1b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c995822_7271_4e6b_a74b_9ef90afd7f16
GAIN-569560-2016 | GA-382114-2016 | 5/9/2016 8:49:28 AM | ASSESS: GA: Final | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 |  | 2 | Installation clearances or set backs to propane containers not met | Non-compliant_tank_location.png | file://x:/photopub/docs/0000000427/e5af6878-3089-457b-88fb-62c9b6cad1c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8440ab89_8fdd_4f68_98d4_0d007624a495
ELIN-534085-2016 | EL-350322-2016 | 2/29/2016 2:04:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | The service conductors that are terminated in the meterbase run underground to the power shed. As they entered the ground they had no mechanical protection. Over time, the cable could get damaged and expose the unprotected service conductors to contact with people in the area. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Dip_service.png | file://x:/photopub/docs/0000000398/29ee5f4a-79bc-41e4-a93d-fd9929b25e29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9fc43bc_57b9_4a5f_9b0a_f94d520e54ed
ELIN-576568-2016 | UW-387017-2016 | 5/13/2016 11:34:10 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | At the time of assessment the main electrical panel cover was not installed and live expose the busbar was exposed. Existing nonmetallic sheath cables ends were exposed and not terminated safely in a junction box. The resulting affect could lead to someone accidentally making contact with a cable and Been accidentally electrocuted | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Incorrect_use__incorrect_use_of_junction_box_no_connecter_used_and_nonmetallic_chief_cable_on_the_outside_of_a_house.png | file://x:/photopub/docs/0000000429/939e7581-e732-4846-896b-566573eaf8b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089c3de9_3ce2_45a5_8e0b_3e2de7f0f910
ELIN-576568-2016 | UW-387017-2016 | 5/13/2016 11:34:10 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | At the time of assessment the main electrical panel cover was not installed and live expose the busbar was exposed. Existing nonmetallic sheath cables ends were exposed and not terminated safely in a junction box. The resulting affect could lead to someone accidentally making contact with a cable and Been accidentally electrocuted | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | As_found_cover_missing_from_energized_electrical_panel.png | file://x:/photopub/docs/0000000429/9d89cbc9-0258-49ad-9893-439cbe597b91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089c3de9_3ce2_45a5_8e0b_3e2de7f0f910
ELIN-576568-2016 | UW-387017-2016 | 5/13/2016 11:34:10 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | At the time of assessment the main electrical panel cover was not installed and live expose the busbar was exposed. Existing nonmetallic sheath cables ends were exposed and not terminated safely in a junction box. The resulting affect could lead to someone accidentally making contact with a cable and Been accidentally electrocuted | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Cover_plate__Cover_plate_missing_from_junction_box.png | file://x:/photopub/docs/0000000429/61d697ab-5d1b-46b2-9274-8aa57f63ff8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089c3de9_3ce2_45a5_8e0b_3e2de7f0f910
ELIN-576568-2016 | UW-387017-2016 | 5/13/2016 11:34:10 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | At the time of assessment the main electrical panel cover was not installed and live expose the busbar was exposed. Existing nonmetallic sheath cables ends were exposed and not terminated safely in a junction box. The resulting affect could lead to someone accidentally making contact with a cable and Been accidentally electrocuted | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Nonmetallic_sheet_cab__nonmetallic_sheath_cables_not_terminated.png | file://x:/photopub/docs/0000000429/ef5747e4-24d3-4144-bc2b-149f6b440f1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089c3de9_3ce2_45a5_8e0b_3e2de7f0f910
ELIN-576568-2016 | UW-387017-2016 | 5/13/2016 11:34:10 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | At the time of assessment the main electrical panel cover was not installed and live expose the busbar was exposed. Existing nonmetallic sheath cables ends were exposed and not terminated safely in a junction box. The resulting affect could lead to someone accidentally making contact with a cable and Been accidentally electrocuted | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Incorrect_wiring__incorrect_wiring_method_used_junction_box_hidden_in_the_wall.png | file://x:/photopub/docs/0000000429/3fac4327-3420-4ae6-b860-d7bdb5f130ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__089c3de9_3ce2_45a5_8e0b_3e2de7f0f910
GAIN-535760-2016 | GA-301779-2015 | 3/3/2016 3:21:39 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Regulator_vent.png | file://x:/photopub/docs/0000000399/f1f38708-25d4-4bfb-b9fa-fcd885a4b710.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8449f8ce_1ec5_4d40_9cc6_9dce7d04f1b4
ELIN-534859-2016 | EL-154283-2014 | 3/1/2016 7:45:38 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Junction boxes containing energized conductors must be covered to avoid accidental contact. In this installation covers had been removed from light fixture circuitry in an eave. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Wrong_fitting.png | file://x:/photopub/docs/0000000398/a5a12fa5-df5f-459c-bf08-0e3f2ebc28e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75a6b5d9_fe20_4da7_ba7e_76e4a3ef77de
ELIN-534859-2016 | EL-154283-2014 | 3/1/2016 7:45:38 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Junction boxes containing energized conductors must be covered to avoid accidental contact. In this installation covers had been removed from light fixture circuitry in an eave. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_joints.png | file://x:/photopub/docs/0000000398/675ca7ef-d20e-4a33-9c66-198be05663a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75a6b5d9_fe20_4da7_ba7e_76e4a3ef77de
ELIN-570488-2016 | EL-382542-2016 | 5/5/2016 12:51:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Insulated conductors went bent over sharp edges of connectors without a plastic bushing to provide protection may displace insulation and cause major electrical fault | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Meter_base_conductor_entry_no_bushing.png | file://x:/photopub/docs/0000000426/3a731a7e-226a-4025-b7dd-6a3fda05bbe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5d494330_7dc1_469b_9bc9_2d452f466842
ELIN-544798-2016 | EL-323758-2015 | 4/1/2016 9:59:32 AM | ASSESS: EL: Final | png | #asFound | EL110 | Conductors Conductors are not suitably identified. | 3 | 3 | The indentified conductor is not labelled at the panel board and has minimal labelling at the top of the pole. The use of the black conductor as the identified conductor is not standard practice per rule 4-038 for colour of conductors, this can create a shock hazard | 3 | Conductors Conductors are not suitably identified. | Indentified_conductor.png | file://x:/photopub/docs/0000000410/565c18ec-7480-48e9-bf4f-d8c5f68fe020.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c511bc_0d4b_4704_abd8_5c8eba34dcb0
ELIN-509795-2016 | EL-284525-2015 | 4/8/2016 2:29:35 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Service_cable_not_well_supported_and_has_pulled_out_of_connector.png | file://x:/photopub/docs/0000000414/1a835d9c-5482-4093-b8ed-35b54055c7c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e91a23b5_62e5_46ca_89f4_d0b9638e5f3e
ELOP-320910-2015 | EL-211354-2015 | 2/26/2016 5:50:38 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | In mill and industrial installations higher voltages are often used and extra care is required to ensure accidental contact to energized parts cannot happen. In this installation there were open doors on large motor control cabinets and motors were installed without access ports being adequately plugged. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 200_horse_switch_vs_caterpillar.png | file://x:/photopub/docs/0000000397/c6e2f47e-0706-4b2c-b460-cf7d2db4bda2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b020daa_29e5_4194_81cd_8c2725582000
ELOP-320910-2015 | EL-211354-2015 | 2/26/2016 5:50:38 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | In mill and industrial installations higher voltages are often used and extra care is required to ensure accidental contact to energized parts cannot happen. In this installation there were open doors on large motor control cabinets and motors were installed without access ports being adequately plugged. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Motor_JB_open.png | file://x:/photopub/docs/0000000397/593c6bc8-f0db-4771-90e1-d2165b8e80b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b020daa_29e5_4194_81cd_8c2725582000
ELOP-320910-2015 | EL-211354-2015 | 2/26/2016 5:50:38 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | In mill and industrial installations higher voltages are often used and extra care is required to ensure accidental contact to energized parts cannot happen. In this installation there were open doors on large motor control cabinets and motors were installed without access ports being adequately plugged. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Door_open.png | file://x:/photopub/docs/0000000397/b3e56b83-8ab2-408f-9435-e7073d805ef9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b020daa_29e5_4194_81cd_8c2725582000
ELOP-320910-2015 | EL-211354-2015 | 2/26/2016 5:50:38 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | In mill and industrial installations higher voltages are often used and extra care is required to ensure accidental contact to energized parts cannot happen. In this installation there were open doors on large motor control cabinets and motors were installed without access ports being adequately plugged. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Access_to_MCC_room.png | file://x:/photopub/docs/0000000397/29586954-6f01-4c1c-8443-819d2d0269b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b020daa_29e5_4194_81cd_8c2725582000
BPVOP-538033-2016 | 2265148 | 3/3/2016 11:01:22 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of the Domestic hot water indirect heater with Maximum Allowable Working Pressure (MAWP) of 150 psig and Maximum Allowable Water Temperature (MAWT) of 600Fahrenheit, it was determined that safety relief valve has exceeded the required 6 year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject the pressure vessel to pressure above MAWP if control fails or heat exchanger is operated inadvertently with valve on heat receiving side shut. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SRV.png | file://x:/photopub/docs/0000000400/eee8f74e-d0fa-4868-9436-be3191999903.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2350a258_879f_4613_8e7f_998dd3f5a21b
BPVOP-531900-2016 | 4976859 | 2/23/2016 11:52:03 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | Certified individuals are required to operate and monitor high pressure steam boilers that are more than 10m2. I found no certificate of qualifications or individuals onsite. This can lead to safety hazards of personal and the boiler from improper operation. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_data_stamp.png | file://x:/photopub/docs/0000000400/786e242c-969b-46f3-80ae-fbe7ee8536db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e2cd4736_894a_4485_9fdd_e2aa4fbbc601
ELIN-566841-2016 | EL-353215-2016 | 4/27/2016 2:24:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | This assessment found a house panel board to be exposed to the weather. If the equipment becomes wet there is a shock/fire hazard if the main breaker fails to operate properly. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel.png | file://x:/photopub/docs/0000000421/ae2e2066-38c2-40f5-84d2-a775dff9c63a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc8f3f7b_08c6_4d0b_8a77_46d7bb3c99e8
ELIN-546702-2016 | EL-232128-2015 | 3/30/2016 9:36:29 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | A new residence has not been provided weatherproof covers that maintain a weatherproof condition when a cord is installed into the receptacle operating on a 15 amp breaker at 120 volts. Water can enter the receptacle along cord and cord cap and can lead to corrosion of equipment, loss of functionality and in some cases fire. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | In_use_covers_not_provided__tamper_resistant_recptacle_not_provided.png | file://x:/photopub/docs/0000000409/15b77756-f431-4f6f-ac99-fc905a8fedca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d755f728_3247_47f8_863f_97f974612908
ELIN-548746-2016 | EL-289347-2015 | 3/30/2016 11:37:07 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | A separate 400 amp 240 volt system fed by a back up generator was installed. The neutral for this system enters an automated transfer switch with the utility system neutral conductor. These neutral conductors when not identified as separate systems can be confused by maintenance workers and can lead to safety issues for workers should the incorrect neutral system be interrupted. | 3 | General Equipment is not approved for the specific use | Bio_security_no_access_for_photo_non_compliance_identified_by_fsr_in_interview.png | file://x:/photopub/docs/0000000409/8569a9bd-399e-4e61-b887-987e272ebac5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52f66914_804a_40f8_827e_b3c317bb231a
BPVOP-546826-2016 | 2301814 | 3/8/2016 10:40:04 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this moisture separator for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Discharge_separator_1.png | file://x:/photopub/docs/0000000406/6a5172f0-57ce-43d3-9312-cd7a08c23ba5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9ac227b_4a50_45b9_843e_e6421d5032b4
BPVOP-546826-2016 | 2301814 | 3/8/2016 10:40:04 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this moisture separator for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_relief_valve_data_plate.png | file://x:/photopub/docs/0000000406/6d343d08-169f-4fe0-97d9-88cbf890f789.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9ac227b_4a50_45b9_843e_e6421d5032b4
BPVOP-546858-2016 | 2301807 | 3/11/2016 11:59:16 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this air receiver for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_receiver_.png | file://x:/photopub/docs/0000000406/b2e8fbd5-c128-423b-b31c-e787e126ac2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d780321_2140_400a_98ae_3171bcf248bc
ELIN-533718-2016 | EL-339895-2016 | 3/1/2016 2:54:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | This assessment found the kitchen counter receptacles wired with # 14/2 wire. The code requires a heavier wiring method to meet the needs of the kitchen appliances. There is a possible fire hazard with nuisance tripping and the potential use of extension cords to work around the problem, or even increasing the breaker sizes to a dangerous level. | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 14-2_counter_receptacle.png | file://x:/photopub/docs/0000000398/8819388c-c4cd-463e-a76a-eb41bfc306e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8685c95b_b582_4010_84cf_73f1689e02c3
GAIN-533570-2016 | GA-344625-2016 | 3/8/2016 7:52:18 AM | ASSESS: GA: Final | png | #asFound | GA045 | Gas connector passes through wall, floor, ceiling, partition or into appliance | 2 | 2 |  | 2 | Gas connector passes through wall, floor, ceiling, partition or into appliance | Gas_connector.png | file://x:/photopub/docs/0000000402/625d0ef6-d59e-47ba-be6b-a877c68ff279.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fe7ed43_4358_4f7f_9fe4_11e7b71e80cd
BPVOP-575572-2016 | 4090833 | 5/16/2016 1:55:09 PM | ASSESS: BPV OP: Re-Inspection REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a Receiver with MAWP of 225 psig I found the Pressure Relief Valve overdue as per CSA B 51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overall.png | file://x:/photopub/docs/0000000430/72111a36-4f02-418d-b3a4-cb5c524920cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfc1736f_ac16_4165_b395_fd8430124e0d
BPVOP-546858-2016 | 2301807 | 3/11/2016 11:59:16 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this air receiver for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_receiver_data_plate_.png | file://x:/photopub/docs/0000000406/2ea440dd-a113-4cfb-8bbf-25af08a6ca8d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d780321_2140_400a_98ae_3171bcf248bc
BPVOP-546858-2016 | 2301807 | 3/11/2016 11:59:16 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this air receiver for the last 14 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data_plate_.png | file://x:/photopub/docs/0000000406/a7c3d3ee-9144-49db-9b83-41b9e2f223d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d780321_2140_400a_98ae_3171bcf248bc
EDIN-533108-2016 | ED-121944-2014 | 2/22/2016 2:55:42 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting of the escalator brake was not set properly. The brake torque was set during the installation, but the colder temperature (No Outdoor protection) at which the brake torque had been set may have caused an incorrect torque reading. No operating temperature is maintained on this escalator. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 108.1Nm (Newton Meter). The actual brake torque recorded was set at 90Nm. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving. The escalator steps could travel uncontrolled towards the lower landing creating a dangerous situation for the passengers on t | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate29195.png | file://x:/photopub/docs/0000000398/3588387c-f222-48b8-a4d6-cfda21fb90ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cef9b1db_499f_450c_a2a3_bdfc9a793220
EDIN-533100-2016 | ED-121951-2014 | 2/22/2016 3:41:26 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting of the escalator brake was not set properly. The brake torque was set during the installation, but the colder temperature (No Outdoor protection) at which the brake torque had been set may have caused an incorrect torque reading. No operating temperature is maintained on this escalator. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 108.1Nm (Newton Meter). The actual brake torque recorded was set at 94Nm. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving. The escalator steps could travel uncontrolled towards the lower landing creating a dangerous situation for the passengers on t | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate29196.png | file://x:/photopub/docs/0000000398/436533a3-07ee-45b2-8465-c2d6c421f786.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec62c067_0b63_4739_997e_aa3d73795dd4
EDIN-533091-2016 | ED-121935-2014 | 2/23/2016 2:26:56 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting of the escalator brake was not set properly. The brake torque was set during the installation, but the colder temperature (No Outdoor protection) at which the brake torque had been set may have caused an incorrect torque reading. No operating temperature is maintained on this escalator. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 108.1Nm (Newton Meter). The actual brake torque recorded was set at 80Nm. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving. The escalator steps could travel uncontrolled towards the lower landing creating a dangerous situation for the passengers on t | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Tag29194.png | file://x:/photopub/docs/0000000398/e460881a-9791-4ad4-8aff-6b1e74b7c5cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d6768ba_a2ff_4136_b000_cc6a6d2b3921
ELIN-550661-2016 | EL-356908-2016 | 4/1/2016 9:42:52 AM | ASSESS: EL: Final | png | #asFound | EL210 | All Classes, All Zones Area is classified: wiring method is not suitable for area. | 4 | 4 | 240V 15A equipment has been located within a hazardous area containing explosive gas, equipment is not rated for this location and could be the ignition source for the gas because of improper sealing and construction for location. | 4 | All Classes, All Zones Area is classified: wiring method is not suitable for area. | Stop_Button.png | file://x:/photopub/docs/0000000413/c444ae1d-508a-43d2-81ba-dbd63988f166.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59560a63_034f_47de_9ccd_9ee8a27c1732
ELIN-553663-2016 | EL-372143-2016 | 4/6/2016 8:34:21 AM | ASSESS: EL: Service Connection | png | #asFound | EL082 | Continuity Multiple grounded systems are not interconnected. | 3 | 3 | Two consumer's services 400 & 60 amp, 120/240 volt single phase, are installed at the same building without the ground electrodes interconnected. This is a potential shock hazard in a fault condition. | 3 | Continuity Multiple grounded systems are not interconnected. | Multiple_services_without_ground_interconnection.png | file://x:/photopub/docs/0000000413/d6245227-dae1-4e00-993c-99886a81975c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a66f4a9c_addc_4498_8335_a32acc6a7e27
ELIN-537108-2016 | EL-353993-2016 | 3/3/2016 11:13:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 1 | Point of attachment above weather head | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Point_of_attachment.png | file://x:/photopub/docs/0000000399/0d239fc0-c07b-4129-b36d-a6b4fcb7b6ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32a99039_1108_4148_a0f4_48c00a4b1b7d
ELIN-544352-2016 | EL-328550-2015 | 3/21/2016 12:54:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Point of attachment for over head service is above the weather head. Over head conductors when installed in this manner provide a path for moisture and rain to get into the meter base, thus causing the equipment inside to corrode. failure of internal equipment in the meter may cause shock and fire to persons and property. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Point_of_attachement_above_weatherhead.png | file://x:/photopub/docs/0000000406/97e5af54-97d3-44f2-84b6-c9852413b3d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19088ab6_4d32_4e05_93b9_143558f1afa1
ELIN-546182-2016 | EL-344291-2016 | 3/21/2016 4:09:42 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Point of attachement for overhead service is in line with conductor weather head. Conductors installed in this manner have a risk of rain and moisture entering in to conduit and into meter base as the drip loops will not be adequate. Water and moisture entering meter base may cause corrosion and premature failure of metering equipment. A potential of shock and fire to persons or property are present. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Point_of_attachement_in_line_with_weatherhead.png | file://x:/photopub/docs/0000000406/e9f23e06-514c-4e39-a0ec-0afb31fbedf4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f35aeb04_d55f_4000_ada1_88896f37c4ef
ELIN-523675-2016 | UW-214737-2015 | 5/16/2016 3:46:24 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Overhead lines and consumer electrical services must be maintained on safe working order. In this installation two cabins had been wired to an existing service. The wiring metrology was not safe and the condition of the services had deteriorated to the point of disconnection being necessary. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Pole_to_pole_with_splices.png | file://x:/photopub/docs/0000000430/93a12a85-c07d-4340-9117-140481942897.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__973f4228_3929_4f04_b716_741a51cb5207
ELIN-568811-2016 | EL-349091-2016 | 5/2/2016 7:36:31 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Found ACWU armoured cable for service installation outdoors with cable jacket stripped back too far and it's dry type cable outdoors is not approved electrical equipment approved for use in outdoors wet location. When cables or conductors are damaged or not approved for the use in wet location to eke tribal equipment could become damaged and become a fire or shock hazard to people and property. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 2.png | file://x:/photopub/docs/0000000424/585cd962-ddc6-421c-a41e-282676a2cb46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef4c683_02a3_4840_8320_c1150d74500e
ELIN-568811-2016 | EL-349091-2016 | 5/2/2016 7:36:31 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Found ACWU armoured cable for service installation outdoors with cable jacket stripped back too far and it's dry type cable outdoors is not approved electrical equipment approved for use in outdoors wet location. When cables or conductors are damaged or not approved for the use in wet location to eke tribal equipment could become damaged and become a fire or shock hazard to people and property. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3_outdoors_wet_location_service_meterbase_and_ACWU_cable_stripped_back_too_far.png | file://x:/photopub/docs/0000000424/157615e5-3b0a-4ccf-8623-20c5ea68268b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef4c683_02a3_4840_8320_c1150d74500e
BPVIN-537622-2016 | UW-355852-2016 | 3/3/2016 4:30:30 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000399/1fce1932-c0fe-44b8-a39b-c915a263a24c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ae58610_7a86_4788_84c0_95c12b1de081
ELIN-568811-2016 | EL-349091-2016 | 5/2/2016 7:36:31 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Found ACWU armoured cable for service installation outdoors with cable jacket stripped back too far and it's dry type cable outdoors is not approved electrical equipment approved for use in outdoors wet location. When cables or conductors are damaged or not approved for the use in wet location to eke tribal equipment could become damaged and become a fire or shock hazard to people and property. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 1.png | file://x:/photopub/docs/0000000424/9db8bcd2-d088-4e5b-9bb8-df514116d628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ef4c683_02a3_4840_8320_c1150d74500e
ELIN-546222-2016 | EL-368170-2016 | 3/22/2016 5:05:20 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL274 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | 3 | 3 | Hydro massage tubs must be equipped with GFCI protection to avoid accidental shock. In this installation GFCI protection had not been provided in four rental cabins. | 3 | Pools, Spas and Hot Tubs Protection; GFCI not provided. | No_GFCI_or_disconnect.png | file://x:/photopub/docs/0000000407/aa29d505-c146-4084-859b-a5f6ac8c262e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20a162d2_ea7f_4dbb_a152_8f16dbea66b0
ELIN-545767-2016 | EL-366879-2016 | 3/22/2016 9:10:10 AM | ASSESS: EL: Final | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Secondary service poles must be capable of holding overhead wires coming from Hydro pole. In this installation the pole on the property had deteriorated to the point of not being safe. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | The_tower_of_pizza.png | file://x:/photopub/docs/0000000407/335ee563-cc92-4a28-93c8-49190fa95d79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56e8b96a_2799_48fd_86c5_d3684bed62f4
ELIN-578122-2016 | EL-387982-2016 | 5/17/2016 10:35:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 4 | Overhead service conductors within reach. These conductors are to be positioned a minimum of 3m above grade. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | A.png | file://x:/photopub/docs/0000000431/1190fb76-8bc5-45d4-b6f6-6852321d977a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b579cc2_eedd_4ff9_846e_d7fc2961afbd
ELIN-545768-2016 | EL-361205-2016 | 3/22/2016 10:54:02 AM | ASSESS: EL: Final | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | Electrical services must be grounded where the service conductors encounter the first disconnect. In this installation the system ground had not been installed. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | No_system_ground.png | file://x:/photopub/docs/0000000407/92bcd85a-e95a-47ad-92b5-a932fe34599d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99554af2_f457_4e74_b8bb_34298cdda65f
ELIN-566255-2016 | UW-380148-2016 | 4/22/2016 9:49:35 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | 240 v service disconnect installed without permission and outside scope of FSR and contractor license. The installation is subject to weather and installed improperly and may lead to equipment failure. In addition, the utility was requested to remove meter without permit reference. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Invoice.png | file://x:/photopub/docs/0000000420/9d54260e-3517-4e0f-9cfb-c60fea968b1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5effa13f_36e4_44f2_aa69_294032735f26
ELIN-566255-2016 | UW-380148-2016 | 4/22/2016 9:49:35 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 3 | 240 v service disconnect installed without permission and outside scope of FSR and contractor license. The installation is subject to weather and installed improperly and may lead to equipment failure. In addition, the utility was requested to remove meter without permit reference. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Disconnect.png | file://x:/photopub/docs/0000000420/7b9c1f5e-1603-4183-be39-4c66703742d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5effa13f_36e4_44f2_aa69_294032735f26
ELIN-545489-2016 | EL-367754-2016 | 3/23/2016 8:07:21 AM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | During an inspection of a used mobile home, a cable splice was found in the wall behind an installed ventilation fan. The splice was not contained within a device box and conductor overheating or arcing at the splice could pose a fire hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Open_splice.png | file://x:/photopub/docs/0000000407/ef484108-1a60-407d-a862-3b201d928f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ecf09ff_8fc1_42d6_ac14_5f618c7d69d7
ELIN-576167-2016 | EL-380661-2016 | 5/15/2016 3:24:14 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Most electrical systems are required have their neutral conductors connected to ground. In this installation, after one prior inspection request to bury the grounding electrode, a physical inspection revealed that there was no effective system ground established. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Plate_not_buried.png | file://x:/photopub/docs/0000000430/77039277-61f6-443d-a3b1-7ccdb51c4b6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5dacddba_6ba6_4eb5_8219_ab8720fa0606
ELIN-575187-2016 | EL-369481-2016 | 5/16/2016 7:23:11 AM | ASSESS: EL: Final | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In electrical services the neutral conductor is to be connected to ground at the first switch or disconnect. In this installation the system ground had been removed from the first disconnect and moved to an automatic transfer switch. This grounding conductor was not continuous. | 4 | Installation Grounding; conductor is not continuous. | Ground_connection_passes_to_transfer_switch.png | file://x:/photopub/docs/0000000430/28269f26-c7bc-4129-b1b8-87494baf2194.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__04b5e6c5_7ca1_417a_9894_ccb1bbd9e4af
ELIN-574698-2016 | EL-309582-2015 | 5/16/2016 11:50:35 AM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found the baptismal water heater to be unapproved. There is a shock hazard to persons in the water with unapproved Equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Heater2.png | file://x:/photopub/docs/0000000430/f482692b-5c5d-4788-b3ed-e709cba27912.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac0e4ba6_15d8_40b3_98fd_b3124b18e708
ELIN-574698-2016 | EL-309582-2015 | 5/16/2016 11:50:35 AM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found the baptismal water heater to be unapproved. There is a shock hazard to persons in the water with unapproved Equipment. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Heater.png | file://x:/photopub/docs/0000000430/46d7577f-d33d-412e-bb74-d0393261fc83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac0e4ba6_15d8_40b3_98fd_b3124b18e708
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Existing_mobile_home.png | file://x:/photopub/docs/0000000403/a5eafd31-7327-48a0-b74d-6b491c2c7326.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Interior_of_house_service_panel.png | file://x:/photopub/docs/0000000403/00c0eafc-ca72-4172-bac5-022fc2e2f2dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Extension_cord_used_to_connect_temporarily_connect_new_service_panel_in_the_house.png | file://x:/photopub/docs/0000000403/4751dc04-5e94-4154-80b4-232825bed6e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | New_service_panel_in_house.png | file://x:/photopub/docs/0000000403/e7d95cc8-0110-4ea0-9362-927f4148f752.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Cord_connected_to_receptacle_at_mobile_home_to_supply_power_to_new_house.png | file://x:/photopub/docs/0000000403/d01173c6-8901-41fd-be00-c38014fa7013.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | Cord_connected_to_panel_in_house.png | file://x:/photopub/docs/0000000403/ddf085f7-f73b-4795-a877-58a723e174b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-542546-2016 | EL-106889-2014 | 3/11/2016 5:50:10 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Temporary wiring is not permitted to be used to connect permanent installations to temporary installations. This is required in part to prevent mechanical and thermal damage to potentially under sized and inadequately installed wiring methods. Another consideration is the back feeding of permanent feeder, service cables, and equipment for permanent systems can create a potential shock hazard for unsuspecting persons working on or contacting these energized parts. This installation has a 20A, 120V flexible cord (extension cord) used to back feed the 200A, 120/240V service panel of a new house to temporarily provide power to the new house circuits. The cable is under sized for the load, and back feeding the house service cable may unexpectedly energize the service cable that is exposed at the service pole if the main breaker is turned on. Left uncorrected this is a potential shock and fire hazard. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | New_house_.png | file://x:/photopub/docs/0000000403/ed0f9244-7647-40f2-9a40-6995273c317c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22a2fc77_0011_40b5_ade3_9d5e646b2571
ELIN-548131-2016 | EL-356637-2016 | 3/22/2016 4:41:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In a new public park, a temporary construction panel was found containing 15amp 120volt receptacles that are over fused with a 20amp breaker and no Ground Fault Circuit Interruption protection. This is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Breaker_sizing.png | file://x:/photopub/docs/0000000407/3c89733b-1aa7-44b6-92be-3174613954b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64779905_67ae_499c_b775_a56a44c1f672
ELIN-548131-2016 | EL-356637-2016 | 3/22/2016 4:41:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | In a new public park, a temporary construction panel was found containing 15amp 120volt receptacles that are over fused with a 20amp breaker and no Ground Fault Circuit Interruption protection. This is a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Duplex_receptacles_with_OC_rating.png | file://x:/photopub/docs/0000000407/9cc3407c-e484-4215-8e9d-f00d435d212f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64779905_67ae_499c_b775_a56a44c1f672
ELIN-565674-2016 | EL-379489-2016 | 4/27/2016 11:41:02 AM | ASSESS: EL: Final | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Non-treated pole is showing major signs of decay. Pole is non-supported as there is no guy present. If left there would be a possibility of a collapse causing a risk of person and property damage, shock hazard, and a fire risk. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Rotten_pole.png | file://x:/photopub/docs/0000000421/6c4676d7-59e5-4c64-aa93-cf99d24f7a6a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__898f0ee4_9bbd_490d_941b_1d1d2a7c49ba
ELIN-565674-2016 | EL-379489-2016 | 4/27/2016 11:41:02 AM | ASSESS: EL: Final | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Non-treated pole is showing major signs of decay. Pole is non-supported as there is no guy present. If left there would be a possibility of a collapse causing a risk of person and property damage, shock hazard, and a fire risk. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Rotten_pole_base_.png | file://x:/photopub/docs/0000000421/51d3480c-16e4-4ecf-bd83-005901dc1c9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__898f0ee4_9bbd_490d_941b_1d1d2a7c49ba
BPVIN-553957-2016 | UW-372321-2016 | 4/4/2016 10:41:56 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Expansion_tank_.png | file://x:/photopub/docs/0000000417/d03c1eab-7177-4d19-9e15-430b235ddeda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66a75074_d007_4b02_9449_3e8c1c3b8d34
BPVOP-554542-2016 | 2752929 | 4/15/2016 12:46:26 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Pitting_evidence.png | file://x:/photopub/docs/0000000417/b69adc77-0b54-43e5-b64b-3fce73e15111.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f81194a_0ddd_4806_a576_17f18a443674
BPVOP-554542-2016 | 2752929 | 4/15/2016 12:46:26 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Cushion_tank_internal.png | file://x:/photopub/docs/0000000417/0af566ef-a539-4ae3-98e3-b0c0f78fa1dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f81194a_0ddd_4806_a576_17f18a443674
BPVOP-554519-2016 | 2258668 | 4/15/2016 12:48:12 PM | ASSESS: BPV OP: Miscellaneous REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Vessel_internal.png | file://x:/photopub/docs/0000000417/075b4284-05bd-4227-b4f5-ef0489018bac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37bf3eb1_8eb7_47a1_a55a_a7f2015a7c44
ELIN-539078-2016 | UW-356404-2016 | 3/4/2016 10:42:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Branch circuit portion of panel was found uncovered and cover was lost. Wiring for range was found exiting the front of the panel and a cable connector was not in use as required, exposed breaker terminations and panel bussing are present. This is in a residential location and is exposed to unqualified individuals. If accidental contact occurs with the energized equipment a risk of shock, death and fire to persons and property are present. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_enrgized_equipment_and_non_approved_cable_termination_methods.png | file://x:/photopub/docs/0000000401/255b64a8-fbec-4de1-9d80-f62c1159ddf9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3928a9b2_bb76_46fd_ac4b_4344b052bbaa
ELIN-539078-2016 | UW-356404-2016 | 3/4/2016 10:42:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Branch circuit portion of panel was found uncovered and cover was lost. Wiring for range was found exiting the front of the panel and a cable connector was not in use as required, exposed breaker terminations and panel bussing are present. This is in a residential location and is exposed to unqualified individuals. If accidental contact occurs with the energized equipment a risk of shock, death and fire to persons and property are present. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Panel_cover_missing_exposed_terminations_and_bussing.png | file://x:/photopub/docs/0000000401/cdc349fe-844a-475f-9321-ab4fcd4552cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3928a9b2_bb76_46fd_ac4b_4344b052bbaa
ELIN-578143-2016 | EL-382781-2016 | 5/17/2016 3:10:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Communication_wiring_power_cables.png | file://x:/photopub/docs/0000000431/ec267781-0396-4191-a7ca-bc3629ebe78d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26dc3980_4a42_47b6_8344_789f95d941f4
ELIN-567854-2016 | EL-332995-2016 | 5/3/2016 11:39:11 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | 120 volt branch circuits protected by a 15 amp overcurrent device are energized and the possibility of contact for persons exists. The area of concern is a commercial tenant improvement area. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_branch_wiring.png | file://x:/photopub/docs/0000000424/d33a750d-a429-42f4-b0aa-19d243bf1fe6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21420746_70e5_4070_bad5_0f42a63b5019
ELIN-570304-2016 | UW-382393-2016 | 5/3/2016 3:39:41 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | 4/0 Aluminum, 3 conductor overhead neutral support cable does not have the required clearance from a deck location. This is a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Overhead_conductors.png | file://x:/photopub/docs/0000000424/20c4b6f1-78a2-4aeb-a52f-d0f7a3ce8248.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68224ae7_1d3a_4180_8a21_5fcdbab4a22b
ELOP-226609-2014 | 5149468 | 4/14/2016 10:00:40 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Electrical equipment must be kept in good working order. In this large strata complex some of the raceways and enclosures are beginning to rust due mainly to an ocean location. Attention was recommended. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | EMT_rusted_out.png | file://x:/photopub/docs/0000000416/0c8b7ec5-bc2c-4446-b598-25e090538b07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dc36fc52_2ae3_456f_846b_080ca6f2e739
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_105_panel_directory.png | file://x:/photopub/docs/0000000416/34bf0f0c-2aa8-4e31-a7fe-fa72d3923e21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_104_panel_directory.png | file://x:/photopub/docs/0000000416/57f57fbf-f28f-47aa-84a4-623c6ca64b4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Improperly_terminated_three-wire_circuits_in_unit_105_panel_.png | file://x:/photopub/docs/0000000416/50f9f806-d3bc-4b3c-848b-de8a83f46255.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-571934-2016 | EL-256986-2015 | 5/9/2016 11:13:13 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | The 125 kVA step up transformer from 240 V to 600 V was not grounded. Any fault currents found in the distribution equipment would not be finding their way back to the system ground and the likelihood of somebody getting accidentally shocked is high | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Photo_2_main_neutral_not_grounded_in_the_correct_location.png | file://x:/photopub/docs/0000000427/156620ba-d03a-4f7d-a2ab-d086314384b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05dbce69_3b12_402d_b924_27882b93e2ae
ELIN-571934-2016 | EL-256986-2015 | 5/9/2016 11:13:13 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | The 125 kVA step up transformer from 240 V to 600 V was not grounded. Any fault currents found in the distribution equipment would not be finding their way back to the system ground and the likelihood of somebody getting accidentally shocked is high | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Photo_1__step_transformer_not_grounded.png | file://x:/photopub/docs/0000000427/d6ca8c9c-9a45-4713-9129-68deba8bf146.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__05dbce69_3b12_402d_b924_27882b93e2ae
ELIN-559234-2016 | EL-337403-2016 | 4/14/2016 4:57:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | Ground bushing not installed on consumer service conductor. This is a fire hazard because the consumer service conductor is protected by the utility fuse which are generally over sized. Ground bushings ensure a low resistance bond which will help facilitate the flow of current in the event the cable becomes damaged. | 3 | Continuity Bonding; method for equipment is not adequate. | A.png | file://x:/photopub/docs/0000000416/c9455d6d-9069-4bba-8f4c-0f9b34edce6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76508dad_86da_4b53_9d3a_305ab6443c45
ELIN-554745-2016 | EL-344825-2016 | 4/14/2016 8:33:11 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | 1000W metal hallide discharge lighting ballasts mounted on combustible material. Ballasts are a source of heat and should not be mounted on combustible material. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | C.png | file://x:/photopub/docs/0000000416/31582f70-0777-4f55-9f77-e80fafd5d349.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e3b87dc_0644_48c1_b864_0ca1c2807858
ELIN-554745-2016 | EL-344825-2016 | 4/14/2016 8:33:11 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | 1000W metal hallide discharge lighting ballasts mounted on combustible material. Ballasts are a source of heat and should not be mounted on combustible material. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | D.png | file://x:/photopub/docs/0000000416/fdd1a325-bbfc-4306-a73e-a16a06d03029.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e3b87dc_0644_48c1_b864_0ca1c2807858
ELIN-569372-2016 | EL-212536-2015 | 5/4/2016 3:39:31 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | NMD90 (standard household inside wire) was installed in a raceway and a wet location. This type of wire is not approved for wet locations or raceways. The use of this wire in these locations could result in an electric shock or short circuit condition. | 3 | Conductors Equipment is not approved for the specific use. | NMD90_installed_in_RPVC_.png | file://x:/photopub/docs/0000000424/15d5e9ce-1b05-4c03-858a-269962eae4bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af2fc707_56df_4865_9bba_b52a0757d071
ELIN-549517-2016 | UW-369934-2016 | 3/24/2016 10:52:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The bath fan in the upper washroom has stopped working which leads to corrosion on equipment in the room, this leads to further equipment damage | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Washroom_outlet.png | file://x:/photopub/docs/0000000409/542c0119-723d-48c7-9042-c47d85117eb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1caa2619_b884_4a6e_837f_d903da055ffb
ELIN-549517-2016 | UW-369934-2016 | 3/24/2016 10:52:03 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | The bath fan in the upper washroom has stopped working which leads to corrosion on equipment in the room, this leads to further equipment damage | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Bath_fan.png | file://x:/photopub/docs/0000000409/74764bb8-6c20-4d6c-9804-5c7067aebe61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1caa2619_b884_4a6e_837f_d903da055ffb
BPVOP-551564-2016 | BPV-041265-2013 | 3/30/2016 2:40:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a hot water heating plant with a heating capacity greater than 150m2 while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_2_data_plate.png | file://x:/photopub/docs/0000000409/0c42a678-561f-4f03-b5d5-f89f417813a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf6e8215_561f_4c31_b3b2_12344a4ed234
BPVOP-551564-2016 | BPV-041265-2013 | 3/30/2016 2:40:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a hot water heating plant with a heating capacity greater than 150m2 while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_3_data_plate.png | file://x:/photopub/docs/0000000409/1cd41d52-02ff-413b-87af-04009f738a50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf6e8215_561f_4c31_b3b2_12344a4ed234
BPVOP-551564-2016 | BPV-041265-2013 | 3/30/2016 2:40:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a hot water heating plant with a heating capacity greater than 150m2 while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | hot_water_heating_plant.png | file://x:/photopub/docs/0000000409/17d13966-4adb-45a6-b980-473c2ca49525.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf6e8215_561f_4c31_b3b2_12344a4ed234
BPVOP-551564-2016 | BPV-041265-2013 | 3/30/2016 2:40:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a hot water heating plant with a heating capacity greater than 150m2 while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Boiler_1_name_plate.png | file://x:/photopub/docs/0000000409/e01786cc-1e28-465f-948c-bbe1aee0c2d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf6e8215_561f_4c31_b3b2_12344a4ed234
BPVOP-551564-2016 | BPV-041265-2013 | 3/30/2016 2:40:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP168 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | 3 | 3 | The person in charge of the plant must be present at all times in the machinery room or in the immediate vicinity within the plant premises while the plant is in operation. I found that continuous supervision was not provided for a hot water heating plant with a heating capacity greater than 150m2 while the plant was in operation. Potential exists for an incident to occur due to lack of timely corrective actions. | 3 | 5.0.1 Operator non-compliance - Continuous supervision not provided by the certified operators (for plant requiring certified operators) | Heating_plant_drawings.png | file://x:/photopub/docs/0000000409/6cff9e9b-c9d0-4630-b210-e59d18471aa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf6e8215_561f_4c31_b3b2_12344a4ed234
ELIN-559988-2016 | EL-369739-2016 | 4/15/2016 9:34:09 AM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | Unapproved panel fillers installed. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Sub_panel.png | file://x:/photopub/docs/0000000417/04b74c1f-ec6d-4f50-93de-c50d77ad14df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c40ee05d_cebc_467d_98e1_6703bc77b9e9
ELIN-550171-2016 | EL-234501-2015 | 4/14/2016 8:51:59 AM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 | Dry location connector used to terminate consumer service conductors in wet location below meter base, failing to prevent ingress of moisture into cabling. This leads to a risk of personal injury (shock) or property damage (thermal event/interface fire) as a result of fault conditions. | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Detail01_service_cabling.png | file://x:/photopub/docs/0000000418/9f1105f4-694b-4899-a259-f28e6eedba56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a41d311_2b66_4277_b678_2c86fe03ecf0
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_105_panel.png | file://x:/photopub/docs/0000000416/97f03bce-dad7-4714-b5e6-78b9136939d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | End_of_conductor_from_circuit_11b_in_unit_105_insulation_thermally_damaged_from_incorrect_termination_at_breaker.png | file://x:/photopub/docs/0000000416/e030cf7e-4686-437d-8e52-0bc30072beb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_104_improperly_terminated_three_wire_circuits.png | file://x:/photopub/docs/0000000416/8c4729e2-f228-45b4-aa5e-5116b405022f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Exterior_of_multi-residential_senior_building.png | file://x:/photopub/docs/0000000416/ed4750ca-20db-42d1-8b4c-742c84e3442e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Unit_104_improperly_terminated_three-wire_circuits.png | file://x:/photopub/docs/0000000416/8a53eac1-5683-44e2-ac5c-4d639f3ecf0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Improperly_terminated_three-wire_circuits_in_unit_105_panel.png | file://x:/photopub/docs/0000000416/608a9fe6-2a0a-4b34-b69d-8e87f6ab2bbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Front_entrance_of_building.png | file://x:/photopub/docs/0000000416/60d6767a-6060-4a81-b6cc-b4563adc5f0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-560284-2016 | EL-054400-2013 | 4/14/2016 5:12:33 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to be terminated to circuit breakers connected to different buses in panel boards. This is required so that the neutral conductor carries only the unbalanced current of a three wire circuit rather than the sum of the current from both circuits. This is intended to prevent the neutral conductor from becoming overloaded. Terminations of conductors at circuit breakers are required to be fully inserted into the termination lug to ensure a proper connection after tightening the termination screw. This is required in order to prevent thermal damage to conductors and equipment associated with a high resistance connection often caused by a loose or improper connection. This installation has improperly terminated three wire circuits and an improperly terminated conductor at a circuit breaker termination. The improper conductor termination has caused thermal damage to the conductor insulation and tripping of the circuit breaker. Left uncorrected this is a potential fire hazard should w | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Circuit_11b_from_unit_105_panel_-_insulation_s_thermally_damaged_from_incorrect_installation_at_breaker_termination.png | file://x:/photopub/docs/0000000416/42900b89-919f-41eb-adbb-03db4d6437ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29e76237_252e_4773_bede_2ca5abfa6d48
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Photo_of_temporary_service_enclosure_from_the_drive_way.png | file://x:/photopub/docs/0000000410/43dfe5df-132e-4d03-affe-3046a734b45e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Photo_of_sub-panels_and_receptacles_installed_adjacent_to_hot_tub_-_hot_tub_is_behind_the_ivy.png | file://x:/photopub/docs/0000000410/ae72f3a9-f169-4551-939a-fcae29578811.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Sub-panels_and_receptacles_installed_adjacent_to_the_hot_tub.png | file://x:/photopub/docs/0000000410/8b3ff125-184e-4f67-9e9f-a4acd6b0a034.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Panel_with_GFCI_breaker_installed_adjacent_to_the_hot_tub.png | file://x:/photopub/docs/0000000410/75cf5add-e848-4751-a460-ccd8c6af91d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Non-weather_proof_panel_beside_hot_tub.png | file://x:/photopub/docs/0000000410/2497a403-13af-4e4d-a76b-b833389c1d85.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Photo_of_service_pole_from_the_drive_way.png | file://x:/photopub/docs/0000000410/ce67d863-e5f7-41e9-be1a-737030510aff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-552041-2016 | UW-371328-2016 | 3/31/2016 2:25:27 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Receptacles are required to be installed a minimum of 1.M from a hot tub. The ground fault circuit interrupter (GFCI) for the hot tub is required to be installed at least 3M from the the hot tub. These requirements are intended to prevent occupants of the hot tub from plugging portable devices or appliances into receptacles, and to prevent the operation of the GFCI device while in the tub. This is required to prevent occupants of the tub from shock hazards relative to the wet location and utilization and operation of electrical equipment. This installation has sub-panels, receptacles, and the hot tub GFCI device located within reach and approximately 1M from the hot tub water. Left uncorrected this is a potential shock hazard for occupants of the hot tub. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Photo_of_property_from_the_street.png | file://x:/photopub/docs/0000000410/d04e27ef-9579-4386-9a14-d47871ffd71c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0375d212_b64b_4ddf_a30b_8cecfd0e0032
ELIN-566782-2016 | EL-231917-2015 | 4/29/2016 2:10:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | When installing meter bases, switches, or other electrical equipment to poles in exterior locations the equipment should not be mounted to wood that has been fastened to the pole. This is not permitted because over time wood will deteriorate and equipment will no longer be properly secured to the pole. This installation has a meter base mounted to plywood that has been fastened to a service pole. Left uncorrected over an extended period of time the wood may deteriorate leaving the meter base unsecured at the pole. This can lead to a fire and shock hazard if equipment becomes damaged from relative movement between the service cables and the meter base or from water entering the meter base through open mounting holes. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_to_new_cabin.png | file://x:/photopub/docs/0000000422/7efca94c-ab68-4cc1-9526-bcc1565d7f0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__928a6113_18ce_4399_abb7_5201ab20c502
ELIN-566782-2016 | EL-231917-2015 | 4/29/2016 2:10:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | When installing meter bases, switches, or other electrical equipment to poles in exterior locations the equipment should not be mounted to wood that has been fastened to the pole. This is not permitted because over time wood will deteriorate and equipment will no longer be properly secured to the pole. This installation has a meter base mounted to plywood that has been fastened to a service pole. Left uncorrected over an extended period of time the wood may deteriorate leaving the meter base unsecured at the pole. This can lead to a fire and shock hazard if equipment becomes damaged from relative movement between the service cables and the meter base or from water entering the meter base through open mounting holes. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_base_mounted_to_pole.png | file://x:/photopub/docs/0000000422/273ca249-97a5-4bfc-a6c2-cc7493d53e41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__928a6113_18ce_4399_abb7_5201ab20c502
ELIN-566782-2016 | EL-231917-2015 | 4/29/2016 2:10:47 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | When installing meter bases, switches, or other electrical equipment to poles in exterior locations the equipment should not be mounted to wood that has been fastened to the pole. This is not permitted because over time wood will deteriorate and equipment will no longer be properly secured to the pole. This installation has a meter base mounted to plywood that has been fastened to a service pole. Left uncorrected over an extended period of time the wood may deteriorate leaving the meter base unsecured at the pole. This can lead to a fire and shock hazard if equipment becomes damaged from relative movement between the service cables and the meter base or from water entering the meter base through open mounting holes. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Plywood_used_to_mount_meter_base_to_pole_.png | file://x:/photopub/docs/0000000422/0a785265-984a-4f91-b418-33bb253dfebb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__928a6113_18ce_4399_abb7_5201ab20c502
ELIN-549965-2016 | EL-181882-2014 | 3/29/2016 12:28:51 PM | ASSESS: EL: Final | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | 20A 120V kitchen outlet is not properly mounted to the outlet box, this could result in a shock hazard to persons or equipment failure. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Outlet.png | file://x:/photopub/docs/0000000409/4204967e-a9a5-40e1-be61-004d30b182a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a9a2536_7e2b_42d4_95b6_9cd6b4d3282b
ELIN-553318-2016 | EL-277484-2015 | 4/8/2016 10:45:34 AM | ASSESS: EL: Final | png | #asFound | EL214 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | 4 | 4 | The propane relief valve has been place directly under the enclosure where the 60A 240V electrical panel in installed. This could result in a possible ignition of the gas upon relief and explosion. | 4 | All Classes, All Zones Area is classified: electrical equipment is installed where ignitable or explosive gases or vapours are present. | Propane_relief.png | file://x:/photopub/docs/0000000414/0278b254-bdce-4ea8-ba0a-9fd273a87b18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d955814f_b4ea_427a_a0b3_73762c041226
ELIN-553317-2016 | EL-309000-2015 | 4/7/2016 9:52:19 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Outdoor 15A 120V receptacle has not been provided with GFCI protection which could result in a shock hazard to persons using it. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outdoor_receptacle.png | file://x:/photopub/docs/0000000414/b2842255-d4dd-45b5-82ce-c8b6abbfab95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39001fb8_34dd_450c_9bf9_7e8b3df5f5f5
ELIN-532044-2016 | EL-299001-2015 | 2/25/2016 11:22:51 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | A shock hazard may result if water from rain etc wets the receptacle when a cord is plugged into it. An outdoor receptacle outfitted with a standard hinged cover plate is only weatherproof when there is no cord inserted and it is closed. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Weatherproof_cover.png | file://x:/photopub/docs/0000000396/35bf10e8-4954-47fd-a840-ced8c8b11ca4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0028bd8_347f_4c7a_bf57_e87447fb04fd
ELIN-542985-2016 | EL-350179-2016 | 3/14/2016 4:21:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL106 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | Bending_radii.png | file://x:/photopub/docs/0000000403/59ddd14d-4994-4fad-bc95-bbd36875fa7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09a0c4b4_6fd2_48ab_bee4_bad11e737a87
ELIN-542985-2016 | EL-350179-2016 | 3/14/2016 4:21:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL106 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | DB2_mechanicalprotection.png | file://x:/photopub/docs/0000000403/7a732564-4363-4a66-a28f-554f286c55aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09a0c4b4_6fd2_48ab_bee4_bad11e737a87
ELIN-555789-2016 | EL-359489-2016 | 4/11/2016 9:35:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | A 200 amp 120/240 volt duplex meter base is rated at 100 amp maximum per position. The installed main residence's overcurrent protection is rated at 125 amps. The equipment is not rated for the corresponding amperage ratings. This is a thermal concern. | 3 | Protection and control Loading of distribution equipment exceeded | Meter_base_ratings__.png | file://x:/photopub/docs/0000000415/21465c6b-1550-4f5b-988d-a3b00a4c415d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2556a5e0_5319_406b_bc5f_ee39b1bf8876
ELIN-556283-2016 | EL-359489-2016 | 4/11/2016 9:16:25 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 120 volt 15 amp non metallic sheathed cable within 32 mm of surface framing. There is the possibility of a nail or screw damaging the branch wiring. This is a thermal issue. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_wiring_within_32mm_of_surface_framing_.png | file://x:/photopub/docs/0000000415/6fd0f4a4-3e28-4c60-b609-97ba792f2ac3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e8f0d02_8812_4c1d_8825_3360b1d3f12b
ELIN-555378-2016 | EL-351804-2016 | 4/11/2016 2:40:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | 3 conductor 250 kcm aluminum armoured cable exceeds the permitted 1.5 meters inside a wood framed area. This is a thermal hazard should a fault occur in the service conductors. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_conductor_greater_than_1_5_meters.png | file://x:/photopub/docs/0000000415/2bf0ccbd-93df-4644-8d43-38b48531c344.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed98abe6_79b5_42e5_844c_884129f9199d
ELIN-569619-2016 | EL-376249-2016 | 5/3/2016 8:17:33 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Pig-tail type lamp connection used without approved termination method. Potential of accidental contact to energized termination. This area is a low dropped ceiling in a bathroom addition. Temporary lighting connection is located 1.5 meters from from at eye height. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exposed_energized_temporary_lighting_terminations.png | file://x:/photopub/docs/0000000424/1d0e8135-38ec-49e2-9f81-6bcd8606246c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf825140_cb95_4cc2_b276_8376ca181ad7
GAIN-532302-2016 | GA-344034-2016 | 3/24/2016 8:51:41 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | The steel piping and fittings are not rated for the propane tank pressure they are connected to. This pipe or fittings could fail, causing a leak and possible fire or explosion. | 3 | Non-compliant material/fittings installed | Piping.png | file://x:/photopub/docs/0000000407/6723109a-e7df-4d82-9eae-8a4dbb1aa882.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b9c14eb2_5928_4026_aad8_abce3bd051ea
BPVOP-544001-2016 | 2267437 | 3/15/2016 3:34:19 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve on a Machine Mounted Air Receiver With MAWP of 160 psi and a MAWT of 450F . The date on the safety valve is 1990 which is way beyond the 3 year interval as per Safety Order SO-B60505303. Potential exists for a safety valve not functioning properly in a critical situation and an overpressure or explosion to occur. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SV_dated_1990.png | file://x:/photopub/docs/0000000404/6a5757fb-f8a4-4392-8733-b6860816a666.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b4f59f8_72e4_484a_ba7b_eb5711585a06
AMOP-548494-2016 | 2045474 | 3/23/2016 10:48:07 AM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | During a periodic inspection of the passenger restraint devices on the ride ( lap bars), a large crack in a structural weld on the restraint device was discovered. It appeared that the restraint device had received an impact that affected the weld. This is a hazard because the strength of the restraint device member that is designed to prevent persons from falling out of the seat has been compromised. Failure of the restraint device could result in serious injury or death and equipment damage. This hazard may not be easily identified by the maintenance program and is likely to propagate. All other restraint welds inspected. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Lap_bar_weld.png | file://x:/photopub/docs/0000000407/8fff834a-7658-4ea4-9b06-b2b8ef968c76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d28e201d_23ad_4b16_b7f1_5cba90546f2c
ELIN-556726-2016 | EL-367777-2016 | 4/11/2016 11:36:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2__rigid_was_just_flipped_around.png | file://x:/photopub/docs/0000000414/f486aa9a-f6c4-46a1-89ce-633347ea8422.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__018f2b93_a476_4ada_85b1_732eb2b44741
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shed_sub-feed_conductors_connected_to_breaker_in_main_panel.png | file://x:/photopub/docs/0000000417/bae9d9e4-d2fb-4f47-a3e5-2678aaa3a72c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Main_panel_in_house.png | file://x:/photopub/docs/0000000417/3c51708f-0f60-4481-b3af-2f4057b912e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Front_of_house_.png | file://x:/photopub/docs/0000000417/47a794a2-000b-4d76-a027-bc17f3dd0632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Incomplete_and_open_branch_circuit_wiring_in_shed.png | file://x:/photopub/docs/0000000417/c94aa941-7967-4d84-a665-fa810f4210ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shed_load_center.png | file://x:/photopub/docs/0000000417/97ea0ddd-b2f8-4eed-9427-982e91260c07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Shed_where_load_center_and_branch_circuit_wiring_is_located.png | file://x:/photopub/docs/0000000417/1c967d2d-9747-4c2a-a6ac-30234bf087e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
BPVIN-552265-2016 | UW-371441-2016 | 4/20/2016 3:08:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Boiler_3_nameplate.png | file://x:/photopub/docs/0000000418/bfce987b-2e13-4591-8ed5-e3cf54d4a58c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3757afeb_45d0_4eb8_b026_dfa96a1d97c7
BPVIN-552265-2016 | UW-371441-2016 | 4/20/2016 3:08:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Boiler_3_label.png | file://x:/photopub/docs/0000000418/25ef7e99-7f06-414f-9024-32b140a8e22c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3757afeb_45d0_4eb8_b026_dfa96a1d97c7
ELIN-548591-2016 | EL-359281-2016 | 4/20/2016 11:04:34 AM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | The 100 amp 120/240 volt panelboard is not labelled, this is an operational issue | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Panel_board.png | file://x:/photopub/docs/0000000419/cc33505e-2068-4a5c-bb64-430bebd95365.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__027c0855_316d_4f1a_8093_c60ff289af07
ELOP-384142-2015 | EL-074142-2013 | 4/20/2016 5:36:25 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | The cover plates for the 600 amp 600 volt breakers in the main electrical distribution room accessible only to qualified personnel are not secured in position and loose. This is a shock hazard | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 600_amp_breaker_covers.png | file://x:/photopub/docs/0000000419/250c1500-ba85-47ba-b432-682c4c1ac11b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df93a124_1d53_47c2_97e6_16f8c03ba4ae
GAIN-556605-2016 | GA-374338-2016 | 4/14/2016 1:21:25 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Metal_roof_overhang.png | file://x:/photopub/docs/0000000419/a65f42ba-b532-46c3-9959-692ebff867e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6e4bda1_6324_40bc_8120_19b1d5203aa4
BPVOP-558932-2016 | 3059272 | 4/12/2016 6:14:03 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Domestic hot water storage tank (2.4m long and 0.91m wide) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it is determined that temperature and pressure relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject storage tank to pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | T_AND_P_RELIEF_VALVE.png | file://x:/photopub/docs/0000000415/3246d9ae-b694-428f-9a4d-cf1c9992edb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5a28b58c_b95b_4533_bd18_922295e27c5f
BPVIN-552131-2016 | BPV-214260-2015 | 3/31/2016 1:07:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP141 | 4.0.1 Incorrect readings/alarms - Instrumentation or alarms installed contrary to manufacturer or code requirement | 2 | 2 | Upon assessment of hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) of 250*Fahrenheit, it is determined that TRIDICATOR range is below code requirement but within operating range. There is no way to detect exact anomaly in the event of excursion. | 2 | 4.0.1 Incorrect readings/alarms - Instrumentation or alarms installed contrary to manufacturer or code requirement | TRIDICATOR_WITH_RANGE_BELOW_CODE_REQUIREMENT.png | file://x:/photopub/docs/0000000410/beaa575b-3745-471b-bd2b-5802eb2dc003.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f6c2963_5edc_453c_8314_1315860334cf
AMOP-342901-2015 | 2040369 | 3/24/2016 3:05:45 PM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | The swagged eye of a guy cable utilized in providing support for the rotating structure appears in correctly installed. It is suspected that this is not manufacturer's specified equipment and there is a risk the this equipment will not withstand the forces and wear criteria of the designer. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Swagged_eye_on_right_side_suspect.png | file://x:/photopub/docs/0000000408/5f1115a2-ec85-4d3a-95b9-4dcf7bca77f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ca22fb9e_4508_49f1_b6d9_76b6ef3296f7
ELIN-557464-2016 | EL-325427-2015 | 4/15/2016 5:02:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Wiring and electrical equipment that are connected to circuit breakers are required to be complete and safe to energize. This is required so that if circuit breakers are turned on either intentionally or accidentally the energized wiring and electrical equipment does not pose a shock or fire hazard if a person or object contacts the energized parts. This installation of a load center and branch circuit wiring in a shed on a residential property has the load center sub-feeder conductors and branch circuit wiring that is connected to circuit breakers. The circuit breakers were not turned on at the time of the inspection but they were easily accessible and could have been turned on causing the 15A, 120V energized circuit conductors to be exposed. Left uncorrected this is potential shock and fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Interior_of_shed_load_center.png | file://x:/photopub/docs/0000000417/104ce4f4-0df7-4325-9aa8-f203438faf34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0000c946_78b0_4b51_a5a2_20e0eb799288
EDOP-541718-2016 | 2052393 | 3/9/2016 11:00:42 AM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | The dry wall at the top of the shaft is deteriorated due to water and could fall on top of car and or mechanic. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | Top_of_shaft.png | file://x:/photopub/docs/0000000406/cd3249b3-1833-433d-badd-cecbbd7d6d9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__305e19ad_7b71_460f_bafe_d01dbd4afa9b
BPVIN-543149-2016 | UW-360980-2016 | 3/14/2016 11:23:06 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 | Scale on the dial of pressure gauge is found to be higher than operating range but less than safety valve setting. There is no way detect how close the pressure is to safety valve setting when operating control malfunctions. | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | PRESSURE_GAUGE.png | file://x:/photopub/docs/0000000404/4fd0cf9e-cb2a-4d68-964e-92fc41a58ca0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae296bc_7c44_46c0_aa9e_7e81504f3d8c
GAIN-521278-2016 | GA-282761-2015 | 3/8/2016 4:31:19 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | 2 psi regulator mounted in enclosure and too close to the generator air intake This could create a hazard as propane is heavier than air and will accumulate in enclosure with regulator vent reliefs, and source of ignition from the generator. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | Alkali_gen.png | file://x:/photopub/docs/0000000401/c63bcfb0-5550-4349-9032-2d7d674b0b2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28c1727c_1fbb_4b78_a573_778be962caac
BPVOP-558543-2016 | BPV-094719-2014 | 4/13/2016 11:36:37 AM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | Called to site by contractor to inspect leaking area and discuss repair options. Found boiler tube(s) to be leaking significantly with only city water pressure (approximately 80 PSI). This poses a significant risk to the operation of their boiler as the leak caused water to build up on the floor of the furnace during normal operation which reduced the heat transfer abilities of the boiler in the lower section of the furnace. Contractor will attempt repair of suspect tube. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | LEAKAGE_RATE.png | file://x:/photopub/docs/0000000416/5230e1ed-3626-46ce-961d-6bc0c89f4536.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100de69e_2ed2_4264_9245_ba2c8a990b3c
BPVOP-558543-2016 | BPV-094719-2014 | 4/13/2016 11:36:37 AM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP058 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | 3 | 3 | Called to site by contractor to inspect leaking area and discuss repair options. Found boiler tube(s) to be leaking significantly with only city water pressure (approximately 80 PSI). This poses a significant risk to the operation of their boiler as the leak caused water to build up on the floor of the furnace during normal operation which reduced the heat transfer abilities of the boiler in the lower section of the furnace. Contractor will attempt repair of suspect tube. | 3 | 1.2.2 Boiler leakage: procedure - Minor boiler tube leaks. | SUSPECT_AREA.png | file://x:/photopub/docs/0000000416/03361ba5-6d65-4d19-b4c1-0fdd698a67d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__100de69e_2ed2_4264_9245_ba2c8a990b3c
ELIN-571606-2016 | EL-369208-2016 | 5/4/2016 8:34:18 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 3 | Conductor exiting outlet box does not meet minimum requirements of 150mm. This could be shock/fire hazard to persons or property if their isn't enough conductor to do a proper splice. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | Not_enough_conductor_exiting_outlet_box.png | file://x:/photopub/docs/0000000424/7742949a-6f7e-41bd-8d39-f32e8a387506.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e682bb85_de54_428b_9382_015a5298162c
ELOP-276158-2014 | 5285586 | 3/16/2016 7:37:31 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | A 250 horsepower electric motor connected at 480 volts 3 phase has been damaged as a result of a combination of vibration and strain of the weight of two large teck 90 feeder cables on motor connection box. In this location the motor is situated, dust from the operation can enter the motor winding. Additionally the motor connection conductors could abrade entering motor from the damaged connection box. This damage could result in a fire or injury to persons | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Motor_connection_box_hog_motor_250_horsepower_severely_damaged__dust_entering_motor.png | file://x:/photopub/docs/0000000404/f77b15e3-08d2-4d5c-9806-016c7627aa26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf55b299_c785_4c90_81b0_d3d9357d5680
ELIN-538061-2016 | EL-007449-2013 | 3/15/2016 9:06:49 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | A 100 amp 240 volt subfeed to a 100 amp sub panel was installed. Aluminum conductors were connected to the terminals in an older switch that was not specifically approved for termination of aluminum conductors. Aluminum conductors when connected to equipment that has not been tested and approved for aluminum can cause overheating of the conductors and or the equipment and has a potential for creating damage to property or injury to persons | 3 | General Equipment is not approved for the specific use | Amalgamated_switch_not_rated_for_aluminum.png | file://x:/photopub/docs/0000000404/e75213d8-1f13-4427-b299-0f257885b553.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4092f67f_6910_4a89_a555_2bb143b8926e
ELIN-534931-2016 | EL-289063-2015 | 3/9/2016 1:59:07 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | An electric furnace which draws 60 amps at 240 volts. The furnace has been connected to a 60 amp breaker rated for a maximum of 48 amps. The breaker may fail unpredictably and leave the heating system without power and contribute to property damage . | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 60_amp_draw_furnace_on_60_amp_breaker.png | file://x:/photopub/docs/0000000402/785d0152-e2cb-421c-bb53-6b7868a9f5e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__faa7b5f7_a1df_4037_9742_04716ebb1359
ELIN-567773-2016 | EL-069711-2013 | 5/2/2016 3:03:34 PM | ASSESS: EL: Final | png | #asFound | EL175 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | 2 | 2 | A 240 volt single phase compressor protected do by a 2P 40 amp breaker does not have a local disconnect. This a a shock hazard. | 2 | Equipment location Motor disconnect is not in sight of motor, or is not readily accessible | Compressor.png | file://x:/photopub/docs/0000000423/b959d4d8-6225-4c7b-ab7e-ad6177a1c257.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a230e6b6_b27d_41a0_adfd_0a6d14278961
ELIN-527831-2016 | EL-303786-2015 | 3/15/2016 9:27:55 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Kitchen counter receptacles in day care facilities are to be tamper resistant and accessible. In this day care a non tamper resistant counter plug was installed behind a stove so that a power bar had to be used to plug in appliances. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Behind_stov.png | file://x:/photopub/docs/0000000404/68933de7-9b0e-4b18-9e03-93ccfbab795b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__043fccc0_2956_4bba_ba10_8749c2b4ed2e
ELIN-527831-2016 | EL-303786-2015 | 3/15/2016 9:27:55 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Kitchen counter receptacles in day care facilities are to be tamper resistant and accessible. In this day care a non tamper resistant counter plug was installed behind a stove so that a power bar had to be used to plug in appliances. | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Power_bar.png | file://x:/photopub/docs/0000000404/643ab87c-5c6d-497e-9203-60ccb1e14c72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__043fccc0_2956_4bba_ba10_8749c2b4ed2e
ELIN-538825-2016 | EL-069475-2013 | 3/15/2016 11:17:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Interior gas piping must be bonded to ground. In this installation the propane system was installed after the electrician had finished the system ground and rough wire and the bond was omitted | 3 | Equipment Gas line, cast or water pipe has not been bonded | Pig.png | file://x:/photopub/docs/0000000404/6a2331f4-dd74-42c5-add9-3bd5fc5fabad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__534ba143_bba3_4ac0_ad43_3d7158c2ed9f
ELIN-542312-2016 | EL-303772-2015 | 3/15/2016 11:43:54 AM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Electrical devices must be installed in approved boxes to prevent accidental contact. In this installation a receptacle was observed energized outside the junction box in which it should have been installed. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_receptacle.png | file://x:/photopub/docs/0000000404/22e5ec28-5671-4a87-9ba1-04bbeb172153.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c30e50f_f464_44b8_b6d2_a2db9b005103
BPVOP-514884-2016 | BPV 00000056273-2013 | 3/31/2016 11:17:03 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP054 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | 2 | 2 |  | 2 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | Leak.png | file://x:/photopub/docs/0000000410/f1c8f2f3-5a85-4e38-92e3-994b273f0d38.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e9e3604_a5b2_4e7d_a42a_dadd5541f5c4
ELIN-535363-2016 | EL-345392-2016 | 3/4/2016 1:51:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Where service conductors enter consumer service equipment the equipment and raceway must be bonded to ground. This portion of the installation is normally only protected from overcurrent by the utility fusing at a transformer. In this installation the metal raceway between the meter base and main panel was not adequately bonded. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_bushing.png | file://x:/photopub/docs/0000000400/d36b5b93-cde0-449b-8e62-0c8df735c365.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32d88637_9c2e_4cb9_b0f0_f8b332c646c9
ELIN-538228-2016 | EL-345392-2016 | 3/4/2016 2:34:04 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Interior gas lines must be bonded to ground to avoid accidental energization of the metal piping system. In this installation the gas line was run after the electrician did the main service. | 3 | Equipment Gas line, cast or water pipe has not been bonded | New_gas_line.png | file://x:/photopub/docs/0000000400/502f9915-3f1e-45b6-8ebe-44fb26113add.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8e8f341_9f74_4792_8a44_3ad7f82496c2
ELIN-536513-2016 | EL-353754-2016 | 3/30/2016 10:49:20 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The 30 amp 240 volt air conditioner disconnect is missing the plug in switching device, this leaves exposed energized terminals to contact when door is open and this is a shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Air_conditioning_disconnect.png | file://x:/photopub/docs/0000000409/db3158c5-8c40-4df0-b029-faa9dacbca29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a57fa0d_b801_4ee1_a1c7_03114cb96048
ELIN-559395-2016 | UW-376207-2016 | 4/13/2016 8:16:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Hot tub feeder exposed in back yard. Breaker is not adequately locked out. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Deck.png | file://x:/photopub/docs/0000000416/25c19218-320e-46b4-af2d-5cabe34e5961.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72b18146_483a_443b_a94a_3c9eb99bc7d9
ELIN-559395-2016 | UW-376207-2016 | 4/13/2016 8:16:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Hot tub feeder exposed in back yard. Breaker is not adequately locked out. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | B.png | file://x:/photopub/docs/0000000416/1f9ff638-02c8-4966-b7ab-1749b73d7386.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72b18146_483a_443b_a94a_3c9eb99bc7d9
ELIN-559395-2016 | UW-376207-2016 | 4/13/2016 8:16:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Hot tub feeder exposed in back yard. Breaker is not adequately locked out. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000416/9f363fe2-2b7f-408c-a518-4eb4e7e3d69a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72b18146_483a_443b_a94a_3c9eb99bc7d9
ELIN-559395-2016 | UW-376207-2016 | 4/13/2016 8:16:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Hot tub feeder exposed in back yard. Breaker is not adequately locked out. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors.png | file://x:/photopub/docs/0000000416/b46d1141-ffaa-428d-85a8-a79abcb2f176.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72b18146_483a_443b_a94a_3c9eb99bc7d9
ELIN-533266-2016 | EL-325295-2015 | 2/26/2016 11:14:12 AM | ASSESS: EL: Final | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | The 15amp 120 volt switch controlling the light in the room does not protect the electrical from the wet location of the mop sink and taps, this is a shock hazard | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | Light_switch_at_mop_sink.png | file://x:/photopub/docs/0000000397/151f1d42-ce3c-4270-92fb-83579fdc4085.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a481db80_e543_4229_b6c9_ca937c62460a
ELOP-529886-2016 | 449 | 3/4/2016 2:27:47 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | On a routine operating permit site assessment at a lumber mill, a cable tray housing many feeders from 15amp to 60 amp and multiple voltages was found to be overloaded and full of debris. This can result in a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Cable_tray_overfill.png | file://x:/photopub/docs/0000000401/58f19a1e-abcf-4c50-ab2c-c4b16178226f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e69ec1c9_58f6_4ebc_90d7_7d12549066a8
BPVIN-544643-2016 | UW-367248-2016 | 3/15/2016 7:28:56 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Found a coil type Potable Water Heater with signs of leaking from the T&P valve connection. This can cause the relief valve to malfunction in case of overpressure and result in an explosion or scalding of the maintenance staff. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | T_and_P_valve_leak_trace.png | file://x:/photopub/docs/0000000404/77b96f25-9b61-463e-9b32-91594aa1269e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53a297cf_facf_442b_8432_0f7bd74e3ece
BPVIN-544643-2016 | UW-367248-2016 | 3/15/2016 7:28:56 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Found a coil type Potable Water Heater with signs of leaking from the T&P valve connection. This can cause the relief valve to malfunction in case of overpressure and result in an explosion or scalding of the maintenance staff. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | T_and_P.png | file://x:/photopub/docs/0000000404/c6297500-c729-4724-a68d-35b674ebc2fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53a297cf_facf_442b_8432_0f7bd74e3ece
ELIN-549829-2016 | EL-320990-2015 | 3/30/2016 3:21:59 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The gas and waterlines are not bonded. Accidental contact with an energized electrical line may not allow the breaker to trip and can create a shock hazard as the equipotential with the grounding system does not exist until a path is created. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Waterline.png | file://x:/photopub/docs/0000000409/a61f01a6-e0d3-472b-87bc-0113a314d29e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed9b2d42_010d_4a4f_9ec1_c54915531d80
ELIN-549829-2016 | EL-320990-2015 | 3/30/2016 3:21:59 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The gas and waterlines are not bonded. Accidental contact with an energized electrical line may not allow the breaker to trip and can create a shock hazard as the equipotential with the grounding system does not exist until a path is created. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_line.png | file://x:/photopub/docs/0000000409/08ca3561-bf6d-447a-9c66-7a5807fc4665.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed9b2d42_010d_4a4f_9ec1_c54915531d80
GAIN-541105-2016 | GA-355704-2016 | 3/14/2016 3:59:37 PM | ASSESS: GA: Final | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | Contractor has not vented appliance in accordance with manufactures installation instructions. | 3 | Power vent not installed according to installation instruction. | Power_vent_.png | file://x:/photopub/docs/0000000404/b7299b92-1105-4959-ae25-1a6fa9c98da1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8ca330d_d0ce_4838_b19b_74b368c4be4a
GAIN-541105-2016 | GA-355704-2016 | 3/14/2016 3:59:37 PM | ASSESS: GA: Final | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | Contractor has not vented appliance in accordance with manufactures installation instructions. | 3 | Power vent not installed according to installation instruction. | No_gas_shut_off_access.png | file://x:/photopub/docs/0000000404/f29d39fe-d322-46c8-936a-1960d05f74bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8ca330d_d0ce_4838_b19b_74b368c4be4a
GAIN-541105-2016 | GA-355704-2016 | 3/14/2016 3:59:37 PM | ASSESS: GA: Final | png | #asFound | GA103 | Power vent not installed according to installation instruction. | 3 | 3 | Contractor has not vented appliance in accordance with manufactures installation instructions. | 3 | Power vent not installed according to installation instruction. | Flex_gas_connector_.png | file://x:/photopub/docs/0000000404/df07cb9f-3d00-4226-9d61-4f5792ab06f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8ca330d_d0ce_4838_b19b_74b368c4be4a
ELIN-552420-2016 | EL-369838-2016 | 4/4/2016 2:40:12 PM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | A three phase subpanel had holes not covered, resulting in a possible shock hazard to employees. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Basement_7-11_panel.png | file://x:/photopub/docs/0000000412/592dd420-4ef3-46f2-98cf-6027b884875e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5ea9ac7_ebef_45d5_84dc_66e388fe1cfe
GAIN-514693-2016 | GA-337418-2016 | 3/14/2016 4:34:59 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | No_swing_joint_at_gas_meter__.png | file://x:/photopub/docs/0000000404/d9ce3c59-6bd5-426f-94a9-ee9f2eaf9714.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e76af0d_c200_44fe_b274_3efffe1fd025
ELIN-543964-2016 | EL-354211-2016 | 3/17/2016 1:04:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Gas line brass clamp found loose and with dissimilar metal action possible. When a gas line is not bonded a voltage can be induced into the gas line and when work is performed on the gas line if an arc is produced due to induction an explosion or fire could occur | 3 | Equipment Gas line, cast or water pipe has not been bonded | Brass_clamp_not_attached.png | file://x:/photopub/docs/0000000406/0c4b397e-8a20-4a73-8707-b08c147a8ab3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35cb4c84_0b74_46eb_bf67_8d54d00a2972
ELIN-537852-2016 | UW-355942-2016 | 2/29/2016 4:45:33 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | This assessment found the temporary 200A service to be in an enclosure that was not lockable nor weatherproof. There is a shock hazard that kids could access the temporary service during the construction stage. There is also an overheating hazard should the main breaker become wet and not function properly during a fault situation. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Temp_service.png | file://x:/photopub/docs/0000000400/9e519de4-7a55-41df-a0b6-93d2f7720e29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d09b104c_3b1d_48c7_ac9e_3ad248db2293
ELIN-551777-2016 | EL-364186-2016 | 4/7/2016 3:07:57 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables installed in under ground locations are required to be buried to the proper depth. This is required to prevent the cable from getting damaged. This important to protect persons from contacting the cables live conductors and to protect the cable installation from damage causing the installation to fail. This installation has an armored cable used as an underground feeder to a sub-panel and electrical equipment located in a semi trailer being used as a shop and ancillary building. Left uncorrected this is a potential shock and fire hazard if the cable becomes damaged in the future. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Semi_trailer_used_as_shop_and_horticultural_room.png | file://x:/photopub/docs/0000000414/8b86ed2c-2d8c-4840-9b8e-9970b49dd51f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68930ad6_bf6c_43fc_8773_26298e57993a
ELIN-551777-2016 | EL-364186-2016 | 4/7/2016 3:07:57 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cables installed in under ground locations are required to be buried to the proper depth. This is required to prevent the cable from getting damaged. This important to protect persons from contacting the cables live conductors and to protect the cable installation from damage causing the installation to fail. This installation has an armored cable used as an underground feeder to a sub-panel and electrical equipment located in a semi trailer being used as a shop and ancillary building. Left uncorrected this is a potential shock and fire hazard if the cable becomes damaged in the future. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_cable_buried_to_approximately_10_inch_depth_through_field.png | file://x:/photopub/docs/0000000414/2413eff8-3172-41bc-baad-a172503cc412.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__68930ad6_bf6c_43fc_8773_26298e57993a
GAIN-532982-2016 | GA-330926-2015 | 3/17/2016 10:24:14 AM | ASSESS: GA: Rough-In | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Regulator_in_crawl_space.png | file://x:/photopub/docs/0000000412/302f5200-5b1e-4726-849c-87d00006c64c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__528fbc53_ee4d_4694_9ed3_b63170f273a7
GAIN-532982-2016 | GA-330926-2015 | 3/17/2016 10:24:14 AM | ASSESS: GA: Rough-In | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | No_dirt_pocket_before_regulator__.png | file://x:/photopub/docs/0000000412/38e6b62c-755b-4f38-9942-aca57aee6007.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__528fbc53_ee4d_4694_9ed3_b63170f273a7
ELIN-545902-2016 | EL-147627-2014 | 3/21/2016 5:49:45 PM | ASSESS: EL: Service Connection | png | #asFound | EL251 | Category 1 Area classification required | 2 | 2 | Thin wall conduit is installed above grade and is not UV rated which overtime conduit is likely to crack and distort. | 2 | Category 1 Area classification required | DB2_communication.png | file://x:/photopub/docs/0000000406/ef383f14-fb2b-4561-854a-889bc2dcd575.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdd109d3_e1c6_47ed_99ce_3120ee00c8ec
ELIN-546566-2016 | EL-323580-2015 | 3/21/2016 6:30:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 | CSA c22.2 no3 has not been meet. | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | Furnace_switch.png | file://x:/photopub/docs/0000000406/bbc2c30e-ce5c-4af4-94b3-4f21ae80c8a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70a3c485_624c_44bf_901e_e65c18894af4
ELIN-561421-2016 | EL-339580-2016 | 4/19/2016 10:05:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 120 v branch circuits within edge of structural member and if damaged can create shock or fire hazard when energized. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 12-516.png | file://x:/photopub/docs/0000000418/56293530-301f-4dca-a00d-accfb508bacb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5957542c_4df3_44ce_8482_4b61892bfd9e
ELIN-507772-2016 | EL-279371-2015 | 3/11/2016 9:34:15 AM | ASSESS: EL: Final | png | #asFound | EL066 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | EL066, the panelboards are not labeled as required creating difficulties with future servicing requirements. this could create a shock hazard | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Panel_P2.png | file://x:/photopub/docs/0000000400/aef5a542-14e1-48a6-8031-199c21247316.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ec74bd3_b955_427d_a7e7_880fc0965373
ELIN-568136-2016 | UW-381448-2016 | 4/28/2016 8:54:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel installed at a park with no cover. This is a shock hazard as bare live parts could be accidentally contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000422/50e0499b-ed87-4702-86d8-a66740a2754c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cae6e8ed_85ac_47b6_bb39_225ea2a8569a
ELIN-568136-2016 | UW-381448-2016 | 4/28/2016 8:54:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel installed at a park with no cover. This is a shock hazard as bare live parts could be accidentally contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | B.png | file://x:/photopub/docs/0000000422/7bcd1f4a-e4a0-4f29-be59-5f9d18b282f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cae6e8ed_85ac_47b6_bb39_225ea2a8569a
ELIN-568136-2016 | UW-381448-2016 | 4/28/2016 8:54:35 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Panel installed at a park with no cover. This is a shock hazard as bare live parts could be accidentally contacted. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | C.png | file://x:/photopub/docs/0000000422/ce9e8ede-7c45-4f47-884e-29aa41870042.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cae6e8ed_85ac_47b6_bb39_225ea2a8569a
ELIN-536664-2016 | EL-341129-2016 | 3/4/2016 12:54:28 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed in locations where they are protected from mechanical damage or in locations where they are unlikely to be damaged. This is because the cable jacket and conductor insulation can be damaged more easily that other types of armored cables or conduits. The electrical installation at this house has two (NMSC) that are in contact with moving garage door operator hardware. The cables are subject to a rotating rod that is contacting the cables and may damage the cable sheath and conductor insulation. Left uncorrected this is a potential shock and fire hazard should the energized conductors contact the metal parts of the door opener and operating hardware. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_contact_with_moving_garage_door_operator_bar.png | file://x:/photopub/docs/0000000401/0b1b97e9-c025-483e-9a11-86a9bc8d5a47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6292574_dd8c_44a2_8638_5c47dcb86b94
ELIN-536664-2016 | EL-341129-2016 | 3/4/2016 12:54:28 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed in locations where they are protected from mechanical damage or in locations where they are unlikely to be damaged. This is because the cable jacket and conductor insulation can be damaged more easily that other types of armored cables or conduits. The electrical installation at this house has two (NMSC) that are in contact with moving garage door operator hardware. The cables are subject to a rotating rod that is contacting the cables and may damage the cable sheath and conductor insulation. Left uncorrected this is a potential shock and fire hazard should the energized conductors contact the metal parts of the door opener and operating hardware. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_contact_with_moving_garage_door_operator_bar_.png | file://x:/photopub/docs/0000000401/dc105e29-0ace-4ac5-ad15-782c5077a054.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6292574_dd8c_44a2_8638_5c47dcb86b94
ELIN-536664-2016 | EL-341129-2016 | 3/4/2016 12:54:28 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed in locations where they are protected from mechanical damage or in locations where they are unlikely to be damaged. This is because the cable jacket and conductor insulation can be damaged more easily that other types of armored cables or conduits. The electrical installation at this house has two (NMSC) that are in contact with moving garage door operator hardware. The cables are subject to a rotating rod that is contacting the cables and may damage the cable sheath and conductor insulation. Left uncorrected this is a potential shock and fire hazard should the energized conductors contact the metal parts of the door opener and operating hardware. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_contact_with_moving_door_operator_rod_.png | file://x:/photopub/docs/0000000401/979f2fab-89d8-4215-ad7d-a23ce631d331.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6292574_dd8c_44a2_8638_5c47dcb86b94
ELIN-536664-2016 | EL-341129-2016 | 3/4/2016 12:54:28 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed in locations where they are protected from mechanical damage or in locations where they are unlikely to be damaged. This is because the cable jacket and conductor insulation can be damaged more easily that other types of armored cables or conduits. The electrical installation at this house has two (NMSC) that are in contact with moving garage door operator hardware. The cables are subject to a rotating rod that is contacting the cables and may damage the cable sheath and conductor insulation. Left uncorrected this is a potential shock and fire hazard should the energized conductors contact the metal parts of the door opener and operating hardware. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Front_of_house.png | file://x:/photopub/docs/0000000401/e3b55426-3b20-4b05-bb66-5197db91005c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6292574_dd8c_44a2_8638_5c47dcb86b94
ELIN-552213-2016 | EL-297385-2015 | 4/8/2016 6:43:02 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Cover not installed on junction box accessible to general public, presenting the risk of accidental contact with unguarded branch circuit conductors leading to personal injury (shock) or property damage (thermal event). | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | View01_outlet.png | file://x:/photopub/docs/0000000414/fa6e43ff-1403-4979-8c3d-b2e40bd973f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa2a1a84_3a50_4401_b87f_dae2e269aaed
ELIN-554798-2016 | EL-330971-2016 | 4/8/2016 5:52:04 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The main service disconnect enclosure is not adequately secured to the service pole using properly rated fasteners, resulting in unsealed openings on rear of enclosure. This allows for the ingress of insects into the service disconnect enclosure and the failure of the fasteners due to corrosive reaction the the environment. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_rear_of_enclosure.png | file://x:/photopub/docs/0000000414/a17ec543-a9f4-4380-8352-0abd63239c03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b230b34_81e6_4693_a930_81887bc693bc
ELIN-537624-2016 | EL-337843-2016 | 3/7/2016 3:50:31 PM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A single family dwelling has had the service upgraded to 100 amps 240 volt single phase from 60 amps single phase. Existing wiring and branch circuits were not checked for safety during the work done. Flexible cord was open spliced to non metallic sheathed cable and run at chest height to an adjacent tree, and then to an outbuilding with permanent wiring. The flexible cord was cord cap connected to,the outside receptacle found without a cover plate. Flexible cord can fail when used for fixed wiring of structures and be a potential for injury to persons or potential fire to building or as in this case to forest interface. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_spliced_to_nmd_90_run_through_trees_to_shed.png | file://x:/photopub/docs/0000000401/c8cd2392-a177-4fe8-8483-4b14823dd109.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e6645dc_f13e_4d4e_a5a6_c744fd7ca39c
ELIN-538774-2016 | EL-355700-2016 | 3/7/2016 12:31:58 PM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | A 240 volt 100 amp service panel rated for copper only has been fed with aluminum. Aluminum can overheat conductor terminations or the electrical equipment and cause property damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Not_approved_for_aluminum.png | file://x:/photopub/docs/0000000401/33704102-b464-44a9-bb9f-5c418ca69842.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d34e25d1_391c_4354_be06_f16b354a61c6
ELIN-540200-2016 | EL-356980-2016 | 3/14/2016 7:49:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | A 100 amp, 120/240 volt, sub-distribution # 4 Aluminum neutral support cable does not have required clearances and is subject to mechanical damage. This could lead to equipment damage and is a thermal hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | O_H_conductors.png | file://x:/photopub/docs/0000000404/9341eff7-b358-401c-b56d-94cf0e7996c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa2614d4_b01d_442a_b621_237bc927a47a
ELIN-565282-2016 | EL-253575-2015 | 5/2/2016 12:11:04 PM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | 600/347 volt 200 amp fused disconnect has the main ground terminated at the equipment enclosure not the neutral assembly. This could cause equipment damage or be a shock hazard should a fault occur. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_at_main_disconnect.png | file://x:/photopub/docs/0000000423/8bcb747c-3f18-4fa3-8dd2-2f221fcfd81b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2b5cc85_0bcc_4720_b080_52002d0720bb
ELIN-547928-2016 | EL-355095-2016 | 3/23/2016 4:43:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | #6 stranded bond conductor wrapped around light pole stud. Stranded conductors larger than #10 awg are required to terminate in a lug or approved compression fitting. All strands of bonding conductor may not be in contact with metal enclosures when installed in this manner. If a fault were to occur ,over current equipment may not operate as required resulting in a potential shock or damage to persons or equipment. | 3 | Continuity Bonding; method for equipment is not adequate. | 6awg_stranded_conductor_wrapped_around_light_pole_stud.png | file://x:/photopub/docs/0000000407/cffcc307-e3c7-4524-a86e-07d1a5277618.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ced7688_2d14_4912_aa12_c799f027e211
ELIN-569123-2016 | EL-274885-2015 | 5/3/2016 11:29:51 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 15A 120V outlet has been installed next to a sink in the laundry room, the outlet is within 1.5m of the sink and not GFCI protected, this could result in a shock hazard to persons using the outlet. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Laundry_outlet.png | file://x:/photopub/docs/0000000424/d30a0f49-0b9b-417f-b189-0608d5bc9fa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30f5616a_37ad_42e4_ace2_b82915c8807c
ELIN-546228-2016 | EL-304810-2015 | 3/21/2016 2:39:06 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | In day care facilities receptacles must be tamper resistant and they must be marked as such. In this new day care there was not one tamper resistant receptacle installed. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | General_purpose.png | file://x:/photopub/docs/0000000406/1578235a-f899-4f02-8903-55feba7be060.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b65f0e7a_499d_43ab_948b_00e4edf4684f
ELIN-546332-2016 | EL-360456-2016 | 3/18/2016 3:59:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Service conductors installed subject to damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | ACWU1.png | file://x:/photopub/docs/0000000405/1f8c5b0e-1a57-44cb-90d6-0e114f45bfa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63c2185a_d98f_4c22_bf5b_8cda9db80177
ELIN-546332-2016 | EL-360456-2016 | 3/18/2016 3:59:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Service conductors installed subject to damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | ACWU2.png | file://x:/photopub/docs/0000000405/c767f465-10f4-4f3d-ba69-5b48e7f20009.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63c2185a_d98f_4c22_bf5b_8cda9db80177
ELIN-546332-2016 | EL-360456-2016 | 3/18/2016 3:59:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Service conductors installed subject to damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | ACWU3.png | file://x:/photopub/docs/0000000405/0ea0529d-b44f-4a94-b809-3857ea77f4dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63c2185a_d98f_4c22_bf5b_8cda9db80177
ELIN-546332-2016 | EL-360456-2016 | 3/18/2016 3:59:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Service conductors installed subject to damage | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Acwu4.png | file://x:/photopub/docs/0000000405/6ef1f5bb-40ec-4282-b632-ec22bb650fa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63c2185a_d98f_4c22_bf5b_8cda9db80177
ELIN-536089-2016 | EL-338026-2016 | 3/14/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service and its distribution is not grounded and is not bonded at all. The bonding conductors are terminated onto neutral bar and bonding lug is very loose with use of wood screws screwed onto bonding lug. When a service and its distribution system is not grounded and is not bonded fully as required by code, the system is a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 6.png | file://x:/photopub/docs/0000000406/33431d19-69e1-45c6-9efc-96d2b3e88f56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d703b697_a2ff_4218_83b6_7f4cc051c460
ELIN-536089-2016 | EL-338026-2016 | 3/14/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service and its distribution is not grounded and is not bonded at all. The bonding conductors are terminated onto neutral bar and bonding lug is very loose with use of wood screws screwed onto bonding lug. When a service and its distribution system is not grounded and is not bonded fully as required by code, the system is a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 5.png | file://x:/photopub/docs/0000000406/bb177913-ef2d-4f35-8b48-8b21054b837c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d703b697_a2ff_4218_83b6_7f4cc051c460
ELIN-536089-2016 | EL-338026-2016 | 3/14/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service and its distribution is not grounded and is not bonded at all. The bonding conductors are terminated onto neutral bar and bonding lug is very loose with use of wood screws screwed onto bonding lug. When a service and its distribution system is not grounded and is not bonded fully as required by code, the system is a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 1.png | file://x:/photopub/docs/0000000406/ab7383b2-ac3c-44cd-b3c0-ecbbb7d5278d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d703b697_a2ff_4218_83b6_7f4cc051c460
ELIN-536089-2016 | EL-338026-2016 | 3/14/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service and its distribution is not grounded and is not bonded at all. The bonding conductors are terminated onto neutral bar and bonding lug is very loose with use of wood screws screwed onto bonding lug. When a service and its distribution system is not grounded and is not bonded fully as required by code, the system is a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 2.png | file://x:/photopub/docs/0000000406/47497854-07b6-4aa6-8f8d-64c44be54667.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d703b697_a2ff_4218_83b6_7f4cc051c460
ELIN-536089-2016 | EL-338026-2016 | 3/14/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service and its distribution is not grounded and is not bonded at all. The bonding conductors are terminated onto neutral bar and bonding lug is very loose with use of wood screws screwed onto bonding lug. When a service and its distribution system is not grounded and is not bonded fully as required by code, the system is a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4.png | file://x:/photopub/docs/0000000406/5f73ccdc-4801-46db-b353-c87c829e1b47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d703b697_a2ff_4218_83b6_7f4cc051c460
ELIN-542530-2016 | EL-360340-2016 | 3/14/2016 9:44:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized exposed busbars and energized conductors inside main panelboard that were missing all cover plates and covers and contractor had installed paper cardboard as a temporary cover to prevent fire or shock hazards. When approved metal covers are not installed on approved panel boards as per the approved use of electrical equipment, the entire electrical system is an electrical fire or shock hazard to people and property and is unapproved use of electrical equipment. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | These_are_the_covers_that_were_not_installed_on_energized_exposed_conductors_and_bus_bars.png | file://x:/photopub/docs/0000000406/183cd87e-0462-4789-9c1e-49c505d1879e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ed5f1b7_115c_4ad2_a04d_a50455b1c12c
ELIN-536089-2016 | EL-338026-2016 | 3/14/2016 10:43:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service and its distribution is not grounded and is not bonded at all. The bonding conductors are terminated onto neutral bar and bonding lug is very loose with use of wood screws screwed onto bonding lug. When a service and its distribution system is not grounded and is not bonded fully as required by code, the system is a possible electrical fire or shock hazard to people and property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 3.png | file://x:/photopub/docs/0000000406/cace5260-da8a-4a25-8384-59c726fa3b31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d703b697_a2ff_4218_83b6_7f4cc051c460
ELIN-542530-2016 | EL-360340-2016 | 3/14/2016 9:44:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized exposed busbars and energized conductors inside main panelboard that were missing all cover plates and covers and contractor had installed paper cardboard as a temporary cover to prevent fire or shock hazards. When approved metal covers are not installed on approved panel boards as per the approved use of electrical equipment, the entire electrical system is an electrical fire or shock hazard to people and property and is unapproved use of electrical equipment. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | This_is_the_energized_exposed_busbars_and_conductors_that_were_covered_with_paper_cardboard_and_missing_covers.png | file://x:/photopub/docs/0000000406/156b1f61-2719-4b3f-aa66-115f72b11841.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ed5f1b7_115c_4ad2_a04d_a50455b1c12c
ELIN-542530-2016 | EL-360340-2016 | 3/14/2016 9:44:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized exposed busbars and energized conductors inside main panelboard that were missing all cover plates and covers and contractor had installed paper cardboard as a temporary cover to prevent fire or shock hazards. When approved metal covers are not installed on approved panel boards as per the approved use of electrical equipment, the entire electrical system is an electrical fire or shock hazard to people and property and is unapproved use of electrical equipment. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | This_is_paper_cardboard_used_to_cover_energized_exposed_panel_busbars_and_conductors_which_is_not_approved_for_the_use_.png | file://x:/photopub/docs/0000000406/1a6961e6-629f-4556-8ab1-75b150281037.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ed5f1b7_115c_4ad2_a04d_a50455b1c12c
BPVOP-533582-2016 | 2292743 | 2/25/2016 3:42:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Allowable Working Pressure (AWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 240*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_room_without_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000396/eb20f8e1-69ba-4ac1-b4b3-44a5c3f5463f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__331a316c_d6c2_4faa_837a_432908b28ac8
BPVIN-533616-2016 | UW-119328-2014 | 2/25/2016 4:53:49 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | Upon assessment of heat exchanger (2m long and 0.8m wide) with Maximum Allowable Working Pressure (MAWP) of 50psig and Maximum Allowable Water Temperature (MAWT) of 275*Fahrenheit, is determined that there is no pressure relief device installed on the side receiving heat. Inadvertent operation of heat exchanger with secondary side (side receiving heat) valves shut may subject vessel to pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot waste and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Heat_exchaner.png | file://x:/photopub/docs/0000000396/15c8c9b0-8b02-4371-bac6-b643630474b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1326d0e9_7598_4355_b6cb_c0b52ed0334f
ELOP-549568-2016 | EL-259778-2015 | 3/30/2016 4:01:02 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Doors have been left open for the frequency drives located in the electrical room. This is hazardous if there is access to individuals who are not authorized to be in the electrical room. A risk of shock and damage to persons or property exists if accidentally contacted. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Exposed_connections_are_in_boxes_with_doors_and_located_in_electrical_room_.png | file://x:/photopub/docs/0000000409/0f95b30e-b51c-4edc-8a91-a3b0e85b525c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57854cfe_3639_4ac8_ade8_87bf773cafd7
BPVOP-574311-2016 | BPV-0000208558-2015 | 5/10/2016 11:38:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found water droplets at the end of the discharge pipe on a 50 psi hot water boiler. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Safety_valve_data_.png | file://x:/photopub/docs/0000000428/b8214822-1899-4eba-bc71-71939873b3a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29faaf52_aa78_4447_9f86_9896b3e33b9d
BPVOP-574311-2016 | BPV-0000208558-2015 | 5/10/2016 11:38:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found water droplets at the end of the discharge pipe on a 50 psi hot water boiler. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leakage_from_safety_valve_.png | file://x:/photopub/docs/0000000428/b6bab662-8309-4c43-8729-c6b8379d6690.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29faaf52_aa78_4447_9f86_9896b3e33b9d
ELOP-226633-2014 | 5304 | 2/24/2016 4:09:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not to be used as a substitute for permanent wiring. In this installation, a primary school, extensive use of cords was found in areas where computers and projectors are used. | 4 | Conductors, Misuse of flexible cords. | Flex_cord_1.png | file://x:/photopub/docs/0000000395/03df4608-5461-4b34-a3a0-d5add188e310.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8488054f_859a_4b00_bab1_d80bdc98516a
ELOP-226633-2014 | 5304 | 2/24/2016 4:09:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not to be used as a substitute for permanent wiring. In this installation, a primary school, extensive use of cords was found in areas where computers and projectors are used. | 4 | Conductors, Misuse of flexible cords. | Flex_cord_3.png | file://x:/photopub/docs/0000000395/2e7d19b5-14a5-45a4-8615-a99684cbbd80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8488054f_859a_4b00_bab1_d80bdc98516a
ELOP-226633-2014 | 5304 | 2/24/2016 4:09:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not to be used as a substitute for permanent wiring. In this installation, a primary school, extensive use of cords was found in areas where computers and projectors are used. | 4 | Conductors, Misuse of flexible cords. | Flex_cord_4.png | file://x:/photopub/docs/0000000395/a70cfcaa-8a00-42c8-95fc-b2b4afdedcfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8488054f_859a_4b00_bab1_d80bdc98516a
BPVOP-526585-2016 | 2250765 | 2/25/2016 1:03:07 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Corrosion__.png | file://x:/photopub/docs/0000000396/7a021009-c330-4b64-a38a-5ca618d34e45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08a1d8a8_c8c5_4574_8979_9ecd1c69baa4
ELIN-556060-2016 | EL-332407-2016 | 4/11/2016 3:11:32 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Exposed energized terminals | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_power.png | file://x:/photopub/docs/0000000415/83ed11e6-38a5-4993-8efd-d3611a504a14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47923f4e_ca3f_412b_886c_9a830518dffd
ELIN-533159-2016 | EL-349753-2016 | 2/25/2016 8:55:01 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The installation of the 200 amp 120/240 volt service does not adequately protect the distribution equipment from weather conditions. This is both a shock and equipment damage hazard | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service.png | file://x:/photopub/docs/0000000396/04f5937e-976c-444f-959c-3e88bebadaf5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__213cf693_95e8_4d09_a46e_52bc2397cfdb
ELIN-536296-2016 | EL-347585-2016 | 3/3/2016 9:28:46 AM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Armoured cable is not properly terminated in fluorescent fixtures. The branch circuit is 120 volts, protected by a 15 amp overcurrent device. This is a thermal hazard and it could cause equipment damage. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | AC_anti_shorts_not_installed.png | file://x:/photopub/docs/0000000399/b8847291-31eb-4355-969a-9c0b40d7a489.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02cf151d_a851_44ea_b068_cd07b41f899a
ELIN-534810-2016 | EL-292135-2015 | 3/3/2016 11:55:34 AM | ASSESS: EL: Final | png | #asFound | EL169 | Protection and control Disconnect is not of proper type or rating. | 3 | 3 | A gas furnace does not have a local disconnect switch installed. The 120 volt branch circuit is non-metallic sheathed cable - 14 awg protected by a 15 amp overcurrent device. Not having a local disconnect switch for the furnace is a safety issue, and could result in equipment damage. | 3 | Protection and control Disconnect is not of proper type or rating. | Furnace_without_disconnect.png | file://x:/photopub/docs/0000000399/2d4a5e5f-adae-4ab4-822f-f261805f4561.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62e6faf3_26ff_4169_915a_13dbe541fba1
BPVOP-569492-2016 | 3433492 | 5/2/2016 12:38:31 PM | ASSESS: BPV OP: Repair Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Contractor suspects that the tube wasn't properly seal welded on installation and opened up over time. No cracks were observed. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | REPAIRED_TUBE.png | file://x:/photopub/docs/0000000424/ede7aa99-d0f3-4477-874a-90c983a5b64a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f61d787_69fa_41ad_8edf_1a5b6734f6c5
ELOP-226633-2014 | 5304 | 2/24/2016 4:09:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not to be used as a substitute for permanent wiring. In this installation, a primary school, extensive use of cords was found in areas where computers and projectors are used. | 4 | Conductors, Misuse of flexible cords. | Flex_cord_2.png | file://x:/photopub/docs/0000000395/40fc8ff4-6d3c-492f-b3b5-4ff19c1c8943.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8488054f_859a_4b00_bab1_d80bdc98516a
ELIN-561360-2016 | EL-275892-2015 | 4/12/2016 9:07:58 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Existing 200 amp service panel-board does not have cover installed which has exposed the energized buss to workers and owner. There is also open splicing of wiring that is not terminated in a safe manner, which may lead to accidental contact of energized conductors. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_panelboard.png | file://x:/photopub/docs/0000000423/ea810abd-25cb-4921-b616-8ae076b3e7d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ffe19e3_24fc_48bf_aac1_d09b9620cd15
ELIN-561360-2016 | EL-275892-2015 | 4/12/2016 9:07:58 AM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Existing 200 amp service panel-board does not have cover installed which has exposed the energized buss to workers and owner. There is also open splicing of wiring that is not terminated in a safe manner, which may lead to accidental contact of energized conductors. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_splicing_of_back_feed_to_new_panel.png | file://x:/photopub/docs/0000000423/4358346c-ae30-4821-b16b-61c5ae07776c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ffe19e3_24fc_48bf_aac1_d09b9620cd15
ELIN-558444-2016 | EL-320911-2015 | 4/13/2016 12:18:28 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | 200Amp 120/240V 1Ph, combination panel for temporary construction. Panel is mounted on 2x4 construction without support over 2meters and is not weatherproof. Potential for panel to be knocked over and shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_mounted_too_high.png | file://x:/photopub/docs/0000000416/a524afc0-5c3d-48ac-aadb-39f68d1409dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6dfbd53_0eab_4354_a6cf_8d7109b0da91
ELIN-567580-2016 | EL-346984-2016 | 5/9/2016 10:13:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt overhead meter base is installed on a plywood backing. Plywood backing is screwed to approved pole. Over time plywood backing may rot leaving the meter base subject to equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Meter_installed_on_plywood.png | file://x:/photopub/docs/0000000427/9a0f4425-620f-4b97-af0c-b6bf36f8ceac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9525dc0_1822_4558_905a_79de5860d8bf
EDIN-535818-2016 | ED-121791-2014 | 2/25/2016 12:21:21 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | Moody_Station2.png | file://x:/photopub/docs/0000000398/d50d8519-6b98-45a1-93b6-30ba174b9f0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd45926a_24dc_4149_818c_521dfe8b7d9d
BPVIN-545567-2016 | UW-367788-2016 | 4/11/2016 4:44:25 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment it is determined that relief valve discharge is not installed 4.5m above accessible roof level. Refrigerant in the system is heavier than air. Refrigerant concentration may cause oxygen deficiency in the vicinity and lead to asphyxiation of personnel if relief valve pops or leaks. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | RELIEF_VALVE_DISCHARGE.png | file://x:/photopub/docs/0000000415/9542b30e-e1f6-43f8-89d6-6d45f44d69f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__413b42ee_6f9d_450f_bf51_6ba87fc99572
BPVIN-557727-2016 | UW-374923-2016 | 4/11/2016 5:31:12 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | Upon assessment of heat exchanger (0.61m long and 0.36m wide) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 257*Fahrenheit, is determined that there is no pressure relief device installed on the side receiving heat. Inadvertent operation of heat exchanger with secondary side (side receiving heat) valves shut may subject vessel pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | HEAT_EXCHANGER_3_WITHOUT_RELIEF_VALVE_ON_SECONDARY_SIDE.png | file://x:/photopub/docs/0000000415/75e20f31-60d0-4932-a374-20a7506808fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ec7b0bf_3f99_4cfd_9cb6_5a6db3b0c5ce
BPVIN-545595-2016 | UW-367829-2016 | 4/11/2016 5:18:50 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Upon assessment it is determined that relief valve discharge is not installed 4.5m above accessible roof level. Refrigerant in the system is heavier than air. Refrigerant concentration may cause oxygen deficiency in the vicinity and lead to asphyxiation of personnel if relief valve pops or leaks. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Pressure_relief_valve_discharge.png | file://x:/photopub/docs/0000000415/7f3a4b5d-4b4a-4d6e-90c3-39cbb79fae41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__429a47df_edd5_4151_83e3_4e0bbe403e2e
ELIN-553655-2016 | EL-371645-2016 | 4/12/2016 6:19:12 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | The minimum conductor ampacity indicated on the nameplate has not been followed and a smaller conductor installed, this could result in equipment and cable damage. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | NMD.png | file://x:/photopub/docs/0000000415/ee8dc8c6-6881-4016-9fe3-2a9931e33292.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c6d9e52_5227_4a07_b0e1_cdcc035d28cd
ELIN-553655-2016 | EL-371645-2016 | 4/12/2016 6:19:12 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | The minimum conductor ampacity indicated on the nameplate has not been followed and a smaller conductor installed, this could result in equipment and cable damage. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Nameplate.png | file://x:/photopub/docs/0000000415/31b25c45-f164-4fef-9806-a828d483f22c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c6d9e52_5227_4a07_b0e1_cdcc035d28cd
ELIN-553648-2016 | EL-371642-2016 | 4/12/2016 7:36:23 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | The minimum size conductor ampacity recommended by the manufacturer has not be provided, this could result in equipment and cable damage. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 2_NMD.png | file://x:/photopub/docs/0000000415/c4406f23-5b99-4475-959f-eed505b7bcb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddb54ec8_c164_403f_97e5_82b1ea3f7132
ELIN-553648-2016 | EL-371642-2016 | 4/12/2016 7:36:23 PM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | The minimum size conductor ampacity recommended by the manufacturer has not be provided, this could result in equipment and cable damage. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Furnace_nameplate.png | file://x:/photopub/docs/0000000415/4715f2ba-d90c-4c8d-8597-789908eab4c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ddb54ec8_c164_403f_97e5_82b1ea3f7132
BPVOP-558935-2016 | 3059253 | 4/12/2016 6:50:34 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that machine mounted horizontal air receiver (0.58m long and .31m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 150psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressure boundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000415/73626242-8e14-4e64-9622-b7d80e167cdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5a0e94b_9c76_4e1b_b1f7_30d37e0aa5f7
ELIN-537868-2016 | EL-350093-2016 | 3/4/2016 8:38:19 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Where temporary power is provided at construction sites general purpose receptacles must be GFCI-equipped to protect personnel against electric shock. In this installation GFCI receptacles had been removed and placed with standard receptacles. The construction site is a floating barge with as much as 2" of water on the construction floor. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | No_GFCI.png | file://x:/photopub/docs/0000000400/6dfa16cb-1afc-49ea-9ac4-43ef3bdfaf59.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fe297cc_42b6_4274_9ff1_4ff04215bc12
ELIN-551942-2016 | EL-150236-2014 | 4/4/2016 8:04:50 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 4 | The 15 amp 120 volt wiring installation of the NMSC into the lighting boxes directly mounted on wood backing do not include the required connectors, this can create a thermal hazard | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Typical_lighting_box.png | file://x:/photopub/docs/0000000411/658fd996-198c-4bd9-9f0d-fe8e8d2b391f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6ab9db6_5928_458f_8e9f_95ace245d412
ELIN-567421-2016 | UW-380992-2016 | 4/27/2016 9:58:24 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | A 15 amp / 120 volt receptacle that was being used for demolition purposes was left hanging outside of the box exposing the energized terminals. This condition exposed occupants to a potential shock and fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 2890Islehwy.png | file://x:/photopub/docs/0000000422/fb1d2732-0e4d-49a6-9995-1f9acd001eaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5bfa8d8_99ef_456c_81e8_26ad13b1a1ec
ELIN-567421-2016 | UW-380992-2016 | 4/27/2016 9:58:24 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | A 15 amp / 120 volt receptacle that was being used for demolition purposes was left hanging outside of the box exposing the energized terminals. This condition exposed occupants to a potential shock and fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 2890pic2.png | file://x:/photopub/docs/0000000422/35d44c28-4e9f-481b-8180-a6d65a040db0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5bfa8d8_99ef_456c_81e8_26ad13b1a1ec
ELIN-571326-2016 | EL-370586-2016 | 5/3/2016 12:47:37 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Energized240 v/100a temporary cable and distribution for commercial site not protected from mechanical or accidental contact; contact may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel.png | file://x:/photopub/docs/0000000424/91d7ed28-fda7-406f-a023-af55f3ba41d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01ac258c_0a10_4e04_b298_5e9592a1ddb7
ELIN-571326-2016 | EL-370586-2016 | 5/3/2016 12:47:37 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Energized240 v/100a temporary cable and distribution for commercial site not protected from mechanical or accidental contact; contact may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel_2.png | file://x:/photopub/docs/0000000424/3660a57f-f5d9-4d53-9b7a-adcd4117212a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01ac258c_0a10_4e04_b298_5e9592a1ddb7
ELIN-571326-2016 | EL-370586-2016 | 5/3/2016 12:47:37 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Energized240 v/100a temporary cable and distribution for commercial site not protected from mechanical or accidental contact; contact may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel_sub.png | file://x:/photopub/docs/0000000424/762ed409-3fa7-41d8-a159-51f35234ba26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01ac258c_0a10_4e04_b298_5e9592a1ddb7
ELIN-571326-2016 | EL-370586-2016 | 5/3/2016 12:47:37 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Energized240 v/100a temporary cable and distribution for commercial site not protected from mechanical or accidental contact; contact may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Temp.png | file://x:/photopub/docs/0000000424/ef3a21af-bb17-491c-9d4d-b0e0f16884cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01ac258c_0a10_4e04_b298_5e9592a1ddb7
ELIN-571326-2016 | EL-370586-2016 | 5/3/2016 12:47:37 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Energized240 v/100a temporary cable and distribution for commercial site not protected from mechanical or accidental contact; contact may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel4.png | file://x:/photopub/docs/0000000424/25d811c9-f362-497e-bcde-6adb7d1923d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01ac258c_0a10_4e04_b298_5e9592a1ddb7
ELIN-571326-2016 | EL-370586-2016 | 5/3/2016 12:47:37 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | Energized240 v/100a temporary cable and distribution for commercial site not protected from mechanical or accidental contact; contact may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel3.png | file://x:/photopub/docs/0000000424/5d3ae9c8-dc0e-479f-94d2-e17836a30c94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01ac258c_0a10_4e04_b298_5e9592a1ddb7
ELIN-570746-2016 | EL-241987-2015 | 5/3/2016 12:58:22 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 240 volt temporary distribution cable not protected from mechanical damage which may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel-2.png | file://x:/photopub/docs/0000000424/c6ca8e5b-c709-4943-aafc-2fcca446eaf2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1669e5d0_3890_412d_9e10_a0c17e850969
ELIN-570746-2016 | EL-241987-2015 | 5/3/2016 12:58:22 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 240 volt temporary distribution cable not protected from mechanical damage which may lead to shock or fire hazard. | 3 | General Equipment is not approved for the specific use | Motel_1.png | file://x:/photopub/docs/0000000424/1ad78227-6a13-42a5-88c6-444872ec83c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1669e5d0_3890_412d_9e10_a0c17e850969
ELIN-556254-2016 | EL-169037-2014 | 4/20/2016 4:41:31 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | 20A 240V armoured cable feed to the well equipment has not be terminated with a proper cable fitting, this could result in damage to the cable and equipment. | 0 | No Created Hazard Identified | Well_teck.png | file://x:/photopub/docs/0000000418/e4953145-53df-4856-a387-184bb8897295.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b4305b90_375c_4b83_b4eb_e78ca6f6e0bc
ELIN-536454-2016 | UW-355274-2016 | 3/2/2016 6:54:31 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Electrical service equipment must be adequately attached to the structure it serves to avoid damage to the service conductors and accidental contact to either persons or property. In this installation a vertical timber supporting the service had deteriorated due to environmental conditions and was no longer providing that attachment point. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Mast_roped_to_structural_member.png | file://x:/photopub/docs/0000000398/0e9cae98-19c4-4364-a72a-7475acefb200.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e8f9aee_0356_4f5d_b94b_ca287157ee39
EDIN-535818-2016 | ED-121791-2014 | 2/25/2016 12:21:21 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | Moody_Station1.png | file://x:/photopub/docs/0000000398/1fcbd5e7-12a8-4b97-aad9-0ab09ecbbc22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cd45926a_24dc_4149_818c_521dfe8b7d9d
EDIN-535811-2016 | ED-121921-2014 | 2/25/2016 12:58:13 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0003.png | file://x:/photopub/docs/0000000398/e208ba64-98a9-4e1c-bf59-e48cab67ea41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7df066b7_3427_4b58_9547_4f6d8c34b385
EDIN-535811-2016 | ED-121921-2014 | 2/25/2016 12:58:13 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0002.png | file://x:/photopub/docs/0000000398/aa7dc866-a564-417e-b03e-424eb2ab23d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7df066b7_3427_4b58_9547_4f6d8c34b385
EDIN-535808-2016 | ED-121923-2014 | 2/25/2016 1:07:26 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0004.png | file://x:/photopub/docs/0000000398/b6588955-6e0f-42e4-a7f4-57efaaa3ed30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64429c9f_a1a2_43ac_9635_c782619465cc
EDIN-535808-2016 | ED-121923-2014 | 2/25/2016 1:07:26 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0005.png | file://x:/photopub/docs/0000000398/b401515a-c5c7-48f2-8d16-0300e50bdea4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64429c9f_a1a2_43ac_9635_c782619465cc
EDIN-535804-2016 | ED-121925-2014 | 2/26/2016 1:14:10 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0006.png | file://x:/photopub/docs/0000000398/a9ada293-9cca-4adc-8fe6-5447b143b670.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__600dd419_263e_4758_af6c_c206c250b7ad
EDIN-535804-2016 | ED-121925-2014 | 2/26/2016 1:14:10 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0007.png | file://x:/photopub/docs/0000000398/bbbb6843-24f7-4a98-9af1-dded3ce1ed9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__600dd419_263e_4758_af6c_c206c250b7ad
EDIN-535799-2016 | ED-121929-2014 | 2/26/2016 1:26:02 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0008.png | file://x:/photopub/docs/0000000398/f2e3abaa-08ad-482c-bbe2-4ded47f83402.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5796b9e1_f2ee_4881_b1c8_845ea6e338e2
EDIN-535799-2016 | ED-121929-2014 | 2/26/2016 1:26:02 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED018 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 3 | 3 | Escalators that are subject to outdoor conditions, such as temperature, moisture, etc, must be provided with outdoor protection. Outdoor protection requires heating of the deck plates and stair treads to prevent ice from forming on these surfaces when subject to cold temperatures or conditions. The operating range (temperature) must also be maintained to ensure all electrical and mechanical equipment (Electrical wiring, circuit boards, switches, brakes, drives, etc.) function properly to manufacturer specifications. During an inspection, it was found that while outdoor conditions were present, no outdoor protection was provided. The escalator was under construction and not in operation to the public at this time. Pictures are attached. | 3 | Oil/Water/Other Debris that: Is not affecting components or operation but is likely to progress | 0009.png | file://x:/photopub/docs/0000000398/958fe455-c9ca-4249-896f-60bf4a842388.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5796b9e1_f2ee_4881_b1c8_845ea6e338e2
ELIN-554690-2016 | EL-372520-2016 | 4/12/2016 12:13:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A new service 100 amps 240 volts single phase service feeder cable is run from the meter to the service panel for 12 meters inside a combustible crawlspace. Service conductors lack effective overcurrent protection. For this reason service conductors are to be limited in length with a maximum of 1.5 meters service cable permitted for connection to the main service. Conductors lacking effective overcurrent protection can fail unpredictably and cause property damage or injury to persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Service_cable_12_plus_meters_inside_crawl_to_panel_main.png | file://x:/photopub/docs/0000000415/24a3ec57-e7df-4ec9-90be-64a164225132.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aa68864c_9cca_4d9d_871c_917aa48f3a5d
ELIN-556336-2016 | EL-374220-2016 | 4/12/2016 6:53:18 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | A 240 volt 15 amp armoured cable is fed to a water well casing, the armor of the Teck cable was not installed to be electrically continuous and the well casing was not bonded to ground. Should the cabling in the well casing fault to the well casing, the well casing will be energized and the overcurrent device protecting the circuit will not react. The well casing is accessible to the public and a fault of this nature could damage property or cause injury to persons | 3 | Equipment Gas line, cast or water pipe has not been bonded | Teck_armor_isolated__well_casing_not_bonded.png | file://x:/photopub/docs/0000000415/45d7ab8d-350a-4fc5-8624-000d5bb4da0d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28acad23_9b07_472d_9f78_7a7eb3ef9d1b
ELIN-551035-2016 | EL-368721-2016 | 4/4/2016 1:22:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | A new residential service cable feeding a 200 amp single phase 240 volt system has been installed. The service cable was stripped at the residence end and sleeved in rigid PVC pipe. The cable armor is not effectively bonded at the residence end and the conductors are not properly protected from anti abrasion or from strain relief. These three conditions can lead to damage to conductors and potential property damage or danger to persons | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Cable_armor_terminated_in_lb_no_strain_or_bonding_.png | file://x:/photopub/docs/0000000412/b8f0e14c-18c3-4908-bcfd-cae6fc368237.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12ee4276_76c0_4d3f_8f63_703a68ee49b4
ELIN-563146-2016 | EL-329183-2015 | 4/21/2016 10:55:15 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL192 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | 4 | 4 | 240 volt single phase main panel bus exposed and contact leads to shock hazard. | 4 | Site condition, Risk Reg EL-26-2017 Energized, qualified person on site, within area of energized parts. | Saddleback.png | file://x:/photopub/docs/0000000419/1b2d625b-b9a7-4fc6-a3c1-c425bd713d28.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__946f7d2f_38ac_4858_ace0_1ce50f2f4962
ELOP-571329-2016 | 6363 | 4/29/2016 8:32:16 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 v/15 a receptacles in shop and storage areas have unapproved wiring methods that leave area subject to shock and fire hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Shop.png | file://x:/photopub/docs/0000000425/d1b91332-7565-4332-9dc8-f73fa93ae569.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f658c9c_2e57_4ba7_85f7_63154ccb34ff
ELOP-571329-2016 | 6363 | 4/29/2016 8:32:16 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 v/15 a receptacles in shop and storage areas have unapproved wiring methods that leave area subject to shock and fire hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Storqge.png | file://x:/photopub/docs/0000000425/3c883d32-9139-467c-8d1a-b7bb08068f4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f658c9c_2e57_4ba7_85f7_63154ccb34ff
ELOP-571329-2016 | 6363 | 4/29/2016 8:32:16 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 v/15 a receptacles in shop and storage areas have unapproved wiring methods that leave area subject to shock and fire hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Exterior.png | file://x:/photopub/docs/0000000425/b20a465f-3682-4f40-95a8-edf8e89df405.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f658c9c_2e57_4ba7_85f7_63154ccb34ff
ELOP-571329-2016 | 6363 | 4/29/2016 8:32:16 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 v/15 a receptacles in shop and storage areas have unapproved wiring methods that leave area subject to shock and fire hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Shop2.png | file://x:/photopub/docs/0000000425/54829f54-f1ce-434d-9bbe-565176396b18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f658c9c_2e57_4ba7_85f7_63154ccb34ff
ELOP-571329-2016 | 6363 | 4/29/2016 8:32:16 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 v/15 a receptacles in shop and storage areas have unapproved wiring methods that leave area subject to shock and fire hazard. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | General.png | file://x:/photopub/docs/0000000425/f8e5b647-1e10-4fee-8a6b-c9a7a030b9e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f658c9c_2e57_4ba7_85f7_63154ccb34ff
ELIN-534108-2016 | EL-344549-2016 | 2/26/2016 12:04:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Asbestos hazard removed | 0 | No Created Hazard Identified | Asbestos.png | file://x:/photopub/docs/0000000396/485caa36-1c47-46d0-adf3-9f4c84eedbb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6054e26d_46b4_4c9e_9f00_0052b1f077c3
GAIN-539270-2016 | GA-334792-2016 | 5/10/2016 12:46:05 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_term.png | file://x:/photopub/docs/0000000428/cda4356b-cf4e-4869-b36f-66329f7f4c23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df7728f0_d1d8_4418_b751_1f325e2bab39
GAIN-539227-2016 | GA-345882-2016 | 5/10/2016 9:01:58 AM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Combustion air inlet is directly above regulator relief. If regulator were to relieve gas and boiler was firing, gas could be drawn in and cause over firing of boiler which in turn could cause overheating and building fire | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Vent_termination.png | file://x:/photopub/docs/0000000428/c4a6c59d-58ea-453d-8979-81fd4406d35b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e25c9ea7_8a5e_40ff_b783_4060dc8b1dbb
ELIN-571107-2016 | EL-344000-2016 | 5/9/2016 12:50:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service conductors will rub on roof shingles | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Mech_prot_req.png | file://x:/photopub/docs/0000000427/e227d1b1-8f52-49e2-9fb3-7fba27753f94.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37992e55_30c8_4dfc_8985_7bebdda1e74b
ELIN-572767-2016 | EL-383990-2016 | 5/9/2016 1:47:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary service in very poor condition, not safely maintained, not safely installed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | POA_WH.png | file://x:/photopub/docs/0000000427/7d56f473-2af3-43ee-8963-8d01a9c6b741.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aacb662_34ac_4873_ae4d_e102e043f097
ELIN-572767-2016 | EL-383990-2016 | 5/9/2016 1:47:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary service in very poor condition, not safely maintained, not safely installed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Enclosure.png | file://x:/photopub/docs/0000000427/1b1e0ccf-e36d-4321-9c27-6d7fe25d2ef4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aacb662_34ac_4873_ae4d_e102e043f097
ELIN-572767-2016 | EL-383990-2016 | 5/9/2016 1:47:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary service in very poor condition, not safely maintained, not safely installed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Meter.png | file://x:/photopub/docs/0000000427/b4ef8f29-81f8-412f-aab3-650561dc69a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aacb662_34ac_4873_ae4d_e102e043f097
ELIN-571107-2016 | EL-344000-2016 | 5/9/2016 12:50:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service conductors will rub on roof shingles | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 650_Victoria.png | file://x:/photopub/docs/0000000427/c16cf91b-7c3b-4b93-882a-895b147982b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37992e55_30c8_4dfc_8985_7bebdda1e74b
ELIN-572767-2016 | EL-383990-2016 | 5/9/2016 1:47:34 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary service in very poor condition, not safely maintained, not safely installed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel.png | file://x:/photopub/docs/0000000427/89de437c-cb7c-495b-8e5e-1f4b4b471ff7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aacb662_34ac_4873_ae4d_e102e043f097
ELIN-537870-2016 | UW-355950-2016 | 2/29/2016 5:55:59 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | This assessment found the service panel was not protected from the weather and was not lockable. The panel was was in the process of being energized for a house during construction . There is a shock hazard for unauthorized persons accessing the panel. There is a fire hazard if the main breaker gets wet and fails to operate as required. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Temp_service.png | file://x:/photopub/docs/0000000399/e9ce68c4-f803-4fae-8579-07b7b7b9c07a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__890a9134_b048_494f_a43b_6ecb6c7f0b67
ELIN-537925-2016 | UW-355990-2016 | 3/2/2016 5:10:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 3 | 120/240v -100Amp residential consumer service conductors and equipment are not protected from over-current or fault condition therefore a potential fire hazard could arise if conductors overheated due to a short circuit condition. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Consumer_main_switch.png | file://x:/photopub/docs/0000000399/5a5b5f54-6a98-48fe-9c31-87575e30dbe5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32a71c67_8d4a_4478_9c52_16bb331a9810
ELIN-531978-2016 | EL-265671-2015 | 3/4/2016 10:01:46 AM | ASSESS: EL: Final | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | 20 amp 240 volt overcurrent device does not have there handles joined together. This is a shock hazard. | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Breaker_handles_not_tied_together.png | file://x:/photopub/docs/0000000401/37bf748f-4ec3-40f7-82bc-fcd2c41f281c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77077ef1_1fdd_474a_8f4e_fbb06c1de686
ELIN-562578-2016 | EL-328163-2015 | 4/22/2016 2:56:02 PM | ASSESS: EL: Final | png | #asFound | EL040 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | 3 | 3 | Shock and fire hazard, in case of need to turn a circuit off but not knowing which one. | 3 | Equipment is not marked / identified Proper arc flash warning labels have not been provided | No_directory.png | file://x:/photopub/docs/0000000419/23e86991-a75d-4320-a9f3-8128b0c721ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__00a53f11_be93_4a21_9169_9d42e4d00a95
ELIN-566350-2016 | EL-345557-2016 | 4/29/2016 1:25:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found cover or filler plates missing on panelboard. When cover or filler plates are not installed on a panelboard, any fault condition inside a panelboard would not be fully contained within the approved electrical equipment and could become an electrical fire or shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_filler_plates_missing1.png | file://x:/photopub/docs/0000000423/93783ddf-6693-4e38-bbc8-4726496dfbaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b8b9ab9_b373_4491_bb5d_eeeccba0c752
ELIN-566350-2016 | EL-345557-2016 | 4/29/2016 1:25:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Found cover or filler plates missing on panelboard. When cover or filler plates are not installed on a panelboard, any fault condition inside a panelboard would not be fully contained within the approved electrical equipment and could become an electrical fire or shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_filler_plates_missing2.png | file://x:/photopub/docs/0000000423/50e32003-5c82-4b04-ac05-b6fdb6dcbd46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b8b9ab9_b373_4491_bb5d_eeeccba0c752
GAIN-569592-2016 | GA-308297-2015 | 5/4/2016 2:07:57 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Wrong_connector.png | file://x:/photopub/docs/0000000424/de84815a-3f60-4a36-8126-12062401152d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__520e10c0_1de8_4196_8289_409dd954c82a
GAIN-569592-2016 | GA-308297-2015 | 5/4/2016 2:07:57 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Fryer_missing_shield.png | file://x:/photopub/docs/0000000424/7118b66a-0d51-4056-ace5-c4c38099500d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__520e10c0_1de8_4196_8289_409dd954c82a
ELIN-554757-2016 | EL-370543-2016 | 4/5/2016 1:02:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found approved luminaires that are installed in building insulated ceiling but are not the correct type of luminaire approved for the use in insulation covering. When electrical equipment is not installed and is not used as per the approved use of the equipment or is not the correct type of equipment as required by code standards, the luminaire installation may become overloaded or overheated and may possibly become an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_insulated_ceiling_with_several_recessed_luminaires1.png | file://x:/photopub/docs/0000000413/12fd8885-2876-4782-a2fa-618e5343aaa6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__399e6534_2ab1_4d0d_bc66_14388eef5a8d
ELIN-554757-2016 | EL-370543-2016 | 4/5/2016 1:02:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found approved luminaires that are installed in building insulated ceiling but are not the correct type of luminaire approved for the use in insulation covering. When electrical equipment is not installed and is not used as per the approved use of the equipment or is not the correct type of equipment as required by code standards, the luminaire installation may become overloaded or overheated and may possibly become an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_insulated_ceiling_does_not_have_the_correct_type_of_luminaire_installed_for_insulated_ceilings3.png | file://x:/photopub/docs/0000000413/e141a157-3298-4825-8cb4-c91d708fa955.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__399e6534_2ab1_4d0d_bc66_14388eef5a8d
ELIN-554757-2016 | EL-370543-2016 | 4/5/2016 1:02:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found approved luminaires that are installed in building insulated ceiling but are not the correct type of luminaire approved for the use in insulation covering. When electrical equipment is not installed and is not used as per the approved use of the equipment or is not the correct type of equipment as required by code standards, the luminaire installation may become overloaded or overheated and may possibly become an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_insulated_ceiling_does_not_have_the_correct_type_of_luminaire_installed_for_insulated_ceilings2.png | file://x:/photopub/docs/0000000413/ff7936ea-e16b-4afe-842a-18a2313d221e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__399e6534_2ab1_4d0d_bc66_14388eef5a8d
ELIN-554757-2016 | EL-370543-2016 | 4/5/2016 1:02:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found approved luminaires that are installed in building insulated ceiling but are not the correct type of luminaire approved for the use in insulation covering. When electrical equipment is not installed and is not used as per the approved use of the equipment or is not the correct type of equipment as required by code standards, the luminaire installation may become overloaded or overheated and may possibly become an electrical fire or shock hazard to people and property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Kitchen_insulated_ceiling_does_not_have_the_correct_type_of_luminaire_installed_for_insulated_ceilings.png | file://x:/photopub/docs/0000000413/8c5da95f-afd2-41ca-96bb-f954c71ba9f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__399e6534_2ab1_4d0d_bc66_14388eef5a8d
ELIN-573150-2016 | EL-382542-2016 | 5/10/2016 1:05:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Insulated service conductors sharply bent around metallic connectors may displace their insulation enough to cause a fault and significant equipment damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Split_bushing_installed_instead_of_screwed_on__Insulation_damage_may_occur_causing_significant_equipment_damaga.png | file://x:/photopub/docs/0000000428/1f5d9568-a704-4414-825c-2bdf7dae4165.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d01c2f55_fa40_4ef0_b3b9_eacbb195867d
ELIN-570492-2016 | EL-382542-2016 | 5/10/2016 11:45:37 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Split bushing allows insulation displace,ENT against ends of metallic connector. This may cause short circuit and severe equipment damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Purposely_split_bushing_allows_installation_w_o_removing_conductors.png | file://x:/photopub/docs/0000000428/787a2105-5bc6-4269-8d88-2bf58eef38af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f344b6d_e97b_4aee_89dc_40df2bd1e183
ELIN-572600-2016 | EL-349469-2016 | 5/10/2016 12:18:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL113 | Conductors High Voltage conductors are exposed. | 4 | 4 | Cables installed on upper faces of rafters in attic with a vertical distance greater than 1m. This is a fire hazard as individuals could walk on cables and damage them. | 4 | Conductors High Voltage conductors are exposed. | A.png | file://x:/photopub/docs/0000000428/80d251d1-501c-46d1-9ca0-637994d0724b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__534a4f92_d92f_4df3_bdfe_f748fb916738
BPVOP-535032-2016 | 2255949 | 3/2/2016 9:49:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve on hot water heating boilers shall match or exceed heating capacity of the corresponding boiler. I found the relieving capacity of the safety valve was less than what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_.png | file://x:/photopub/docs/0000000403/46d13105-2d37-48b7-a08a-38215af82193.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__006472f2_8a32_4e73_b380_64d3fdca1582
BPVOP-535032-2016 | 2255949 | 3/2/2016 9:49:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve on hot water heating boilers shall match or exceed heating capacity of the corresponding boiler. I found the relieving capacity of the safety valve was less than what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_valve_data.png | file://x:/photopub/docs/0000000403/a945a006-3ec6-4d2d-a7de-38890f34fd61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__006472f2_8a32_4e73_b380_64d3fdca1582
BPVOP-535032-2016 | 2255949 | 3/2/2016 9:49:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve on hot water heating boilers shall match or exceed heating capacity of the corresponding boiler. I found the relieving capacity of the safety valve was less than what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_data_label.png | file://x:/photopub/docs/0000000403/7c7b8670-cf43-4b3b-afe3-9247e5484fd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__006472f2_8a32_4e73_b380_64d3fdca1582
BPVOP-535065-2016 | 2255917 | 3/2/2016 1:58:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_2_data_label.png | file://x:/photopub/docs/0000000403/f6acc57b-1e8a-42e3-b62b-6d05c74e7fd3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b46ec7d_88c5_42b2_86a6_787da228a927
BPVOP-535065-2016 | 2255917 | 3/2/2016 1:58:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_2.png | file://x:/photopub/docs/0000000403/64cbeea0-4601-4dfa-b3fb-307e36fc087c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b46ec7d_88c5_42b2_86a6_787da228a927
BPVOP-535065-2016 | 2255917 | 3/2/2016 1:58:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valve shall match or exceed heating capacity of the corresponding boiler. I found that heat relieving capacity of the safety valve was less that what's required. An incident may occur if boiler components overheat due to restricted capacity of the safety valve | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_valve_2_data.png | file://x:/photopub/docs/0000000403/ec818581-d2c7-4ae9-a8b8-616c4a1c5dc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b46ec7d_88c5_42b2_86a6_787da228a927
ELOP-548880-2016 | 1336 | 3/23/2016 11:51:42 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL067 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | No_bond.png | file://x:/photopub/docs/0000000408/ca38d1ed-fc9d-4ef2-bd4b-918dcbc03b91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6213455_b380_4fd1_a613_96e89953903e
ELOP-548880-2016 | 1336 | 3/23/2016 11:51:42 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL067 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | DDC_.png | file://x:/photopub/docs/0000000408/dd44e00a-850b-4fbd-9019-cd4cdf0c797e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6213455_b380_4fd1_a613_96e89953903e
ELOP-548880-2016 | 1336 | 3/23/2016 11:51:42 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL067 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Well_head.png | file://x:/photopub/docs/0000000408/bdbddd90-1527-47d6-9499-6d95aeb21836.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6213455_b380_4fd1_a613_96e89953903e
ELOP-548880-2016 | 1336 | 3/23/2016 11:51:42 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL067 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Storage_in_front_of_pane.png | file://x:/photopub/docs/0000000408/67597b57-83b5-4bb9-a644-ad27c28a4a40.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6213455_b380_4fd1_a613_96e89953903e
ELIN-545656-2016 | EL-168311-2014 | 4/7/2016 3:45:29 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | 120 volt 15 amp receptacles located within 1.5 meters of sinks are not ground fault protected to prevent possible electrical shock | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Kitchen_counter_receptacle_not_ground_fault_protected.png | file://x:/photopub/docs/0000000413/3e0f8e68-28fd-47f7-9df4-9907f812cd1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71547052_5847_40e5_9128_cd2beb151221
ELIN-545656-2016 | EL-168311-2014 | 4/7/2016 3:45:29 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | 120 volt 15 amp receptacles located within 1.5 meters of sinks are not ground fault protected to prevent possible electrical shock | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Laundry_room_receptacle_not_ground_fault_protected.png | file://x:/photopub/docs/0000000413/118939d3-7af4-48e7-b5c6-f64095fe96af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71547052_5847_40e5_9128_cd2beb151221
ELIN-545656-2016 | EL-168311-2014 | 4/7/2016 3:45:29 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | 120 volt 15 amp receptacles located within 1.5 meters of sinks are not ground fault protected to prevent possible electrical shock | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Kitchen_counter_receptacle_not_tamper_resistant.png | file://x:/photopub/docs/0000000413/92c25faf-c3c3-40c2-b3ec-d8f950efdb35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71547052_5847_40e5_9128_cd2beb151221
ELIN-545656-2016 | EL-168311-2014 | 4/7/2016 3:45:29 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | 120 volt 15 amp receptacles located within 1.5 meters of sinks are not ground fault protected to prevent possible electrical shock | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Another_14_AWG_branch_circuit_and_20a_breaker.png | file://x:/photopub/docs/0000000413/a48298cc-31e2-48f8-a862-be7bcaa10769.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71547052_5847_40e5_9128_cd2beb151221
ELIN-545656-2016 | EL-168311-2014 | 4/7/2016 3:45:29 PM | ASSESS: EL: Final | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | 120 volt 15 amp receptacles located within 1.5 meters of sinks are not ground fault protected to prevent possible electrical shock | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | _14_AWG_branch_circuit_and_20a_breaker_.png | file://x:/photopub/docs/0000000413/d320b129-70c4-4fef-9ea0-93962ef46fab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71547052_5847_40e5_9128_cd2beb151221
ELIN-551385-2016 | EL-369396-2016 | 4/7/2016 12:15:13 PM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | An extension cord has been plugged into a general 15A outlet to feed the washing machine, the general 15A outlet is not a dedicated circuit and feeds the other bedroom and storage room outlets and lights. This could overload the branch circuit resulting in a fire and equipment damage. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Washer.png | file://x:/photopub/docs/0000000413/a4dee2f9-9478-414f-a450-dfffd40e6245.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__216539e9_b413_4f4d_9c7b_fd58f3d7c2d2
ELIN-510134-2016 | EL-309763-2015 | 4/7/2016 12:40:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | DBII conduit is designed to be covered by concrete or underground, when exposed could be broken giving access to the energized conductors | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Service_DBII_Exposed_at_service_location_.png | file://x:/photopub/docs/0000000413/86bac3b5-288b-4b5e-9c40-214aa88c90ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d08a007_2e1d_4b26_84ad_af28fd68f106
ELOP-238374-2014 | EL-155007-2014 | 4/14/2016 2:10:24 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 | The transformer T2 has a type one enclosure that is rated for dust only. The room has two sprinkler heads and if the heads activated they would spray water into the transformer windings resulting in a shock hazard. | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Storage.png | file://x:/photopub/docs/0000000416/2ce430d8-d0f3-4a51-b417-c94f7b441c1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__303a3053_f779_4110_9904_550dedecee89
ELOP-238374-2014 | EL-155007-2014 | 4/14/2016 2:10:24 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL188 | Installation of electrical equipment Equipment is not approved for the specific use | 2 | 2 | The transformer T2 has a type one enclosure that is rated for dust only. The room has two sprinkler heads and if the heads activated they would spray water into the transformer windings resulting in a shock hazard. | 2 | Installation of electrical equipment Equipment is not approved for the specific use | Type_1_transformer_enclosure.png | file://x:/photopub/docs/0000000416/5ffda6a0-a068-47a0-8aa8-356cc9080955.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__303a3053_f779_4110_9904_550dedecee89
GAIN-548816-2016 | GA-331883-2016 | 3/22/2016 8:36:11 AM | ASSESS: GA: Rough-In | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Special_vent_outdoors.png | file://x:/photopub/docs/0000000409/d8a5dcdf-6016-4f74-b2d9-6aaefc508cd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1066f95_1e18_4964_b7c5_507fd37c34ba
GAIN-547299-2016 | GA-348525-2016 | 3/29/2016 8:57:51 AM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Vent_termination.png | file://x:/photopub/docs/0000000409/5ed4b7fa-18d9-46ec-ae43-94dd2bf62d92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__623490c6_3997_4414_850f_cd276cc684e6
ELIN-544817-2016 | UW-367345-2016 | 3/3/2016 1:41:32 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 volt gas furnace connection cable termination strained and if fails, can produce equipment damage or fire risk. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Furnace_termination.png | file://x:/photopub/docs/0000000404/d5fb0fde-648a-4504-af3a-8f82bd8238bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1b9db5b_8ae9_4db8_a206_e3f8988e0011
ELIN-544817-2016 | UW-367345-2016 | 3/3/2016 1:41:32 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | 120 volt gas furnace connection cable termination strained and if fails, can produce equipment damage or fire risk. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Ac.png | file://x:/photopub/docs/0000000404/b40a7c2b-2c3a-4d10-8509-91877f1cb47d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1b9db5b_8ae9_4db8_a206_e3f8988e0011
ELIN-565341-2016 | EL-378098-2016 | 5/2/2016 2:15:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 4 | Existing 240 volt 100 amp main panel energized and live parts exposed. Incidental contact may lead to electrical shock or arc flash conditions. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Main_panel.png | file://x:/photopub/docs/0000000423/f2cb7046-7af7-4e56-9c8a-86562efa28d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a027dd6_6243_4ae2_854e_e5c83adbac13
ELIN-561769-2016 | EL-377274-2016 | 4/22/2016 8:51:53 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Installation of underground DB2 (thin wall PVC raceway) 90 degree sweep was not buried or concrete encased as required. Potential damage of raceway, which would of exposed unprotected BC Hydro service feeder. This could of occurred if service had been energized. The homeowner service connection request was denied. Failed inspection request. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Exposed_DB2_service_raceway_.png | file://x:/photopub/docs/0000000420/8974fb68-9851-4683-a043-1810e8bc3abb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e432abd_53af_405e_bdc8_e78d86a3002c
BPVOP-548477-2016 | 2288609 | 3/15/2016 10:22:11 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valves on hot water boilers must match or exceed the boiler minimum reliving capacity. I found the relieving capacity of the safety valve was less than that what's required. The hot water boiler may be subjected to thermal and mechanical damage due to restricted relieving capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_1.png | file://x:/photopub/docs/0000000407/9449491c-cf64-4e76-b808-775cd9842596.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a04a125c_be87_477e_a3f3_f069db8368bc
BPVOP-548477-2016 | 2288609 | 3/15/2016 10:22:11 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valves on hot water boilers must match or exceed the boiler minimum reliving capacity. I found the relieving capacity of the safety valve was less than that what's required. The hot water boiler may be subjected to thermal and mechanical damage due to restricted relieving capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Boiler_1_data_label.png | file://x:/photopub/docs/0000000407/e738eb30-2e52-4e14-bf57-38a2b3accf31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a04a125c_be87_477e_a3f3_f069db8368bc
BPVOP-548477-2016 | 2288609 | 3/15/2016 10:22:11 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valves on hot water boilers must match or exceed the boiler minimum reliving capacity. I found the relieving capacity of the safety valve was less than that what's required. The hot water boiler may be subjected to thermal and mechanical damage due to restricted relieving capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_valve_1_data_tag.png | file://x:/photopub/docs/0000000407/77a788e6-c380-46c1-91ea-f23209298b39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a04a125c_be87_477e_a3f3_f069db8368bc
BPVOP-548477-2016 | 2288609 | 3/15/2016 10:22:11 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | Relieving capacity of a safety valves on hot water boilers must match or exceed the boiler minimum reliving capacity. I found the relieving capacity of the safety valve was less than that what's required. The hot water boiler may be subjected to thermal and mechanical damage due to restricted relieving capacity of the safety valve. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_valve_discharge.png | file://x:/photopub/docs/0000000407/5aeb88bd-1ce4-4c8e-ace3-d5fcb6cc6241.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a04a125c_be87_477e_a3f3_f069db8368bc
ELIN-559723-2016 | EL-356702-2016 | 4/14/2016 10:22:47 AM | ASSESS: EL: Service Connection | png | #asFound | EL079 | Installation Grounding; conductor is not properly sized. | 4 | 4 | 200 amp, 120/240 volt main distribution panel has ground conductor not installed on identified conductor. This is a thermal issue. | 4 | Installation Grounding; conductor is not properly sized. | Ground_conductor_not_terminated_on_identified_conductor_.png | file://x:/photopub/docs/0000000417/459c4310-0222-40d6-9746-426330fba1e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44e157cd_09be_4003_bae1_bb44609c3a7f
GAUP-372591-2015 | UW-247163-2015 | 3/14/2016 1:08:33 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Venting size increasing couplings installed on a horizontal section of pipe. These couplings installed this way trap condensate in the venting system not allowing it to drain back to the furnace. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Furnace_venting.png | file://x:/photopub/docs/0000000403/671b5caf-7d6f-4925-8ab4-69af3cd16aba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01bba58e_7adc_4432_96d5_81d97c87e60e
ELIN-541315-2016 | EL-281342-2015 | 3/10/2016 7:15:53 AM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Energized branch circuit conductor for dishwasher unit not adequately protected or terminated as required and accessible to general public. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | View01_dishwasher_branch_circuit.png | file://x:/photopub/docs/0000000403/83bb9173-65a1-42dd-9f99-712270e1ed95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6a408dc5_8d74_4c92_a65f_6178d8902511
ELIN-566039-2016 | EL-335589-2016 | 5/13/2016 8:41:55 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp 120 volt exterior outlet does not utilize the required in use cover, this exposes cord connections to weather conditions and is a shock hazard | 3 | Installation of electrical equipment Equipment is not approved for the specific use | No_in_use_cover.png | file://x:/photopub/docs/0000000430/ada0ceab-edb7-4786-8ebb-7073540710a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfc11cff_c9a7_4acc_88a6_59eac7a6f768
BPVIN-541189-2016 | UW-359863-2016 | 3/2/2016 1:58:58 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP037 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | 2 | 2 | Expansion tanks are designed to absorb pressure fluctuations in closed loop systems. I found an expansion tank not rated for the systems applications. This can lead to abnormal conditions created by improper expansion. | 2 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | AMTROL_exp_tank.png | file://x:/photopub/docs/0000000403/e66de00f-acb0-4746-85dc-ec3bc7e39e26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79b75e76_e5a8_4297_b67f_435d1bed140e
BPVIN-541189-2016 | UW-359863-2016 | 3/2/2016 1:58:58 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP037 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | 2 | 2 | Expansion tanks are designed to absorb pressure fluctuations in closed loop systems. I found an expansion tank not rated for the systems applications. This can lead to abnormal conditions created by improper expansion. | 2 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | Non_ASME_exp_tank.png | file://x:/photopub/docs/0000000403/a0aafeaf-1efe-4c4e-80af-4477776918d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79b75e76_e5a8_4297_b67f_435d1bed140e
BPVOP-577620-2016 | 2717331 | 5/17/2016 9:55:11 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP055 | 1.2.2 Boiler leakage: procedure - Corroded hand hole covers. | 2 | 2 | EROSION OF SEATING SURFACES | 2 | 1.2.2 Boiler leakage: procedure - Corroded hand hole covers. | HAND_HOLE_COVERS.png | file://x:/photopub/docs/0000000430/0fce42d8-877b-4cfa-9280-e14a2a2035be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a525df0_c388_4066_805d_29f8fb934905
ELIN-542727-2016 | EL-340569-2016 | 3/15/2016 10:07:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 | The non-metallic sheathed branch circuit wiring is in contact with heat ducting therefore the insulation of the wiring will be damaged over time. | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | Furnace_switch_location.png | file://x:/photopub/docs/0000000404/e5383b7a-2143-4b26-9c65-e6e1da7f36d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6512d975_9541_4aa0_bcfb_e13d514c7b0f
ELIN-542727-2016 | EL-340569-2016 | 3/15/2016 10:07:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 | The non-metallic sheathed branch circuit wiring is in contact with heat ducting therefore the insulation of the wiring will be damaged over time. | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | Heat_duct_proximity.png | file://x:/photopub/docs/0000000404/055887f1-5ca1-43bb-bc81-3587efff446b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6512d975_9541_4aa0_bcfb_e13d514c7b0f
ELIN-531979-2016 | EL-214957-2015 | 2/24/2016 4:15:41 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | The unfused 100 amp 120/240 volt feeders from the supply service meterbase location does not include mechanical protection for the feeders. This exposes the cables to mechanical damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_feeders.png | file://x:/photopub/docs/0000000395/c9aab48f-71a9-45d3-8351-b9b79553caa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c5a47886_22d2_4cae_9c80_06931c51287d
ELIN-532718-2016 | EL-274122-2015 | 3/23/2016 2:53:52 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | A standard 15 amp duplex receptacle installed within 1.5m of a sink creates a potential shock hazard for someone using an electrical appliance such as a hair dryer plugged in and within reach of the sink. A GFCI protected outlet here provides protection should there be contact between water, an energized appliance and a person. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | No_GFCI_prorection.png | file://x:/photopub/docs/0000000408/8b45d528-de0b-4f35-be15-d432f46fb550.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec3fd04d_d78b_4a85_abc8_03ed21bbc4f8
ELOP-559587-2016 | EL-351759-2016 | 4/18/2016 8:29:36 AM | ASSESS: EL OP: Acceptance | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | The operating handle on the 400 amp 208 volt 3-phase breaker is broken off, equipment damage is the result and proper,operation is not possible to manually de-energize breaker without the use of a tool. | 3 | General Equipment is not approved for the specific use | Breaker_handle.png | file://x:/photopub/docs/0000000418/434ed635-c0bb-46bd-9985-2913d71a6047.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcb7ed4e_6f52_4124_a11f_782239d172e3
BPVOP-558470-2016 | BPV 00000017808-2013 | 4/12/2016 11:36:29 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Boiler_internal_2.png | file://x:/photopub/docs/0000000418/ff5c4cc8-d7ef-4c67-a393-f06a7dfcc152.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee0c38e4_7377_44b5_9d2c_53c27755e2b8
BPVOP-558470-2016 | BPV 00000017808-2013 | 4/12/2016 11:36:29 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Boiler_internal_manhole.png | file://x:/photopub/docs/0000000418/93054413-5da2-48d3-b129-f09cbc569def.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee0c38e4_7377_44b5_9d2c_53c27755e2b8
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Unprotected_feeder.png | file://x:/photopub/docs/0000000430/73f394b5-2fb3-4919-9275-8c4c840da3b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Live_unsupported_branch_circuits_.png | file://x:/photopub/docs/0000000430/43d0a0b0-cf08-469f-a0c9-a4e72d2cdf08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Sub_panel_without_cover_.png | file://x:/photopub/docs/0000000430/18962f1f-e33f-4bcc-ac1f-31634cc6ae45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Unsupported_service_conductor.png | file://x:/photopub/docs/0000000430/3a28f559-1456-4d77-8bff-151a31b1ea89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Live_conductor.png | file://x:/photopub/docs/0000000430/1a70be09-c235-46c8-b935-1338e2c1273b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Lighting_with_no_covers.png | file://x:/photopub/docs/0000000430/e7fdbde3-92d0-4cd3-b7c1-f2cae11b6ecc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Pump_with_un-approved_wiring_.png | file://x:/photopub/docs/0000000430/9b07e2c6-7aaa-410e-a9d8-f655fd473274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-573296-2016 | UW-384013-2016 | 5/16/2016 1:50:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | ESO observed several non-compliances. Unprotected conductors make them likely for mechanical damage. Open breaker spaces in panel leaving a possible shock and Arc flash condition . Extension cord extending over 200' creating a thermal hazard. Exposed wiring in lighting making them a shock hazard. Reduced feeder conductors making them a thermal risk as they are under sized for breaker. Live branch circuits exposed to occupants. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Sub_panel_feeder_.png | file://x:/photopub/docs/0000000430/3bc52075-391a-415c-87d0-26824a728e34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceda2262_9234_4dac_96a3_b691cebcc134
ELIN-575427-2016 | EL-384719-2016 | 5/16/2016 4:36:34 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | Original ground electrodes are not approved. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Rigid_pipe.png | file://x:/photopub/docs/0000000430/1faec1c4-15e2-4868-9f30-7035d4428109.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41ce938a_ee4e_4a0d_a93f_f9e84d854b8c
ELIN-575326-2016 | EL-373773-2016 | 5/16/2016 2:44:59 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp 120 volt receptacle installed with 1.5 meters of a sink. The receptacle does not have ground fault protection. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Sink_receptacle.png | file://x:/photopub/docs/0000000430/32b91bc6-3b1b-4624-9c72-cc758776412f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21982d53_bd86_409b_9e2f_fe637c19bd4a
ELIN-576215-2016 | EL-367906-2016 | 5/16/2016 11:30:28 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The electrical meter is installed below the grade of the supply authority pull box. 75 mm supply authority duct installed without required draining installed. This is a thermal issue and equipment damage could occur should water run in the service duct to the meter location. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | U_G_conduit.png | file://x:/photopub/docs/0000000430/8e319cc2-1729-49d5-8e1f-6b52e4ed6491.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf3477dd_e813_4308_8d68_97f1cb575ebe
ELIN-576278-2016 | EL-384458-2016 | 5/16/2016 4:12:31 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | A 120 volt light fixture, mounted on wood partial board is protected by a 15 amp breaker. An outlet box has not been installed. This is a thermal hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Fixture_installed_without_outlet_box.png | file://x:/photopub/docs/0000000430/0d7f06e3-3623-48de-a25f-2383d2ece073.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe60e2d3_cf24_418d_a42f_128d0733ca20
ELIN-574270-2016 | EL-353609-2016 | 5/13/2016 8:37:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | 240 volt cables feeding existing service temporarily is crossing utility equipment and poses safety risk to utility personnel. | 0 | No Created Hazard Identified | Meter.png | file://x:/photopub/docs/0000000430/6bdb3bf8-3489-47b6-9511-48219c07feab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69e614c1_1bd3_447d_a03b_c9ef7a439801
ELIN-545036-2016 | EL-324228-2015 | 3/23/2016 11:47:02 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 2 | An electrical panel in a detached work shop had several unused cable openings which were not covered. This creates the possibility of a shock hazard should someone inadvertently enter a tool into one of these openings. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Missing_KO_fillers_.png | file://x:/photopub/docs/0000000408/955998ff-6e01-45ef-8bb5-4081cc3be781.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb209216_39dc_402d_9a5c_2c2d9e40ad99
ELIN-543575-2016 | EL-360361-2016 | 3/14/2016 3:03:14 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found exposed energized branch circuit conductors for temporary wiring electrical equipment which are not supported and are not entered into a junction box with a cover plate and with proper supports as required by code. When energized exposed branch circuit conductors are not properly entered into a junction box with a cover and with proper support of the electrical equipment then this is an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 204.png | file://x:/photopub/docs/0000000404/ff32b68a-465c-4f6c-affa-1374c71202cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b615b4f_4fc2_4835_926f_2b1e9fb2b999
ELIN-558228-2016 | EL-324029-2015 | 4/19/2016 11:57:50 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Panel_clearance.png | file://x:/photopub/docs/0000000418/cad4e70a-9d3f-4fd2-af5b-fd03ba86fc16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a90dfbc2_96e5_417a_a25e_f9730adb6f91
ELIN-546026-2016 | EL-359660-2016 | 3/22/2016 2:49:25 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | 150 amp, 120/240V Overhead service does not have identified conductor grounded. This is a thermal effect condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_not_terminated_to_neutral_system_.png | file://x:/photopub/docs/0000000407/53ddbcd9-dde7-4744-a707-786e4ccbdba2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae2b1006_8c8e_463c_977b_5ad612c7bc21
ELIN-546017-2016 | EL-368032-2016 | 3/22/2016 7:38:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | The 3c-4/0 service conductor used requires a demand calculation to meet the requirements of table 39. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3c-4_0_ACWU_feeder_to_main_distribution.png | file://x:/photopub/docs/0000000407/eb3bf041-6bc0-4a55-a201-77ebb9e557f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53994499_372e_46b2_8d56_a58e9d867647
ELIN-542899-2016 | EL-350425-2016 | 3/14/2016 11:27:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL035 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | 3 | 3 | Cable exits ground and is uncovered for about 2 feet at service pole, unable to see marker tape. Cable has been buried at multiple depths throughout its run, unable to see marker tape. Marker tape above the cable will give anyone digging in the area in the future a warning of a buried cable. If persons or equipment were to come in contact with a buried energized service cable there would be a risk of shock or damage to persons or equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Location of conductors is not marked where required | Cable_exiting_ground_to_meter_base_unable_to_locate_marker_tape.png | file://x:/photopub/docs/0000000403/6500b11b-8c91-4aaf-b218-13c819c487af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ca09667_40d1_4ef2_8537_52e122dd2e59
ELIN-543985-2016 | EL-019590-2013 | 3/29/2016 1:15:05 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Branch circuit conductors are required to be terminated to branch circuit over current devices to protect the conductors, devices (receptacles and switches), fixtures, portable equipment plugged into receptacles, and hard wired equipment. This is required to prevent equipment from overloading and creating excessive thermal energy that the conductors and equipment connected to them are not designed to carry. This installation has new branch circuit wiring installed in a house for lighting and receptacles. The branch circuits are rated at 15A and are connected to 20A breakers. Left uncorrected this is a potential fire hazard if the branch circuit conductors and equipment connected to them become overloaded. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 15A_conductor_on_20A_breaker_for_circuit_1_3_and_4_.png | file://x:/photopub/docs/0000000408/d434beda-fd11-4531-a610-a3fba304f868.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b37fb8_7ef8_46d5_a6cb_34eddc4a334a
ELIN-543985-2016 | EL-019590-2013 | 3/29/2016 1:15:05 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Branch circuit conductors are required to be terminated to branch circuit over current devices to protect the conductors, devices (receptacles and switches), fixtures, portable equipment plugged into receptacles, and hard wired equipment. This is required to prevent equipment from overloading and creating excessive thermal energy that the conductors and equipment connected to them are not designed to carry. This installation has new branch circuit wiring installed in a house for lighting and receptacles. The branch circuits are rated at 15A and are connected to 20A breakers. Left uncorrected this is a potential fire hazard if the branch circuit conductors and equipment connected to them become overloaded. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 15A_conductor_on_20A_breaker_circuit_1_3_4.png | file://x:/photopub/docs/0000000408/1a5ec412-213f-4e4a-afbb-88daabdc141f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b37fb8_7ef8_46d5_a6cb_34eddc4a334a
ELIN-556610-2016 | UW-374380-2016 | 4/8/2016 10:46:48 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | The main service mast and disconnect are pulled off the wall. The damage may become a shock hazard if not repaired. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Disconnect.png | file://x:/photopub/docs/0000000414/1f2f59f3-665f-4359-ba0a-3224a67cfa3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0ad4a86_ecc3_4aaa_b4b3_f1c9e76c1a65
ELIN-556610-2016 | UW-374380-2016 | 4/8/2016 10:46:48 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | The main service mast and disconnect are pulled off the wall. The damage may become a shock hazard if not repaired. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Service_conduit.png | file://x:/photopub/docs/0000000414/10efe103-1f32-41b7-8af2-669dde7eccef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0ad4a86_ecc3_4aaa_b4b3_f1c9e76c1a65
BPVOP-546360-2016 | 2294918 | 5/12/2016 5:26:07 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP046 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | 4 | 4 | All pressure vessels must maintain minimal required shell thickness in order to contain a substance at maximum allowable working pressure. I found that this wood treatment high pressure cylinder (150 PSI) is affected by general corrosion on the internal surfaces which reduced nominal thickness of the shell by 50% at maximum. | 4 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion that causes thinning of a pressure retaining component which reduces the thickness below the minimum design thickness and the vessel has to be de-rated | Crack.png | file://x:/photopub/docs/0000000429/9366ff1e-2828-4f20-99c7-6fbe97bac584.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b38c235c_b860_4421_b7fe_90e00b5ffc41
BPVIN-575402-2016 | UW-368761-2016 | 5/12/2016 4:50:50 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | Pressure retaining equipment must be operated withing it's design pressure limit. I found that this high pressure air storage tank (135PSI) has a pressure relief device that is set higher than the maximum allowable working pressure of the tank by 15%. Potential exists for an incident because of excessive pressure conditions. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Tank.png | file://x:/photopub/docs/0000000429/14dd8480-7e3f-4837-9126-bd47f31a7a91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48ce37c1_9846_4724_bf0c_e7837b012053
BPVIN-575402-2016 | UW-368761-2016 | 5/12/2016 4:50:50 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | Pressure retaining equipment must be operated withing it's design pressure limit. I found that this high pressure air storage tank (135PSI) has a pressure relief device that is set higher than the maximum allowable working pressure of the tank by 15%. Potential exists for an incident because of excessive pressure conditions. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Pressure_relief_device_1.png | file://x:/photopub/docs/0000000429/a8147158-308f-41e2-a509-21f9c8abf8e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48ce37c1_9846_4724_bf0c_e7837b012053
BPVIN-575402-2016 | UW-368761-2016 | 5/12/2016 4:50:50 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | Pressure retaining equipment must be operated withing it's design pressure limit. I found that this high pressure air storage tank (135PSI) has a pressure relief device that is set higher than the maximum allowable working pressure of the tank by 15%. Potential exists for an incident because of excessive pressure conditions. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Nameplate____.png | file://x:/photopub/docs/0000000429/abf536ab-60ab-4b75-a468-bc437bccd13c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48ce37c1_9846_4724_bf0c_e7837b012053
BPVIN-575402-2016 | UW-368761-2016 | 5/12/2016 4:50:50 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 5 | Pressure retaining equipment must be operated withing it's design pressure limit. I found that this high pressure air storage tank (135PSI) has a pressure relief device that is set higher than the maximum allowable working pressure of the tank by 15%. Potential exists for an incident because of excessive pressure conditions. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | Pressure_setting_.png | file://x:/photopub/docs/0000000429/2d0376fe-0bc9-48f8-89aa-1f02f85b361f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48ce37c1_9846_4724_bf0c_e7837b012053
ELIN-549443-2016 | UW-369882-2016 | 3/24/2016 1:47:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Conductors must be approved for use. In this grow op a series of cables intended for interior use had been draped some 200 feet from an existing residence across the ground to a new building under construction. | 3 | Conductors Equipment is not approved for the specific use. | Surface_conductors4.png | file://x:/photopub/docs/0000000408/08659532-6af5-4019-afce-4b0a98e9cd41.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dc6379a_249a_4021_9cdc_17284e6fd346
ELIN-549443-2016 | UW-369882-2016 | 3/24/2016 1:47:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Conductors must be approved for use. In this grow op a series of cables intended for interior use had been draped some 200 feet from an existing residence across the ground to a new building under construction. | 3 | Conductors Equipment is not approved for the specific use. | Surface_conductors2.png | file://x:/photopub/docs/0000000408/fa0efb6c-21f8-4bab-81df-56bdea53c08f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dc6379a_249a_4021_9cdc_17284e6fd346
ELIN-549443-2016 | UW-369882-2016 | 3/24/2016 1:47:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Conductors must be approved for use. In this grow op a series of cables intended for interior use had been draped some 200 feet from an existing residence across the ground to a new building under construction. | 3 | Conductors Equipment is not approved for the specific use. | Entry_to_building.png | file://x:/photopub/docs/0000000408/c2e12d19-312c-46a7-bb28-e9a741e6150f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dc6379a_249a_4021_9cdc_17284e6fd346
ELIN-549443-2016 | UW-369882-2016 | 3/24/2016 1:47:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Conductors must be approved for use. In this grow op a series of cables intended for interior use had been draped some 200 feet from an existing residence across the ground to a new building under construction. | 3 | Conductors Equipment is not approved for the specific use. | Surface_conductors3.png | file://x:/photopub/docs/0000000408/6490a348-267c-4620-b997-ab8a5ee5e7cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dc6379a_249a_4021_9cdc_17284e6fd346
ELIN-549443-2016 | UW-369882-2016 | 3/24/2016 1:47:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Conductors must be approved for use. In this grow op a series of cables intended for interior use had been draped some 200 feet from an existing residence across the ground to a new building under construction. | 3 | Conductors Equipment is not approved for the specific use. | Surface_conductors1.png | file://x:/photopub/docs/0000000408/91bc3600-69ac-4e27-a855-47fea37d9928.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dc6379a_249a_4021_9cdc_17284e6fd346
ELIN-549443-2016 | UW-369882-2016 | 3/24/2016 1:47:03 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Conductors must be approved for use. In this grow op a series of cables intended for interior use had been draped some 200 feet from an existing residence across the ground to a new building under construction. | 3 | Conductors Equipment is not approved for the specific use. | New_HVAC_equipment.png | file://x:/photopub/docs/0000000408/52fe3d23-c8b1-490d-abeb-3bb61e7e1e6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6dc6379a_249a_4021_9cdc_17284e6fd346
ELIN-545135-2016 | EL-291032-2015 | 3/21/2016 1:27:08 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found exposed conductors and bus bars on panelboards that are connected to power supply system which could easily become energized and hazardous and non-compliant once service is connected as contractor had declared and requested for service connection. When electrical conductors are exposed and energized with all panelboard covers missing and energized conductors could come in contact with people or property, the electrical system is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 2.png | file://x:/photopub/docs/0000000408/70791f6b-8e03-4ce9-8113-324aa5714b97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54e5ada0_c434_455e_ba82_3ebd634044dd
ELIN-545133-2016 | EL-269402-2015 | 3/21/2016 3:21:41 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found exposed conductors and bus bars on panelboards that are connected to power supply system which could easily become energized and hazardous and non-compliant once service is connected as contractor had declared and requested for service connection. When electrical conductors are exposed and energized with all panelboard covers missing and energized conductors could come in contact with people or property, the electrical system is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 11.png | file://x:/photopub/docs/0000000408/448d1b8e-a261-4a3a-8de9-82599025e1b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49336761_f28f_49db_8670_32d931a3d085
ELIN-545137-2016 | EL-291033-2015 | 3/21/2016 3:32:18 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found exposed conductors and bus bars on panelboards that are connected to power supply system which could easily become energized and hazardous and non-compliant once service is connected as contractor had declared and requested for service connection. When electrical conductors are exposed and energized with all panelboard covers missing and energized conductors could come in contact with people or property, the electrical system is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 12.png | file://x:/photopub/docs/0000000408/4c9afe51-a759-4c92-b306-3ddac4e62f62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0a11379_c421_4fa7_80ee_7957af4d841f
ELIN-545137-2016 | EL-291033-2015 | 3/21/2016 3:32:18 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found exposed conductors and bus bars on panelboards that are connected to power supply system which could easily become energized and hazardous and non-compliant once service is connected as contractor had declared and requested for service connection. When electrical conductors are exposed and energized with all panelboard covers missing and energized conductors could come in contact with people or property, the electrical system is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 13.png | file://x:/photopub/docs/0000000408/f6d33e5e-274c-49cf-9a10-f6a6d22e1008.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0a11379_c421_4fa7_80ee_7957af4d841f
ELIN-545133-2016 | EL-269402-2015 | 3/21/2016 3:21:41 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Found exposed conductors and bus bars on panelboards that are connected to power supply system which could easily become energized and hazardous and non-compliant once service is connected as contractor had declared and requested for service connection. When electrical conductors are exposed and energized with all panelboard covers missing and energized conductors could come in contact with people or property, the electrical system is a possible electrical fire or shock hazard to people and property. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 10.png | file://x:/photopub/docs/0000000408/ea710c41-21e0-4cca-8362-f5730b6b8eb0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49336761_f28f_49db_8670_32d931a3d085
BPVOP-506402-2016 | 4064808 | 3/9/2016 12:53:58 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. On this domestic hot water boiler the Safety Relief Valve is more than 6 years old. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately changed. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000402/5030cdf8-4ab4-4bfc-b33a-475992749109.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__925e4b2b_9d38_43e0_9a13_6e8f95d612d4
ELIN-557934-2016 | EL-372780-2016 | 4/19/2016 11:23:36 AM | ASSESS: EL: Final | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The bond conductor for two branch circuits were not connected. A fault in the circuits would not open the branch circuit breaker and could energize the metal parts of the electrical product which could shock a person if they touched the metal. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonds_not_connected.png | file://x:/photopub/docs/0000000418/8e68a62d-9ea1-405f-ad61-e05c311f4872.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e159ad40_c162_43c5_91d5_83a3228122e1
ELIN-549247-2016 | EL-356748-2016 | 3/29/2016 12:19:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Length of unfused service conductor inside pump house. Possible fire hazard if cable is damaged | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Photo_showing_service_conductor_inside_building.png | file://x:/photopub/docs/0000000408/4d9514aa-83d5-493c-9f10-5e4c9cd89434.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4997c7a8_dbe3_4a88_9bf4_e8d7a7744aa2
ELIN-543575-2016 | EL-360361-2016 | 3/14/2016 3:03:14 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found exposed energized branch circuit conductors for temporary wiring electrical equipment which are not supported and are not entered into a junction box with a cover plate and with proper supports as required by code. When energized exposed branch circuit conductors are not properly entered into a junction box with a cover and with proper support of the electrical equipment then this is an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 203.png | file://x:/photopub/docs/0000000404/32ce40ec-b65d-401a-b191-fa7ccaf2b9c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b615b4f_4fc2_4835_926f_2b1e9fb2b999
ELIN-543575-2016 | EL-360361-2016 | 3/14/2016 3:03:14 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found exposed energized branch circuit conductors for temporary wiring electrical equipment which are not supported and are not entered into a junction box with a cover plate and with proper supports as required by code. When energized exposed branch circuit conductors are not properly entered into a junction box with a cover and with proper support of the electrical equipment then this is an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 201.png | file://x:/photopub/docs/0000000404/ac773569-70b3-4110-8549-0275df217bc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b615b4f_4fc2_4835_926f_2b1e9fb2b999
ELIN-543575-2016 | EL-360361-2016 | 3/14/2016 3:03:14 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found exposed energized branch circuit conductors for temporary wiring electrical equipment which are not supported and are not entered into a junction box with a cover plate and with proper supports as required by code. When energized exposed branch circuit conductors are not properly entered into a junction box with a cover and with proper support of the electrical equipment then this is an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 202.png | file://x:/photopub/docs/0000000404/1dacbf52-2ebe-4ecd-b697-1222fb369be0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b615b4f_4fc2_4835_926f_2b1e9fb2b999
ELIN-543575-2016 | EL-360361-2016 | 3/14/2016 3:03:14 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Found exposed energized branch circuit conductors for temporary wiring electrical equipment which are not supported and are not entered into a junction box with a cover plate and with proper supports as required by code. When energized exposed branch circuit conductors are not properly entered into a junction box with a cover and with proper support of the electrical equipment then this is an electrical fire or shock hazard to people or property. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 200.png | file://x:/photopub/docs/0000000404/26492efa-f4f1-4112-a4ed-bef43a57a9ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b615b4f_4fc2_4835_926f_2b1e9fb2b999
ELIN-542898-2016 | EL-350425-2016 | 3/14/2016 12:04:00 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Furnace circuit cable has been installed without connector, jagged hole has been punched into the side of the furnace enclosure. Non metallic sheathed cable installed in this manner is susceptible to damage of the sheathing and conductor insulation. Energized conductors coming in contact with metal furnace enclosure poses a risk of fire, or shock to persons and property. | 3 | Conductors Equipment is not approved for the specific use. | Furnace_circuit_terminated_without_connector.png | file://x:/photopub/docs/0000000403/77d5c9de-bd62-4ffe-8a7c-9286bf451012.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7404fb8f_1ab8_451c_943f_36418800df41
ELIN-543985-2016 | EL-019590-2013 | 3/29/2016 1:15:05 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Branch circuit conductors are required to be terminated to branch circuit over current devices to protect the conductors, devices (receptacles and switches), fixtures, portable equipment plugged into receptacles, and hard wired equipment. This is required to prevent equipment from overloading and creating excessive thermal energy that the conductors and equipment connected to them are not designed to carry. This installation has new branch circuit wiring installed in a house for lighting and receptacles. The branch circuits are rated at 15A and are connected to 20A breakers. Left uncorrected this is a potential fire hazard if the branch circuit conductors and equipment connected to them become overloaded. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 20A_breakers_installed_for_15A_circuits_1_3_and_4.png | file://x:/photopub/docs/0000000408/4bd3689c-5496-462c-b09f-19ec703c4ec5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b37fb8_7ef8_46d5_a6cb_34eddc4a334a
ELIN-543985-2016 | EL-019590-2013 | 3/29/2016 1:15:05 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Branch circuit conductors are required to be terminated to branch circuit over current devices to protect the conductors, devices (receptacles and switches), fixtures, portable equipment plugged into receptacles, and hard wired equipment. This is required to prevent equipment from overloading and creating excessive thermal energy that the conductors and equipment connected to them are not designed to carry. This installation has new branch circuit wiring installed in a house for lighting and receptacles. The branch circuits are rated at 15A and are connected to 20A breakers. Left uncorrected this is a potential fire hazard if the branch circuit conductors and equipment connected to them become overloaded. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Front_of_house.png | file://x:/photopub/docs/0000000408/cfd864e1-5185-4708-87ec-c3eedff16498.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b37fb8_7ef8_46d5_a6cb_34eddc4a334a
ELIN-543985-2016 | EL-019590-2013 | 3/29/2016 1:15:05 PM | ASSESS: EL: Final | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Branch circuit conductors are required to be terminated to branch circuit over current devices to protect the conductors, devices (receptacles and switches), fixtures, portable equipment plugged into receptacles, and hard wired equipment. This is required to prevent equipment from overloading and creating excessive thermal energy that the conductors and equipment connected to them are not designed to carry. This installation has new branch circuit wiring installed in a house for lighting and receptacles. The branch circuits are rated at 15A and are connected to 20A breakers. Left uncorrected this is a potential fire hazard if the branch circuit conductors and equipment connected to them become overloaded. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 15A_conductor_on_20A_breaker_for_circuit_1_3_and_4.png | file://x:/photopub/docs/0000000408/3fbc1d3a-5a1a-41df-872a-da90f6e93a22.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6b37fb8_7ef8_46d5_a6cb_34eddc4a334a
ELIN-475923-2015 | EL-311392-2015 | 3/16/2016 3:06:04 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | 15 amp 120 volt receptacles are being utilized for multiple connections of branch wiring at outlet box locations. This could cause equipment damage and be a thermal hazard. | 3 | Conductors Equipment is not approved for the specific use. | Receptacle_without_pigtails.png | file://x:/photopub/docs/0000000405/ff635d53-9ed2-40f5-831a-e2a48fcdb9a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66b3404a_7d6e_4fa6_bc17_c701b50ff672
ELIN-546810-2016 | EL-360671-2016 | 3/29/2016 1:15:18 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Non metallic sheathed cable not terminated in an approved box. Wire nuts may fall of over time and if circuit is energized may provide a fire and shock hazard to persons or property. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | non_metallic_sheathed_cable_not_terminated_in_box_.png | file://x:/photopub/docs/0000000408/80548342-e12b-4c08-9844-a189bdcda436.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__219b4852_af22_4627_b602_522a1ba271f4
ELIN-570743-2016 | EL-270296-2015 | 5/17/2016 10:45:51 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Metal flex is not approved to work with 250 volt 60 amp male cord end. This could exceed the limits of conductor flexibility for temporary cord connected electrical equipment, which could cause electrical shock/harm to persons and properly. | 3 | General Equipment is not approved for the specific use | Make_cord_end.png | file://x:/photopub/docs/0000000430/1bdf6cf9-b342-47ae-b581-1e91094d57a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8183c06f_015d_4330_a80d_c2b3d7eea4d3
ELIN-570801-2016 | EL-360340-2016 | 5/5/2016 8:16:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found service conductors at service attachment device and service head are too close to metal down spout rain gutter and overhead service conductors would end up making direct contact with metal downspout rain gutters if hydro utility connects service supply system. When service is connected and energized and are in contact with building structure metal components, the metal components could become energized and this would be a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3.png | file://x:/photopub/docs/0000000427/a32bb78d-946f-406a-92e5-1525476b9aa1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e51442c_4f7e_4868_a068_181823f24c35
ELIN-570801-2016 | EL-360340-2016 | 5/5/2016 8:16:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found service conductors at service attachment device and service head are too close to metal down spout rain gutter and overhead service conductors would end up making direct contact with metal downspout rain gutters if hydro utility connects service supply system. When service is connected and energized and are in contact with building structure metal components, the metal components could become energized and this would be a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 2.png | file://x:/photopub/docs/0000000427/a842d04a-747b-461f-9157-3e4b40d4a7ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e51442c_4f7e_4868_a068_181823f24c35
ELIN-570801-2016 | EL-360340-2016 | 5/5/2016 8:16:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found service conductors at service attachment device and service head are too close to metal down spout rain gutter and overhead service conductors would end up making direct contact with metal downspout rain gutters if hydro utility connects service supply system. When service is connected and energized and are in contact with building structure metal components, the metal components could become energized and this would be a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 4.png | file://x:/photopub/docs/0000000427/714c2c81-1924-4bc1-b687-faf0bb52a818.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e51442c_4f7e_4868_a068_181823f24c35
ELIN-570801-2016 | EL-360340-2016 | 5/5/2016 8:16:06 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found service conductors at service attachment device and service head are too close to metal down spout rain gutter and overhead service conductors would end up making direct contact with metal downspout rain gutters if hydro utility connects service supply system. When service is connected and energized and are in contact with building structure metal components, the metal components could become energized and this would be a possible electrical fire or shock hazard to people and property. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 1.png | file://x:/photopub/docs/0000000427/983d12b7-64f0-4a54-bca6-e3fd2cccc6e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e51442c_4f7e_4868_a068_181823f24c35
ELIN-537317-2016 | EL-342427-2016 | 3/15/2016 5:21:08 PM | ASSESS: EL: Final | png | #asFound | EL066 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | View01_sub-distribution_in_structure.png | file://x:/photopub/docs/0000000404/e1aea2b4-f89c-4d9c-a7df-719acf5ed5d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db0bf2dd_af26_41fe_bfc5_7fcdd7130fd2
ELIN-537317-2016 | EL-342427-2016 | 3/15/2016 5:21:08 PM | ASSESS: EL: Final | png | #asFound | EL066 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | Protection and control Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | View01_A-side_micro_home.png | file://x:/photopub/docs/0000000404/a3b942f8-6c0c-4cca-977a-82a20998686d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db0bf2dd_af26_41fe_bfc5_7fcdd7130fd2
BPVIN-054811-2013 | BPV-037811-2013 | 4/11/2016 11:56:29 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | RELIEF_HORIZONTAL.png | file://x:/photopub/docs/0000000414/df4492bf-478f-41c9-ae3a-fcb85544bf44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba503fc3_01fa_4019_b1df_ac2a56e4db59
ELIN-554429-2016 | EL-334875-2016 | 4/8/2016 3:27:38 PM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Unprotected, energized bus work of electrical distribution equipment accessible to general public and not protected from effects of weather. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Detail02_sub-distribution.png | file://x:/photopub/docs/0000000415/889252ee-3653-4409-b625-5d54f7c7f691.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47120d23_b379_4275_a4f0_c50d3022e0cb
ELIN-554429-2016 | EL-334875-2016 | 4/8/2016 3:27:38 PM | ASSESS: EL: Final | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Unprotected, energized bus work of electrical distribution equipment accessible to general public and not protected from effects of weather. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | View01_sub-distribution.png | file://x:/photopub/docs/0000000415/39433728-10c3-4110-97fa-0442a93a0fa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47120d23_b379_4275_a4f0_c50d3022e0cb
ELIN-576750-2016 | UW-387150-2016 | 5/17/2016 3:29:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Open junction box with energized wires exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 1155_Ganske.png | file://x:/photopub/docs/0000000431/666e9234-5d1f-4c4e-9c84-866c4d19248d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79980b1c_1c85_4e70_aae6_55adbc72cb9a
ELIN-576750-2016 | UW-387150-2016 | 5/17/2016 3:29:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Open junction box with energized wires exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Kitchen.png | file://x:/photopub/docs/0000000431/f24cc177-56f4-497e-9f92-a460775c3e15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79980b1c_1c85_4e70_aae6_55adbc72cb9a
ELIN-576750-2016 | UW-387150-2016 | 5/17/2016 3:29:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Open junction box with energized wires exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | NMD_wiring_outdoors_.png | file://x:/photopub/docs/0000000431/63599034-7d6c-49e4-9b64-8ecd169ee43c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79980b1c_1c85_4e70_aae6_55adbc72cb9a
ELIN-529068-2016 | EL-340563-2016 | 2/29/2016 12:19:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | The 20 amp 120/240 volt main service panel does not have a 2pole breaker installed as per manufacturers approval label for service entrance requirements, this can lead to a shock hazard | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Service_installation.png | file://x:/photopub/docs/0000000398/1b4900eb-b34f-4a88-bc5e-938a08bcc4d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e2b032_1d5c_495b_bde7_fced9592cfb4
ELIN-529068-2016 | EL-340563-2016 | 2/29/2016 12:19:54 PM | ASSESS: EL: Service Connection | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | The 20 amp 120/240 volt main service panel does not have a 2pole breaker installed as per manufacturers approval label for service entrance requirements, this can lead to a shock hazard | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Manufacturers_approval_label.png | file://x:/photopub/docs/0000000398/dd1c0d94-1087-4f41-b84d-4961c7a0ac65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e2b032_1d5c_495b_bde7_fced9592cfb4
BPVIN-535988-2016 | UW-354305-2016 | 3/1/2016 12:03:04 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 2 | Upon assessment of Heat Exchanger with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject heat exchanger to pressure above MAWP if control fails or heat exchanger is operated inadvertently with valve on heat receiving side shut. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000398/8d744037-926b-41a4-b5c1-7f4b38a7d355.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96162000_e24a_4079_b083_decdff9e9a84
BPVOP-535924-2016 | 3505964 | 3/1/2016 1:17:18 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 7.7square meters, Maximus Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it is determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_relief_valve_of_boiler.png | file://x:/photopub/docs/0000000398/4cab34d7-4e8a-4853-aa9d-3d8dca1d5101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__222e953e_5d3b_47c7_a124_36e08111a261
ELIN-561318-2016 | EL-290663-2015 | 4/25/2016 11:27:27 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles to right and left of sink installed. Receptacle to the right is GFCI protected, the receptacle to the left is not on the same circuit and is not GFCI protected. Receptacles installed within 1.5 meters of wash basins are susceptible to splashing water, which may cause the water to come in contact with electrical equipment plugged into these receptacles. GFCI protected circuits identify an unbalance in circuits due to leakage of currents caused by the presence of water. Risk of shock and fire are present to persons and property without GFCI protection. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Non_gfci_receptacle_installed_within_1_5_meters_of_sink__.png | file://x:/photopub/docs/0000000420/8480a449-de37-4610-b977-e9cb6d029683.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87e3b5b3_776a_426d_91c6_eca25a523756
ELIN-551787-2016 | EL-368786-2016 | 4/1/2016 3:10:28 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | Energized cable located in dishwasher space, in kitchen of mobile home. Cable is not terminated to equipment or in a approved box with a cover. Cables left in this manner pose a risk of shock and fire to persons and property if energized conductors are accidentally come in contact with. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Armoured_cable_in_dishwasher_location_not_terminated_in_box_and_energized.png | file://x:/photopub/docs/0000000411/d4cf9328-bdff-435f-b9a2-490afac11c92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55017e8a_52a7_410f_af13_5634ba781be5
ELIN-565729-2016 | UW-379880-2016 | 4/25/2016 3:36:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Multiple #14AWG branch circuits terminated on a 50Amp GFCI 2P | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Ground_plate_not_installed_at_time_of_service_connection_.png | file://x:/photopub/docs/0000000420/f18022a9-3a4c-401e-ae3e-9f43469a5990.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3550a1_45d6_4409_848f_e848cc852e27
ELIN-565729-2016 | UW-379880-2016 | 4/25/2016 3:36:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Multiple #14AWG branch circuits terminated on a 50Amp GFCI 2P | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Multiple_circuits_50Amp_CB.png | file://x:/photopub/docs/0000000420/12156c12-491d-4091-8870-acfc055d8e49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3550a1_45d6_4409_848f_e848cc852e27
BPVOP-565567-2016 | 2285443 | 4/25/2016 11:42:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Safety_relief_valve_horizontal.png | file://x:/photopub/docs/0000000420/7f7bf37d-fbee-45b0-b84c-ef3d4f2f0657.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6af2e254_f6a8_4917_a6e0_1a9ab94c84b8
BPVOP-573291-2016 | BPV-152241-2014 | 5/4/2016 9:53:59 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | IMPROPER_INSTALLATION_OF_LWLCO.png | file://x:/photopub/docs/0000000428/b759012c-8a6d-4282-ba2d-c95c6d92bad2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0d471c6_ee13_42fa_84ee_12a5938c8e51
BPVOP-569542-2016 | 3781567 | 5/2/2016 10:59:14 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Upon assessment it is determined that machine mounted vertical air receiver (1.5m long and .51m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Safety_Valve.png | file://x:/photopub/docs/0000000428/fa0891d2-a3da-47fc-b205-0497abc15b75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aaea4c65_6ed2_4b7f_a5c7_cd54e762fcbd
ELIN-572141-2016 | UW-383683-2016 | 5/5/2016 3:03:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | No permit found for address. Temporary construction panel is not lockable and house is not at lock up stage, therefor accessible to public. Over current protection oversized for connected load. Temporary construction receptacle not protected by GFCI. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 5201_Norton_4.png | file://x:/photopub/docs/0000000425/6d598304-3395-4ca5-a888-f45606e225e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__447cc0e1_3dc1_46d2_8a9e_7bdcbd933e71
ELIN-572141-2016 | UW-383683-2016 | 5/5/2016 3:03:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | No permit found for address. Temporary construction panel is not lockable and house is not at lock up stage, therefor accessible to public. Over current protection oversized for connected load. Temporary construction receptacle not protected by GFCI. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 5201_Norton_1.png | file://x:/photopub/docs/0000000425/ffae7f60-608e-44da-a3ab-521cfbc50395.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__447cc0e1_3dc1_46d2_8a9e_7bdcbd933e71
ELIN-572141-2016 | UW-383683-2016 | 5/5/2016 3:03:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | No permit found for address. Temporary construction panel is not lockable and house is not at lock up stage, therefor accessible to public. Over current protection oversized for connected load. Temporary construction receptacle not protected by GFCI. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 5201_Norton_3.png | file://x:/photopub/docs/0000000425/fd4df14d-4a8f-434d-a91a-d23e4c1880c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__447cc0e1_3dc1_46d2_8a9e_7bdcbd933e71
ELIN-572141-2016 | UW-383683-2016 | 5/5/2016 3:03:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | No permit found for address. Temporary construction panel is not lockable and house is not at lock up stage, therefor accessible to public. Over current protection oversized for connected load. Temporary construction receptacle not protected by GFCI. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 5201_Norton_5.png | file://x:/photopub/docs/0000000425/420905ca-f92d-4270-b60f-c747f04080ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__447cc0e1_3dc1_46d2_8a9e_7bdcbd933e71
ELIN-572141-2016 | UW-383683-2016 | 5/5/2016 3:03:44 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | No permit found for address. Temporary construction panel is not lockable and house is not at lock up stage, therefor accessible to public. Over current protection oversized for connected load. Temporary construction receptacle not protected by GFCI. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 5201_Norton_2.png | file://x:/photopub/docs/0000000425/14db1a4d-fff7-4922-a0f4-393b09b9e12d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__447cc0e1_3dc1_46d2_8a9e_7bdcbd933e71
ELIN-557563-2016 | EL-374839-2016 | 4/12/2016 1:12:57 PM | ASSESS: EL: Service Connection | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | 125 amp, 120/240 volt main distribution panel located in garage has been exposed to smoke damage from fire in garage area. This has caused equipment damage to the electrical equipment. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Main_distribution_exposed_to_smoke_damage_from_fire_.png | file://x:/photopub/docs/0000000416/583ac35e-c02a-48b6-9798-90d3fd6cdebb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bb0971d_2675_4383_8b06_0542297a3386
ELIN-558439-2016 | EL-371698-2016 | 4/12/2016 1:00:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL048 | General Equipment is not protected from sprinklers in area. | 2 | 2 |  | 2 | General Equipment is not protected from sprinklers in area. | Detail02_main_distribution.png | file://x:/photopub/docs/0000000416/f8fc40e7-d296-42a3-a066-d258c22e1dc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ab16e4_d1b5_4f7f_b887_b00b87ec5ff6
ELIN-558439-2016 | EL-371698-2016 | 4/12/2016 1:00:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL048 | General Equipment is not protected from sprinklers in area. | 2 | 2 |  | 2 | General Equipment is not protected from sprinklers in area. | View01_main_distribution.png | file://x:/photopub/docs/0000000416/5d947598-117f-4b32-8e51-2f93f3940efc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__08ab16e4_d1b5_4f7f_b887_b00b87ec5ff6
GAUP-559638-2016 | UW-376397-2016 | 4/13/2016 12:00:28 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The as found hazard was an uncapped valve installed on a live gas piping system. This is a hazard because if the valve were to be accidentally opened or if it were to begin to leak propane gas would be allowed to escape into the living space. Risk of fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Red_tag_on_valve_and_piping_assembly.png | file://x:/photopub/docs/0000000416/b8d86b9e-5bfe-4fd1-8bba-6d00ab56ef47.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c682d5be_b034_4d82_93e0_05abc3cab47a
GAUP-559638-2016 | UW-376397-2016 | 4/13/2016 12:00:28 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The as found hazard was an uncapped valve installed on a live gas piping system. This is a hazard because if the valve were to be accidentally opened or if it were to begin to leak propane gas would be allowed to escape into the living space. Risk of fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | bus.png | file://x:/photopub/docs/0000000416/aca6771e-bd4a-4467-b302-33c64a30ddea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c682d5be_b034_4d82_93e0_05abc3cab47a
GAUP-559638-2016 | UW-376397-2016 | 4/13/2016 12:00:28 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The as found hazard was an uncapped valve installed on a live gas piping system. This is a hazard because if the valve were to be accidentally opened or if it were to begin to leak propane gas would be allowed to escape into the living space. Risk of fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | uncapped_valve.png | file://x:/photopub/docs/0000000416/9b60b890-156b-4c5e-88e6-915627cce3d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c682d5be_b034_4d82_93e0_05abc3cab47a
GAUP-559638-2016 | UW-376397-2016 | 4/13/2016 12:00:28 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The as found hazard was an uncapped valve installed on a live gas piping system. This is a hazard because if the valve were to be accidentally opened or if it were to begin to leak propane gas would be allowed to escape into the living space. Risk of fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | bus_and_cylinder.png | file://x:/photopub/docs/0000000416/d73235ca-ce2e-435b-b707-370e16ceae4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c682d5be_b034_4d82_93e0_05abc3cab47a
ELIN-560287-2016 | UW-376788-2016 | 4/14/2016 9:26:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Buildings with a service capacity or rating of 250 KVA or greater require an electrical operating permit for the operation and maintenance of the electrical system. This multi-residential seniors building has a service capacity of 432 KVA and does not currently have an electrical operating permit in place. An electrical operating permit is required to ensure the safe operation and maintenance of the electrical system at this facility. | 0 | No Created Hazard Identified | Front_entrance_of_seniors_buildng.png | file://x:/photopub/docs/0000000417/0d46de42-daae-4712-9410-7425528a4c19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a712d6dd_8aab_4bff_8746_a8b3da50e7b7
ELIN-560287-2016 | UW-376788-2016 | 4/14/2016 9:26:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Buildings with a service capacity or rating of 250 KVA or greater require an electrical operating permit for the operation and maintenance of the electrical system. This multi-residential seniors building has a service capacity of 432 KVA and does not currently have an electrical operating permit in place. An electrical operating permit is required to ensure the safe operation and maintenance of the electrical system at this facility. | 0 | No Created Hazard Identified | Exterior_of_seniors_building.png | file://x:/photopub/docs/0000000417/87c99e5c-d28d-495c-9d08-b1648ee0668e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a712d6dd_8aab_4bff_8746_a8b3da50e7b7
ELIN-571759-2016 | EL-269868-2015 | 5/10/2016 11:28:19 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | The 15 amp,120 volt floor boxes utilize unapproved boxes, this can lead to shock and equipment damage | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Plastic_floor_boxes.png | file://x:/photopub/docs/0000000428/e797d587-76d6-42b1-a115-eb78d00ef88a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31105ecc_89db_4ea1_a30b_11f17d6bdf88
ELIN-533651-2016 | UW-351408-2016 | 2/26/2016 3:53:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Multiple locations at this site have exposed energized conductors present. The locations are in areas that are restricted to authorized persons that are employed at this site. The presence of exposed energized conductors and equipment pose a shock, death, fire and damage to property and persons hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_conductors_present_and_not_protected.png | file://x:/photopub/docs/0000000397/f8c84932-dbd1-443b-b575-d2aa809fe5f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d518da8_7611_4840_a2ea_220a8460f647
ELIN-533651-2016 | UW-351408-2016 | 2/26/2016 3:53:00 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Multiple locations at this site have exposed energized conductors present. The locations are in areas that are restricted to authorized persons that are employed at this site. The presence of exposed energized conductors and equipment pose a shock, death, fire and damage to property and persons hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_energized_conductors_not_protected.png | file://x:/photopub/docs/0000000397/14ebddc3-5d8d-4727-90cb-7120bbd8b7fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d518da8_7611_4840_a2ea_220a8460f647
ELOP-226703-2014 | 1877 | 5/6/2016 7:55:39 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | In this marina installation the owner had obtained the services of four qualified contractors to wire floating salt water equipment. None were able to provide a safe environment. See attached photos. A marina contractor has now been hired to salvage this installation. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_fillers.png | file://x:/photopub/docs/0000000426/54b68e79-3dc6-4586-a3af-b05f439aaf7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66c7bbd9_5c1a_49ac_ad7f_e94134e632a4
ELIN-576750-2016 | UW-387150-2016 | 5/17/2016 3:29:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Open junction box with energized wires exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Outside_receptacle_open_ground.png | file://x:/photopub/docs/0000000431/b62b0cde-1f45-4b4c-af9a-2622335ef003.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79980b1c_1c85_4e70_aae6_55adbc72cb9a
ELIN-576750-2016 | UW-387150-2016 | 5/17/2016 3:29:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Open junction box with energized wires exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Meter_in_dwelling_unit.png | file://x:/photopub/docs/0000000431/4ab9754c-ed0c-46b3-aa53-51de35e502d8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79980b1c_1c85_4e70_aae6_55adbc72cb9a
ELIN-576750-2016 | UW-387150-2016 | 5/17/2016 3:29:22 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Open junction box with energized wires exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_junction_.png | file://x:/photopub/docs/0000000431/cff8acd5-a1d7-4091-a194-d6bc9f47c519.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__79980b1c_1c85_4e70_aae6_55adbc72cb9a
ELIN-580028-2016 | EL-317643-2015 | 5/19/2016 12:06:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15 amp receptacles installed outdoors. No GFCI protection on temporary construction receptacles. Three conductor number 14 Nmd 90 installed on 40 amp circuit breaker. Very high likelihood of an electrical fire or shock as a result of incorrect wiring method | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 15_amp.png | file://x:/photopub/docs/0000000432/f81d0bf7-8371-4b7c-a129-bbc4f975276a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d3a9701_4668_4688_bc66_f0642c2775f1
ELIN-580028-2016 | EL-317643-2015 | 5/19/2016 12:06:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15 amp receptacles installed outdoors. No GFCI protection on temporary construction receptacles. Three conductor number 14 Nmd 90 installed on 40 amp circuit breaker. Very high likelihood of an electrical fire or shock as a result of incorrect wiring method | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 40_amp__40_amp_circuit_breaker_Protecting_branch_circuit_wiring.png | file://x:/photopub/docs/0000000432/b69de831-8235-4071-89b6-cb811f6f0a68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d3a9701_4668_4688_bc66_f0642c2775f1
ELIN-580031-2016 | UW-389193-2016 | 5/19/2016 3:48:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | Energized open splice of conductors feeding hot water tank. The branch circuit wiring is terminated on a 60 amp breaker, but the conductors are only rated for 30 amps | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Open_splicing_of_branch_wiring.png | file://x:/photopub/docs/0000000432/fefaa75e-8338-4f8c-a8ec-e0b4ccefe96b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26009c31_5b3f_423b_aeec_89abd800a280
GAIN-560770-2016 | GA-353847-2016 | 5/13/2016 4:13:50 PM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | 1) A permanent fresh air supply from outdoors and sized in accordance with section 8 of the B149.1 gas code must be provided at an appliance. 2) A lack of fresh air is provided at the installed appliances 3) a lack of combustion air may cause an upset burner condition and possible unsafe operation and venting of the appliance. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 6_inch_passive_combustion_air_supply.png | file://x:/photopub/docs/0000000432/57c63851-4144-4b4b-9c9c-f0ae32f29c01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b661aa54_6629_4a80_abb8_d8b7a97280dd
ELIN-535829-2016 | EL-145214-2014 | 3/2/2016 2:02:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Pic2.png | file://x:/photopub/docs/0000000399/4fce12b1-a0d0-4bb7-9675-5a22135de8f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37183839_5663_4a62_ae32_399066540ad7
ELIN-535829-2016 | EL-145214-2014 | 3/2/2016 2:02:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Pic1.png | file://x:/photopub/docs/0000000399/187c2e17-f347-490c-8a2d-0214215f1473.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37183839_5663_4a62_ae32_399066540ad7
BPVOP-549390-2016 | 3620111 | 5/11/2016 3:35:14 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. I found a Safety Relief Valve on a Hot Water Boiler overdue by 4 years( installed 2006). Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_overdue.png | file://x:/photopub/docs/0000000429/23b863d8-9486-4b92-9b0c-aed803258e4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8b9b0c4_91fe_4d7a_96da_6d9dbbf4842b
ELIN-541387-2016 | EL-308392-2015 | 3/10/2016 9:46:43 AM | ASSESS: EL: Service Connection | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 200 amp, 120/240 volt main distribution panel greater then 100 millimetres in size only supported on one side. This is a thermal effect. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Panel_only_supported_on_one_side.png | file://x:/photopub/docs/0000000403/60778435-c9a8-484c-9470-c62ca7253cef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a3c7f72_7454_4456_8425_94869635e8a8
BPVOP-559953-2016 | BPV-0000324378-2015 | 4/14/2016 10:18:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scaling_.png | file://x:/photopub/docs/0000000416/c76611d5-89b4-4110-b46f-f857b0acf37f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30c06abb_8ff1_46d2_b988_913ff9e7e893
GAIN-576625-2016 | GA-295846-2015 | 5/16/2016 3:21:44 PM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | Piping_at_building.png | file://x:/photopub/docs/0000000430/4a131075-7403-487f-8214-92c32b4f2e2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8abea69d_d2fd_4aa0_9342_1efad1614505
GAIN-576625-2016 | GA-295846-2015 | 5/16/2016 3:21:44 PM | ASSESS: GA: Final | png | #asFound | GA039 | Painting of exterior piping | 1 | 1 |  | 1 | Painting of exterior piping | Meter_location.png | file://x:/photopub/docs/0000000430/bff87f70-bf53-47cc-9532-120a20f65f2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8abea69d_d2fd_4aa0_9342_1efad1614505
ELIN-580766-2016 | UW-389812-2016 | 5/20/2016 3:57:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 2.png | file://x:/photopub/docs/0000000432/922225fd-1ed1-430d-a9d0-ea98e1dfe50f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c45d8ed_2497_4e9d_86a3_4ef59b3cc201
ELIN-580766-2016 | UW-389812-2016 | 5/20/2016 3:57:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 4.png | file://x:/photopub/docs/0000000432/1ed5b035-c1e6-4353-aa25-52d69da867d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c45d8ed_2497_4e9d_86a3_4ef59b3cc201
ELIN-580766-2016 | UW-389812-2016 | 5/20/2016 3:57:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 1.png | file://x:/photopub/docs/0000000432/b0b1e221-8d6c-4e03-a68e-2c1a32720b49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c45d8ed_2497_4e9d_86a3_4ef59b3cc201
ELIN-580766-2016 | UW-389812-2016 | 5/20/2016 3:57:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 3.png | file://x:/photopub/docs/0000000432/0264cb57-0f3f-4b0f-b9cc-e63e71224b3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c45d8ed_2497_4e9d_86a3_4ef59b3cc201
ELIN-580766-2016 | UW-389812-2016 | 5/20/2016 3:57:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 5.png | file://x:/photopub/docs/0000000432/95219b7f-5508-496b-b1e6-dfa5a60b2f04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c45d8ed_2497_4e9d_86a3_4ef59b3cc201
ELIN-577618-2016 | EL-385986-2016 | 5/16/2016 1:48:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL134 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | 3 | 3 | Outlet boxes recessed back from wall finish cannot properly support the receptacle device | 3 | Installation of electrical equipment General: boxes in walls or ceilings are not flush (or within 6 mm of finished surface). | Outlet_boxes_not_flush_with_finished_wall.png | file://x:/photopub/docs/0000000430/df767252-a063-4079-9518-1f11091dbcda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69b1a89b_8964_46d7_ba55_a786fcf0c17f
ELIN-534396-2016 | EL-349575-2016 | 2/29/2016 1:44:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Metal interior gas line is not bonded to ground, bonding conductor is not installed from main panel. Interior gas lines require bonding to avoid gas lines from becoming energized in the case of accidental contact with energized conductors. A risk of shock,fire and damage to persons and property exists if not installed. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Interior_gas_line_not_bonded.png | file://x:/photopub/docs/0000000398/1cf52484-e7eb-43ee-9f65-011ede14b602.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__807b9e5e_f66d_4e55_a444_5b999535b362
ELIN-579202-2016 | EL-386334-2016 | 5/19/2016 10:55:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15 amp dry type receptacle has been installed outdoors, nonmetallic sheath cable is approved for indoor use only. 40 amp circuit breaker protecting 15 amp receptacle there's a strong likelihood Of an electrical shock and electrocution as the over current device will not trip. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Three_conductor___three_conductor_number_14_and_MD-90_cable_connected_to_40_amp_circuit_breaker.png | file://x:/photopub/docs/0000000432/bb0457a4-5997-4115-8800-5a6a672c430a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f6bf223_2139_4ddd_a917_45f86e592d25
ELIN-579202-2016 | EL-386334-2016 | 5/19/2016 10:55:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15 amp dry type receptacle has been installed outdoors, nonmetallic sheath cable is approved for indoor use only. 40 amp circuit breaker protecting 15 amp receptacle there's a strong likelihood Of an electrical shock and electrocution as the over current device will not trip. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Two___2_15_amp_receptacles_not_GFCI_protected.png | file://x:/photopub/docs/0000000432/255e3f18-ea17-4a26-a1e8-fe315637448e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f6bf223_2139_4ddd_a917_45f86e592d25
ELIN-579201-2016 | EL-386334-2016 | 5/19/2016 11:28:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Bonding between the mast and metre base has not been completed. Very high likelihood of an arc fault fire at this point because the current has no path back to ground. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Bonding_gym__bonding_Jam_screw_not_tightened.png | file://x:/photopub/docs/0000000432/871767dd-8763-4d44-9ed1-bd259bea0afe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93215ca1_03a7_4e2a_a95e_0cf5d56aaf6c
ELIN-573350-2016 | EL-383820-2016 | 5/13/2016 4:02:31 PM | ASSESS: EL: Final | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | The bond conductor of a sub feed cable supplying a 40 amp load centre was terminated by simply being wrapped around a stud in the load centre rather than being terminated securely with an approved lug. Under a fault condition, this unreliable bond connection may have prevented overcurrent devices from functioning properly resulting in a potential shock hazard. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Sub_feed_bond_conductor_wrapped_around_stud_in_load_centre.png | file://x:/photopub/docs/0000000432/a4702900-e326-4097-99ad-a39bae51c9ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66f79f51_01aa_407d_8269_6f9df6ea4bcb
ELIN-580029-2016 | UW-389185-2016 | 5/17/2016 12:34:21 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Knock out filers missing from panel, bare bus is exposed. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A.png | file://x:/photopub/docs/0000000432/11debd84-6f1d-4690-a72a-ce24e57c096d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__24f49741_ea7b_4814_949a_2344e7b696cc
BPVOP-530646-2016 | 2264962 | 3/11/2016 2:46:14 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this hot water heating boiler for the last 13 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Old_pressure_relief_device_.png | file://x:/photopub/docs/0000000403/b446ebae-5c11-44e6-ac9c-07d9ba3b08d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97d67e12_4555_4a2d_8459_ea0807adcb8d
ELIN-565090-2016 | EL-329953-2015 | 4/25/2016 9:48:51 AM | ASSESS: EL: Final | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Unprotected portions of consumer service raceway have been concealed without prior submission of request for inspection. Without verification of proper burial depths and adequate means of mechanical protection being put in place there is an increased potential for serious personal injury (shock) and property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_meterbases_2323_Belair.png | file://x:/photopub/docs/0000000422/4f09d3ab-049b-4a63-b4a4-3e920965506c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2486b04c_41e6_4a8f_899d_c461978590aa
ELIN-565089-2016 | EL-329954-2015 | 4/25/2016 11:45:13 AM | ASSESS: EL: Final | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Receptacles not installed in open wall space to required spacing limits. This leads to the potential of personal injury (shock) or property damage (thermal event) due to misuse of flexible cords. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | View_01_laundry_room.png | file://x:/photopub/docs/0000000422/26d7d234-2a23-4fc1-80f4-a7eec6e66b3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb43dcda_6a52_4a15_80f1_c55db19da17f
ELOP-191782-2014 | 5184924 | 5/5/2016 1:28:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Breaker slots are open and exposed the main panel bus that can be a shock hazard if a person should contact the bus. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_spa_backroom.png | file://x:/photopub/docs/0000000426/a289c05e-cac2-4486-ae6f-a0622a2ef40d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d2719c6_e0f8_42ee_9948_f838b7307c13
ELOP-191782-2014 | 5184924 | 5/5/2016 1:28:10 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Breaker slots are open and exposed the main panel bus that can be a shock hazard if a person should contact the bus. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | HVAC_panel.png | file://x:/photopub/docs/0000000426/ac53f109-8471-4bf2-9374-2548f53c321f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d2719c6_e0f8_42ee_9948_f838b7307c13
ELOP-226639-2014 | 6056 | 5/19/2016 2:57:11 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Electrical services are designed to be contained in continuous raceways to avoid accidental contact and to minimize water intrusion. In this installation a PVC raceway had pulled apart on the service pole. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | PVC_apart.png | file://x:/photopub/docs/0000000432/822ef6c7-d9cf-4a7d-9565-2bdbf9e02623.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dce9571f_d09e_490c_9143_0980cb8f585a
ELOP-226597-2014 | 6070 | 5/19/2016 9:54:01 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not to be used as a replacement for permanent wiring. In this fire hall the 911 TV monitor was fed with a long extension cord. | 4 | Conductors, Misuse of flexible cords. | Extension_cord.png | file://x:/photopub/docs/0000000432/ff43e99e-0bf7-4300-b95b-1c0039b3d84f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6024cd2_f320_4516_82e0_0e65bc7cd1a1
ELIN-540605-2016 | EL-270021-2015 | 3/9/2016 1:24:53 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Cable is not mechanically protected from damage and is in contact with heating equipment. Cable in this condition may get mechanically damaged causing short circuit, shock and fire. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Cable-1.png | file://x:/photopub/docs/0000000402/7923279d-89a4-48e8-9533-b52791fedfb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb364864_2e1f_4d94_912f_333caa431533
ELIN-573696-2016 | EL-382261-2016 | 5/11/2016 10:42:34 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 20A 120V outlets have been provided for construction use but have not been GFCI protected, this could result in a shock hazard or equipment damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Temporary_outlets.png | file://x:/photopub/docs/0000000428/ed0f73b7-6333-4aff-b72c-67aaffadd434.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75548181_2d4e_497a_8621_13512a03a625
ELIN-573819-2016 | EL-371155-2016 | 5/11/2016 12:28:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Triplex_travellin__triplex_travelling_through_tree_branches.png | file://x:/photopub/docs/0000000428/541d3060-ea76-4ce6-a6ae-5be17ae1b498.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd8a31b_7fcb_4ec8_8b75_93ccd26ac7a6
ELIN-573819-2016 | EL-371155-2016 | 5/11/2016 12:28:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Existing_triplex__existing_triplex_has_been_cut_by_others.png | file://x:/photopub/docs/0000000428/a936c1d7-85c1-4eda-aa43-15529520e0fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd8a31b_7fcb_4ec8_8b75_93ccd26ac7a6
ELIN-573819-2016 | EL-371155-2016 | 5/11/2016 12:28:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Existing_triplex.png | file://x:/photopub/docs/0000000428/80346490-f459-42d2-b5a1-fe613121744d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd8a31b_7fcb_4ec8_8b75_93ccd26ac7a6
ELOP-535819-2016 | 3807554 | 3/1/2016 12:34:48 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | A compressor control assembly operating at 208 volts, 30 amps 3 phase was found with a cover missing. This left open live electrical terminals exposed to the walkway through the equipment room. This room was found accessible to unauthorized persons. Persons were left exposed to real potential for electric shock or worse | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Cover_missing_open_live_conductors_accessible_to_unauthorized_persons.png | file://x:/photopub/docs/0000000399/852533a7-55f4-4a29-b1f9-d64f47826709.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__032cfc2d_048c_449f_9a5b_a54b60456c49
ELIN-528809-2016 | EL-284378-2015 | 3/1/2016 8:54:23 AM | ASSESS: EL: Final | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | A 200 amp 600 V three-phase delta sub distribution raceway to a step down transformer has a number six bonding conductor installed in raceway. this conductor is undersized in accordance with minimum requirements. overcurrent devices can fail to react predictably when bonding is not correctly sized and installed and can lead to shock or fire hazard. | 2 | Continuity Bonding; conductor is not properly sized. | 6_copper_bond_230_amp_rated_conductors.png | file://x:/photopub/docs/0000000399/ced90c64-8330-486a-bde5-eddf6fc27e15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9ef5f99_5d60_49a0_9d4b_20f085b2465c
ELIN-535667-2016 | EL-324653-2015 | 3/1/2016 7:06:07 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 4 | A 208 volt 3 phase 250 kva generator was connected to a 4 conductor ACWU cable. There was no means to make a permanent connection of the cable to the generator. Aluminum conductors were terminated in lugs that were not marked for use with aluminum conductors and the specific nature of the lugs physically damaged the conductors. The area was accessible to the general public. Property damage or potential injury to persons can occur with these hazards present. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Copper_only_specific_duty_lugs_show_damaged_strands_.png | file://x:/photopub/docs/0000000399/d937e293-44eb-4a91-b9a5-0ca0927730eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59f90444_12e8_4105_bf67_6200fc4e9ea4
ELIN-535667-2016 | EL-324653-2015 | 3/1/2016 7:06:07 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 4 | A 208 volt 3 phase 250 kva generator was connected to a 4 conductor ACWU cable. There was no means to make a permanent connection of the cable to the generator. Aluminum conductors were terminated in lugs that were not marked for use with aluminum conductors and the specific nature of the lugs physically damaged the conductors. The area was accessible to the general public. Property damage or potential injury to persons can occur with these hazards present. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Cable_laying_on_grade_no_strain_relief_or_termination_means.png | file://x:/photopub/docs/0000000399/396436ea-7b26-46ef-b109-ac318be27b2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__59f90444_12e8_4105_bf67_6200fc4e9ea4
ELIN-572507-2016 | EL-351638-2016 | 5/9/2016 1:15:18 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200A 240V permanent Main Panel has been installed for temporary power use but is not protected from the weather or unauthorized use, this could result in equipment damage and a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_Panel.png | file://x:/photopub/docs/0000000427/a2382f42-47fc-40ad-a533-d02745e51153.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73b880f2_679a_439f_b6da_0f06db13062f
ELIN-571043-2016 | EL-377672-2016 | 5/9/2016 3:36:55 PM | ASSESS: EL: Final | png | #asFound | EL081 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | 40A 240V armoured metal cable has not been terminated with a fitting, the continuity of the armour has not been maintained, this could result in a shock hazard or equipment damage. | 3 | Installation Electrical and mechanical continuity for metal raceways or enclosures is not continuous | Fitting.png | file://x:/photopub/docs/0000000427/ed799462-142c-4a63-9b06-9df04d0d28b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e02f46c_a55b_4eb1_a3be_18c9c2f04b98
ELIN-571562-2016 | EL-345311-2016 | 5/9/2016 8:50:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected consumer service cabling exceeds 1.5m inside structure, exposing the cabling to increased risk of mechanical damage during and after construction. This has the potential for serious personal injury (shock) or property damage (thermal event,). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View02_main_distribution.png | file://x:/photopub/docs/0000000427/3006473f-a8d6-4f06-b06b-6771d6ac966e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__701c136d_e579_457f_aa92_cc9ecdbc0a20
ELIN-573052-2016 | EL-345311-2016 | 5/9/2016 5:12:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected consumer service cabling exceeds 1.5m inside structure, exposing the cabling to increased risk of mechanical damage during and after construction. This has the potential for serious personal injury (shock) or property damage (thermal event,). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View02_main_distribution_.png | file://x:/photopub/docs/0000000427/87212945-b5f8-4902-8490-321abf8d312d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__841656c6_12a5_4ed7_9536_dbee7d50383f
ELIN-571562-2016 | EL-345311-2016 | 5/9/2016 8:50:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected consumer service cabling exceeds 1.5m inside structure, exposing the cabling to increased risk of mechanical damage during and after construction. This has the potential for serious personal injury (shock) or property damage (thermal event,). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_meter_base.png | file://x:/photopub/docs/0000000427/b9b8f11e-c03a-42d9-9c69-183862010cfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__701c136d_e579_457f_aa92_cc9ecdbc0a20
ELIN-571591-2016 | EL-305686-2015 | 5/9/2016 6:21:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 2 | Consumer service mast for overhead utility supply service conductor attachment point is secured to structure with two out of three required support clamps. This increases the risk of property damage (thermal event) due to failure of the mast support components. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | View01_mast.png | file://x:/photopub/docs/0000000427/3dcceb6a-13b5-4536-a149-3366e80f250d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9059d27f_5af8_4489_bbf6_ed3b7c5aac1c
ELIN-573052-2016 | EL-345311-2016 | 5/9/2016 5:12:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unprotected consumer service cabling exceeds 1.5m inside structure, exposing the cabling to increased risk of mechanical damage during and after construction. This has the potential for serious personal injury (shock) or property damage (thermal event,). | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_meter_base_.png | file://x:/photopub/docs/0000000427/f0b92f60-afc7-4f35-8fb9-13e0423ca573.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__841656c6_12a5_4ed7_9536_dbee7d50383f
ELIN-568590-2016 | EL-287163-2015 | 5/9/2016 5:58:22 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | The use of 15 amp 120 volt non- tamper resistant outlets in the house can creat a shock hazard | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Receptacles.png | file://x:/photopub/docs/0000000427/005a8b2b-a79b-4475-91b8-f5e8a1f7342f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f16919d_5c5c_4d84_b332_197f2b03ec0d
ELIN-554954-2016 | EL-284441-2015 | 5/9/2016 9:40:52 PM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | The 15 amp 120 volt exterior light fixture junction box has no light fixture installed and has exposed wires. This is both a shock and equipment damage concern. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Exterior_light.png | file://x:/photopub/docs/0000000427/fb1b2d94-e5ed-43fd-9047-e6d1bc00eb54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90ce2fe8_400b_4230_8c0f_a45925c82c27
ELOP-226599-2014 | 6075 | 5/19/2016 10:28:51 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Radio towers must be bonded to ground. In this fire hall a tower had been installed by the bond conductor was omitted. | 3 | Continuity Bonding conductor is not observed or broken | No_bond.png | file://x:/photopub/docs/0000000432/8b996167-507b-4a88-bfd1-0d31faea6664.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e73674c5_5a02_4f1b_a88d_888a5844bfc8
ELOP-198869-2014 | 2383 | 5/19/2016 9:08:00 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unused openings in electrical equipment must be closed to avoid accidental contact. In this municipal building a panel filler in a large panel had fallen out making it possible to reach in and touch a live bus bar. The electrical room is only accessible to authorized personnel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Taped_over.png | file://x:/photopub/docs/0000000432/a2ee178f-5561-43a9-a832-6ac7205db119.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd35f146_50d0_4bad_9741_102a29f4716c
ELOP-267338-2014 | 7243 | 5/19/2016 11:34:47 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles within 1.5 m of sinks must be GFCI protected. In this sewage treatment plant lab a sink was added where existing receptacles are not GFCI protected. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_gfci.png | file://x:/photopub/docs/0000000432/aeb9bc3f-c4bb-42aa-a15a-d34b724bbed6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e284ccc_62da_4027_a8e3_577fe4989459
ELIN-540952-2016 | EL-249553-2015 | 3/21/2016 2:39:58 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 15 amp, 120 volt switch bank is missing cover plate. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_missing.png | file://x:/photopub/docs/0000000406/3ff03f01-d9e7-42ee-a8c6-d5fc154d0177.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b30dbb04_47d3_46d5_b6fe_074606f2a0d1
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 105.png | file://x:/photopub/docs/0000000432/3cd11d16-c93c-4a5c-85fd-a0d40a04cf24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 100.png | file://x:/photopub/docs/0000000432/3a4d9a08-984c-437d-9274-cc5c6a16c91a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 104.png | file://x:/photopub/docs/0000000432/011ba489-903b-46fa-b863-6246b8e472c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 106.png | file://x:/photopub/docs/0000000432/2235eab5-3a7d-4326-8812-b5bf2bb256f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 109.png | file://x:/photopub/docs/0000000432/1c02b390-39db-4017-aba2-ff151b23f157.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 107.png | file://x:/photopub/docs/0000000432/68bc75f2-1b78-4f34-85ab-b54fe654bd27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 103.png | file://x:/photopub/docs/0000000432/93e3cfc7-35d3-4955-a969-89add91d0baf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 108.png | file://x:/photopub/docs/0000000432/5ffb6676-6cc7-40ca-8d27-2aa443e35a7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 101.png | file://x:/photopub/docs/0000000432/0d6b2e58-3a27-4d17-8e45-95cd39b023e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
ELIN-575488-2016 | EL-377189-2016 | 5/19/2016 1:35:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found that main consumer's service, rated 600 volts 200 amps 3phase, is not grounded in service equipment with a grounding conductor and electrode connected to consumer's service neutral conductor bus bar as required by code. When service equipment is not grounded within service equipment as required by code, then there is the potential any fault current will take a path that is not safe and the system is not designed for and could could cause an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 102.png | file://x:/photopub/docs/0000000432/de71f79d-282c-4d11-96ea-2c1df0771441.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__606822d7_4e2a_4a21_8296_e49e2ad37e07
BPVIN-575529-2016 | BPV-386420-2016 | 5/17/2016 7:26:12 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 4 | Every pressure retaining component of a regulated equipment or pressure piping must be provided with a suitable pressure relief device in order to protect from over pressurization and possible rupture. I did not find a the pressure relief device on a high pressure air receiver (125psi). Potential exists for an incident due to a missing overpressure protection device. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | No_pressure_relief_devices.png | file://x:/photopub/docs/0000000431/11946896-60b7-497d-886a-6391fe228995.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4450bd2_b82c_49f0_ac93_8237b28cc58d
ELIN-578664-2016 | EL-349017-2016 | 5/19/2016 2:02:52 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Service panel is not protected from the weather. This could result in breakers getting wet and not operating properly | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_exposed_to_weather.png | file://x:/photopub/docs/0000000432/d2d17066-73d4-41a6-9cb8-be118baa0c1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18d62e60_8210_4281_9968_490019e4c328
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red2.png | file://x:/photopub/docs/0000000432/97b4913e-76d9-4a08-a6e3-1793991d2b8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red9.png | file://x:/photopub/docs/0000000432/344709e5-4f08-49e2-a59b-bf8351568bd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red3.png | file://x:/photopub/docs/0000000432/4734017b-14fa-47fe-b64c-78374e7a9aea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red8.png | file://x:/photopub/docs/0000000432/3cca9115-6560-46fe-acda-925cc7d32309.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red7.png | file://x:/photopub/docs/0000000432/bc7ec31d-c29e-4f9b-b069-e52abd80bc86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red_1.png | file://x:/photopub/docs/0000000432/23e4e14b-49c7-410d-9d85-f6d15d8e8e9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red6.png | file://x:/photopub/docs/0000000432/95baef6c-3096-4aa3-9854-979cd989c65e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
GAHE-580279-2016 | HE-367907-2016 | 5/19/2016 3:43:52 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Combustible materials around unit and no access to the burner or electrical cabinet or the gas shutoff valve. This is a hazard as unit drawing air into building, and if unit needs to be turned off can't get to the gas valve. | 2 | Appliance installed in a proposed hazardous location | Red4.png | file://x:/photopub/docs/0000000432/1907eb26-35b2-4d6b-9b25-71dce9bb077d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4066e2_3ece_4d28_a600_7a6c53b41751
ELIN-572836-2016 | EL-371910-2016 | 5/9/2016 2:27:38 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Energized 240 v residential temporary Subdistribution centre panel not mounted upright and susceptible to damage and debris which may create unsafe condition and potential fire hazard. | 3 | General Equipment is not approved for the specific use | Haker.png | file://x:/photopub/docs/0000000427/f0cb7c8a-d1b5-4ef4-8556-8a08440e804b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ec3cec9_6c13_4477_8bad_e383e532a2e3
ELOP-192790-2014 | EL-086052-2014 | 4/27/2016 4:18:09 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Volt_storage.png | file://x:/photopub/docs/0000000422/44109bb9-aac9-4cd9-981c-1e9dce1ec099.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf9943f7_ca9f_4b35_a70e_494f391aaa2d
ELOP-192790-2014 | EL-086052-2014 | 4/27/2016 4:18:09 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Ground_relay.png | file://x:/photopub/docs/0000000422/7c22fdbb-47f4-4dfa-9b9c-5b1640eba22c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf9943f7_ca9f_4b35_a70e_494f391aaa2d
ELIN-533686-2016 | EL-311499-2015 | 2/26/2016 12:44:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 100 amp, 120/240 volt non-metallic sheathed cable ran through metal studs without mechanical protection from metal stud edge. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD90_running_through_metal_stud.png | file://x:/photopub/docs/0000000397/4de1be59-0762-405e-aeb9-251fd4b3f1a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8422f156_14e9_4841_ab30_22f4d06fc0c5
ELIN-569273-2016 | EL-381995-2016 | 5/19/2016 5:48:33 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Energized receptacles installed in an exterior location, accessible to general public and exposed to the effects of weather not provided with adequate cover plates. This presents a risk of personal injury (shock) or property damage (thermal event/interface fire). | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Detail01_receptacles.png | file://x:/photopub/docs/0000000432/4d6f9695-79d2-4bcc-b960-98750e645e63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f49ada3_6e09_4c0f_bf5b_b0b5ae15b0c5
ELIN-579520-2016 | EL-388227-2016 | 5/19/2016 11:06:20 AM | ASSESS: EL: Final | png | #asFound | EL235 | Class II, all locations Markings | 1 | 1 |  | 1 | Class II, all locations Markings | Label.png | file://x:/photopub/docs/0000000432/d2838c59-0684-41a3-b96f-d8c4233082e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0bbc112_9ba3_4f35_b57b_c2551c827998
ELIN-579520-2016 | EL-388227-2016 | 5/19/2016 11:06:20 AM | ASSESS: EL: Final | png | #asFound | EL235 | Class II, all locations Markings | 1 | 1 |  | 1 | Class II, all locations Markings | Box.png | file://x:/photopub/docs/0000000432/3e0fc9b9-9957-4438-93c9-2335bee4292a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0bbc112_9ba3_4f35_b57b_c2551c827998
ELIN-579520-2016 | EL-388227-2016 | 5/19/2016 11:06:20 AM | ASSESS: EL: Final | png | #asFound | EL235 | Class II, all locations Markings | 1 | 1 |  | 1 | Class II, all locations Markings | Raceway_2.png | file://x:/photopub/docs/0000000432/49764936-2677-4edc-af85-189e292eb418.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0bbc112_9ba3_4f35_b57b_c2551c827998
ELIN-579520-2016 | EL-388227-2016 | 5/19/2016 11:06:20 AM | ASSESS: EL: Final | png | #asFound | EL235 | Class II, all locations Markings | 1 | 1 |  | 1 | Class II, all locations Markings | Raceway_3.png | file://x:/photopub/docs/0000000432/279b88b7-2e88-4cae-8385-1a9d78238815.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0bbc112_9ba3_4f35_b57b_c2551c827998
ELIN-579520-2016 | EL-388227-2016 | 5/19/2016 11:06:20 AM | ASSESS: EL: Final | png | #asFound | EL235 | Class II, all locations Markings | 1 | 1 |  | 1 | Class II, all locations Markings | Raceway.png | file://x:/photopub/docs/0000000432/164517fc-4be5-4af6-93fe-05077f454309.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0bbc112_9ba3_4f35_b57b_c2551c827998
ELIN-579520-2016 | EL-388227-2016 | 5/19/2016 11:06:20 AM | ASSESS: EL: Final | png | #asFound | EL235 | Class II, all locations Markings | 1 | 1 |  | 1 | Class II, all locations Markings | Raceway_.png | file://x:/photopub/docs/0000000432/17f9048e-2129-4e26-b7f6-0566444a5cf1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0bbc112_9ba3_4f35_b57b_c2551c827998
ELIN-547057-2016 | EL-289862-2015 | 3/22/2016 1:43:37 PM | ASSESS: EL: Final | png | #asFound | EL165 | Protection and control Overload is not properly sized. | 3 | 3 | 20A 240V A/C unit has a max breaker size indicated but this has been exceeded by the contractor. Equipment damage is possible as breaker may not operate as it's not sized to the manufacturers recommendations. | 3 | Protection and control Overload is not properly sized. | Nameplate.png | file://x:/photopub/docs/0000000407/fc6413cc-9fcc-4eb6-80f6-4d6f424b5a65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d39d3821_933b_43fe_b7dd_0d07ef756697
ELIN-574305-2016 | EL-315072-2015 | 5/12/2016 2:34:38 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Switch.png | file://x:/photopub/docs/0000000429/253a32a3-ec98-4fb6-b6b7-852b2cc66ac1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d67987de_9e46_426d_8c70_eee326d046b0
ELIN-574305-2016 | EL-315072-2015 | 5/12/2016 2:34:38 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Transformer.png | file://x:/photopub/docs/0000000429/84226dd9-df71-4bd6-836d-d897aa93e623.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d67987de_9e46_426d_8c70_eee326d046b0
ELIN-574305-2016 | EL-315072-2015 | 5/12/2016 2:34:38 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 3R_equipment.png | file://x:/photopub/docs/0000000429/0a1ea51f-e200-4314-815a-81fe2b3e58e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d67987de_9e46_426d_8c70_eee326d046b0
ELIN-546396-2016 | EL-214702-2015 | 3/21/2016 11:41:36 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazards | 3 | Equipment Gas line, cast or water pipe has not been bonded | Open_box-1.png | file://x:/photopub/docs/0000000406/856b6a11-07b6-477e-a7b7-a96cbb9aaab3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecee5ae4_f691_4383_9c61_915be179d864
ELIN-546396-2016 | EL-214702-2015 | 3/21/2016 11:41:36 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazards | 3 | Equipment Gas line, cast or water pipe has not been bonded | Open_box-2.png | file://x:/photopub/docs/0000000406/7560b1ad-8459-465b-9997-471a8902348d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecee5ae4_f691_4383_9c61_915be179d864
ELIN-546396-2016 | EL-214702-2015 | 3/21/2016 11:41:36 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazards | 3 | Equipment Gas line, cast or water pipe has not been bonded | Open-KO_1.png | file://x:/photopub/docs/0000000406/7e1b6d94-80d4-4f45-a0d0-4a233b5d5373.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecee5ae4_f691_4383_9c61_915be179d864
ELIN-546396-2016 | EL-214702-2015 | 3/21/2016 11:41:36 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazards | 3 | Equipment Gas line, cast or water pipe has not been bonded | Loosecable-1.png | file://x:/photopub/docs/0000000406/fe2d00f9-b342-4b7f-8799-1b9698737d17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecee5ae4_f691_4383_9c61_915be179d864
ELIN-546396-2016 | EL-214702-2015 | 3/21/2016 11:41:36 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazards | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gasline.png | file://x:/photopub/docs/0000000406/c7dde486-5c96-4d8d-b4b6-4d567cf86315.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecee5ae4_f691_4383_9c61_915be179d864
ELIN-546396-2016 | EL-214702-2015 | 3/21/2016 11:41:36 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Shock hazards | 3 | Equipment Gas line, cast or water pipe has not been bonded | Ext-cable.png | file://x:/photopub/docs/0000000406/84536876-8d9b-415c-973a-d3a73738150c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecee5ae4_f691_4383_9c61_915be179d864
BPVOP-517490-2016 | 2302127 | 5/19/2016 12:21:12 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valve not this low pressure hot water boiler (30 PSI) since 2002. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Old_pressure_relief_device_.png | file://x:/photopub/docs/0000000432/b88fdaa3-1b03-4ffe-88ac-9b34947b432d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67c4ec41_39b3_452a_913d_6d841a57d20d
ELIN-575405-2016 | EL-343678-2016 | 5/19/2016 1:06:55 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Approved wet location covers have not been provided for exterior 120v receptacles | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_receptacles_on_detached_garage.png | file://x:/photopub/docs/0000000432/18454409-84ee-4352-80ac-453e666b0dba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11a21b2d_34a7_4274_b72e_d4fc3b775cd3
ELIN-574625-2016 | 5376005 | 5/18/2016 5:47:45 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found bonding conductor hanging mid air inside junction box while this bonding conductor is not spliced or connected to branch circuit bonding conductor splice made in box. All electrical equipment is not bonded or spliced properly with a good solid splice connection. When electrical equipment is not bonded fully and properly as required by code, the electrical equipment could become an electrical fire or shock hazard if there is no good solid bonding path for carrying fault current so that over-current devices immediately trip in a fault condition. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Bonding_conductor_not_terminated_properly_and_came_apart_or_not_connected.png | file://x:/photopub/docs/0000000431/b7e93588-b180-49f4-a92f-857327c0f2fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f05f2c7e_5c8b_4af7_8dae_57fd90d6e836
GAIN-529214-2016 | GA-293322-2015 | 3/23/2016 10:02:36 AM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Upon inspection I found no combustion air supply present in the mechanical room. When the boiler turns on the flame will starve of air causing the stack temperature and carbon monoxide to rise outside of acceptable limits. This creates the potential for a fire or carbon monoxide poisoning. | 4 | Combustion air supply missing | Mechanical_room1.png | file://x:/photopub/docs/0000000407/3ff8331f-3b8b-4859-929a-2ca3369147fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12b32502_3439_47e1_b9c8_96fcdd4c1f08
GAIN-529214-2016 | GA-293322-2015 | 3/23/2016 10:02:36 AM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Upon inspection I found no combustion air supply present in the mechanical room. When the boiler turns on the flame will starve of air causing the stack temperature and carbon monoxide to rise outside of acceptable limits. This creates the potential for a fire or carbon monoxide poisoning. | 4 | Combustion air supply missing | Mechanical_room2.png | file://x:/photopub/docs/0000000407/82640295-eecf-4766-8c97-1e7a289e23a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12b32502_3439_47e1_b9c8_96fcdd4c1f08
GAIN-529214-2016 | GA-293322-2015 | 3/23/2016 10:02:36 AM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Upon inspection I found no combustion air supply present in the mechanical room. When the boiler turns on the flame will starve of air causing the stack temperature and carbon monoxide to rise outside of acceptable limits. This creates the potential for a fire or carbon monoxide poisoning. | 4 | Combustion air supply missing | Mechanical_room3.png | file://x:/photopub/docs/0000000407/613bcab4-1b6b-43ff-9006-0b091d35ed26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12b32502_3439_47e1_b9c8_96fcdd4c1f08
AMOP-547959-2016 | 3808795 | 3/22/2016 10:21:27 AM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | On this ride the seat belts are used as a secondary restraining device in the passenger cars, the lap bar is the primary restraining device. During a periodic inspection of the Super Sizzler at its first set up for 2016, many of the seat belts were found to be worn and in need of replacement. Failure of a seat belt during operation could increase the chance of a passenger being ejected from the passenger car. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Worn_Seat_Belt.png | file://x:/photopub/docs/0000000407/0087e94f-b2fb-490b-bacc-313300d7b3f3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23f27399_d933_44af_8445_ccb2cddaf41c
ELIN-543700-2016 | EL-345073-2016 | 3/21/2016 12:15:10 PM | ASSESS: EL: Service Connection | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | A 120/240 volt single phase, 400 amp fused disconnect has a second neutral/ground point connection installed. The main ground connection to the neutral point has been installed at the 400 amp meterbase location. Should a fault occur, this could cause equipment damage and is a thermal hazard. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Bond_conductors_to_neutral.png | file://x:/photopub/docs/0000000406/9ab26024-abd9-43d8-aa22-57495b232592.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fbca1977_a219_44bd_91b6_60ae1f5c7faf
ELIN-567231-2016 | EL-279448-2015 | 4/28/2016 12:03:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Service equipment grounding conductor is not grounded at service entrance equipment, i.e. Duplex meter base. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Service.png | file://x:/photopub/docs/0000000422/05b6c5fd-4832-4a0b-b60f-03b3695e02fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__788eb4ae_616f_4bb6_bc96_b91a512b1616
ELIN-567125-2016 | EL-270604-2015 | 4/28/2016 3:52:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Potential fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cable-534br2.png | file://x:/photopub/docs/0000000422/6681ccf7-93e6-475c-8626-1b649e79f059.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fbb17f6_4bf9_4c9d_a39e_fbb33821ce45
ELIN-580005-2016 | UW-389131-2016 | 5/18/2016 5:10:36 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Found junction box with missing cover plate above office ceiling space and has energized insulated conductors that are exposed. When energized insulated conductors are exposed from within a junction box that is missing a cover plate, the electrical equipment is a possible electrical fire or shock hazard to people or property if people or other building structure components come in contact with energized insulated conductors and cause a fault condition. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Exposed_insulated_conductors_energized_in_box_that_has_missing_cover_plate.png | file://x:/photopub/docs/0000000432/743b4298-8277-4f0b-adcf-574918730fa0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2c52321_1534_4e4a_a66a_228a6a73bbb4
BPVIN-576402-2016 | BPV-036092-2013 | 5/13/2016 2:49:49 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | The electrical power switch for the boiler can not be LOCKED in the OPEN or OFF position. The power switch may inadvertently be turned on when the boiler is being serviced and possibly causing a serious accident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Lock_out_switch.png | file://x:/photopub/docs/0000000431/5539e0c5-037e-4ee8-8417-afd18ca7514f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cd0c6e2_0f5f_487a_9694_6dcbfbd8b74a
ELIN-538214-2016 | EL-291547-2015 | 3/10/2016 12:16:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in an area that is a hazardous location. This could result in a fire or explosion. | 3 | Conductors Equipment is not approved for the specific use. | emt_and_pit_lighting.png | file://x:/photopub/docs/0000000402/ac625751-88c0-4e63-a05c-193dd128bd5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__693728fa_6187_4c62_9849_f9f7f0b93275
ELIN-538214-2016 | EL-291547-2015 | 3/10/2016 12:16:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in an area that is a hazardous location. This could result in a fire or explosion. | 3 | Conductors Equipment is not approved for the specific use. | Receptacles_in__pit.png | file://x:/photopub/docs/0000000402/0b7d5530-16fc-41ee-a6a9-a87aca7aacc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__693728fa_6187_4c62_9849_f9f7f0b93275
ELIN-538214-2016 | EL-291547-2015 | 3/10/2016 12:16:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Ordinary location wiring methods are being used in an area that is a hazardous location. This could result in a fire or explosion. | 3 | Conductors Equipment is not approved for the specific use. | Lubrication_room___lubrication_room_and_stairs_to_pit.png | file://x:/photopub/docs/0000000402/b668fac0-325e-48a8-935a-ebf4cacef191.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__693728fa_6187_4c62_9849_f9f7f0b93275
ELIN-554053-2016 | UW-372378-2016 | 4/4/2016 3:32:32 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Covers not installed on main distribution equipment in multi-unit residential structure, resulting in energized supply service conductor terminations accessible to general public. This presents the risk of serious personal injury (shock) or property damage (thermal event). | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | View01_main_distribution.png | file://x:/photopub/docs/0000000415/47df7225-f238-4291-a0c1-c72d124dd47d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__085723ed_33ab_449c_9a4e_e3f2b29b4f5d
GAIN-554476-2016 | GA-332023-2016 | 4/5/2016 10:49:50 AM | ASSESS: GA: Final | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 4 | A live gas piping system must have all outlets capped or plugged when not connected to an appliance. Shut- off valve for gas range was found in off position however the valve outlet was not capped or plugged. The range shut off valve could be accidentally hit or bumped by workers opening the valve allowing gas to flow freely in to the new construction home. Gas could leak undetected and build up to flammable levels possibly leading to damage to structure or harm to individuals. | 5 | Open gas line connected to fuel supply (no cap/plug) | Regulator_vent_limiter.png | file://x:/photopub/docs/0000000415/93f71497-ab3b-48dd-b023-65fa804460e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bda51f56_8332_49c0_9f62_ed63960ce6bd
GAIN-554476-2016 | GA-332023-2016 | 4/5/2016 10:49:50 AM | ASSESS: GA: Final | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 4 | A live gas piping system must have all outlets capped or plugged when not connected to an appliance. Shut- off valve for gas range was found in off position however the valve outlet was not capped or plugged. The range shut off valve could be accidentally hit or bumped by workers opening the valve allowing gas to flow freely in to the new construction home. Gas could leak undetected and build up to flammable levels possibly leading to damage to structure or harm to individuals. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_gas_valve_outlet_.png | file://x:/photopub/docs/0000000415/d44a7111-f88b-484b-aa5a-6e7b8315e476.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bda51f56_8332_49c0_9f62_ed63960ce6bd
GAIN-554476-2016 | GA-332023-2016 | 4/5/2016 10:49:50 AM | ASSESS: GA: Final | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 4 | A live gas piping system must have all outlets capped or plugged when not connected to an appliance. Shut- off valve for gas range was found in off position however the valve outlet was not capped or plugged. The range shut off valve could be accidentally hit or bumped by workers opening the valve allowing gas to flow freely in to the new construction home. Gas could leak undetected and build up to flammable levels possibly leading to damage to structure or harm to individuals. | 5 | Open gas line connected to fuel supply (no cap/plug) | Vent_pipe_support_spacing.png | file://x:/photopub/docs/0000000415/311af81e-1d20-4aa8-9386-b2e36cd613b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bda51f56_8332_49c0_9f62_ed63960ce6bd
GAIN-552627-2016 | GA-367978-2016 | 4/6/2016 10:10:04 AM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | All appliances with a input exceeding 400,000 but require combustion and ventilation. Combustion air not present, mechanical air supply not functioning, air flow not proven or interlocked. Lack of combustion air may create an upset or negative air pressure condition in the mechanical room. This could effect the appliance main burner operation and prevent the venting action of any atmospheric appliance in the room. | 4 | Combustion air supply missing | Combustion_air_missing__.png | file://x:/photopub/docs/0000000415/24fb61e4-cf33-4122-bf90-7f40455381bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6de01624_4063_4979_9a60_33f854bd9dff
ELIN-513672-2016 | EL-307776-2015 | 1/22/2016 2:48:25 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Transformer_location.png | file://x:/photopub/docs/0000000401/99210ae0-d7b2-4edc-ae42-79e4d740f83e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fc7643c_9164_4346_8b6b_0e004f042ee4
ELIN-513672-2016 | EL-307776-2015 | 1/22/2016 2:48:25 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Pump_house_wiring.png | file://x:/photopub/docs/0000000401/f3abe481-2816-45ce-a7cd-c229250ddc49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fc7643c_9164_4346_8b6b_0e004f042ee4
ELIN-513672-2016 | EL-307776-2015 | 1/22/2016 2:48:25 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | UG_Raceways.png | file://x:/photopub/docs/0000000401/ed9df853-43a9-4ada-9b20-886a11afb64b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fc7643c_9164_4346_8b6b_0e004f042ee4
ELIN-513672-2016 | EL-307776-2015 | 1/22/2016 2:48:25 PM | ASSESS: EL: Final | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Transformer_spec.png | file://x:/photopub/docs/0000000401/e2519399-11bd-4b22-8888-daa23daaacd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2fc7643c_9164_4346_8b6b_0e004f042ee4
BPVIN-561962-2016 | BPV-355406-2016 | 5/3/2016 12:06:37 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of a hot water boiler with Maximum Allowable Working Pressure (MAWP) of 160psig and Maximum Allowable Working Temperature (MAWT) 250*Fahrenheit and heating surface of 24 square meters, it was determined that safety relief valves were installed with the spindle in the horizontal position. Safety relief valves may stick and fail to properly function when operated in this position. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_1_with_safety_valve_spindle_horizontal.png | file://x:/photopub/docs/0000000424/7fd5b63f-1829-4828-8803-62e5c54b7b53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c40b33b_e023_4870_9b43_338b45623c4c
ELIN-551202-2016 | EL-347398-2016 | 4/21/2016 3:19:44 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 1 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Unprotected_conductors.png | file://x:/photopub/docs/0000000419/32eb1b9e-9e8e-4ee4-b756-6323a6fff3e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2e1fc6c_468f_42b9_99fb_58680fead540
ELIN-551202-2016 | EL-347398-2016 | 4/21/2016 3:19:44 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 1 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Mislabelled_panel.png | file://x:/photopub/docs/0000000419/0c3f4f85-f07c-454c-92c4-c7dda27327a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2e1fc6c_468f_42b9_99fb_58680fead540
ELIN-564321-2016 | EL-342680-2016 | 4/22/2016 9:00:45 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | 15 amp, 120 volt non-metallic sheathed cable is embedded in concrete. This is a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | NMD90_in_encased_in_concrete.png | file://x:/photopub/docs/0000000419/ca8ff35e-cd09-4997-89cf-099176a1b80f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__778ec18a_9898_4f26_a715_1515540d5cc4
ELIN-540963-2016 | EL-337701-2016 | 3/14/2016 12:41:02 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Type SJOOW cable is not approved for use in concealed locations. | 3 | Conductors Equipment is not approved for the specific use. | sjoow.png | file://x:/photopub/docs/0000000403/13e68268-9ef3-4e15-a97d-10d38356414e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df94ca92_83e5_4a3d_975b_c97a0e34aaa5
ELIN-548653-2016 | UW-369470-2016 | 3/18/2016 12:00:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | 240 v overhead Subdistribution nsf cables at mobile home park showing evidence of insulation deterioration from uv exposure and requires repair. Failure can lead to electrical fault and fire. | 3 | General Equipment is not approved for the specific use | 2.png | file://x:/photopub/docs/0000000407/b38da8ce-3d6d-4e9d-9882-0e630f95de5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0169b1a_2ade_4036_9bed_d1ef6e1141b1
ELIN-548653-2016 | UW-369470-2016 | 3/18/2016 12:00:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | 240 v overhead Subdistribution nsf cables at mobile home park showing evidence of insulation deterioration from uv exposure and requires repair. Failure can lead to electrical fault and fire. | 3 | General Equipment is not approved for the specific use | 3.png | file://x:/photopub/docs/0000000407/487d38ab-95ba-4223-bf68-27a18ee44274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0169b1a_2ade_4036_9bed_d1ef6e1141b1
ELIN-548653-2016 | UW-369470-2016 | 3/18/2016 12:00:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | 240 v overhead Subdistribution nsf cables at mobile home park showing evidence of insulation deterioration from uv exposure and requires repair. Failure can lead to electrical fault and fire. | 3 | General Equipment is not approved for the specific use | 1.png | file://x:/photopub/docs/0000000407/e1d3a84a-0a85-4e3b-a76e-cbca741e74c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0169b1a_2ade_4036_9bed_d1ef6e1141b1
ELIN-548653-2016 | UW-369470-2016 | 3/18/2016 12:00:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | 240 v overhead Subdistribution nsf cables at mobile home park showing evidence of insulation deterioration from uv exposure and requires repair. Failure can lead to electrical fault and fire. | 3 | General Equipment is not approved for the specific use | 5.png | file://x:/photopub/docs/0000000407/9581de0f-c9c4-4b8b-ae36-aee59ce8ced2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0169b1a_2ade_4036_9bed_d1ef6e1141b1
ELIN-548653-2016 | UW-369470-2016 | 3/18/2016 12:00:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 4 | 240 v overhead Subdistribution nsf cables at mobile home park showing evidence of insulation deterioration from uv exposure and requires repair. Failure can lead to electrical fault and fire. | 3 | General Equipment is not approved for the specific use | 4.png | file://x:/photopub/docs/0000000407/ebe06acb-d285-435f-9e42-1bc5d32e1747.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0169b1a_2ade_4036_9bed_d1ef6e1141b1
ELIN-532860-2016 | EL-350515-2016 | 2/29/2016 2:03:07 PM | ASSESS: EL: Final | png | #asFound | EL093 | Continuity Grounding conductor has been spliced | 2 | 2 |  | 2 | Continuity Grounding conductor has been spliced | Grounding.png | file://x:/photopub/docs/0000000398/4789f3c7-01b8-4445-9841-98c0ca35e0f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a36f3f97_a7f1_42cf_aef5_8c31b6f7ecf8
ELIN-569743-2016 | EL-332769-2016 | 5/4/2016 6:51:44 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | Luminaire's located in basement suite are not protected from mechanical damage below 2.1 meters. The luminaire could break if bumped into. This could become a shock/burn hazard if the luminaire breaks. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Fixtures_located_below_2_1_meters.png | file://x:/photopub/docs/0000000424/8ba9d2df-b40c-4510-bf2e-56992ab2dccd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b444a056_8ea2_4bf7_892b_032850b15058
ELIN-568071-2016 | EL-228469-2015 | 5/4/2016 11:52:16 AM | ASSESS: EL: Final | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | In dwelling unit number two the receptacle and switch outlet located by the main entry was obstructed by wood trim. This is hazard because all electrical equipment must have accessibility as per electrical code requirements. | 3 | Installation of electrical equipment General: boxes are not accessible. | Receptacle_blocked_by_trim.png | file://x:/photopub/docs/0000000424/9dc77bda-250a-4b35-a82e-84ac0860c852.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94b337da_b3c6_41ea_aec2_91bafeb4ecd1
ELIN-568071-2016 | EL-228469-2015 | 5/4/2016 11:52:16 AM | ASSESS: EL: Final | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | In dwelling unit number two the receptacle and switch outlet located by the main entry was obstructed by wood trim. This is hazard because all electrical equipment must have accessibility as per electrical code requirements. | 3 | Installation of electrical equipment General: boxes are not accessible. | Switch_blocked_by_trim.png | file://x:/photopub/docs/0000000424/62366189-8875-484e-824b-0b07e4af8fb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94b337da_b3c6_41ea_aec2_91bafeb4ecd1
ELIN-552746-2016 | EL-336011-2016 | 4/5/2016 12:50:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 15 amp, 120 volt, # 12 AWG non-metallic sheathed cables are installed with 32 mm of surface framing. A screw or nail could cause damage to the conductors. This is a thermal concern. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_wiring_within_32_mm_of_surface_framing.png | file://x:/photopub/docs/0000000412/e8a26ce4-f959-41bf-84ed-5719e4d32b72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7ab8916_414d_47dc_aa2d_6f303f7a274f
ELIN-569766-2016 | EL-320342-2015 | 5/6/2016 4:17:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | This assessment found the BC Hydro pull box being bonded via standard locknuts and bolts. This type of service equipment is to be bonded more substantial with the use of bonding jumpers between pieces of equipment. There is a shock hazard when improperly bonded equipment doesn't allow breakers to see a fault and trip as intended. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Wireways_bonding.png | file://x:/photopub/docs/0000000426/0d3be401-2c58-4748-91c5-925723470893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1947b01f_b2c0_4326_8206_51ea9295559f
ELIN-571676-2016 | EL-333863-2016 | 4/29/2016 3:21:01 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | -approx. 27cables- 3 copper conductor #12 awg armoured cables installed in open ladder tray. Due to the multiple cables in contact with each other the conductors have a derating multiplier of .50 making each conductor rated at 12.5 amps due to possible overheating. the conductors are only protected by a 15 amp breaker thus making the conductor unprotected causing possible thermal break down of the conductor insulation. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | ladder_cable_tray.png | file://x:/photopub/docs/0000000427/69fd9cd2-142d-48ea-9e30-cca5af8b7830.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8f1aa735_e156_495c_a15f_e845eda518ab
BPVOP-567307-2016 | 3058895 | 4/27/2016 2:58:20 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 17.10 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000421/7476171c-6a23-40d2-b92b-c1b152ae4ff1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c204745_4376_4528_81ed_17d22307d80a
BPVOP-567296-2016 | 3058880 | 4/27/2016 2:22:56 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 17.10 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000421/dc0b704a-a871-49e4-a2c9-40ddbd8f9329.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfb165ba_532d_4979_9184_894ce2242214
ELOP-556969-2016 | EL-374474-2016 | 3/10/2016 3:17:17 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Unused openings in energized electrical enclosures must be filled to avoid accidental contact. In this installation panel fillers had been omitted when circuit breakers were installed in a sewage lift kiosk. The kiosk is not normally accessible. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | FPE_panel_fillers_missing.png | file://x:/photopub/docs/0000000417/ead3d78a-6d24-44d0-b282-19efd42e6465.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bff9cd71_8d5c_43ad_be8a_5715f3d25d5a
BPVOP-548529-2016 | 2287375 | 3/23/2016 1:22:29 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 | Inactive corrosion was noted with camera. | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | PHOTOGRAPH_WITH_ENDOSCOPE.png | file://x:/photopub/docs/0000000408/86fa744b-b9c7-48e8-9596-90b316a7c92f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e499070d_86d3_4585_8eac_48c1f80f5157
BPVOP-548537-2016 | 2260843 | 3/23/2016 11:24:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment it is determined that pressure and temperature rating of valve on blow off line is not rated to code. Valve may fail early in service due to type of stress valve sustain in service. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | QUICK_OPENING_BLOW_OFF_VALVE.png | file://x:/photopub/docs/0000000408/e7e028ce-9952-4a47-99d9-c75c90ca7a8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e472f7c_3832_4de5_814f_9f4c8f3d9c46
GAIN-539614-2016 | UW-356934-2016 | 3/2/2016 5:52:53 PM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Gas riser should be outside of building instead of coming up through the floor. In the event of a underground gas leak. The gas could go directly into the building instead of on the exterior of the building | 3 | Code prohibited practices or materials | Flynn_Rd_4.png | file://x:/photopub/docs/0000000402/3bfc6c0c-6e35-45f7-80d5-a4a27a302a33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d9b87c_0c68_4aee_86c8_cd236bc7dad0
GAIN-539614-2016 | UW-356934-2016 | 3/2/2016 5:52:53 PM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Gas riser should be outside of building instead of coming up through the floor. In the event of a underground gas leak. The gas could go directly into the building instead of on the exterior of the building | 3 | Code prohibited practices or materials | Flynn_Rd.png | file://x:/photopub/docs/0000000402/28680672-35d7-4ebf-a7d6-22df413cc87e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d9b87c_0c68_4aee_86c8_cd236bc7dad0
GAIN-539614-2016 | UW-356934-2016 | 3/2/2016 5:52:53 PM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Gas riser should be outside of building instead of coming up through the floor. In the event of a underground gas leak. The gas could go directly into the building instead of on the exterior of the building | 3 | Code prohibited practices or materials | Flynn_Rd_2.png | file://x:/photopub/docs/0000000402/b4047456-3a29-4169-87a8-430e0ecee9f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d9b87c_0c68_4aee_86c8_cd236bc7dad0
GAIN-539614-2016 | UW-356934-2016 | 3/2/2016 5:52:53 PM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | Gas riser should be outside of building instead of coming up through the floor. In the event of a underground gas leak. The gas could go directly into the building instead of on the exterior of the building | 3 | Code prohibited practices or materials | Flynn_Rd_3.png | file://x:/photopub/docs/0000000402/b008ed8b-8d98-47b2-9100-a6e88325afcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37d9b87c_0c68_4aee_86c8_cd236bc7dad0
BPVIN-548714-2016 | UW-369494-2016 | 3/23/2016 3:54:53 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 4 | A pressure vessel must be operated within it's design pressure limit. I found a non ASME expansion tank rated for 30 psig operating in a hot water system with 2 Safety Relief Valves set at 45 psig. Potential exists for an incident because of excessive pressure conditions that the expansion tank sustains. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 45_psig_Safety_Relief_Valves.png | file://x:/photopub/docs/0000000407/076e9b1a-ca6c-4545-b60d-d2be51769c72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3e4237_16b7_48e7_8447_6965881a6b6e
BPVIN-548714-2016 | UW-369494-2016 | 3/23/2016 3:54:53 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP001 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 5 | 4 | A pressure vessel must be operated within it's design pressure limit. I found a non ASME expansion tank rated for 30 psig operating in a hot water system with 2 Safety Relief Valves set at 45 psig. Potential exists for an incident because of excessive pressure conditions that the expansion tank sustains. | 5 | 1.0.1 Temp/Pressure ratings not met - Maximum Allowable Working Pressure of the pressure retaining items(s) less than set pressure of the safety relief device | 30_PSI_expansion_tank.png | file://x:/photopub/docs/0000000407/5f1120bf-4c91-486b-aa3f-a20b6eef960e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3e4237_16b7_48e7_8447_6965881a6b6e
ELIN-531617-2016 | EL-343435-2016 | 3/8/2016 2:44:12 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | A new residential service rated 200 amps 240 volt single phase was authorized for connection. The service panel was located inside a structure with no roof or permanent roof membrane installed. The service was also accessible to unauthorized access. The panel and components can be permanently damaged should water enter panel or circuit breakers including the main disconnect. Water damaged overcurrent devices may fail to react predictably as a result of this damage and create a hazard for persons or a potential for property damage. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel_not_lockable_or_weatherproof.png | file://x:/photopub/docs/0000000402/3dfed781-f725-4d90-ad11-5fb213df841c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5688e0ed_31d7_40af_99bb_b9b7241464aa
GAUP-556946-2016 | UW-374596-2016 | 4/8/2016 4:46:33 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 4 | The as found hazard was an on-demand water heater which had its venting partially dislodged from the appliance. This is a hazard because if the appliance were put into operation the products of combustion would enter the living space creating a high risk of carbon monoxide poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Vent_termination.png | file://x:/photopub/docs/0000000414/e4b878ae-c559-4265-b253-5748ea32aa17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdb2ea72_5c9c_4f10_8fd0_982b1e3792b7
ELIN-540904-2016 | EL-359574-2016 | 3/10/2016 1:44:03 PM | ASSESS: EL: Service Connection | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Weatherproof cover is only partially installed , box plate is installed and the cover is missing. Receptacles exposed to weather provide a risk of leakage currents as well it may cause gfci receptacles to repeatedly trip and be reset causing strain on receptacle internal components. Both are a risk of shock, fire and damage to persons or property. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Weather_proof_cover_missing_from_receptacles.png | file://x:/photopub/docs/0000000402/0e297115-5d65-41ca-bfb7-be897a4563d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9d050fca_82e0_4a6d_a480_bfb23c998534
GAIN-498364-2015 | GA-288927-2015 | 3/22/2016 8:02:07 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | Roll out safety switch had been removed and signs of over heating. This could create a hazard if the burners are over fired or blocked, no device to shut the heater off. | 4 | Missing mandatory safety controls | Limit2.png | file://x:/photopub/docs/0000000407/e8d198ee-9d19-41df-bbe4-13f5f80f7373.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6ef86ae_e716_453d_a352_b548e6742267
GAIN-498364-2015 | GA-288927-2015 | 3/22/2016 8:02:07 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | Roll out safety switch had been removed and signs of over heating. This could create a hazard if the burners are over fired or blocked, no device to shut the heater off. | 4 | Missing mandatory safety controls | Heater1.png | file://x:/photopub/docs/0000000407/a7812d72-5b59-4508-a2ab-7ba8ea68a15e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6ef86ae_e716_453d_a352_b548e6742267
GAIN-494816-2015 | GA-320261-2015 | 3/22/2016 10:23:42 AM | ASSESS: GA: Final | png | #asFound | GA079 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | 3 | 3 | At time of inspection observed 2 PSIG deliver from gas meter and no regulator in the system to deliver inches water column. This could create a hazard as the appliance could be overfired | 3 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | M.png | file://x:/photopub/docs/0000000407/f9fbe869-d986-421c-badb-f53f8fc89f9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bc8a2db_517d_40d5_a112_e96394b7f0fa
GAIN-494816-2015 | GA-320261-2015 | 3/22/2016 10:23:42 AM | ASSESS: GA: Final | png | #asFound | GA079 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | 3 | 3 | At time of inspection observed 2 PSIG deliver from gas meter and no regulator in the system to deliver inches water column. This could create a hazard as the appliance could be overfired | 3 | Over ½ psig inlet line pressure regulator of the non-positive shut off type | W.png | file://x:/photopub/docs/0000000407/ded9aa87-8fab-4222-86fc-c0666ea65884.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bc8a2db_517d_40d5_a112_e96394b7f0fa
GAIN-498364-2015 | GA-288927-2015 | 3/22/2016 8:02:07 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | Roll out safety switch had been removed and signs of over heating. This could create a hazard if the burners are over fired or blocked, no device to shut the heater off. | 4 | Missing mandatory safety controls | Limit1.png | file://x:/photopub/docs/0000000407/6267ead6-14e8-43f5-a4bf-bed545d904a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6ef86ae_e716_453d_a352_b548e6742267
ELIN-543969-2016 | EL-349567-2016 | 3/22/2016 10:56:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The main 200 amp 120/240 volt service compartment does not include the incentivized conductor extended from the supply side. Secondly the ground conductor terminates only to the equipment and not to the indentified conductor termination point. Should a fault occur, the fault cannot complete its path back to the source and will rely on the ground conductor, this is a shock hazard and could lead to equipment damage as well. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Main_service_1.png | file://x:/photopub/docs/0000000407/b8d6b869-adee-4d4e-878d-cc4523136600.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36c9d20a_125a_4a8c_8d53_bab17e6c7ca7
ELIN-543969-2016 | EL-349567-2016 | 3/22/2016 10:56:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL083 | Continuity Separately derived system, communication or similar system has not been properly grounded | 4 | 4 | The main 200 amp 120/240 volt service compartment does not include the incentivized conductor extended from the supply side. Secondly the ground conductor terminates only to the equipment and not to the indentified conductor termination point. Should a fault occur, the fault cannot complete its path back to the source and will rely on the ground conductor, this is a shock hazard and could lead to equipment damage as well. | 4 | Continuity Separately derived system, communication or similar system has not been properly grounded | Main_ground.png | file://x:/photopub/docs/0000000407/ea220f1b-d889-43ba-b5cb-c07321c8a7b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__36c9d20a_125a_4a8c_8d53_bab17e6c7ca7
BPVOP-572687-2016 | 4345695 | 5/6/2016 10:55:06 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Boiler_tubes_water_side_.png | file://x:/photopub/docs/0000000427/6dbef124-0661-4147-bf0c-ce450a52f146.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8b893f8_1bf2_4fbf_800d_08b2d8c1f10d
ELIN-533688-2016 | EL-308951-2015 | 2/26/2016 12:04:28 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | 15A 120V non-metallic-sheathed cable passes through steel beams without protection from abrasion. This could result in damage to the cable a shock hazard and eventual failure of the cable. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD.png | file://x:/photopub/docs/0000000396/d7235c64-63b3-4b2c-8e11-175212c2685b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3529305_954c_4169_81de_1dffdd64b586
ELOP-196649-2014 | 5266224 | 2/26/2016 1:04:43 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | Electrical equipment must be maintained in safe working order. In this installation a plywood enclosure has been damaged exposing the main service switchgear to a salty marine environment. The equipment has failed both internally and externally. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Interior.png | file://x:/photopub/docs/0000000397/8025125c-50c4-4f3a-a4b1-2a005df3e082.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51e7ee54_af68_487a_aa84_cb59c9e1754e
ELOP-226734-2014 | 1867 | 2/26/2016 11:27:19 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Poles carrying electrical cables outside must be kept in safe working order. In this installation one pole has deteriorated at the top to the point it could fail. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Top_gone.png | file://x:/photopub/docs/0000000397/b01faa30-ed19-480e-95e7-404f7ed692f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aabc2a92_a6c9_4abc_b895_2dbe4b1c4f59
ELOP-196649-2014 | 5266224 | 2/26/2016 1:04:43 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 4 | Electrical equipment must be maintained in safe working order. In this installation a plywood enclosure has been damaged exposing the main service switchgear to a salty marine environment. The equipment has failed both internally and externally. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Exterior.png | file://x:/photopub/docs/0000000397/4befce16-36f5-447a-8d98-4b2b7fac9783.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51e7ee54_af68_487a_aa84_cb59c9e1754e
ELIN-546666-2016 | EL-190125-2014 | 3/23/2016 10:19:07 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A GFCI outlet has not been provided by the laundry sink, this poses a shock hazard to persons using the outlet if an appliance was in use and the sink was full of water. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Laundry_Outlet.png | file://x:/photopub/docs/0000000407/bd07f7f8-f551-4fc4-8397-513b01a001a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c221600_80e8_48c9_98c1_0324ba5da54a
ELIN-559890-2016 | EL-289942-2015 | 4/14/2016 6:20:59 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 4 | This assessment found an ungrounded electrical supply without a ground fault detection device. This type of supply is required to be equipped with a "ground fault detection device" so that persons know the status of the system before a shock hazard becomes present. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Main_panel.png | file://x:/photopub/docs/0000000417/61da8a04-2f6e-4994-8d6c-11378f44daca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2b11b6b_a0d6_4c66_bfc2_80da1d4cbbf0
AMOP-549179-2016 | 2047259 | 3/24/2016 9:47:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | The lap bar is used to ensure riders stay inside the passenger carrier while the ride is operating. This lap bar has a left and a right side latch on it. During a periodic inspection, it was found that the left side latch of the lap bar was no engaging correctly and the lap bar was being secured closed by one latch. If the right side latch failed the lap bar could open during operation and possibly eject the passenger for the carrier. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Lap_Bar_Passenger_Carrier.png | file://x:/photopub/docs/0000000408/621966d7-e3e3-4002-b510-f0d55001eb7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afbd5017_751e_4548_baec_6d0e23094abc
AMOP-549180-2016 | 2044758 | 3/23/2016 10:02:21 AM | ASSESS: AM OP: Periodic | png | #asFound | AM031 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | The electrical controls and wiring of an amusement ride must be in safe working condition. During an inspection of this ride, the power cable to the control box was found to be in need of repair, additionally the circuit board inside the control box was found to be loose. This problem could lead to an electrical failure that may pose a electrical hazard to maintenance staff and ride operators. | 3 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | Control_box_and_wiring_to_it_.png | file://x:/photopub/docs/0000000408/9f27bb77-54f5-471b-91db-42c988bbcd42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2164a7b9_6765_4184_a29c_56ac2634512d
GAIN-532983-2016 | GA-294281-2015 | 5/6/2016 11:18:09 AM | ASSESS: GA: Rough-In | png | #asFound | GA038 | Pipe supports not compliant but in place | 1 | 1 |  | 1 | Pipe supports not compliant but in place | Plastic_support_of_tubing__.png | file://x:/photopub/docs/0000000427/68439a39-7d60-488a-8216-11d70d712fd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99b80769_4639_471b_904b_9cc587e6b005
GAIN-532983-2016 | GA-294281-2015 | 5/6/2016 11:18:09 AM | ASSESS: GA: Rough-In | png | #asFound | GA038 | Pipe supports not compliant but in place | 1 | 1 |  | 1 | Pipe supports not compliant but in place | Plastic_talon_support_.png | file://x:/photopub/docs/0000000427/2d5a8ea0-0541-45c9-9063-01586338474b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99b80769_4639_471b_904b_9cc587e6b005
BPVOP-535122-2016 | 4330689 | 2/29/2016 12:07:17 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Found a machine mounted vertical air receiver (1.5m long and .51m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Safety_valve.png | file://x:/photopub/docs/0000000398/9e41a6cf-8d8c-453b-b707-afbd1142b1e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bba746e4_d399_47a8_afbf_9e2a79071320
AMOP-549179-2016 | 2047259 | 3/24/2016 9:47:24 AM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | The lap bar is used to ensure riders stay inside the passenger carrier while the ride is operating. This lap bar has a left and a right side latch on it. During a periodic inspection, it was found that the left side latch of the lap bar was no engaging correctly and the lap bar was being secured closed by one latch. If the right side latch failed the lap bar could open during operation and possibly eject the passenger for the carrier. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Lap_Bar_Latch.png | file://x:/photopub/docs/0000000408/4dd8df39-e77a-452a-aa64-9a223257beda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afbd5017_751e_4548_baec_6d0e23094abc
ELIN-566848-2016 | EL-282776-2015 | 4/27/2016 9:13:54 AM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #2 Aluminum feeder supplied from 100 amp over current device. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 5705_linley_valley_1.png | file://x:/photopub/docs/0000000421/944ce5bc-dd79-49c8-8b83-9a800e0705ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ab0f389_9c8e_4911_8fd1_bfbf404610de
ELIN-566848-2016 | EL-282776-2015 | 4/27/2016 9:13:54 AM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 3 | #2 Aluminum feeder supplied from 100 amp over current device. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 5705_linley_valley_2.png | file://x:/photopub/docs/0000000421/78eb3e9e-8e22-43de-a30e-5a6322743623.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6ab0f389_9c8e_4911_8fd1_bfbf404610de
ELIN-556368-2016 | EL-351723-2016 | 4/11/2016 4:05:18 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are not permitted to be installed in contact with metal heating ducts. This is not permitted because cables in contact with metal heating ducts may become thermally or mechanically damaged compromising the cable sheath and conductor insulation. Compromising the cable sheath and conductor insulation may cause a fault between the energized conductors and the metal ducting causing arcing, thermal damage, or energizing metal ducting. This installation of new wiring for a house under construction has multiple locations where NMSC is installed in contact with metal heating ducts. Left uncorrected this is a potential fire and shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_ducts_.png | file://x:/photopub/docs/0000000415/98ea2622-9c09-45b0-adc9-7b162d254353.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd4237f9_e197_4688_86b3_64d0f8f528d2
ELIN-556368-2016 | EL-351723-2016 | 4/11/2016 4:05:18 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are not permitted to be installed in contact with metal heating ducts. This is not permitted because cables in contact with metal heating ducts may become thermally or mechanically damaged compromising the cable sheath and conductor insulation. Compromising the cable sheath and conductor insulation may cause a fault between the energized conductors and the metal ducting causing arcing, thermal damage, or energizing metal ducting. This installation of new wiring for a house under construction has multiple locations where NMSC is installed in contact with metal heating ducts. Left uncorrected this is a potential fire and shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Front_on_new_house_under_construction.png | file://x:/photopub/docs/0000000415/11704a9b-736a-4907-9101-408dcb32646b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd4237f9_e197_4688_86b3_64d0f8f528d2
GAIN-565160-2016 | GA-335442-2016 | 5/3/2016 9:08:25 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Limiting device must be installed correctly otherwise the possibility of gas leaking out at higher pressure may result if pressure ruptures diaphragm inside | 2 | Not installed according to certified installation instructions | Tube_heaters_phillips.png | file://x:/photopub/docs/0000000424/a1445fdc-18df-43d8-9285-43edbdeaf74c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e9caf25_c12d_4538_88b1_2e0e0d86b59e
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | Unapproved_fitting_try_to_pull_through_this.png | file://x:/photopub/docs/0000000399/01caaa71-b535-4b8c-a55e-0a9989620181.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | Terminus_of_flexible_cords_in_lb.png | file://x:/photopub/docs/0000000399/4c56d38c-e73a-4fe8-95d1-bf3d84e68a55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | Power_supply_in_PVC_cabinet.png | file://x:/photopub/docs/0000000399/e1848285-d7eb-44ef-857f-12fabcd96274.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | No_bushing_at_terminus_behind_sound_system.png | file://x:/photopub/docs/0000000399/06991360-a45a-457b-8497-dbcde16e3d61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | Misuse_of_flexible_cords.png | file://x:/photopub/docs/0000000399/44cf0868-9f22-41d6-83ba-f2b37490a87e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | No_bushing_at_terminus_behind_TVs.png | file://x:/photopub/docs/0000000399/daa1195d-9a85-4af8-9bca-4dcbfadb90d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-537909-2016 | UW-355972-2016 | 3/3/2016 4:53:57 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cord is not intended to be used as a replacement for permanent wiring. It is designed for relocatable or temporary applications and where the transmission of vibration could cause damage to equipment. In this installation an audio/video system had been installed in a school cafeteria using flexible cords contained in an unapproved surface raceway. | 4 | Conductors, Misuse of flexible cords. | Home_made_cabinet_cutout.png | file://x:/photopub/docs/0000000399/7d3b6971-2995-4248-94e2-6894f5aaee18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4be53a85_f318_40c3_9971_a30b6ee87f0d
ELIN-556368-2016 | EL-351723-2016 | 4/11/2016 4:05:18 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are not permitted to be installed in contact with metal heating ducts. This is not permitted because cables in contact with metal heating ducts may become thermally or mechanically damaged compromising the cable sheath and conductor insulation. Compromising the cable sheath and conductor insulation may cause a fault between the energized conductors and the metal ducting causing arcing, thermal damage, or energizing metal ducting. This installation of new wiring for a house under construction has multiple locations where NMSC is installed in contact with metal heating ducts. Left uncorrected this is a potential fire and shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_ducts.png | file://x:/photopub/docs/0000000415/4e34ed87-be62-48c9-a907-2a8413bae34d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd4237f9_e197_4688_86b3_64d0f8f528d2
ELIN-556368-2016 | EL-351723-2016 | 4/11/2016 4:05:18 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are not permitted to be installed in contact with metal heating ducts. This is not permitted because cables in contact with metal heating ducts may become thermally or mechanically damaged compromising the cable sheath and conductor insulation. Compromising the cable sheath and conductor insulation may cause a fault between the energized conductors and the metal ducting causing arcing, thermal damage, or energizing metal ducting. This installation of new wiring for a house under construction has multiple locations where NMSC is installed in contact with metal heating ducts. Left uncorrected this is a potential fire and shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_meal_heating_ducts.png | file://x:/photopub/docs/0000000415/7a2ef390-a3ad-463c-b9f4-577c940c6ebe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd4237f9_e197_4688_86b3_64d0f8f528d2
ELIN-531770-2016 | EL-346683-2016 | 4/11/2016 4:35:19 PM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | The XO point of the transformer has grounding strap that is connected by a strap to the transformer shell. The neutral goes from the XO to the neutral bar in the 200 Amp disconnect the bonding screw is still remaining , This creates a shock and thermal hazard as the neutral will carry the unbalanced current from the switch to the transformer through the bonding conductors. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bonding_screw.png | file://x:/photopub/docs/0000000415/5ccc8428-08b0-4863-9b7a-938c9dab618f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b2633e47_9fe7_41fb_ab31_54a22c3801bf
ELIN-488268-2015 | UW-320476-2015 | 12/2/2015 10:51:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 2 | Overhead service conductors from secondary of utility transformer run through area of newly constructed addition are subject to mechanical damage and accidental contact with general public. This poses a serious risk to personal safety (shock) and property damage (thermal event) due to the large capacity of the transformer fusing. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | View02_secondary_service_cabling.png | file://x:/photopub/docs/0000000403/eab1a78f-8cf3-41dc-87e6-1f8a9fd3fcaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89692a5c_b8ed_456e_845e_93db873776ea
ELIN-488268-2015 | UW-320476-2015 | 12/2/2015 10:51:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 2 | Overhead service conductors from secondary of utility transformer run through area of newly constructed addition are subject to mechanical damage and accidental contact with general public. This poses a serious risk to personal safety (shock) and property damage (thermal event) due to the large capacity of the transformer fusing. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | View01_secondary_service_cabling.png | file://x:/photopub/docs/0000000403/3d8afe55-a977-4acb-b44e-5e4701ba4d78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89692a5c_b8ed_456e_845e_93db873776ea
ELIN-488268-2015 | UW-320476-2015 | 12/2/2015 10:51:02 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 2 | Overhead service conductors from secondary of utility transformer run through area of newly constructed addition are subject to mechanical damage and accidental contact with general public. This poses a serious risk to personal safety (shock) and property damage (thermal event) due to the large capacity of the transformer fusing. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | View03_secondary_service_cabling.png | file://x:/photopub/docs/0000000403/b0b57773-56c3-449f-ba5c-54bd741b4ffd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89692a5c_b8ed_456e_845e_93db873776ea
ELIN-531109-2016 | EL-347585-2016 | 2/29/2016 11:09:24 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cable branch wiring installed for a 15 amp 120 volt smoke detector is not terminated in an approved assembly. This could cause equipment damage and could be a shock and thermal issue. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Smoke_detector_branch_wiring.png | file://x:/photopub/docs/0000000398/85e6814b-7438-4786-887a-2d1e0a160a89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7440345_ae88_4ca7_82e7_6fb475e93387
ELIN-553532-2016 | EL-368684-2016 | 4/4/2016 7:22:43 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Counter receptacle within 1.5m of sink basin not provided with ground fault protection to prevent fault condition occurring when electrical utilization equipment comes in contact with water. This presents a risk of personal injury (shock) or property damage (thermal event) resulting from a fault condition. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | View01_counter_receptacle.png | file://x:/photopub/docs/0000000412/e12ca69b-9547-4c72-a2f4-d29f2687e6b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1ae80ec_173b_4f4c_9c7f_d216827c664c
ELIN-553023-2016 | EL-333941-2016 | 4/19/2016 9:44:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | With panel fillers missing the energized bus bar is open and exposed to accidental contact. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Missing_panel_fillers_in_first_sub_distribution_panel_.png | file://x:/photopub/docs/0000000418/588f29ec-0af5-415b-86de-9784fbf32630.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__990e362a_e40e_47db_82d2_3f91e836a542
ELIN-553023-2016 | EL-333941-2016 | 4/19/2016 9:44:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | With panel fillers missing the energized bus bar is open and exposed to accidental contact. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_fillers_missing_in_second_sub_distribution_panel_.png | file://x:/photopub/docs/0000000418/b9bf401e-b4aa-419b-87fe-1113655adb70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__990e362a_e40e_47db_82d2_3f91e836a542
ELIN-553023-2016 | EL-333941-2016 | 4/19/2016 9:44:00 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | With panel fillers missing the energized bus bar is open and exposed to accidental contact. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Emergency_shutdown_contactor.png | file://x:/photopub/docs/0000000418/86d2e8c4-2ef5-410c-8de2-18f802f9465f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__990e362a_e40e_47db_82d2_3f91e836a542
ELOP-549097-2016 | 1339 | 4/1/2016 9:48:14 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 120 volt 15 amp receptacle within 1.5 meters of a sink without GFCI protection. This is a shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_within_1_5_meters_of_sink.png | file://x:/photopub/docs/0000000411/077f84f0-c650-46e3-991d-481d12296a44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfad4115_8858_4b31_8941_1fba0c3d7036
ELOP-549088-2016 | 1338 | 4/1/2016 9:12:48 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Surface mounted Wiremold wireway is missing covers. 120 volts, 15 amp overcurrent protection provided. Staff access only. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Wiremold_missing_covers.png | file://x:/photopub/docs/0000000411/4473641a-59d8-4f0a-bed1-0a963aaf9679.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d9ddd939_0d4d_4e0c_921e_42e56ce2a0c0
ELOP-549092-2016 | 1340 | 4/1/2016 10:03:47 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Energized 120 volt armoured cable protected by a 15 amp overcurrent device in Basement Gym Storage area could be contacted accidentally by Staff. This is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Exposed_energized__armoured_cable.png | file://x:/photopub/docs/0000000411/a69e214b-f997-42f9-8b83-2d30774d61ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34ef443c_bcb6_46fc_908f_ea92a53d6e76
BPVOP-553481-2016 | 3210942 | 4/30/2016 10:00:27 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Scale.png | file://x:/photopub/docs/0000000423/63e70dfc-c3e8-4645-82f8-769ea2ffc30d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bbf98710_da85_44e1_a2bd_16ef0951cd7e
ELIN-570887-2016 | EL-345610-2016 | 5/9/2016 1:52:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Cover was not installed on the branch circuit section of the 200 amp combination panel. The service was scheduled for connection and could have exposed users to a shock hazard if it was energized. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 200_amp_combination_panel_.png | file://x:/photopub/docs/0000000427/c4e1d916-dd8c-4d65-876e-cb085a3bc8d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7962f423_ea88_4dec_bb7c_ab07c8ea669f
ELIN-570921-2016 | EL-379207-2016 | 5/9/2016 12:31:13 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL058 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | 3 | 3 | This assessment found in-floor heating supply leads that were not installed in the required conduit. As with any cable there is a fire hazard should it become damaged from a screw or nail; however in addition the heating system would fail to operate. | 3 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage and adequate mechanical protection has not been provided | Heating_cable.png | file://x:/photopub/docs/0000000427/bbbeb820-2df2-4df8-b12d-7cbc9fb2b449.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc7ed40f_8f54_410e_825b_982c31370ede
BPVOP-566271-2016 | BPV 00000017782-2013 | 4/12/2016 9:23:44 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Blow_down_tank.png | file://x:/photopub/docs/0000000420/27514f3a-5699-4413-97eb-565bcf248c45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c011076_61d4_4754_b70e_c6e7793c4515
BPVOP-566271-2016 | BPV 00000017782-2013 | 4/12/2016 9:23:44 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Tank_internals.png | file://x:/photopub/docs/0000000420/77a238a7-59c6-47fb-87db-8b88b2a8853b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c011076_61d4_4754_b70e_c6e7793c4515
ELIN-572487-2016 | EL-345814-2016 | 5/9/2016 11:56:05 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Bond strap not removed from sub panel in garage. Bond straps or screws are required to be removed in sub distribution equipment. If a fault were to occur there would be an alternate path for fault current to flow other than the bonding conductor, and may result in a shock or fire to people or property. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Bond_strap_not_removed_from_sub_panel__.png | file://x:/photopub/docs/0000000427/a32f8843-54e8-43d9-85d7-221852bbf5cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ddc2bc1_b28e_4ad1_a0c2_138dc64a4159
BPVOP-534676-2016 | 2293947 | 3/15/2016 9:46:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on this modular hot water boiler for the last 20 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Old_pressure_relief_device_.png | file://x:/photopub/docs/0000000404/6c82924b-bc31-45c4-b601-243d3a61a7ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2cd4cbf_2e6b_4434_b2dc_08b50f33e7cc
ELIN-566211-2016 | EL-264067-2015 | 4/29/2016 1:44:04 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Conductors for a 240 volt wall thermostat in a residential application are energized, but capped off with wire nuts. The branch circuit is protected by a 15 amp overcurrent device. There is the possibility for someone to make accidental contact with the energized conductors. This is a shock hazard. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Exposed_conductors_at_a_wall_thermostat.png | file://x:/photopub/docs/0000000422/730abc74-3f52-48ff-99a2-2182ce9d2c5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a5b5b18_78bd_4c0e_9d9f_6298a212cd86
ELIN-535807-2016 | EL-331292-2016 | 3/2/2016 2:54:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | No_evidence___no_evidence_of_approval_on_wirenut1.png | file://x:/photopub/docs/0000000399/71d7bbf2-2426-47fe-b284-c51557d9137e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e70eae27_e51c_42b2_90fc_29bb94c9e180
ELIN-535807-2016 | EL-331292-2016 | 3/2/2016 2:54:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Top_view__top_view.png | file://x:/photopub/docs/0000000399/6af61d2c-83a6-40a7-8f91-6be9aade38b3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e70eae27_e51c_42b2_90fc_29bb94c9e180
ELIN-535807-2016 | EL-331292-2016 | 3/2/2016 2:54:14 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL059 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; headroom around equipment has not been provided. | Photo_number_two.png | file://x:/photopub/docs/0000000399/08c5fe2e-70e3-468a-9901-9aa8e3d9ad7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e70eae27_e51c_42b2_90fc_29bb94c9e180
ELIN-533817-2016 | EL-340039-2016 | 3/2/2016 9:49:37 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Inadequately supported flexible cord being used in place of permanent branch circuit wiring on exterior of house. This flexible cord is not protected from the effects of weather, mechanical damage or rated for permanent usage. Use of flexible cord in this manner presents risk of personal injury (shock) or property damage (thermal event). | 4 | Conductors, Misuse of flexible cords. | View01_Bside_.png | file://x:/photopub/docs/0000000399/b9c03392-0769-4db1-b94a-d312e2b81f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bb288cf_2de7_43a6_b8d4_0ffe1053dbd8
ELIN-533817-2016 | EL-340039-2016 | 3/2/2016 9:49:37 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Inadequately supported flexible cord being used in place of permanent branch circuit wiring on exterior of house. This flexible cord is not protected from the effects of weather, mechanical damage or rated for permanent usage. Use of flexible cord in this manner presents risk of personal injury (shock) or property damage (thermal event). | 4 | Conductors, Misuse of flexible cords. | Detail02_lighting_fixture.png | file://x:/photopub/docs/0000000399/7be277bd-8528-4327-8fcd-1c5ef640193b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0bb288cf_2de7_43a6_b8d4_0ffe1053dbd8
ELIN-569482-2016 | EL-353609-2016 | 4/29/2016 2:20:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | 240 volt, 300 amp overhead service attachment point does not meet ground clearance which may lead to inadvertent contact and shock. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Service.png | file://x:/photopub/docs/0000000424/3e1b2db3-965a-4e11-b859-66404915a29e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9be619bb_bf0a_439c_870e_0c1157115210
GAIN-567020-2016 | GA-080756-2014 | 4/26/2016 12:26:30 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 4 | The as found hazard was a power vented hot water tank which had been installed using a venting material which is not approved for this application. This is a hazard because the venting material used is not a sealed venting system which may allow flue gases to escape from the venting system at the joints. | 3 | Unapproved venting material | HWT_and_vent_2.png | file://x:/photopub/docs/0000000421/7e425026-0abd-4b36-8675-d8806ed1b1d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c667f93a_ea96_47d4_85f8_0a6006fc8dde
GAIN-567020-2016 | GA-080756-2014 | 4/26/2016 12:26:30 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 4 | The as found hazard was a power vented hot water tank which had been installed using a venting material which is not approved for this application. This is a hazard because the venting material used is not a sealed venting system which may allow flue gases to escape from the venting system at the joints. | 3 | Unapproved venting material | HWT_and_vent.png | file://x:/photopub/docs/0000000421/3fd2f3e1-49ef-4370-b696-b091059f8988.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c667f93a_ea96_47d4_85f8_0a6006fc8dde
ELIN-566200-2016 | EL-377109-2016 | 4/27/2016 3:51:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | Armour of armoured cable not bonded to meter base where terminated to comply with requirements for electrical continuity. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Colour_of_conductors_on_load_side_of_meter_base.png | file://x:/photopub/docs/0000000421/45f0652e-eafc-4a3e-94ec-f6ec3c612db7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9aaf1d58_14d9_4c64_b9d9_241e97dff719
ELIN-566200-2016 | EL-377109-2016 | 4/27/2016 3:51:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | Armour of armoured cable not bonded to meter base where terminated to comply with requirements for electrical continuity. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Unapproved_connector_and_armour_not_bonded.png | file://x:/photopub/docs/0000000421/4d463845-a718-49d1-b7cd-16a163b787b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9aaf1d58_14d9_4c64_b9d9_241e97dff719
ELIN-540876-2016 | EL-298792-2015 | 3/15/2016 12:51:22 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 15 amp 120 volt branch wiring installed in outlet boxes greater than 100 mm only have support on one side of the outlet box. This could cause equipment damage and be a thermal hazard. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Outlet_boxes_without_required_support.png | file://x:/photopub/docs/0000000404/a2f512f3-bc56-4c49-84a9-11aa4dd90ada.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5304bd6e_d34d_41e1_8b69_9b0e77c34a35
ELIN-543350-2016 | EL-199567-2015 | 3/15/2016 10:58:54 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | 15 amp, 120 volt non-metallic sheathed cable bonding conductors are not terminated in an acceptable method at the outlet boxes. This is a shock hazard. | 3 | Continuity Bonding; method for equipment is not adequate. | Bonding_at_outlet_box.png | file://x:/photopub/docs/0000000404/c4976cd3-467c-4bfd-ac0b-f6ac87880f10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f0ed5665_0941_4f8d_bcd3_58c3f75c5324
ELIN-536262-2016 | EL-351150-2016 | 3/2/2016 8:24:42 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The base of primary power line pole adjacent to public roadway is subjected to sustained, focused discharge of surface water resulting in erosion of supporting materials. This ongoing erosion will result in failure of pole placement causing collapse of power line onto busy rural roadway. Downed primary power lines present an extreme level of risk for personal injury (shock/fatality) and property damage (thermal event/interface fire), in this situation there is also a risk posed to vehicular traffic (accident) | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Detail02_base_primary_pole_A.png | file://x:/photopub/docs/0000000399/c864a720-944c-49ac-a01e-aba122bfd9f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f612a04_80e7_457d_9012_6b1b5c79c848
ELIN-536262-2016 | EL-351150-2016 | 3/2/2016 8:24:42 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | The base of primary power line pole adjacent to public roadway is subjected to sustained, focused discharge of surface water resulting in erosion of supporting materials. This ongoing erosion will result in failure of pole placement causing collapse of power line onto busy rural roadway. Downed primary power lines present an extreme level of risk for personal injury (shock/fatality) and property damage (thermal event/interface fire), in this situation there is also a risk posed to vehicular traffic (accident) | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | View01_primary_pole_A.png | file://x:/photopub/docs/0000000399/1ec34c29-aae2-4f23-a305-a7c5041d4b8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9f612a04_80e7_457d_9012_6b1b5c79c848
GAIN-554143-2016 | GA-371263-2016 | 4/6/2016 2:54:20 PM | ASSESS: GA: Final | png | #asFound | GA092 | Single appliance under fired = < 10 % due to improper sizing | 2 | 2 | Appliance regulator undersized for the input of the appliance | 2 | Single appliance under fired = < 10 % due to improper sizing | Appliance_regulator.png | file://x:/photopub/docs/0000000413/bab0cf2a-1e54-4465-a339-37c0374e342a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eec638b0_65e8_4728_8fee_e49e71b1a7ba
ELIN-551338-2016 | EL-321905-2015 | 3/31/2016 2:19:43 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Teck cable buried under ground requires mechanical protection where it comes up from under ground. This is a hazard as the cable can become damaged where it exposed below 2 m. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000410/5a7010ed-91ef-4456-aa56-e5e4ff43e9e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7b87541_022d_40d6_afa8_2d19ca63fcab
ELIN-533918-2016 | EL-309494-2015 | 4/27/2016 4:13:42 PM | ASSESS: EL: Final | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment used installed or sold in BC must bear evidence of approval in the way of a certification mark. In this installation a standby generator without approved certification marks was installed in a remote grocery store. The generator was supplied by the owner and installed by an electrical contractor. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | UL_but_no_C.png | file://x:/photopub/docs/0000000421/9e164744-a3f8-4d8e-b348-9f818f889dec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__caa657e7_03a1_43be_a27b_61487a3b11f7
ELIN-563458-2016 | EL-369481-2016 | 4/27/2016 5:12:44 PM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Where automatic-start standby generators are used to supply power both the generator and automatic transfer switch must be rated so the generator can adequately pick up the load and the transfer switch is protected by a fuse or breaker ahead of it. In this rural residential and commercial installation a generator was installed which was undersized for the load and the switching equipment was too small for the main service fuses. | 4 | Protection and control Interrupt ratings are not adequate for the installation | Equipment_layout.png | file://x:/photopub/docs/0000000421/b9a19a86-62f8-4e9e-9bf3-c40e118b7444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c2c5902_4e03_47b0_9217_a6f74525f6a8
ELIN-547902-2016 | EL-323952-2015 | 3/30/2016 9:09:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a new irrigation pumphouse, a new 15amp 600 to 120/240volt transformer installation was observed with no ground conductor installed. This could lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | TRANSFORMER_WITH_NO_GROUND.png | file://x:/photopub/docs/0000000410/c5d61159-f64a-42c9-b94f-45a8646c839a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc30a8cb_c86f_4198_b3da_35ea73542d03
ELIN-564770-2016 | EL-370630-2016 | 4/28/2016 3:47:01 PM | ASSESS: EL: Service Connection | png | #asFound | EL075 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | 4 | 4 | Electrical services which include a neutral conductor must have that neutral conductor connected to ground to limit system voltages and provide an equipotential plane between ground and equipment. In this installation the system ground was omitted. | 4 | Effective grounding, high voltage Grounding or bonding conductor(s) are damaged or not observed. | No_system_ground.png | file://x:/photopub/docs/0000000422/6c05e708-3d48-4866-ab14-60289dae20b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__892f15f8_2980_4d40_8124_0a203491c5d6
ELIN-564626-2016 | EL-345557-2016 | 4/22/2016 2:48:54 PM | ASSESS: EL: Final | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | Found service raceway installed buried in building wall and covered or concealed. When service conductors in raceway are placed inside building wall and if there is any fault condition or failure or overheating of conductors, then the installation may result in an electrical fire or shock hazard to people and property. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Service_raceway_is_in_the_wall.png | file://x:/photopub/docs/0000000421/07f20bd2-7eb1-4e8c-9a62-45c0ab68c004.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__be6e294d_d4e0_4815_a53b_6ae1a6dced67
BPVOP-538589-2016 | UW-356347-2016 | 3/4/2016 3:11:25 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP191 | 5.1.0 In service proc/process - Incorrect or unsafe repair carried out. | 4 | 4 | All repairs to any regulated equipment must be done by a duly qualified individuals. I found this high pressure steam boiler was repaired and there are no objective evidences provided to conclude that this repair was done by a licensed individual and according to the code of construction. Potential exists for an incident to occur due to a questionnable quality of the repair work. | 4 | 5.1.0 In service proc/process - Incorrect or unsafe repair carried out. | Repair_welds_1.png | file://x:/photopub/docs/0000000400/21919477-f080-4b6b-b3f5-44a8205f44f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8810fc97_8b00_4d0c_be6c_434e9f03538d
BPVOP-538589-2016 | UW-356347-2016 | 3/4/2016 3:11:25 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP191 | 5.1.0 In service proc/process - Incorrect or unsafe repair carried out. | 4 | 4 | All repairs to any regulated equipment must be done by a duly qualified individuals. I found this high pressure steam boiler was repaired and there are no objective evidences provided to conclude that this repair was done by a licensed individual and according to the code of construction. Potential exists for an incident to occur due to a questionnable quality of the repair work. | 4 | 5.1.0 In service proc/process - Incorrect or unsafe repair carried out. | Repair_welds_2.png | file://x:/photopub/docs/0000000400/70d6f719-7564-4cb9-ba03-8018d8a9f233.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8810fc97_8b00_4d0c_be6c_434e9f03538d
BPVOP-538589-2016 | UW-356347-2016 | 3/4/2016 3:11:25 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP191 | 5.1.0 In service proc/process - Incorrect or unsafe repair carried out. | 4 | 4 | All repairs to any regulated equipment must be done by a duly qualified individuals. I found this high pressure steam boiler was repaired and there are no objective evidences provided to conclude that this repair was done by a licensed individual and according to the code of construction. Potential exists for an incident to occur due to a questionnable quality of the repair work. | 4 | 5.1.0 In service proc/process - Incorrect or unsafe repair carried out. | Repair_welds.png | file://x:/photopub/docs/0000000400/3eb51ffe-ba21-40ea-bd07-ec92dfa75b39.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8810fc97_8b00_4d0c_be6c_434e9f03538d
ELIN-563439-2016 | EL-169416-2014 | 4/22/2016 8:24:54 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found incorrect type of receptacle cover installed outdoors on receptacle outlet installed in wet location. When incorrect type of electrical equipment is used outdoors in wet locations the electrical equipment could become wet and be a possible electrical fire or shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outdoor_receptacle_with_incorrect_cover_type1.png | file://x:/photopub/docs/0000000421/ed833d5c-8931-4223-ac22-bfb16db5bd80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d915370_fbed_4254_8d05_2863445bdf2d
ELIN-563439-2016 | EL-169416-2014 | 4/22/2016 8:24:54 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found incorrect type of receptacle cover installed outdoors on receptacle outlet installed in wet location. When incorrect type of electrical equipment is used outdoors in wet locations the electrical equipment could become wet and be a possible electrical fire or shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outdoor_receptacle_with_incorrect_cover_type2.png | file://x:/photopub/docs/0000000421/a4ab2b5d-5c65-477d-bed5-c12a8e799d58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7d915370_fbed_4254_8d05_2863445bdf2d
ELIN-562637-2016 | EL-370339-2016 | 4/21/2016 11:32:04 AM | ASSESS: EL: Final | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Relocatable metal structures must be bonded to ground to avoid accidental shock hazard. In this cellular tower installation great efforts had been made to ensure tower and installation bonding but the connections for the attached relocatable structure had been missed. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bonds_not_made_up.png | file://x:/photopub/docs/0000000419/414956c6-c805-46da-ae16-9e85bfb5b648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1ee00bd_27b8_40a9_a72e_b9ccf15cc3d0
ELOP-526742-2016 | EL-345521-2016 | 4/15/2016 3:43:55 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Propane and other interior metallic gas piping systems must be bonded to ground to avoid accidental shock or spark hazard. In this ski resort installation propane is used as the primary heating source for 8 public buildings but no metal piping system bond could be located. | 3 | Equipment Gas line, cast or water pipe has not been bonded | No_bond.png | file://x:/photopub/docs/0000000417/5b1fb101-17cf-482e-b067-67cd9be193e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76745915_b0b9_4902_9bf7_e1c02f478b05
ELIN-568883-2016 | UW-381840-2016 | 5/3/2016 2:12:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed non metallic sheathed conductors in an area accessible to public. This is a shock hazard as they could be accidentally contacted, and a fire hazard as these conductors are not sunlight resistant. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | B.png | file://x:/photopub/docs/0000000424/06bd55f6-852d-4127-8e31-4b6a5f959abd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38935913_dcbb_4f7a_a490_9ffe0ee47c80
ELIN-568883-2016 | UW-381840-2016 | 5/3/2016 2:12:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed non metallic sheathed conductors in an area accessible to public. This is a shock hazard as they could be accidentally contacted, and a fire hazard as these conductors are not sunlight resistant. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000424/fbdbdc47-b8db-4ab5-a6d8-a508cd1fd8aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__38935913_dcbb_4f7a_a490_9ffe0ee47c80
ELIN-566294-2016 | EL-339029-2016 | 4/29/2016 9:00:02 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 | The sheath on metallic sheathed cables must be bonded to ground. In this installation bond bushings were omitted on large TECK cables. | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | No_bond.png | file://x:/photopub/docs/0000000422/1ecb2694-35fc-4e1b-ab6e-073633dad9ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b64bfa0e_ed83_444f_9063_bce84968183d
ELOP-267350-2014 | 4015159 | 5/17/2016 7:03:44 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL279 | Class II, all locations Seals are not located or installed where required | 4 | 4 | Where electrical cables enter buildings or equipment they must be sealed to avoid transfer of gas and liquids from one environment to another. In this sewage lift station the entry point of wet well cables was not adequately sealed. | 4 | Class II, all locations Seals are not located or installed where required | No_seal_into_kiosk.png | file://x:/photopub/docs/0000000431/6433eea7-ab58-48b9-a8bf-0fd9283b781d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bf146a0_aed8_4954_b445_a16e846eb84f
ELOP-267348-2014 | 4015107 | 5/17/2016 6:44:01 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | Electrical equipment must be approved for use where installed. In this community hall a timer switch had been installed in a furnace control circuit so the furnace would not be left on after the building was vacated. The switch used is not approved for use as installed. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Timer_switch.png | file://x:/photopub/docs/0000000431/34c733e1-1b87-4867-876b-f0a6da0e311a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48b88c33_d99f_48ad_bf96_52c3d690aadd
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Dryer.png | file://x:/photopub/docs/0000000432/05abb1b8-374e-4e0e-8ac2-12eb655cff9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Red_Tag.png | file://x:/photopub/docs/0000000432/41edb2b9-6ff2-49d7-b525-5b1f45940a21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Range_top.png | file://x:/photopub/docs/0000000432/d378afe9-4eee-4451-baef-d529e74bc50d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Solder_joint.png | file://x:/photopub/docs/0000000432/d371b566-6d40-4599-87da-0a864d7d1e72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Leak.png | file://x:/photopub/docs/0000000432/0ffc4c3b-c633-4163-ab01-e6dfc701db90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Garage.png | file://x:/photopub/docs/0000000432/d8448612-ff40-4d08-8b60-c1da6ebeb1ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Furnace.png | file://x:/photopub/docs/0000000432/3188756c-6137-4256-a6e8-39296fb0d1b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
GAUP-580123-2016 | UW-389284-2016 | 5/19/2016 11:43:02 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was an atmospheric furnace which had been installed with its venting terminating through an adjacent exterior wall to the outdoors. This is a hazard because when the furnace is operational with this venting configuration the products of combustion spill out through the draft hood opening into the space. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Side_wall_vent.png | file://x:/photopub/docs/0000000432/8347b93c-5a4c-4e94-b616-5665016952fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e0fe7db_8da3_46f8_8769_1984f508a2c7
ELIN-574412-2016 | EL-371798-2016 | 5/19/2016 11:55:40 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 3 | Observation:Non metallic sheathed cable installed for TV receptacle in master bedroom. Non metallic sheathed cable is required to terminate in approved device boxes, and joints, splices and connection of devices are to be made in the device boxes. If circuit is accidentally energized, exposed conductors would be present, and may create a shock or fire hazard to persons or property. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Media_box_in_use_.png | file://x:/photopub/docs/0000000432/b61a77bc-8b9d-4482-9ff1-246fa87588c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8a96a92_0676_450c_9ee6_179a0b38ba7d
ELIN-574412-2016 | EL-371798-2016 | 5/19/2016 11:55:40 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 3 | Observation:Non metallic sheathed cable installed for TV receptacle in master bedroom. Non metallic sheathed cable is required to terminate in approved device boxes, and joints, splices and connection of devices are to be made in the device boxes. If circuit is accidentally energized, exposed conductors would be present, and may create a shock or fire hazard to persons or property. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Device_box_not_installed_for_TV_receptacle__.png | file://x:/photopub/docs/0000000432/11de3bf4-b42e-436d-883f-37a12a365a8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8a96a92_0676_450c_9ee6_179a0b38ba7d
GAIN-465194-2015 | GA-284542-2015 | 2/24/2016 9:41:04 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | No_dirt_pocket_upstream_of_regulator.png | file://x:/photopub/docs/0000000396/388a7526-c92c-43d4-8c68-fff0d536ed9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__602a4c85_42f0_4485_904f_c086f26b65de
GAIN-465194-2015 | GA-284542-2015 | 2/24/2016 9:41:04 AM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | No_functional_Swing_joint.png | file://x:/photopub/docs/0000000396/55f17946-2f38-4886-8cac-df24fe060347.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__602a4c85_42f0_4485_904f_c086f26b65de
ELIN-568295-2016 | EL-339029-2016 | 4/29/2016 8:45:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Electrical service raceways must be bonded to ground. In this installation the metal veer head service raceway bond connection was omitted. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_raceway_bond.png | file://x:/photopub/docs/0000000422/79e9262f-0ca3-4815-8521-e311e7b632e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f2c3478a_06e3_4c56_9324_83204968c568
ELIN-537150-2016 | EL-304815-2015 | 3/7/2016 12:44:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt temporary receptacles for construction power do not include cover plates or other means of protection. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Garage_receptacle.png | file://x:/photopub/docs/0000000401/987113f9-409b-461c-8cf0-c8af0902e61c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bf5bb11_3d9d_44c1_8973_02401fb6d40d
ELIN-535832-2016 | EL-345185-2016 | 3/7/2016 11:54:10 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | The 100 amp 120/240 volt service is located in the driveway and exposed to mechanical damage. The can lead to equipment damage a as well as a shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Trailer_Service_feed_location.png | file://x:/photopub/docs/0000000401/342cd0b3-7c0f-46dd-a49b-a5c4f62abcea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5db8253_72ba_4471_92c0_cf220a338779
ELIN-537150-2016 | EL-304815-2015 | 3/7/2016 12:44:50 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 15 amp 120 volt temporary receptacles for construction power do not include cover plates or other means of protection. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Kitchen_fridge.png | file://x:/photopub/docs/0000000401/0c66d5d7-55af-4f2d-8ecc-9fec6b0358cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bf5bb11_3d9d_44c1_8973_02401fb6d40d
AMOP-548112-2016 | 2047664 | 3/22/2016 6:06:42 PM | ASSESS: AM OP: Periodic | png | #asFound | AM046 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | A limit switch which control the brake application of the passenger carrier had worked itself out of adjustment. This results in a condition in which a brake that restricts the rotation of the passenger carrier during load and unloading is not functional. There is a hazard that a person could be injured as they enter or exit the carrier because of sudden movement of the carrier. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Limit_switch_out_of_adjustment.png | file://x:/photopub/docs/0000000426/a2558598-a059-411e-bdc0-398d83755aa5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7c440737_ae9b_49a3_9776_c7a4540b7f3b
ELOP-267356-2014 | 4015090 | 5/17/2016 7:58:29 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Electrical cables must be approved for use as installed. In this installation a cable intended for use in a permanent installation was equipped with a cord cap. | 3 | Conductors Equipment is not approved for the specific use. | Cord_cap_on_ac_90.png | file://x:/photopub/docs/0000000431/05d1f5ab-bd76-4228-b464-73e5714534c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3bc3f0b9_c74d_40f4_a603_12c069155eec
ELOP-267358-2014 | 4015086 | 5/17/2016 8:13:54 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Wiring may not be left open to touch if energized. In this hangar open wiring was left exposed where accessible. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | energized_conductors.png | file://x:/photopub/docs/0000000431/128aa72f-e8d0-4196-9132-7a60055049b6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aace865d_f8bf_47cc_b5be_69e71f65a78c
ELOP-268045-2014 | 4015096 | 5/17/2016 8:25:53 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Covers must be installed on junction boxes where energized wiring is installed. In this installation a number of covers were not installed above a stage when the lighting was altered. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Covers_missing_above_stage.png | file://x:/photopub/docs/0000000431/41915d62-60d1-4448-abeb-118b46875fc8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f3c81108_7a4b_486d_b34b_da8bc22cc7a8
ELOP-267352-2014 | 4015082 | 5/17/2016 7:29:45 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL208 | All Classes, All Zones Area is classified: seals are not located or installed where required. | 4 | 4 | Sewage treatment plants can create environments where explosive or corrosive conditions exist. Special care is required to ensure gases do not transfer from one classified area to another. In this sewage treatment plant a sludge bagging building was inadvertently connected to the main electrical room without seals and the main copper conductors were damaged in both buildings. | 4 | All Classes, All Zones Area is classified: seals are not located or installed where required. | Copper_corrosion.png | file://x:/photopub/docs/0000000431/41ce003e-7244-44bd-8135-9487f58412eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__878be63f_fee1_418d_b287_6714cc6c95d5
ELOP-267343-2014 | 4015120 | 5/17/2016 5:53:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Radio towers must be bonded to ground. In this installation the bond to a transmission tower had been omitted. | 3 | Continuity Bonding conductor is not observed or broken | No_bond_on_tower.png | file://x:/photopub/docs/0000000431/75e2b5c5-97d9-485a-be7a-834c9d884be3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d69422d_0abe_4b77_aaba_2d1e2f47b96b
ELOP-267355-2014 | 4015147 | 5/17/2016 7:46:55 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | 1 m of working space is to be provided I front of electrical equipment. In this installation data equipment was installed on a shelf directly in front of electrical equipment. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | Data_in_front_of_panels.png | file://x:/photopub/docs/0000000431/3d9d67b2-d6e6-4631-978e-09796753e6d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c3f1c9d_21e0_44a2_a06d_0c518e6eed51
ELIN-536111-2016 | EL-346092-2016 | 3/2/2016 4:17:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Raceways.png | file://x:/photopub/docs/0000000399/1eecffdd-dff8-4569-a8ba-7ac42406bdf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47112875_cf4a_46d3_86c5_b7503c56a9e0
ELIN-536111-2016 | EL-346092-2016 | 3/2/2016 4:17:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Raceways2.png | file://x:/photopub/docs/0000000399/7011c9ab-4f75-461d-8ec3-2f142ff3e566.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47112875_cf4a_46d3_86c5_b7503c56a9e0
ELIN-536111-2016 | EL-346092-2016 | 3/2/2016 4:17:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Water_separation_.png | file://x:/photopub/docs/0000000399/b2263351-5be6-4f2c-bd68-1b25ddc8f9c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47112875_cf4a_46d3_86c5_b7503c56a9e0
ELIN-536111-2016 | EL-346092-2016 | 3/2/2016 4:17:15 PM | ASSESS: EL: Service Connection | png | #asFound | EL102 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | 2 | 2 |  | 2 | Separation of circuits Conductors of extra-low voltage and low voltage systems are not suitably separated from one and another. | Hidden_cable.png | file://x:/photopub/docs/0000000399/f599537f-b19a-4e1a-b690-62b5752df5cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47112875_cf4a_46d3_86c5_b7503c56a9e0
ELIN-571140-2016 | EL-359861-2016 | 5/4/2016 11:37:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Openings in boxes where conductors pass though are required to be fitted with bushings or equivalent material to protect conductor insulation from abrasion. This is required so that the conductor insulation does not become damaged. This installation of a new 400A, 120/240V service in a commercial building has service conductor pull boxes installed to facilitate the installation of the service conductors. The boxes have openings cut in them to allow the conductors to pass through them. The edges of the openings are sharp and open to contact with the pending installation of the utilities service conductors. Let uncorrected this is a potential shock and fire hazard if the service conductor installation becomes damaged during or after installation. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Exterior_of_building_under_renovation.png | file://x:/photopub/docs/0000000424/3edf95a9-796c-4ba4-b3b4-ce9486c48b97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__061ec20a_6922_4105_bea1_7d0982d0622c
ELIN-571140-2016 | EL-359861-2016 | 5/4/2016 11:37:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Openings in boxes where conductors pass though are required to be fitted with bushings or equivalent material to protect conductor insulation from abrasion. This is required so that the conductor insulation does not become damaged. This installation of a new 400A, 120/240V service in a commercial building has service conductor pull boxes installed to facilitate the installation of the service conductors. The boxes have openings cut in them to allow the conductors to pass through them. The edges of the openings are sharp and open to contact with the pending installation of the utilities service conductors. Let uncorrected this is a potential shock and fire hazard if the service conductor installation becomes damaged during or after installation. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Sharp_edges_on_pull_box.png | file://x:/photopub/docs/0000000424/3afe15ea-38e9-48f9-a8a2-519c559107cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__061ec20a_6922_4105_bea1_7d0982d0622c
ELIN-538118-2016 | EL-335642-2016 | 3/7/2016 10:16:31 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service conductors must be encased in concrete if they exceed 1.5 m in length. In this installation the contractor had installed more than 1.5 m of service conductor and appled for and received a service connection without encasing the wires. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | At_panel.png | file://x:/photopub/docs/0000000401/814fab61-ff73-43fe-80d9-e78ab08a5e96.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1cfcdfa_956b_4e74_bbec_0c0f837ae090
ELIN-538118-2016 | EL-335642-2016 | 3/7/2016 10:16:31 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Consumer service conductors must be encased in concrete if they exceed 1.5 m in length. In this installation the contractor had installed more than 1.5 m of service conductor and appled for and received a service connection without encasing the wires. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | At_meter.png | file://x:/photopub/docs/0000000401/187b9eeb-c222-4240-8af5-5d947b9145a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1cfcdfa_956b_4e74_bbec_0c0f837ae090
ELIN-554701-2016 | EL-270876-2015 | 4/29/2016 2:44:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Exposed service cable | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Eosed_service_conductor.png | file://x:/photopub/docs/0000000423/43da27a5-1ebf-4f53-ac36-a1f95b8e00ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95069a1c_7a38_443f_941b_55dc1117306d
ELIN-572170-2016 | EL-379701-2016 | 5/11/2016 1:19:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | In a single family dwelling, a 120/240volt 200amp feeder cable running from main panel in garage to the sub-panel in basement passes through the floor in a 2x4 wall with no mechanical protection in place on any side. This could lead to a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder_protection.png | file://x:/photopub/docs/0000000429/f541dd76-36c0-4a9f-a743-507237fcef3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7260d272_c783_48b4_847c_eb2752d40d6b
BPVOP-547221-2016 | 4021169 | 3/21/2016 2:13:09 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 17.1 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_valve.png | file://x:/photopub/docs/0000000406/2d5daf1b-4755-4a12-985a-9065673fd997.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5810f700_5634_41f3_9428_62b7ea946e71
BPVOP-547213-2016 | 4021172 | 3/21/2016 3:58:13 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 17.1 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000406/7c50af96-20f6-4343-955e-c6f6281b1087.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e1188fc_2719_4bb6_a381_62a8753dbd0c
ELIN-573174-2016 | EL-383816-2016 | 5/12/2016 5:54:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Exposed and unprotected branch circuit conductors must remain de-energized during construction to prevent shock and fire hazards that can occur if accidental contact with conductors or mechanical damage to conductors occurs. This house renovation installation has energized 120/240V, 15A conductors from non-metallic sheathed cables that are protruding from outlet and switch boxes with wire connectors twisted onto the ends of the conductors. Workers and occupants have access to these conductors that are inadequately protected to prevent contact with them. Left uncorrected this is a potential shock and fire hazard should the energized conductors be contacted or damaged during construction. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Front_and_side_of_renovated_house.png | file://x:/photopub/docs/0000000429/392e82a0-8797-4efe-9d09-a9ef659b72c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44fcb779_dabd_456e_be4b_fe3cfeb4621d
ELIN-564704-2016 | EL-379350-2016 | 5/12/2016 11:18:34 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | Flexible cord is not approved to be used as a substitute for permanent wiring or for use in an under ground location. This is because it does not have a flame test rating, may not provide adequate mechanical protection for the conductors, and does not have properties that make it suitable for burial. This installation has a flexible cord used as a 120/240V sub- feed cable that is permanently connected to the service panel inside a wall and then exits the building to run under ground to an unknown location. The cable is energized and in use. Left uncorrected this is a potential shock and fire hazard if the cable gets mechanically damaged above ground of if the cable deteriorates where installed under ground. | 4 | Conductors, Mis-use of flexible cords. | Cabtire_entering_panel.png | file://x:/photopub/docs/0000000429/aac9183b-f4d0-4a3a-9564-1f9791c68101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff9d641_03b6_4e9a_90ba_12bd39447bb7
ELIN-573174-2016 | EL-383816-2016 | 5/12/2016 5:54:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Exposed and unprotected branch circuit conductors must remain de-energized during construction to prevent shock and fire hazards that can occur if accidental contact with conductors or mechanical damage to conductors occurs. This house renovation installation has energized 120/240V, 15A conductors from non-metallic sheathed cables that are protruding from outlet and switch boxes with wire connectors twisted onto the ends of the conductors. Workers and occupants have access to these conductors that are inadequately protected to prevent contact with them. Left uncorrected this is a potential shock and fire hazard should the energized conductors be contacted or damaged during construction. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_wiring_protruding_from_boxes.png | file://x:/photopub/docs/0000000429/ab59e2a2-2bfd-4744-99c8-05121a5ace6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44fcb779_dabd_456e_be4b_fe3cfeb4621d
ELIN-564704-2016 | EL-379350-2016 | 5/12/2016 11:18:34 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | Flexible cord is not approved to be used as a substitute for permanent wiring or for use in an under ground location. This is because it does not have a flame test rating, may not provide adequate mechanical protection for the conductors, and does not have properties that make it suitable for burial. This installation has a flexible cord used as a 120/240V sub- feed cable that is permanently connected to the service panel inside a wall and then exits the building to run under ground to an unknown location. The cable is energized and in use. Left uncorrected this is a potential shock and fire hazard if the cable gets mechanically damaged above ground of if the cable deteriorates where installed under ground. | 4 | Conductors, Mis-use of flexible cords. | Cabtire_in_PVC_conduit_on_exterior_of_house.png | file://x:/photopub/docs/0000000429/736269bd-fb47-45c7-9c1c-79d29651abf8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff9d641_03b6_4e9a_90ba_12bd39447bb7
ELIN-573174-2016 | EL-383816-2016 | 5/12/2016 5:54:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Exposed and unprotected branch circuit conductors must remain de-energized during construction to prevent shock and fire hazards that can occur if accidental contact with conductors or mechanical damage to conductors occurs. This house renovation installation has energized 120/240V, 15A conductors from non-metallic sheathed cables that are protruding from outlet and switch boxes with wire connectors twisted onto the ends of the conductors. Workers and occupants have access to these conductors that are inadequately protected to prevent contact with them. Left uncorrected this is a potential shock and fire hazard should the energized conductors be contacted or damaged during construction. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_wiring_protruding_from_boxes__.png | file://x:/photopub/docs/0000000429/7eebc2e4-a47b-4e0e-8905-103f30f80b8e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44fcb779_dabd_456e_be4b_fe3cfeb4621d
ELIN-573174-2016 | EL-383816-2016 | 5/12/2016 5:54:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Exposed and unprotected branch circuit conductors must remain de-energized during construction to prevent shock and fire hazards that can occur if accidental contact with conductors or mechanical damage to conductors occurs. This house renovation installation has energized 120/240V, 15A conductors from non-metallic sheathed cables that are protruding from outlet and switch boxes with wire connectors twisted onto the ends of the conductors. Workers and occupants have access to these conductors that are inadequately protected to prevent contact with them. Left uncorrected this is a potential shock and fire hazard should the energized conductors be contacted or damaged during construction. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_wiring_protruding_from_boxes___.png | file://x:/photopub/docs/0000000429/8030d712-a2d6-4c7b-a7dc-4772801e0259.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44fcb779_dabd_456e_be4b_fe3cfeb4621d
ELIN-573174-2016 | EL-383816-2016 | 5/12/2016 5:54:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Exposed and unprotected branch circuit conductors must remain de-energized during construction to prevent shock and fire hazards that can occur if accidental contact with conductors or mechanical damage to conductors occurs. This house renovation installation has energized 120/240V, 15A conductors from non-metallic sheathed cables that are protruding from outlet and switch boxes with wire connectors twisted onto the ends of the conductors. Workers and occupants have access to these conductors that are inadequately protected to prevent contact with them. Left uncorrected this is a potential shock and fire hazard should the energized conductors be contacted or damaged during construction. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_wiring_protruding_from_boxes_.png | file://x:/photopub/docs/0000000429/9ba358b9-7f67-421e-8813-215f8898bfaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44fcb779_dabd_456e_be4b_fe3cfeb4621d
ELIN-564704-2016 | EL-379350-2016 | 5/12/2016 11:18:34 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | Flexible cord is not approved to be used as a substitute for permanent wiring or for use in an under ground location. This is because it does not have a flame test rating, may not provide adequate mechanical protection for the conductors, and does not have properties that make it suitable for burial. This installation has a flexible cord used as a 120/240V sub- feed cable that is permanently connected to the service panel inside a wall and then exits the building to run under ground to an unknown location. The cable is energized and in use. Left uncorrected this is a potential shock and fire hazard if the cable gets mechanically damaged above ground of if the cable deteriorates where installed under ground. | 4 | Conductors, Mis-use of flexible cords. | Cabtire_entering_ground.png | file://x:/photopub/docs/0000000429/e0308d97-b9bc-4e45-b664-f1ad664ef947.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff9d641_03b6_4e9a_90ba_12bd39447bb7
ELIN-549532-2016 | EL-261918-2015 | 3/24/2016 4:44:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt branch circuits installed and run in non-metallic sheathed raceway in concrete (coreline) which comes out of concrete slab and transitions to run in EMT raceway run on surface of building without the use of proper approved electrical equipment for transitioning from non-metallic raceway to EMT raceway. When electrical equipment is not approved and is not installed and used as required for approved electrical equipment installation work, the electrical equipment could become damaged and could energized conductors could get damaged and could become an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 5.png | file://x:/photopub/docs/0000000409/d976b3c7-8d38-49d8-88c1-767839b92472.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb35cc68_75d2_4dbc_9329_1145d62103ca
ELIN-549532-2016 | EL-261918-2015 | 3/24/2016 4:44:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt branch circuits installed and run in non-metallic sheathed raceway in concrete (coreline) which comes out of concrete slab and transitions to run in EMT raceway run on surface of building without the use of proper approved electrical equipment for transitioning from non-metallic raceway to EMT raceway. When electrical equipment is not approved and is not installed and used as required for approved electrical equipment installation work, the electrical equipment could become damaged and could energized conductors could get damaged and could become an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 3.png | file://x:/photopub/docs/0000000409/61f26c96-8be6-48b1-afec-fb9f791d48a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb35cc68_75d2_4dbc_9329_1145d62103ca
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 12.png | file://x:/photopub/docs/0000000409/0ecf060f-7f28-4e7b-b035-8b73f8f98eda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 10.png | file://x:/photopub/docs/0000000409/ad8686ae-e0e9-44f4-8c37-2a5fce53e0b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-530224-2016 | EL-307064-2015 | 2/23/2016 6:40:07 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Bonding conductor for gas system and communications services not installed resulting in no low impedance connection to electrical system grounding electrode. This would result in the metallic parts of these systems becoming energized, posing serious risk of personal injury (shock) or property damage (thermal event). | 3 | Equipment Gas line, cast or water pipe has not been bonded | View01_system_bond_connections.png | file://x:/photopub/docs/0000000395/ef23c6a0-6ff4-402a-96ab-589af9752e9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9f8ebc2_c7fc_492b_80c0_9298f63284ac
ELIN-532753-2016 | EL-329821-2015 | 3/3/2016 2:31:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | A main system ground for a 125 amp 240 volt single phase service for a dwelling is lacking mechanical protection on exterior of dwelling between grade and approximately 30 cm above grade. The main ground may be damaged and will not function to provide minimum safety during an electrical fault. Damage to property or injury to persons can occur when a main system ground is damaged or broken. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Main_system_ground_exposed_to_mechanical_damage.png | file://x:/photopub/docs/0000000400/5fefd925-e354-421a-9225-9030dcdc30e3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5fda05b1_8ea2_4938_ba53_529e8d7006c5
ELIN-534121-2016 | EL-349216-2016 | 3/4/2016 12:56:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A 200 amp 240 Volt service cable has been installed into a building. The service conductors which lack effective overcurrent protection measure 2.2 meters inside the building. Damage can occur to these conductors when not kept as short as possible and lead to potential for fault and resultant damage to property or injury to persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | One_meter_on_panel_end.png | file://x:/photopub/docs/0000000400/dfa77a0d-a424-413a-8a3d-1fba26b532c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7732532_9b3f_44a6_9b48_0b718286d0b0
ELIN-531469-2016 | EL-342642-2016 | 3/4/2016 12:07:54 PM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | 100 amp 240 volt 1 phase feeder from a new residential service was installed. A bushing was not provided for the conductors that pass through the connector into the panel. This can result in an arc fault and cause injury to persons or property damage | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | No_bushing.png | file://x:/photopub/docs/0000000400/7368335d-c078-4d1d-92cc-1eeb5cf49e62.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f0af497_6428_4b9c_8dc7_5ce1a2b9e060
ELOP-536565-2016 | 5397961 | 3/4/2016 6:59:54 AM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | A 600 volt 3 phase welder has been connected into a panelboard using flexible cord. The cord was not provided adequate support or strain relief and was located in an area where employees can access the area and was found to be a tripping hazard. This could result in the cable coming loose from the panel board and lead to potential for arc fault and or shock to persons. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Flexible_cord_enters_panel_with_nmd_90_connector.png | file://x:/photopub/docs/0000000400/a85c69ba-794f-4596-be74-6ede5636265a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41112a7d_cb10_4dec_83a3_a6112375b1d0
ELIN-532513-2016 | EL-350144-2016 | 3/4/2016 10:05:41 AM | ASSESS: EL: Service Connection | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | A new 200 amp 240 volt 1 phase commercial service to a farm building has been installed. The service cable is not mechanically protected below grade at the service pole. The service Cale can be damaged during settling or yard work and result in damaged cable and possible arc fault leading to property damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Mechanical_protection_unfused_service_conductor_stops_at_grade.png | file://x:/photopub/docs/0000000400/24ba55a8-a4a1-4713-a815-4063883a59f5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9adf0611_3903_404f_84d3_e5e058af351c
ELIN-534121-2016 | EL-349216-2016 | 3/4/2016 12:56:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | A 200 amp 240 Volt service cable has been installed into a building. The service conductors which lack effective overcurrent protection measure 2.2 meters inside the building. Damage can occur to these conductors when not kept as short as possible and lead to potential for fault and resultant damage to property or injury to persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 1_2_meters_meter_end.png | file://x:/photopub/docs/0000000400/87649111-04ab-471d-88ff-9321d03bf186.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7732532_9b3f_44a6_9b48_0b718286d0b0
ELOP-267351-2014 | 4015100 | 5/17/2016 7:14:23 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles within 1.5 m of sinks must be GFCI protected. In this public access building the receptacles in washroom and one kitchenette were not equipped with GFCI protection. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | No_GFCI_present.png | file://x:/photopub/docs/0000000431/64f67f72-c38d-461c-9ef0-13cde3160044.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bc7cdb21_aac6_438f_8b0f_b5cd3a72debd
ELOP-267344-2014 | 4015050 | 5/17/2016 6:13:21 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Electrical equipment must be sized for the overcurrent protection levels ahead of it. In this installation a generator transfer switch rated at 60 amperes was installed in a service with overcurrent protection set at 100 amperes. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Transfer_switch_rating.png | file://x:/photopub/docs/0000000431/9aceffcb-588e-4fd2-9ad6-894a9ec5e3dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd6b0317_f38f_44fd_ab9c_b3af391165a2
ELOP-226729-2014 | 4015041 | 5/17/2016 5:36:18 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Electrical conductors must be approved for use in the environments where they are installed. In this installation an interior cable was installed outside where it was exposed to the weather. | 3 | Conductors Equipment is not approved for the specific use. | BX_on_exterior_wall.png | file://x:/photopub/docs/0000000431/092fc0dd-27d4-46a5-9526-03460369ab29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84ef896d_6459_49f7_83cd_167247193336
ELIN-547828-2016 | EL-359844-2016 | 3/23/2016 2:16:07 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Single gang device box with too many wires installed. This s is a fire hazard as excessive heat can build up. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | A.png | file://x:/photopub/docs/0000000407/3ef68fdc-f507-4800-9115-62e9fe76ef97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0deee26f_982c_4261_9676_380d58af14c9
ELIN-559596-2016 | UW-376364-2016 | 4/14/2016 12:38:30 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | 120 volt 15 amp receptacles installed in a residential application does not have access to a grounding means (existing receptacles are 2 pin configuration). This is a shock hazard. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Receptacle_without_a_grounding_means_.png | file://x:/photopub/docs/0000000416/c1d0356b-10d1-4961-8661-7f0e8164d9ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a25a48f_4505_4bae_85e6_63f0fdc6b7e3
ELOP-568983-2016 | EL-374474-2016 | 5/9/2016 7:20:30 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Panel fillers must be used to fill unused openings in electrical cabinets to avoid accidental contact. In this remote sewage lift station two small fillers had been omitted when the insulation was completed. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Open_filler_and_corrosion.png | file://x:/photopub/docs/0000000427/5b582832-afa0-43f5-b60c-236eff9f4c64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40c7a3ee_1878_459d_b7e3_2255f7d629f6
ELIN-570445-2016 | EL-381290-2016 | 4/29/2016 11:34:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 3 | 15Amp circuits being supplied by a 50Amp 2P GFCI overcurrent circuit breaker. Possibility for shock or damage to equipment with circuit failure not rated for 50 Amps. | 4 | Protection and control Interrupt ratings are not adequate for the installation | 50Amp_2P_GFCI_supplying15Amp_crts.png | file://x:/photopub/docs/0000000424/da934ac3-e6c7-4e63-9712-9b5ef8b98cea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7533a4_e277_435b_83ec_839f24c0164c
ELIN-568713-2016 | EL-381290-2016 | 4/29/2016 10:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Ground electrode was not installed on an energized service. Declaration of compliance was not submitted to BCSA but was submitted to BC Hydro. BC Hydro does not verify declarations or permit numbers and consequently, energized this service without a ground electrode. Potential for electric shock and equipment damage. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_electrode_not_installed_on_energized_service.png | file://x:/photopub/docs/0000000424/6655e0cf-3451-4896-b189-42d8b43fd388.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41152686_7df3_4356_b9a9_98b0624ef77f
ELIN-578997-2016 | EL-350600-2016 | 5/19/2016 12:13:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 2 | Less than 1 meter working space in front of sub distribution panel This could cause a worker not to be able to access the panel for maintenance or to install breakers | 3 | General Equipment is not approved for the specific use | Sub_panel.png | file://x:/photopub/docs/0000000432/e712d1de-a324-4bf9-ba6c-2797e3659ca3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c539467_53dd_45cc_9656_af21d2469f97
ELIN-571140-2016 | EL-359861-2016 | 5/4/2016 11:37:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Openings in boxes where conductors pass though are required to be fitted with bushings or equivalent material to protect conductor insulation from abrasion. This is required so that the conductor insulation does not become damaged. This installation of a new 400A, 120/240V service in a commercial building has service conductor pull boxes installed to facilitate the installation of the service conductors. The boxes have openings cut in them to allow the conductors to pass through them. The edges of the openings are sharp and open to contact with the pending installation of the utilities service conductors. Let uncorrected this is a potential shock and fire hazard if the service conductor installation becomes damaged during or after installation. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_equipment_lay_out.png | file://x:/photopub/docs/0000000424/8ef3a99e-e325-4d34-b47b-2e5229568416.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__061ec20a_6922_4105_bea1_7d0982d0622c
ELIN-571140-2016 | EL-359861-2016 | 5/4/2016 11:37:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Openings in boxes where conductors pass though are required to be fitted with bushings or equivalent material to protect conductor insulation from abrasion. This is required so that the conductor insulation does not become damaged. This installation of a new 400A, 120/240V service in a commercial building has service conductor pull boxes installed to facilitate the installation of the service conductors. The boxes have openings cut in them to allow the conductors to pass through them. The edges of the openings are sharp and open to contact with the pending installation of the utilities service conductors. Let uncorrected this is a potential shock and fire hazard if the service conductor installation becomes damaged during or after installation. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Sharp_edge_on_pull_box.png | file://x:/photopub/docs/0000000424/e1939739-fe0b-4469-b8f6-4ad55e2985af.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__061ec20a_6922_4105_bea1_7d0982d0622c
ELIN-563913-2016 | EL-378762-2016 | 5/4/2016 4:15:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to have the two line conductors terminated to breakers connected to different line conductor buses in the panel. This is required so that the neutral conductor carries the unbalanced load on the circuit. When the circuit line conductors are connected to breakers on the same bus in the panel the circuit neutral conductor will carry the sum of the branch circuit currents. This installation has a 20A, 120V three wire receptacle circuit with both line conductors connected to breakers on the same bus in the panel. Left uncorrected this has the potential of over loading the neutral conductor causing thermal damage to the conductor insulation and conductor terminations creating a fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Three_wire_circuit_feeding_receptacles_beside_the_panel.png | file://x:/photopub/docs/0000000425/1e97f6c6-d7a4-450a-b4b3-3de1d170871a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__706628fd_c7af_4816_ae2a_30e961dc842b
ELIN-563913-2016 | EL-378762-2016 | 5/4/2016 4:15:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to have the two line conductors terminated to breakers connected to different line conductor buses in the panel. This is required so that the neutral conductor carries the unbalanced load on the circuit. When the circuit line conductors are connected to breakers on the same bus in the panel the circuit neutral conductor will carry the sum of the branch circuit currents. This installation has a 20A, 120V three wire receptacle circuit with both line conductors connected to breakers on the same bus in the panel. Left uncorrected this has the potential of over loading the neutral conductor causing thermal damage to the conductor insulation and conductor terminations creating a fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Panel_in_the_shop.png | file://x:/photopub/docs/0000000425/6a1af97e-2131-4a05-861e-bfb5e822edeb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__706628fd_c7af_4816_ae2a_30e961dc842b
ELIN-563913-2016 | EL-378762-2016 | 5/4/2016 4:15:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to have the two line conductors terminated to breakers connected to different line conductor buses in the panel. This is required so that the neutral conductor carries the unbalanced load on the circuit. When the circuit line conductors are connected to breakers on the same bus in the panel the circuit neutral conductor will carry the sum of the branch circuit currents. This installation has a 20A, 120V three wire receptacle circuit with both line conductors connected to breakers on the same bus in the panel. Left uncorrected this has the potential of over loading the neutral conductor causing thermal damage to the conductor insulation and conductor terminations creating a fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Branch_circuit_connections_in_the_panel.png | file://x:/photopub/docs/0000000425/ce00d6d1-73c1-4179-8709-7b5237ae8709.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__706628fd_c7af_4816_ae2a_30e961dc842b
ELIN-563913-2016 | EL-378762-2016 | 5/4/2016 4:15:30 PM | ASSESS: EL: Service Connection | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 3 | Three wire circuits are required to have the two line conductors terminated to breakers connected to different line conductor buses in the panel. This is required so that the neutral conductor carries the unbalanced load on the circuit. When the circuit line conductors are connected to breakers on the same bus in the panel the circuit neutral conductor will carry the sum of the branch circuit currents. This installation has a 20A, 120V three wire receptacle circuit with both line conductors connected to breakers on the same bus in the panel. Left uncorrected this has the potential of over loading the neutral conductor causing thermal damage to the conductor insulation and conductor terminations creating a fire hazard. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Detached_shop_where_panel_is_located.png | file://x:/photopub/docs/0000000425/bcc2e246-d372-46f9-936d-adc77d60b102.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__706628fd_c7af_4816_ae2a_30e961dc842b
ELOP-564211-2016 | 6199 | 4/25/2016 6:48:39 PM | ASSESS: EL OP: SO Scheduled Assessment | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | An armoured cable outer jacket providing power to a foot pedal control for a cut-off saw is damaged and showing signs of wear. The supply voltage is 120 volts which is protected by a 5 amp fuse. This is a thermal hazard. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Damaged_teck_cable.png | file://x:/photopub/docs/0000000420/c80fd984-f2d5-4f60-ad89-acce418ec505.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd4642b0_f9f8_4c71_b98e_f34d4a0d6e44
GAIN-538582-2016 | GA-318656-2015 | 3/2/2016 2:59:51 PM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 3 | Open gas line connected to fuel supply. Possibility that gas and valves could be turned on by persons not aware gas piping is not connected. Possibly leading to uncontrolled escape of natural gas inside structure. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_uncapped_gas_lines_.png | file://x:/photopub/docs/0000000401/ae4e3d28-f956-467d-a722-aae26b20363c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2c3448_9cc8_441b_8a24_384a3a9910b2
GAIN-538582-2016 | GA-318656-2015 | 3/2/2016 2:59:51 PM | ASSESS: GA: Rough-In | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 3 | Open gas line connected to fuel supply. Possibility that gas and valves could be turned on by persons not aware gas piping is not connected. Possibly leading to uncontrolled escape of natural gas inside structure. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Open_gas_line__2__valve_off.png | file://x:/photopub/docs/0000000401/70f08bb8-a426-43a2-ae9e-36a85255f814.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f2c3448_9cc8_441b_8a24_384a3a9910b2
ELOP-191749-2014 | 5184923 | 3/9/2016 8:56:50 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 | Sub services are not labeled or not labeled properly, identifying the sub feed locations and panel IDs. If work was going to be started on a panel it would not be possible to know which disconnect feeds the panel. This would result in power disruption to other offices and classes in the building. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Main_disconnect.png | file://x:/photopub/docs/0000000402/6d0ca6e8-ea53-4bb2-968e-868d25b33cc2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65d5ba7a_008c_4e03_8506_7634052002d1
ELIN-574417-2016 | EL-360340-2016 | 5/5/2016 8:13:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device and service head too close to metal rain gutters down spouts and conductors would be in contact with metal gutters if service connected by hydro. When conductors are too close or are in contact with metal rain gutters this installation could become an electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 203.png | file://x:/photopub/docs/0000000430/f63cdf3a-8360-48a1-a992-43896461eeec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f885f749_943f_4050_82c3_05c94c019ca1
ELIN-574417-2016 | EL-360340-2016 | 5/5/2016 8:13:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device and service head too close to metal rain gutters down spouts and conductors would be in contact with metal gutters if service connected by hydro. When conductors are too close or are in contact with metal rain gutters this installation could become an electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 202.png | file://x:/photopub/docs/0000000430/4f4bd627-e470-4852-80d2-f2e0ab756a07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f885f749_943f_4050_82c3_05c94c019ca1
ELIN-574417-2016 | EL-360340-2016 | 5/5/2016 8:13:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device and service head too close to metal rain gutters down spouts and conductors would be in contact with metal gutters if service connected by hydro. When conductors are too close or are in contact with metal rain gutters this installation could become an electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 201.png | file://x:/photopub/docs/0000000430/d979e18d-3f8d-48ed-9e6d-203bb6f8335b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f885f749_943f_4050_82c3_05c94c019ca1
ELIN-574417-2016 | EL-360340-2016 | 5/5/2016 8:13:05 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Found overhead service conductors attachment device and service head too close to metal rain gutters down spouts and conductors would be in contact with metal gutters if service connected by hydro. When conductors are too close or are in contact with metal rain gutters this installation could become an electrical shock or fire hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 200.png | file://x:/photopub/docs/0000000430/8a5b310a-c413-42d5-975e-ad6a26dfaf6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f885f749_943f_4050_82c3_05c94c019ca1
ELIN-546591-2016 | EL-269402-2015 | 3/21/2016 8:25:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service supply side of service equipment did not have any grounding conductor installed or terminated onto main consumer's service equipment neutral bar as required by code. When service grounding is not installed and terminated properly in supply side consumer's service equipment the installation is not properly grounded for preventing step and touch voltage limits to be exceeded and the system could possibly become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_grounding_in_service_supply_side_of_equipment_1.png | file://x:/photopub/docs/0000000407/b02314d3-1b6b-4236-bd30-cb4a45c62e3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83cea82f_3552_4f04_bb57_ec022079a5a3
ELIN-546591-2016 | EL-269402-2015 | 3/21/2016 8:25:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service supply side of service equipment did not have any grounding conductor installed or terminated onto main consumer's service equipment neutral bar as required by code. When service grounding is not installed and terminated properly in supply side consumer's service equipment the installation is not properly grounded for preventing step and touch voltage limits to be exceeded and the system could possibly become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_grounding_in_service_supply_side_of_equipment_as_the_grounding_conductor_was_doubled_up_with_bonding_conductors_on_bonding_bar_only.png | file://x:/photopub/docs/0000000407/81a18642-b0c1-48d7-8621-6ed0f8e05ff5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83cea82f_3552_4f04_bb57_ec022079a5a3
ELIN-546591-2016 | EL-269402-2015 | 3/21/2016 8:25:02 AM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found main service supply side of service equipment did not have any grounding conductor installed or terminated onto main consumer's service equipment neutral bar as required by code. When service grounding is not installed and terminated properly in supply side consumer's service equipment the installation is not properly grounded for preventing step and touch voltage limits to be exceeded and the system could possibly become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_grounding_in_service_supply_side_of_equipment_2_as_this_is_only_bonding_bar_where_grounding_was_tied_in.png | file://x:/photopub/docs/0000000407/f0408362-d1b5-431f-ac77-6cea795694ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83cea82f_3552_4f04_bb57_ec022079a5a3
ELIN-532500-2016 | EL-346553-2016 | 2/24/2016 11:59:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | 240 v, 40 a range connected for temporary heat without proper junction box leaving exposed connection subject to damage and potential shock hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 3.png | file://x:/photopub/docs/0000000395/b6f22623-6488-4aef-a508-08e7af2bfcef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d77e20c1_24c4_451a_9f44_f8ac6eefd4e7
ELIN-532500-2016 | EL-346553-2016 | 2/24/2016 11:59:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | 240 v, 40 a range connected for temporary heat without proper junction box leaving exposed connection subject to damage and potential shock hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Thacker.png | file://x:/photopub/docs/0000000395/52b53f13-f166-43df-847a-233cbee4fe8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d77e20c1_24c4_451a_9f44_f8ac6eefd4e7
ELIN-532500-2016 | EL-346553-2016 | 2/24/2016 11:59:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | 240 v, 40 a range connected for temporary heat without proper junction box leaving exposed connection subject to damage and potential shock hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4.png | file://x:/photopub/docs/0000000395/0171acc9-0091-4ba9-9aef-6c7e859ba3a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d77e20c1_24c4_451a_9f44_f8ac6eefd4e7
ELIN-532500-2016 | EL-346553-2016 | 2/24/2016 11:59:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | 240 v, 40 a range connected for temporary heat without proper junction box leaving exposed connection subject to damage and potential shock hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 2.png | file://x:/photopub/docs/0000000395/8c7d8da0-44f7-472d-a573-26d399d68d8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d77e20c1_24c4_451a_9f44_f8ac6eefd4e7
ELIN-564704-2016 | EL-379350-2016 | 5/12/2016 11:18:34 AM | ASSESS: EL: Final | png | #asFound | EL100 | Conductors, Mis-use of flexible cords. | 4 | 4 | Flexible cord is not approved to be used as a substitute for permanent wiring or for use in an under ground location. This is because it does not have a flame test rating, may not provide adequate mechanical protection for the conductors, and does not have properties that make it suitable for burial. This installation has a flexible cord used as a 120/240V sub- feed cable that is permanently connected to the service panel inside a wall and then exits the building to run under ground to an unknown location. The cable is energized and in use. Left uncorrected this is a potential shock and fire hazard if the cable gets mechanically damaged above ground of if the cable deteriorates where installed under ground. | 4 | Conductors, Mis-use of flexible cords. | Front_of_house_.png | file://x:/photopub/docs/0000000429/520b07bb-f654-41ee-9b0a-196cd7acf1c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff9d641_03b6_4e9a_90ba_12bd39447bb7
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 13.png | file://x:/photopub/docs/0000000409/a9a6a174-9c85-479c-8544-f4d28dabcb6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 16.png | file://x:/photopub/docs/0000000409/0b65812c-7fde-4375-89b7-627ab55c2d79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 15.png | file://x:/photopub/docs/0000000409/d2adf66e-b024-49b3-a87e-24ee636c42c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-549532-2016 | EL-261918-2015 | 3/24/2016 4:44:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt branch circuits installed and run in non-metallic sheathed raceway in concrete (coreline) which comes out of concrete slab and transitions to run in EMT raceway run on surface of building without the use of proper approved electrical equipment for transitioning from non-metallic raceway to EMT raceway. When electrical equipment is not approved and is not installed and used as required for approved electrical equipment installation work, the electrical equipment could become damaged and could energized conductors could get damaged and could become an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 2.png | file://x:/photopub/docs/0000000409/49803de6-3f05-4e36-b2c4-b8377b02091f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb35cc68_75d2_4dbc_9329_1145d62103ca
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 18.png | file://x:/photopub/docs/0000000409/73871126-4cb2-452a-9b79-747456fc7d2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 14.png | file://x:/photopub/docs/0000000409/7d88372d-a589-4943-b557-2fd135a51072.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-549532-2016 | EL-261918-2015 | 3/24/2016 4:44:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt branch circuits installed and run in non-metallic sheathed raceway in concrete (coreline) which comes out of concrete slab and transitions to run in EMT raceway run on surface of building without the use of proper approved electrical equipment for transitioning from non-metallic raceway to EMT raceway. When electrical equipment is not approved and is not installed and used as required for approved electrical equipment installation work, the electrical equipment could become damaged and could energized conductors could get damaged and could become an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 4.png | file://x:/photopub/docs/0000000409/3d4516b6-d350-454b-828a-46ebf0cafb42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb35cc68_75d2_4dbc_9329_1145d62103ca
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 11.png | file://x:/photopub/docs/0000000409/8e143663-2e5b-4fb6-8283-b4eecac3e799.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
ELIN-549532-2016 | EL-261918-2015 | 3/24/2016 4:44:35 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt branch circuits installed and run in non-metallic sheathed raceway in concrete (coreline) which comes out of concrete slab and transitions to run in EMT raceway run on surface of building without the use of proper approved electrical equipment for transitioning from non-metallic raceway to EMT raceway. When electrical equipment is not approved and is not installed and used as required for approved electrical equipment installation work, the electrical equipment could become damaged and could energized conductors could get damaged and could become an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 1.png | file://x:/photopub/docs/0000000409/e359d26d-191a-4b59-84d1-1febb9812069.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb35cc68_75d2_4dbc_9329_1145d62103ca
ELIN-544668-2016 | EL-261918-2015 | 3/23/2016 5:01:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found 120/240 volt exposed, energized, hazardous, non-compliant and unapproved electrical equipment with splicing of energized bare and insulated conductors that were interconnected between temporary construction service electrical equipment and permanent building wiring. The above installation for power, distribution and lighting circuits is an electrical fire or shock hazard to people and property if there was contact made with above energized electrical equipment. | 3 | Conductors Equipment is not approved for the specific use. | 17.png | file://x:/photopub/docs/0000000409/cbcd1504-2a46-4266-9e6b-002fc7252cd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049d0779_f192_4cfa_8d69_8db76ad7705b
GAIN-532453-2016 | GA-300520-2015 | 2/24/2016 1:51:03 PM | ASSESS: GA: Final | png | #asFound | GA135 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | 2 | 2 |  | 2 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | Relief_2305-200.png | file://x:/photopub/docs/0000000395/251d4066-906b-4678-9702-abb688ea2271.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee4f9868_abf1_4453_9219_5409bdb82bb6
GAIN-532453-2016 | GA-300520-2015 | 2/24/2016 1:51:03 PM | ASSESS: GA: Final | png | #asFound | GA135 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | 2 | 2 |  | 2 | Hot Water Tank Temperature and pressure relief termination piping not installed or in a non compliant manner | 2305-200.png | file://x:/photopub/docs/0000000395/8ee9905d-4aa9-4b3f-96ad-a2b8517d6ee6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee4f9868_abf1_4453_9219_5409bdb82bb6
ELIN-570415-2016 | EL-380334-2016 | 5/4/2016 5:17:29 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | Found service grounding conductor does not have any support at all to the structure and grounding conductor is not free from possible mechanical damage where located in underside of relocatable structure and there is no raceway protection installed over top of service grounding conductor located outdoors. When service grounding conductor is not secured and supported and protected from possible mechanical the conductor could get damaged or could be broken completely off and there would be no grounding of service and the electrical system could become a shock hazard to people and property. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Service_grounding_conductor_is_not_properly_protected_from_mechanical_damage.png | file://x:/photopub/docs/0000000427/e7422f15-8d80-4b03-a170-bb89716b5b3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__27d71c4f_ec9f_4653_a485_bdcbbe049691
ELOP-569258-2016 | EL-000758-2013 | 5/2/2016 8:14:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | The front panel cover was off the house panel in a power shed. This exposed the bus to possible accidental contact by individuals working in the shed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Cover_on_floor.png | file://x:/photopub/docs/0000000427/4e53e59e-1516-4543-8717-d7927489afe2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b7683d9_1b0c_4230_bfec_5caa1a4aa91d
ELOP-194691-2014 | 1122 | 5/4/2016 9:49:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | The inside of a high voltage vault the main disconnect has not been tested or cleaned in years. The school closed in 2008 and the high voltage service requires cleaning and testing of the disconnect to ensure the disconnect can safely open all energized conductors. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Dirty_vault.png | file://x:/photopub/docs/0000000427/3c1aa4f0-fefa-4a35-b5a1-721719b00bea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4ba268c_8797_430f_a174_177b30aabd19
ELOP-569258-2016 | EL-000758-2013 | 5/2/2016 8:14:09 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | The front panel cover was off the house panel in a power shed. This exposed the bus to possible accidental contact by individuals working in the shed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | House_panel.png | file://x:/photopub/docs/0000000427/5dbbb607-2370-475f-b8d0-5927b599d0c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b7683d9_1b0c_4230_bfec_5caa1a4aa91d
ELOP-194691-2014 | 1122 | 5/4/2016 9:49:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | The inside of a high voltage vault the main disconnect has not been tested or cleaned in years. The school closed in 2008 and the high voltage service requires cleaning and testing of the disconnect to ensure the disconnect can safely open all energized conductors. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Switch.png | file://x:/photopub/docs/0000000427/7b0f5559-8b85-45e8-a86a-3ee4616032d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4ba268c_8797_430f_a174_177b30aabd19
ELIN-555092-2016 | EL-370709-2016 | 4/13/2016 6:30:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 3 | DB2 underground raceway not concrete encased as required by code. Temporary to permanent weatherproof enclosure depth does not allow access to receptacles with door closed. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | temporary_to_permanent_service_compartment.png | file://x:/photopub/docs/0000000415/69bf852f-a57a-48ad-b15c-723e965daded.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9907267f_d1b4_4766_89fa_3e944135fff9
ELIN-546232-2016 | EL-368167-2016 | 3/21/2016 2:48:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The grounded service conductor was improperly terminated onto the panel case. The result could be a high impedance ground that would be a shock hazard during a fault condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Mast_height_low.png | file://x:/photopub/docs/0000000406/c638a086-6f14-4446-a429-762d9167dd4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fb73bc3_fbbe_49c0_8d9a_fbb13f884bc0
ELIN-546232-2016 | EL-368167-2016 | 3/21/2016 2:48:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The grounded service conductor was improperly terminated onto the panel case. The result could be a high impedance ground that would be a shock hazard during a fault condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Service_panel.png | file://x:/photopub/docs/0000000406/9bc73464-3691-41b0-9ae2-98994972ec82.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fb73bc3_fbbe_49c0_8d9a_fbb13f884bc0
ELIN-550922-2016 | EL-349574-2016 | 3/31/2016 7:42:34 AM | ASSESS: EL: Final | png | #asFound | EL110 | Conductors Conductors are not suitably identified. | 3 | 3 | A 70 amp 208 volt 3 phase generator back up power supply was installed. In one piece of electrical equipment both the utility and generator system neutral are present. The generator system neutral has not been identified to differentiate it from the utility neutral. During service or maintenance, if the incorrect neutral conductor was to be interrupted under load, injury to persons or damage to property could occur | 3 | Conductors Conductors are not suitably identified. | Generator_system_neutral_conductor_not_identified_as_required.png | file://x:/photopub/docs/0000000410/603d26de-9b48-469c-b300-2ac57adcd166.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e51d45a6_1e73_44a1_ba98_9dbcacdec183
ELIN-532118-2016 | EL-347287-2016 | 2/24/2016 2:24:21 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | A 30 amp three phase 3 wire cord cap is being used to power a 120 V panel. This could result in a shock hazard | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 30A_3_phase_3_wire_cord_cap.png | file://x:/photopub/docs/0000000395/286537e5-dde6-4cd2-9438-5400168be5fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad0a6b59_873b_43f9_a86b_15277a887f6f
ELIN-573206-2016 | EL-349126-2016 | 5/9/2016 2:29:34 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Convenience outlets in bedroom areas exceed permissible spacing requirements. Installed branch circuit is supplied by 120 volts and protected by a 15 amp overcurrent device. This is a thermal issue. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Receptacle_spacing_.png | file://x:/photopub/docs/0000000427/e70e36ae-be5a-4b0c-a427-b9fd0cc951ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22beccc2_2d80_47af_aa36_ba848a7fd9ef
ELIN-535517-2016 | EL-349148-2016 | 3/1/2016 1:07:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A 200 amp, 120/240 volt distribution panel utilized for temporary power is not installed in an approved enclosure for a wet location. This could cause equipment damage should moisture enter the distribution panel. This is a thermal and possible shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Poly_wrapped_distribution_panel.png | file://x:/photopub/docs/0000000398/6a7ffbff-57eb-4630-80fa-92ab6bf59af0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6d3afb77_1955_4df3_9ffb_63f26ca37a65
ELIN-534142-2016 | EL-352060-2016 | 3/1/2016 10:17:14 AM | ASSESS: EL: Final | png | #asFound | EL054 | Protection and control Receptacle rating is not compatible with branch circuit rating | 4 | 4 | 15 amp 120 volt rated receptacle installed on a 20 amp 120 volt overcurrent device. This is a thermal issue. | 4 | Protection and control Receptacle rating is not compatible with branch circuit rating | 15A_receptacle_installed_on_20A_breaker.png | file://x:/photopub/docs/0000000399/9d021b2f-2442-4f05-9ed8-7fa225802b71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__718d4074_fff3_470e_b690_c553ebb88b53
ELIN-533809-2016 | EL-351608-2016 | 3/2/2016 4:00:53 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | The 120 volt 15 amp receptacle is energized and exposed to causing a shock to personnel. No protection for the prevention of shock has been installed | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Energized_outlet.png | file://x:/photopub/docs/0000000399/25ec801b-f15a-43fd-a8bb-84d0d3f3369e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ecf5cf26_e6b0_46cd_96fe_edb61fde039d
BPVIN-557744-2016 | UW-374943-2016 | 4/11/2016 3:37:10 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | Upon assessment of heat exchanger (1.12m long and 0.61m wide) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 257*Fahrenheit, is determined that there is no pressure relief device installed on the side receiving heat. Inadvertent operation of heat exchanger with secondary side (side receiving heat) valves shut may subject vessel pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | SWIMMING_POOL_HEAT_EXCHANGER_No_4_WITHOUT_RELIEF_VALVE.png | file://x:/photopub/docs/0000000417/dcd0f5b6-1c2f-439f-a095-a3e3b1c0bbda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b433aba_bc5d_4c8e_9169_f143fbc9306f
ELOP-337238-2015 | EL-213785-2015 | 4/13/2016 2:35:44 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Compression of outer metal jacket on to conductors with repetitive movement will eventually cut or ware into the conductors. This could cause a shock hazard. | 3 | Conductors Equipment is not approved for the specific use. | Ac90_used_for_flexible__cable.png | file://x:/photopub/docs/0000000416/966d0ae6-a10e-49b7-ab81-072beb4773cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb1f1111_78b3_4f79_bb59_cd519e78b5a8
ELIN-560740-2016 | EL-150656-2014 | 4/18/2016 4:58:42 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMW cable for septic system has no mechanical protection. Where it exits the ground. It would be probable to conclude that the possibility of damaging the conductor in time would be 100%. The hazards could be shock and thermal. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMW_exit_.png | file://x:/photopub/docs/0000000418/fe5d67ea-b908-453d-a504-79dba197e1ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dbc2f02_c3e6_4350_a0ad_2930a952ceb6
ELIN-560740-2016 | EL-150656-2014 | 4/18/2016 4:58:42 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMW cable for septic system has no mechanical protection. Where it exits the ground. It would be probable to conclude that the possibility of damaging the conductor in time would be 100%. The hazards could be shock and thermal. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Telephone.png | file://x:/photopub/docs/0000000418/c0e5b213-1b37-453c-934e-383c28fcf9fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dbc2f02_c3e6_4350_a0ad_2930a952ceb6
ELIN-560740-2016 | EL-150656-2014 | 4/18/2016 4:58:42 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMW cable for septic system has no mechanical protection. Where it exits the ground. It would be probable to conclude that the possibility of damaging the conductor in time would be 100%. The hazards could be shock and thermal. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Main_distribution.png | file://x:/photopub/docs/0000000418/f761a6bc-c782-4ba4-b6c5-b7f281840501.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dbc2f02_c3e6_4350_a0ad_2930a952ceb6
ELIN-560740-2016 | EL-150656-2014 | 4/18/2016 4:58:42 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMW cable for septic system has no mechanical protection. Where it exits the ground. It would be probable to conclude that the possibility of damaging the conductor in time would be 100%. The hazards could be shock and thermal. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Service_with_no_exterior_clading.png | file://x:/photopub/docs/0000000418/0c4a671c-1447-468e-a339-bd7fc971a8cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7dbc2f02_c3e6_4350_a0ad_2930a952ceb6
ELOP-229619-2014 | 3193183 | 4/20/2016 7:58:06 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL176 | Installation of electrical equipment Covers or panels removed, exposed energized parts. | 4 | 4 | High voltage transformer installations must be suitably fenced or guarded to prevent accidental contact. In this mill installation a 2300/6900 volt transformer was contained within a chain link fence. Two egress gates were removed however. | 4 | Installation of electrical equipment Covers or panels removed, exposed energized parts. | Transformer_compound_to_lake.png | file://x:/photopub/docs/0000000418/5df9e0a4-368b-4d6a-b90d-bcc93d61acf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9451af7c_28a7_443d_9777_bc4106c1f286
BPVOP-570691-2016 | 4670083 | 5/17/2016 10:58:26 AM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Manifold_and_no_siphons.png | file://x:/photopub/docs/0000000431/d1d2191e-1ee8-47e3-a496-9ce326514182.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81f55f3c_38c4_4f5a_82d4_46add26c621c
BPVIN-552329-2016 | BPV-350098-2016 | 5/17/2016 9:46:19 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 2 | An emergency shutdown switch was provided at one door to the boiler room and not the other as required by code. The plant is a low pressure steam plant and it's located in a saw mill. In case of a boiler emergency the emergency shutdown switch located at the other nearby door could be used to shut the boiler down. The chief engineer was unaware of this requirement. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000431/243e02b1-d034-40dd-9331-149839888398.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__972facfe_89c3_481b_9b64_cd77c75803b7
GAIN-552952-2016 | GA-317568-2015 | 4/25/2016 4:34:40 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | All appliances require combustion air. No combustion air found on site. Upset flame conditions. Possible creating high levels of carbon monoxide. | 4 | Combustion air supply missing | Venting_3.png | file://x:/photopub/docs/0000000422/c04381b3-2a14-4af7-8e17-918785837212.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac5e0b9_7e96_4f62_8872_cf760c16d1d9
GAIN-552952-2016 | GA-317568-2015 | 4/25/2016 4:34:40 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | All appliances require combustion air. No combustion air found on site. Upset flame conditions. Possible creating high levels of carbon monoxide. | 4 | Combustion air supply missing | Venting__4.png | file://x:/photopub/docs/0000000422/2f35cfa1-af1a-49bc-983d-f07c613ed4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac5e0b9_7e96_4f62_8872_cf760c16d1d9
GAIN-552952-2016 | GA-317568-2015 | 4/25/2016 4:34:40 PM | ASSESS: GA: Final | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | All appliances require combustion air. No combustion air found on site. Upset flame conditions. Possible creating high levels of carbon monoxide. | 4 | Combustion air supply missing | Connector_1.png | file://x:/photopub/docs/0000000422/ef813dc0-3561-4768-8a5d-ef168a9f16e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac5e0b9_7e96_4f62_8872_cf760c16d1d9
ELIN-551802-2016 | EL-367033-2016 | 3/31/2016 1:10:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt indoor rated main distribution panel installed were exposed to the outdoor elements. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_exposed_to_outdoor_elements.png | file://x:/photopub/docs/0000000410/a4f382f0-892a-4707-85ad-1c185678cd21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fadf931a_f229_48f9_bb72_61075772e9f3
AMOP-548635-2016 | 2048343 | 3/22/2016 11:57:35 AM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | On this ride safety restraining device has 4 springs that keep the restraining device closed, these springs must be replaced annually. During a periodic inspection of the Spring Ride at its first set up for 2016 it was found that the restraining device springs had not been replaced since an unknown date in 2015. Failure of all 4 of these springs would cause the restraining device to open during operation and possibly eject a passenger from the ride. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Restraining_Device_Latch.png | file://x:/photopub/docs/0000000407/828ce595-92c8-4ddd-915a-1c4d18d83db2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64e7514e_0047_46ac_b2e8_fda3872c3202
AMOP-548635-2016 | 2048343 | 3/22/2016 11:57:35 AM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | On this ride safety restraining device has 4 springs that keep the restraining device closed, these springs must be replaced annually. During a periodic inspection of the Spring Ride at its first set up for 2016 it was found that the restraining device springs had not been replaced since an unknown date in 2015. Failure of all 4 of these springs would cause the restraining device to open during operation and possibly eject a passenger from the ride. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | Restraining_Device_on_Spring_Ride.png | file://x:/photopub/docs/0000000407/9ca3654f-9b73-4d53-8f3b-86730f293345.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__64e7514e_0047_46ac_b2e8_fda3872c3202
ELIN-566685-2016 | EL-335240-2016 | 5/2/2016 1:34:01 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | Inadequate installation of receptacles could cause a shock hazard to dwelling unit persons. Persons could start to use extension cords for permanent installations of plug in equipment, overtime the cord can become damaged which could cause fire/shock/damage to persons and property. | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | Inadequate_receptacle_installation.png | file://x:/photopub/docs/0000000423/515aa42d-f5a6-4af0-88c7-c1554525a582.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__465d74f8_8f86_4c8b_b37e_af8ddcc0e573
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Extension_cord__extension_cord_cables_feeding_into_electrical_panel.png | file://x:/photopub/docs/0000000431/ee45937d-141f-4d49-8ba2-b3c4b911dfdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Subpanel_located__Subpanel_located_on_dock.png | file://x:/photopub/docs/0000000431/921ae270-22b8-49d7-abce-41838384b689.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Termination_of__termination_of_feeder_conductor_into_subpanel_at_dock.png | file://x:/photopub/docs/0000000431/b3b02f4d-353e-41df-b157-6dc8ea4c1bc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Electrical_work_added_by_owner_to_service.png | file://x:/photopub/docs/0000000431/d63f0d2a-c545-437d-9392-d2b139d5b634.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Wiring_method__wiring_method_used_for_dock_electrical_wiring.png | file://x:/photopub/docs/0000000431/6c404527-3f0a-4bb3-b615-c3b03e636ce3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Feeder_cable__feeder_cable_disconnected_and_removed_from_electrical_panel.png | file://x:/photopub/docs/0000000431/132ccd3b-bdab-4332-88c6-244887ce1938.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Feeder_cable__feeder_cable_from_dock_and_into_subpanel.png | file://x:/photopub/docs/0000000431/31f02314-559c-46f9-8762-636363718411.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Safety_officer.png | file://x:/photopub/docs/0000000431/7e75e6be-6794-45a4-9740-5cc0ea30b827.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Safety_officer__safety_officer_red_tag_reapplied.png | file://x:/photopub/docs/0000000431/5cf922db-2bae-4667-b522-ba1a8f1aee7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Method_of__method_of_terminating_cableinto_junction___into_junction_box.png | file://x:/photopub/docs/0000000431/b6ac5348-bfcf-48b5-96d8-5fec0d8cd8ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
ELIN-579309-2016 | UW-388650-2016 | 5/17/2016 10:49:58 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Owner has performed additional electrical work without an electrical permit. subpanel that is located on the dock has exposed live bus when the panel door is open and there is a high likelihood of electrocution when someone reaches into the panel to turn off or on a circuit breaker. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 2_pole_40_amp_circuit_breaker_added_by_owner.png | file://x:/photopub/docs/0000000431/31cce8d7-628c-48d0-9bda-bf112742145e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__521222af_78e3_4bf2_abaa_c46e680d1fa4
EDIN-573233-2016 | ED-220305-2015 | 5/5/2016 9:31:37 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting and spring height of the escalator brake were not set properly to the manufacture specifications. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 118.1Nm (Newton Meter). The actual brake torque recorded was 90Nm. A proper brake torque setting could not be obtained without exceeding the brake spring height measurement as per the brake data plate. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving, uncontrolled, towards the lower landing. There are no redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was n | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate3.png | file://x:/photopub/docs/0000000427/a3e01814-d9f5-464c-9123-18dba2e12abc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b417c272_b3c9_44ae_bdb5_b305e5548fb4
EDIN-573236-2016 | ED-220290-2015 | 5/4/2016 8:42:01 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting and spring height of the escalator brake were not set properly to the manufacture specifications. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 118.1Nm (Newton Meter). The actual brake torque recorded was 77Nm. A proper brake torque setting could not be obtained without exceeding the brake spring height measurement as per the brake data plate. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving, uncontrolled, towards the lower landing. There are no redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was n | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate.png | file://x:/photopub/docs/0000000427/e40536ac-a187-48c1-9e12-688042466b5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a712f62_9bc8_4f3e_9b43_eb30ba97d5e5
EDIN-573234-2016 | ED-220304-2015 | 5/5/2016 9:16:39 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting and spring height of the escalator brake were not set properly to the manufacture specifications. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 118.1Nm (Newton Meter). The actual brake torque recorded was 79Nm. A proper brake torque setting could not be obtained without exceeding the brake spring height measurement as per the brake data plate. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving, uncontrolled, towards the lower landing. There are no redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was n | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate2.png | file://x:/photopub/docs/0000000427/1f500b8d-8294-4722-a378-005aed4a9d2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16908841_da41_4f0e_a4f6_3cb5dfbb844c
GAIN-556605-2016 | GA-374338-2016 | 4/14/2016 1:21:25 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Propane_Vapor_valves_.png | file://x:/photopub/docs/0000000419/7474cc8a-158c-42be-a751-24d4bc5d3719.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6e4bda1_6324_40bc_8120_19b1d5203aa4
GAUP-531347-2016 | UW-349187-2016 | 2/11/2016 2:34:53 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | 3/4" Corrugated stainless steel gas line is not bonded. Could cause fire or occupant injury if damaged from lightning strike or short in electrical wiring | 3 | Bonding for Corrugated Stainless Steel Tubing missing | Deer_Park_Unit_74.png | file://x:/photopub/docs/0000000395/5b417105-3a27-4419-8edd-9a89af04f382.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4fb1e3f8_971d_43af_b8f3_d2826ea433a4
ELIN-563373-2016 | EL-377263-2016 | 4/21/2016 10:19:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | No provisions for bonding neutral to ground in non-service rated load center | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Unapproved_guy_wire_guard.png | file://x:/photopub/docs/0000000419/8aa7aed5-323e-4aab-bcab-533c0b8cb91e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f435044_95d8_471f_b2f8_8d5e21004a9e
ELIN-563373-2016 | EL-377263-2016 | 4/21/2016 10:19:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | No provisions for bonding neutral to ground in non-service rated load center | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Ground_conductor_not_properly_entered_.png | file://x:/photopub/docs/0000000419/440f354b-139d-45f2-a9e0-200f53a8e47f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f435044_95d8_471f_b2f8_8d5e21004a9e
ELIN-563373-2016 | EL-377263-2016 | 4/21/2016 10:19:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | No provisions for bonding neutral to ground in non-service rated load center | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Neutral_not_bonded_to_ground_in_load_center.png | file://x:/photopub/docs/0000000419/f51b7976-1382-4d4c-a1be-aef7d2556d0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f435044_95d8_471f_b2f8_8d5e21004a9e
ELIN-563373-2016 | EL-377263-2016 | 4/21/2016 10:19:57 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | No provisions for bonding neutral to ground in non-service rated load center | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | RV_sub-distribution_load_center.png | file://x:/photopub/docs/0000000419/cf7b79d6-c825-4716-9fda-c681be44a72f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f435044_95d8_471f_b2f8_8d5e21004a9e
EDIN-573235-2016 | ED-220299-2015 | 5/4/2016 9:01:13 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED040 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | 4 | 4 | The escalator brake will stop the movement of the escalator steps when there is an emergency stop activated or a overspeed situation. During an inspection, it was found that the torque setting and spring height of the escalator brake were not set properly to the manufacture specifications. At the time of inspection, the brake torque was below the minimum brake torque setting listed on the brake data plate. The minimum brake torque listed on the brake data plate is 118.1Nm (Newton Meter). The actual brake torque recorded was 86Nm. A proper brake torque setting could not be obtained without exceeding the brake spring height measurement as per the brake data plate. When the escalator is loaded and an emergency stop is activated or an overspeed situation occurs, the brake may not be able to stop the escalator steps from moving, uncontrolled, towards the lower landing. There are no redundant means that would stop the movement of the escalator steps under this condition. The escalator was not in operation and was n | 4 | Wear/Defects resulting in failure of the brake to stop car/step. Additional means of deceleration are functional. Risk Reg ED-02 | Brake_Data_Plate1.png | file://x:/photopub/docs/0000000427/356385dc-2f71-474e-8416-5936258d9d5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a0ddd7bb_8bcd_4033_825e_aadc13c5e450
ELIN-534799-2016 | EL-154988-2014 | 3/1/2016 2:43:25 PM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | During an assessment 2 electrical motors had been installed and connected to an electrical source, the motors did not bear evidence of approval as outlined in BCSA's bulletin B-E3 071019 3 Revision 6 Unapproved equipment may create a fire and shock hazards because they have not been evaluated by an accreditation organization recognized by the Standards Council of Canada. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Photo_motor__1.png | file://x:/photopub/docs/0000000398/260ba8bc-8e6b-4f1b-a661-5545a2c35055.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99d75384_b761_4be8_bc95_a71859cf9579
ELIN-534799-2016 | EL-154988-2014 | 3/1/2016 2:43:25 PM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | During an assessment 2 electrical motors had been installed and connected to an electrical source, the motors did not bear evidence of approval as outlined in BCSA's bulletin B-E3 071019 3 Revision 6 Unapproved equipment may create a fire and shock hazards because they have not been evaluated by an accreditation organization recognized by the Standards Council of Canada. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Photo_of_motor_2.png | file://x:/photopub/docs/0000000398/17a2e224-da67-4cc2-b5c1-e5982cf74b0c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99d75384_b761_4be8_bc95_a71859cf9579
ELIN-534799-2016 | EL-154988-2014 | 3/1/2016 2:43:25 PM | ASSESS: EL: Final | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | During an assessment 2 electrical motors had been installed and connected to an electrical source, the motors did not bear evidence of approval as outlined in BCSA's bulletin B-E3 071019 3 Revision 6 Unapproved equipment may create a fire and shock hazards because they have not been evaluated by an accreditation organization recognized by the Standards Council of Canada. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | _No_evidence_no_evidence_of_approval_on_motor.png | file://x:/photopub/docs/0000000398/20ee452e-b062-4e84-bb19-e40f2771242c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__99d75384_b761_4be8_bc95_a71859cf9579
GAIN-535714-2016 | GA-303353-2015 | 3/4/2016 4:41:31 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | 2 boilers were installed using venting materials that are not listed as approved venting materials in the manufacturers certified installation instructions. The incorrect venting materials may be exposed to flue gas temperature in excess of their manufacturers rating, eventually causing a failure of the appliances venting system. | 3 | Unapproved venting material | CPVC_Venting.png | file://x:/photopub/docs/0000000400/e8b98ead-5ac9-4178-9e98-bc6fc21ebbab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40429b34_3f2c_4afb_8c69_56a0d1f16b70
GAIN-535714-2016 | GA-303353-2015 | 3/4/2016 4:41:31 PM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | 2 boilers were installed using venting materials that are not listed as approved venting materials in the manufacturers certified installation instructions. The incorrect venting materials may be exposed to flue gas temperature in excess of their manufacturers rating, eventually causing a failure of the appliances venting system. | 3 | Unapproved venting material | Venting_instructions_.png | file://x:/photopub/docs/0000000400/8e8fe95b-cf61-4951-8611-e20cb768d265.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40429b34_3f2c_4afb_8c69_56a0d1f16b70
ELOP-226631-2014 | 1982 | 5/18/2016 11:45:37 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Covers are to be installed as required to prevent accidental contact with energized electrical components. In this school installation a welded plate designed to cover a 600 volt chase was installed such that a person could reach into a pit and up to a live bus bar. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Into_pit.png | file://x:/photopub/docs/0000000431/e2b808b9-c539-427d-99a5-020c45e5667d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f5c68d84_019b_4877_8440_0ad967bd1d2e
ELOP-226641-2014 | 1990 | 5/18/2016 9:32:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Interior piping systems must be bonded to ground. In this school a propane system was added after the electrical system had been completed and the bond requirement was overlooked. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Propane_in_boiler_room.png | file://x:/photopub/docs/0000000431/b88be605-b1e6-4804-ab81-e7223a2b16de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90ed6466_a725_4b9e_9361_4185bbd8beba
ELOP-226592-2014 | 1986 | 5/18/2016 10:31:43 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles within 1.5 m of sinks must be equipped with GFCI protection. In this school several sinks were installed close to receptacles without GFCI protection. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Multipurpose_room.png | file://x:/photopub/docs/0000000431/816b72f8-1fbd-4a5e-b7cd-0345b7a00ca3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e20aa07f_975d_4fb6_a743_e90de1622c1c
ELOP-226499-2014 | 6287 | 3/11/2016 1:01:03 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL276 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | 2 | 2 | High voltage equipment should be cleaned and inspected regularly to avoid accumulations of dust and to ensure protective devices will function in a fault. In this high voltage vault no records could be found showing the equipment had been serviced since its installation in the 1970s. | 2 | Life Safety System, Fire Alarm, Emergency systems, Regular maintenance has not been conducted. | Main.png | file://x:/photopub/docs/0000000403/5db64cbc-f01d-4d89-ad5d-17fc9778698b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31009adf_d17d_4e61_a657_860ebe8de8d8
ELIN-562885-2016 | EL-373659-2016 | 4/25/2016 7:17:44 AM | ASSESS: EL: Final | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 200 amp, 120/240 volt main distribution panel has conductors other then service conductors passing through the service box. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Conductors_passing_through_service_box.png | file://x:/photopub/docs/0000000420/86aa6f95-8712-4b7f-bc61-b802af72158b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4403c0b6_134c_4e30_9758_313d665fceaa
ELIN-574148-2016 | EL-384086-2016 | 5/18/2016 2:43:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Enclosure that houses consumer service equipment is not approved for area weather. Water could eventually enter consumer service equipment and could become a shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Enclosure.png | file://x:/photopub/docs/0000000431/c404e759-61d6-4626-8048-814961625d2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d625881f_74e8_49cd_bf24_6142ad8387a7
ELIN-570364-2016 | UW-382231-2016 | 5/3/2016 12:28:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Conduit for garage door sensors has been damaged by steel door cables. Up and down movement of door has steel cables rubbing on conduit, and conduit sidewall has worn through. Continually sliding cables will cut into the conductors in the conduit over time, and may cause a shock or fire to persons and property. | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | Conduit_sidewall_worn_through_by_door_cable.png | file://x:/photopub/docs/0000000424/b375952c-86aa-4266-9c1e-37bf722dc04c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__49e3a1f1_84ef_46b6_a4ed_b14309c33dba
ELIN-579578-2016 | EL-388227-2016 | 5/18/2016 2:15:47 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL205 | All Classes, All Zones Markings | 1 | 1 | Unapproved equipment used as raceways in 3 locations | 1 | All Classes, All Zones Markings | Raceway3.png | file://x:/photopub/docs/0000000431/c9409ccf-ecb9-4835-a9bc-2d07ced5e41c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0ec4586_9f5f_4b60_be77_9dc076fb1af8
ELIN-579578-2016 | EL-388227-2016 | 5/18/2016 2:15:47 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL205 | All Classes, All Zones Markings | 1 | 1 | Unapproved equipment used as raceways in 3 locations | 1 | All Classes, All Zones Markings | Raceway.png | file://x:/photopub/docs/0000000431/90f6044a-e32a-4656-b7d1-61eacf14bde2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0ec4586_9f5f_4b60_be77_9dc076fb1af8
ELIN-579578-2016 | EL-388227-2016 | 5/18/2016 2:15:47 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL205 | All Classes, All Zones Markings | 1 | 1 | Unapproved equipment used as raceways in 3 locations | 1 | All Classes, All Zones Markings | Raceway2.png | file://x:/photopub/docs/0000000431/1e73a3bf-6897-421a-8c26-ec876d5dc17d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0ec4586_9f5f_4b60_be77_9dc076fb1af8
ELIN-554834-2016 | EL-279493-2015 | 4/6/2016 2:26:00 PM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | A 200 amp service cable operating at 240 volts is exposed to mechanical damage on the exterior of the building. The mechanical protection found on this site did not extend to a minimum safe height above grade and did not extend below grade as required to ensure safe longevity of cable. This cable was a service cable and as such lacks effective overcurrent protection. This coupled with the exposure to mechanical damage both above and below grade can lead to hazards to persons or property to should the cable be damaged due to impact injury or damage while gardening or landscaping around the dwelling. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Mechanical_protection_does_not_extend_below_grade_or_high_enough_on_exterior_of_buildin__connector_loose_.png | file://x:/photopub/docs/0000000413/d531edeb-5ddf-4779-9083-c6f9cb4bc456.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70658deb_1d1a_4b90_86ab_07d9777b1c92
BPVOP-574190-2016 | 4616480 | 5/10/2016 10:13:15 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Un_identified_leak_traces.png | file://x:/photopub/docs/0000000428/38050a4d-08c2-43e2-8fd8-b60fb13f16ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f880bb1_4f78_4657_a7bf_76951c06d566
ELIN-574924-2016 | EL-379088-2016 | 5/13/2016 1:42:59 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL147 | Installation of electrical equipment Separation from combustible material is not provided. | 4 | 3 | Vapour boot will not be able to to have separation of 13mm without support. | 4 | Installation of electrical equipment Separation from combustible material is not provided. | Non-_IC_pot_light_with_vapour_boot.png | file://x:/photopub/docs/0000000430/3ac0f819-31b6-4500-a7e5-705b6dc50447.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ccc9ab65_5517_4b8f_834b_b7ea03a12c90
ELIN-543431-2016 | EL-360418-2016 | 3/18/2016 3:28:06 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Poa.png | file://x:/photopub/docs/0000000405/0ad4fcdc-4bc6-4bce-9aba-cc00edd7e328.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__104b342e_7a9c_40bd_bafd_e325300bfaba
ELIN-550734-2016 | EL-348662-2016 | 3/30/2016 3:16:19 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL152 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 2 | 2 |  | 2 | Installation of electrical equipment, Equipment is approved, and installation instructions have not been satisfied. | 3_gang_box_requiring_support_from_2_sides.png | file://x:/photopub/docs/0000000409/035bc98b-d655-4345-8523-ea846d228101.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7e7eab4_2c3f_43f6_8e92_1a6e7b838440
BPVOP-575880-2016 | 2954047 | 5/12/2016 1:08:06 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | During the inspection of a How Water Boiler with a MAWP of 87 psig I found a large amount of combustible materials( cardboard boxes, cleaning solutions, etc) stored against or on the boiler. This can cause a fire. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Combustibles_.png | file://x:/photopub/docs/0000000429/9bd98966-1479-43d9-81e0-c48d100f39da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d67b4f9a_4ea9_4cd8_8747_c76e77798d26
ELIN-560001-2016 | EL-367340-2016 | 4/18/2016 4:47:36 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | This assessment found the panel to be exposed to the weather. If the panel became wet there is a hazard that the main breaker would not operate properly creating a shock/fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel.png | file://x:/photopub/docs/0000000417/8b5984b1-0c00-4aee-8e74-fa786b9fc6b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4e296eb8_1902_42cb_9db0_cecafc591663
ELIN-574878-2016 | UW-385902-2016 | 5/11/2016 3:31:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Cover left off energized panel, feeder to unsafe temp panel | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | panel.png | file://x:/photopub/docs/0000000428/4c6c5923-76ff-40e3-b59b-8416c83e0d5f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e6e557f_05d1_4fe8_aec3_99e8907720ae
ELIN-574878-2016 | UW-385902-2016 | 5/11/2016 3:31:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Cover left off energized panel, feeder to unsafe temp panel | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Temp_panel.png | file://x:/photopub/docs/0000000428/de9d7d0a-e97e-4014-8f9d-6f10b939261b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e6e557f_05d1_4fe8_aec3_99e8907720ae
ELIN-574878-2016 | UW-385902-2016 | 5/11/2016 3:31:46 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Cover left off energized panel, feeder to unsafe temp panel | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Feeder.png | file://x:/photopub/docs/0000000428/79ab2079-7dbe-40bc-bb16-f8e6d43c237b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e6e557f_05d1_4fe8_aec3_99e8907720ae
GAUP-577829-2016 | UW-387764-2016 | 5/16/2016 2:18:52 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The furnace and hot water tank were vented to the outdoors using ABS Cellular Core plastic pipe. The venting for the furnace was loose with joints that could be pulled apart by hand. The venting for the hot water tank was completely broken apart at an elbow and was allowing the appliance to vent freely into the mechanical room. Allowing gas appliance flue products to enter an occupied space could result in carbon monoxide exposure resulting in sickness or death. | 5 | Venting system not connected or dislodged from energized appliance | Water_heater_venting.png | file://x:/photopub/docs/0000000430/24d778ec-2671-4a56-9e8f-d67eda287506.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb55ff38_b7e1_4385_b88b_18fad079da83
GAUP-577829-2016 | UW-387764-2016 | 5/16/2016 2:18:52 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | The furnace and hot water tank were vented to the outdoors using ABS Cellular Core plastic pipe. The venting for the furnace was loose with joints that could be pulled apart by hand. The venting for the hot water tank was completely broken apart at an elbow and was allowing the appliance to vent freely into the mechanical room. Allowing gas appliance flue products to enter an occupied space could result in carbon monoxide exposure resulting in sickness or death. | 5 | Venting system not connected or dislodged from energized appliance | Cellcore_venting.png | file://x:/photopub/docs/0000000430/21d24db2-1505-4f5e-bf65-5fa9d2c0f161.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fb55ff38_b7e1_4385_b88b_18fad079da83
ELIN-577954-2016 | EL-377302-2016 | 5/16/2016 4:23:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL044 | Other categories may be referenced depending upon the as found hazard. Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Holes in live panel, this is a shock hazard. Exposed conductors hooked up to breakers that are not properly locked out, this is a shock hazard. | 4 | Other categories may be referenced depending upon the as found hazard. Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | A.png | file://x:/photopub/docs/0000000430/d54e7e48-55a0-4ef4-9c50-b607c2ab6b30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2398bf1e_dacb_4f13_b530_3b43f4086af6
ELIN-577954-2016 | EL-377302-2016 | 5/16/2016 4:23:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL044 | Other categories may be referenced depending upon the as found hazard. Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Holes in live panel, this is a shock hazard. Exposed conductors hooked up to breakers that are not properly locked out, this is a shock hazard. | 4 | Other categories may be referenced depending upon the as found hazard. Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | B.png | file://x:/photopub/docs/0000000430/93afbb35-592b-4948-8d19-d784fd6f53a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2398bf1e_dacb_4f13_b530_3b43f4086af6
ELIN-573469-2016 | EL-221488-2015 | 5/9/2016 11:58:58 AM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Adequate clearance of high voltage conductor not provided between the neutral and line conductor on a terminal pole, this is a potential shock hazard. No kirk key interlock provided between the transformer and load break switch, this is a fire and shock hazard as the energized transformer parts could be accessed while energized. Fused cut out installed on the line side of the load break switch, this is a shock and fire hazard because the fused cutouts are not rated to be opened under load. | 4 | Protection and control Interrupt ratings are not adequate for the installation | F.png | file://x:/photopub/docs/0000000427/80e7a92e-1457-4904-9d1a-a8ad1795519c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e07042_8a8a_49b8_bf46_4ddcc48259fe
ELOP-507118-2016 | EL-234473-2015 | 5/6/2016 1:59:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Unapproved equipment in a hazardous location. This is an explosion hazard as heat or sparks could ignite the paint fumes in the vicinity. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 2.png | file://x:/photopub/docs/0000000427/fcbc9291-e726-4eda-8dae-acf59be1dcff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14777b6a_a805_4e86_8b0d_1a75b269c8c3
ELIN-573469-2016 | EL-221488-2015 | 5/9/2016 11:58:58 AM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Adequate clearance of high voltage conductor not provided between the neutral and line conductor on a terminal pole, this is a potential shock hazard. No kirk key interlock provided between the transformer and load break switch, this is a fire and shock hazard as the energized transformer parts could be accessed while energized. Fused cut out installed on the line side of the load break switch, this is a shock and fire hazard because the fused cutouts are not rated to be opened under load. | 4 | Protection and control Interrupt ratings are not adequate for the installation | C.png | file://x:/photopub/docs/0000000427/f26450e6-527d-4897-9622-802f4a11637b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e07042_8a8a_49b8_bf46_4ddcc48259fe
ELIN-573469-2016 | EL-221488-2015 | 5/9/2016 11:58:58 AM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Adequate clearance of high voltage conductor not provided between the neutral and line conductor on a terminal pole, this is a potential shock hazard. No kirk key interlock provided between the transformer and load break switch, this is a fire and shock hazard as the energized transformer parts could be accessed while energized. Fused cut out installed on the line side of the load break switch, this is a shock and fire hazard because the fused cutouts are not rated to be opened under load. | 4 | Protection and control Interrupt ratings are not adequate for the installation | D.png | file://x:/photopub/docs/0000000427/7aed7bb4-fbb5-45bf-999c-d0aff4ffb728.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e07042_8a8a_49b8_bf46_4ddcc48259fe
ELOP-507118-2016 | EL-234473-2015 | 5/6/2016 1:59:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Unapproved equipment in a hazardous location. This is an explosion hazard as heat or sparks could ignite the paint fumes in the vicinity. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 3.png | file://x:/photopub/docs/0000000427/56dec461-a0db-4312-ba93-36ba8e40c3f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14777b6a_a805_4e86_8b0d_1a75b269c8c3
ELIN-573469-2016 | EL-221488-2015 | 5/9/2016 11:58:58 AM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Adequate clearance of high voltage conductor not provided between the neutral and line conductor on a terminal pole, this is a potential shock hazard. No kirk key interlock provided between the transformer and load break switch, this is a fire and shock hazard as the energized transformer parts could be accessed while energized. Fused cut out installed on the line side of the load break switch, this is a shock and fire hazard because the fused cutouts are not rated to be opened under load. | 4 | Protection and control Interrupt ratings are not adequate for the installation | E.png | file://x:/photopub/docs/0000000427/388c1f1a-21e2-49e2-891b-d3099c0c1e51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e07042_8a8a_49b8_bf46_4ddcc48259fe
GAIN-579246-2016 | GA-387650-2016 | 5/19/2016 12:20:38 PM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | This water heater has been installed in a closet that has no provisions to isolated the heater from the bathroom potential allowing products of combustion to accumulate in the bathroom | 2 | Appliance installed in a proposed hazardous location | _water_heater_in_closet.png | file://x:/photopub/docs/0000000432/ececfd49-9637-40d4-93b9-3fc14e986d49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4a90b9f6_7fcb_4bf8_a146_eb2589cbad66
GAIN-532279-2016 | GA-317563-2015 | 5/11/2016 12:52:09 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Regulators installed without vent limiters and not vented outdoors. If regulator diaphragm were to fail, release of gas exceeding 2.5 cubic feet/hr could cause flammable mixture and if found ignition source could cause a fire | 3 | Regulator vent not terminated as per manufacturers instruction | Reg_vents.png | file://x:/photopub/docs/0000000429/28932565-0e6c-4890-ba09-fb0363b144cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06937717_0804_4cc0_ac8c_c2542a9dd07f
ELOP-507118-2016 | EL-234473-2015 | 5/6/2016 1:59:40 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL212 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 5 | 5 | Unapproved equipment in a hazardous location. This is an explosion hazard as heat or sparks could ignite the paint fumes in the vicinity. | 5 | All Classes, All Zones The area contains equipment that is not suitable for the location such as exposed heat sources, spark producing equipment or similar devices. | 1.png | file://x:/photopub/docs/0000000427/c09ca332-340b-4738-8fe5-c22e049e299e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__14777b6a_a805_4e86_8b0d_1a75b269c8c3
ELIN-573469-2016 | EL-221488-2015 | 5/9/2016 11:58:58 AM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Adequate clearance of high voltage conductor not provided between the neutral and line conductor on a terminal pole, this is a potential shock hazard. No kirk key interlock provided between the transformer and load break switch, this is a fire and shock hazard as the energized transformer parts could be accessed while energized. Fused cut out installed on the line side of the load break switch, this is a shock and fire hazard because the fused cutouts are not rated to be opened under load. | 4 | Protection and control Interrupt ratings are not adequate for the installation | A.png | file://x:/photopub/docs/0000000427/a2aaa6a0-3559-4546-ba9b-0d13923126bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e07042_8a8a_49b8_bf46_4ddcc48259fe
ELIN-573469-2016 | EL-221488-2015 | 5/9/2016 11:58:58 AM | ASSESS: EL: Final | png | #asFound | EL049 | Protection and control Interrupt ratings are not adequate for the installation | 4 | 4 | Adequate clearance of high voltage conductor not provided between the neutral and line conductor on a terminal pole, this is a potential shock hazard. No kirk key interlock provided between the transformer and load break switch, this is a fire and shock hazard as the energized transformer parts could be accessed while energized. Fused cut out installed on the line side of the load break switch, this is a shock and fire hazard because the fused cutouts are not rated to be opened under load. | 4 | Protection and control Interrupt ratings are not adequate for the installation | B.png | file://x:/photopub/docs/0000000427/71f5076e-e494-4755-9448-be31ff72f145.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4e07042_8a8a_49b8_bf46_4ddcc48259fe
ELIN-546593-2016 | EL-334591-2016 | 3/30/2016 6:06:17 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit wiring consisting on non-metallic sheathed cables (NMSC) is required to be installed in such a way as to prevent the cables from getting mechanically damaged both during and after construction. This is required because NMSC has a jacket and conductor insulation that when not installed properly can be mechanically damaged fairly easily. This installation has multiple NMSC's that are installed in contact with heating ducts, on top of roof trusses where the distance between the truss and roof exceeds 1M, and in locations that are less than 32mm from the face of studs. All of these installation practices can lead to damage to these type of cables which can expose live conductors to accidental contact, or expose live conductors to each other or other conductive materials. Left uncorrected this is a potential shock and fire hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_contact_with_metal_heating_duct__.png | file://x:/photopub/docs/0000000409/bf33f169-4dcd-45c5-bb98-25c246d1a05a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1730eac8_8a6f_4122_b752_91e928f56d8d
GAUP-538094-2016 | UW-356062-2016 | 3/30/2016 10:51:05 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | Homeowner has stopped work at this time and has been told that she will need to get another gas contractor to complete the installation when work starts again | 0 | No Created Hazard Identified | __copy_of_invoice.png | file://x:/photopub/docs/0000000409/f441c740-aaf0-44a0-af17-4881c1330ccf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0ca3d2b_d143_487a_95a3_cb8f028c8e7b
GAUP-538094-2016 | UW-356062-2016 | 3/30/2016 10:51:05 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | Homeowner has stopped work at this time and has been told that she will need to get another gas contractor to complete the installation when work starts again | 0 | No Created Hazard Identified | Picture_of_House.png | file://x:/photopub/docs/0000000409/c1e95ecd-11a6-4f97-9ba0-0312ac2c0dad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c0ca3d2b_d143_487a_95a3_cb8f028c8e7b
ELIN-547392-2016 | EL-228289-2015 | 3/30/2016 3:50:55 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Receptacles are required to be protected by over-current devices that do not exceed the ampacity of the receptacle. This is required so that the receptacle does not get thermally damaged from an over current or over load condition. This installation has eight 30A, 120/240V dryer receptacles connected to 40A branch circuit conductors and 40A breakers. Left uncorrected this is a potential fire hazard if the receptacles become overloaded or if there is a fault causing an over current condition at the receptacles. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | 30A__120_240V_dryer_receptacles_connected_to_40A_branch_circuits_connected_to_40A_breakers.png | file://x:/photopub/docs/0000000409/93fd60a1-4660-4f4e-9588-d4b321d0c173.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__062216c0_fc3f_4301_934d_d7d1ae32993a
GAIN-548729-2016 | GA-369496-2016 | 3/31/2016 1:00:18 PM | ASSESS: GA: Final | png | #asFound | GA117 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | Improper_connection.png | file://x:/photopub/docs/0000000410/8b4beb5e-d53c-49e1-acca-674720a97fcd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1646883a_c865_4534_a75f_48a1c7ccce14
GAIN-548729-2016 | GA-369496-2016 | 3/31/2016 1:00:18 PM | ASSESS: GA: Final | png | #asFound | GA117 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant system ex: incorrect appliance connection, incorrect glue/ fasteners | Replacement_of_them__replacement_oven_installation.png | file://x:/photopub/docs/0000000410/5f522f20-199d-4b8f-86e5-fcc39ce35c23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1646883a_c865_4534_a75f_48a1c7ccce14
AMOP-565393-2016 | 2053232 | 4/26/2016 9:55:42 AM | ASSESS: AM OP: Periodic | png | #asFound | AM031 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | 3 | 2 | Noted that bulbs are missing in the decorative light panel and open sockets would be in reach by the public. Reportedly, lighting panels operate at 120V. Probable electric shock hazard. | 3 | Malfunction that is: may not be reasonably detectable by maintenance program Likely to propagate | Open_decorative__lamp_socket_within_reach_of_public.png | file://x:/photopub/docs/0000000426/eb1a46b8-54cb-4d05-a969-4a12a29de0f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cf0c0aa3_32de_43f1_8509_78b248f0da29
ELIN-562407-2016 | EL-330683-2015 | 5/5/2016 9:12:16 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | # 10 awg copper conductors are installed from Heat Pump disconnect switch to unit connection point. Full load amperage of the Heat Pump is 30 amps at 240 volts. the branch circuit is protected by a 40 amp overcurrent device. This is a thermal issue. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Heat_Pump_conductors.png | file://x:/photopub/docs/0000000425/9f6e25fb-d780-4b67-9f38-baf6714cfafe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1171739e_0774_4b1c_b031_e6026e69ab42
ELIN-572274-2016 | UW-383755-2016 | 5/5/2016 5:27:51 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Unused openings in electrical panels must be closed so as to avoid accidental contact. In this rental residence a service upgrade had been performed by a licensed contractor who is no longer in business. The original panel was used as a junction box but the breaker enclosure was not sealed as required. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Bulldog_fillers_missing.png | file://x:/photopub/docs/0000000425/b6641e64-2b77-4cc7-a929-014c86af6fb1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56c09a0e_a5aa_42b1_adc5_7368e58edf46
ELIN-572274-2016 | UW-383755-2016 | 5/5/2016 5:27:51 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Unused openings in electrical panels must be closed so as to avoid accidental contact. In this rental residence a service upgrade had been performed by a licensed contractor who is no longer in business. The original panel was used as a junction box but the breaker enclosure was not sealed as required. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Directory_not_completed.png | file://x:/photopub/docs/0000000425/6779505c-b219-4c85-80d3-ace788b767e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56c09a0e_a5aa_42b1_adc5_7368e58edf46
ELIN-537673-2016 | UW-355876-2016 | 3/3/2016 1:01:23 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | 240 v heap pump installed without permission and control cable not protected: may lead to manufacture of equipment not applying warranty | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Heat_pump.png | file://x:/photopub/docs/0000000399/666dbb30-9566-40ea-8418-94d22303e250.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d42fd5f7_2b2e_4e3b_88b1_f2f1ad7269da
GAUP-571463-2016 | UW-383218-2016 | 5/4/2016 4:12:16 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA146 | Appliance installed in a hazardous location, where a hazardous material is present | 4 | 4 | The as found hazard was a gas fireplace which had a portion of the seal from the explosion relief damper missing. This is a hazard because when the fireplace is in operation flue gasses are able to escape into the bedroom. Risk of carbon monoxide poisoning. | 4 | Appliance installed in a hazardous location, where a hazardous material is present | Explosion_relief_2.png | file://x:/photopub/docs/0000000426/2eb4437b-0b0d-4627-bc6f-a9ce10bc3f81.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bce6464e_de52_401a_ba3e_28e947feca2a
GAUP-571463-2016 | UW-383218-2016 | 5/4/2016 4:12:16 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA146 | Appliance installed in a hazardous location, where a hazardous material is present | 4 | 4 | The as found hazard was a gas fireplace which had a portion of the seal from the explosion relief damper missing. This is a hazard because when the fireplace is in operation flue gasses are able to escape into the bedroom. Risk of carbon monoxide poisoning. | 4 | Appliance installed in a hazardous location, where a hazardous material is present | Explosion_relief_1.png | file://x:/photopub/docs/0000000426/d147803d-2738-4fd6-b811-199008eb7cfa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bce6464e_de52_401a_ba3e_28e947feca2a
GAUP-571463-2016 | UW-383218-2016 | 5/4/2016 4:12:16 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA146 | Appliance installed in a hazardous location, where a hazardous material is present | 4 | 4 | The as found hazard was a gas fireplace which had a portion of the seal from the explosion relief damper missing. This is a hazard because when the fireplace is in operation flue gasses are able to escape into the bedroom. Risk of carbon monoxide poisoning. | 4 | Appliance installed in a hazardous location, where a hazardous material is present | combustion_anaylizer.png | file://x:/photopub/docs/0000000426/59146e27-ad75-4cc4-a8a5-305eb64cab0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bce6464e_de52_401a_ba3e_28e947feca2a
GAUP-571463-2016 | UW-383218-2016 | 5/4/2016 4:12:16 PM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA146 | Appliance installed in a hazardous location, where a hazardous material is present | 4 | 4 | The as found hazard was a gas fireplace which had a portion of the seal from the explosion relief damper missing. This is a hazard because when the fireplace is in operation flue gasses are able to escape into the bedroom. Risk of carbon monoxide poisoning. | 4 | Appliance installed in a hazardous location, where a hazardous material is present | fireplace.png | file://x:/photopub/docs/0000000426/a7c7682c-f026-40d7-b5a8-0fb5910752ba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bce6464e_de52_401a_ba3e_28e947feca2a
ELIN-544553-2016 | EL-340242-2016 | 3/17/2016 3:09:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | -Sewage pump control kiosk does not bear evidence of a certification approval label or an overall electrical name plate. installer may not know how to connect this piece of equipment without the electrical overall amperage, voltages or electrical characteristics. Installer does not know if the equipment was installed be qualified individuals. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | control_panel_label_.png | file://x:/photopub/docs/0000000405/42120279-2e1c-428d-91f3-f177fc2bb54a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f1b151a_9f02_4971_a8e0_01e3a8037df5
ELIN-544553-2016 | EL-340242-2016 | 3/17/2016 3:09:31 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 3 | -Sewage pump control kiosk does not bear evidence of a certification approval label or an overall electrical name plate. installer may not know how to connect this piece of equipment without the electrical overall amperage, voltages or electrical characteristics. Installer does not know if the equipment was installed be qualified individuals. | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | bonding_and_grounding.png | file://x:/photopub/docs/0000000405/42bde9ec-7134-4206-b8f9-036ddf7a6622.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1f1b151a_9f02_4971_a8e0_01e3a8037df5
ELIN-588218-2016 | EL-394879-2016 | 6/7/2016 11:36:05 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | The feeder neutral in a load side sub panel is still connected to the main ground through the Bond strap. This under a temporary fault condition could prevent grounding conductors to perform there protective function by activating overcurrent devices. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bond_strap_jumper.png | file://x:/photopub/docs/0000000440/ece93cf4-3266-4f95-9376-93916db85fa8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ffde4f7_3467_4e18_9c4d_7a0fee11cfbd
ELIN-583033-2016 | EL-369416-2016 | 6/4/2016 9:14:15 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Kitchen counter receptacles may be either 2 pole 15 amp (split) receptacles or 1 pole 20 amp (t-slot) receptacles. Where these receptacles are within 1.5 m of a sink they must be GFCI protected. The former receptacle requires an expensive GFCI breaker be installed in the main electrical panel. The latter can be provided with a GFCI style receptacle at a fraction of the cost. In this installation the homeowner did not realize receptacles close to sinks require GFCI protection and had installed the wrong configuration. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Split_by_sink.png | file://x:/photopub/docs/0000000438/526ab2f1-1a1c-49b8-ad36-5ea9bb30afa3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56382575_bd5a_4b5b_93c9_16014c84d791
BPVOP-543753-2016 | 4060892 | 5/18/2016 4:24:29 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Electric Steam Boiler with heating surface of 4 square meters and Maximum Allowable Working Pressure (MAWP) of 100psig, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, steam or flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_without_remote_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000433/cfa66a03-9863-44b0-86b3-92e503834922.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87E175D2_BB8D_46B0_A5BE_92988D3A9225
BPVOP-543753-2016 | 4060892 | 5/18/2016 4:24:29 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Electric Steam Boiler with heating surface of 4 square meters and Maximum Allowable Working Pressure (MAWP) of 100psig, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, steam or flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_Remote_Emergency_Shutdown_Switch.png | file://x:/photopub/docs/0000000433/64bd5a98-b3e4-4864-a853-df97a3a47df2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87E175D2_BB8D_46B0_A5BE_92988D3A9225
BPVOP-589846-2016 | 2274587 | 6/7/2016 9:32:28 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound PRD mounted horizontally and is past service interval. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety relief valve may not operate as intended, allowing system pressure to exceed boiler MAWP. This can cause the boiler to rupture and release scalding water which can cause personal injury and/or property damage. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | HW77650_PRD.png | file://x:/photopub/docs/0000000440/380a3928-c7e3-44c3-bebc-ccdaac608a32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d91455c_7c30_443f_b84e_1c1a91d9b6cf
ELIN-581244-2016 | EL-390109-2016 | 5/25/2016 6:49:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Enclosure not built to temporary construction service requirements. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | meter_base_not_to_height.png | file://x:/photopub/docs/0000000434/62985bdb-3ed7-42b6-ba79-950ecdd776b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__324c7795_3090_497f_9eb9_e78f53006001
ELIN-581244-2016 | EL-390109-2016 | 5/25/2016 6:49:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Enclosure not built to temporary construction service requirements. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Enclosure_not_weatherproof.png | file://x:/photopub/docs/0000000434/8a925512-1247-46a6-bb1b-628e59ddcd0f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__324c7795_3090_497f_9eb9_e78f53006001
ELIN-591725-2016 | EL-158907-2014 | 6/10/2016 3:47:06 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found outdoor fixtures that appeared to be homemade. They did not bare a mark of approval. There is a shock and fire hazard with equipment that has not been tested to the applicable standards. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixtures.png | file://x:/photopub/docs/0000000441/3a558cd9-ee53-4956-85ce-d525fbe52fb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ce6131c_77d8_4a3b_bac9_d92ffff22190
ELIN-591725-2016 | EL-158907-2014 | 6/10/2016 3:47:06 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | This assessment found outdoor fixtures that appeared to be homemade. They did not bare a mark of approval. There is a shock and fire hazard with equipment that has not been tested to the applicable standards. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Fixture.png | file://x:/photopub/docs/0000000441/1679d66f-a36a-4b3d-a813-59124a6a2930.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ce6131c_77d8_4a3b_bac9_d92ffff22190
ELIN-594691-2016 | EL-377873-2016 | 6/15/2016 11:52:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | 50 amp, 120/240 volt energized sub panel has cover missing. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_exposed_energized_sub_panel__Cover_missing.png | file://x:/photopub/docs/0000000443/e9a893ca-347e-4dab-b84e-1db2a5d9d71f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8b6232d_1133_403a_87c1_3f303dc2df86
ELIN-594691-2016 | EL-377873-2016 | 6/15/2016 11:52:02 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | 50 amp, 120/240 volt energized sub panel has cover missing. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Open_exposed_energized_panel_.png | file://x:/photopub/docs/0000000443/e6235164-21d8-41c6-8733-75c9bd88f872.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c8b6232d_1133_403a_87c1_3f303dc2df86
ELIN-583995-2016 | UW-391795-2016 | 5/27/2016 11:13:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Live service during demolition, no qualified personnel on site, permit avoidance | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Front.png | file://x:/photopub/docs/0000000435/ec9bddba-f28b-4ca4-9001-903cc22d6586.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5cf3b2d_b8f4_400b_bd25_f59d36848f38
ELIN-583995-2016 | UW-391795-2016 | 5/27/2016 11:13:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Live service during demolition, no qualified personnel on site, permit avoidance | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Temp_Panel.png | file://x:/photopub/docs/0000000435/090cbf83-b515-44a6-ae99-4a2a49cecc75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5cf3b2d_b8f4_400b_bd25_f59d36848f38
ELIN-583995-2016 | UW-391795-2016 | 5/27/2016 11:13:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Live service during demolition, no qualified personnel on site, permit avoidance | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Interior.png | file://x:/photopub/docs/0000000435/62314b21-3086-47b0-aa0b-6e34179fe3a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5cf3b2d_b8f4_400b_bd25_f59d36848f38
ELIN-583995-2016 | UW-391795-2016 | 5/27/2016 11:13:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Live service during demolition, no qualified personnel on site, permit avoidance | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Disconnect.png | file://x:/photopub/docs/0000000435/f0f28568-3238-4959-a4b8-0dc485f62c83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e5cf3b2d_b8f4_400b_bd25_f59d36848f38
ELIN-574581-2016 | EL-361313-2016 | 6/9/2016 6:24:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | Installation of rigid PVC without an expansion joint. Ground can heave with frost or settle causing damage to service equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Te1.png | file://x:/photopub/docs/0000000441/9231b1be-aeb4-4aca-a520-9995c5a8b53f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ac4bb44_0780_4b07_b9e6_9654559bd020
BPVOP-591312-2016 | 2263264 | 6/9/2016 9:02:25 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP101 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | 2 | 2 | Isolation valves in path of discharge on safety relief device. | 2 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable Standards but present and functioning | Twin_valves.png | file://x:/photopub/docs/0000000441/30639316-1fde-45a1-8677-0d06ea6dfcdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d1979812_b2dc_4ede_92b2_bff58276c650
ELIN-580042-2016 | EL-386859-2016 | 5/20/2016 6:06:45 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Energized dry location sub-distribution equipment accessible to general public has been installed in structure without roof and exposed to effects of weather. This presents a serious risk of personal injury (shock) and property damage (thermal event). | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | View02_subdistribution_location.png | file://x:/photopub/docs/0000000434/97dac5e3-0d08-4b9d-9afb-b7c36a83d2d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ef99b54_b847_4505_a032_5a92cc2a6f8f
ELIN-580042-2016 | EL-386859-2016 | 5/20/2016 6:06:45 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Energized dry location sub-distribution equipment accessible to general public has been installed in structure without roof and exposed to effects of weather. This presents a serious risk of personal injury (shock) and property damage (thermal event). | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | View01_subdistribution.png | file://x:/photopub/docs/0000000434/e4ea1612-0915-46c9-8c09-deca88a0e804.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ef99b54_b847_4505_a032_5a92cc2a6f8f
ELIN-590667-2016 | EL-345736-2016 | 6/10/2016 7:47:06 AM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | Cover plates missing exposing live parts allowing for contact | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Lu2.png | file://x:/photopub/docs/0000000441/bd7c7980-12c9-4d3d-8e5b-7b9cd1628458.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a246cd17_0390_4805_a284_e26718cd13e2
ELIN-580607-2016 | EL-279667-2015 | 5/24/2016 7:31:41 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 2 | TWU pump drop cable was installed below grade by unqualified persons and back filled with native backfill material containing large rock and sharp angular materials. The 15 amp 240 volt circuit may fail due to damage to conductors leaving a potential for damage to the electrical equipment or failure of the circuit to provide power to building heating equipment | 3 | Conductors Equipment is not approved for the specific use. | TWU_pump_drop_cable_direcy_buried_no_screened_sand_no_authorization_to_cover.png | file://x:/photopub/docs/0000000433/6cb92f26-7d49-4e6f-a973-a46df0b1565b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee52e035_c1f8_4a3c_b1dc_91af7862b548
ELIN-585763-2016 | EL-392817-2016 | 6/6/2016 7:58:12 AM | ASSESS: EL: Final | png | #asFound | EL052 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | 3 | 3 | This assessment found a 2-pole breakers handles tied together with wire. Without the handles being securely tied together with an approved tie bar, both breakers may not trip. This presents a shock hazard to someone assuming power is off. | 3 | Protection and control Circuit breakers connected to branch circuit derived from a 3-wire grounded neutral system are not 2-pole, or the handles of single pole breakers are not interlocked | Breaker_tiebar.png | file://x:/photopub/docs/0000000438/016ff8d4-0deb-430f-a09f-cc9d25f33ad2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0992262b_2188_44b8_8a5b_d14fbfefbdd5
AMAL-587573-2016 | AM-392599-2016 | 6/2/2016 10:59:34 AM | ASSESS: AM AL: Acceptance | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 1 | At the time of the acceptance inspection/testing the modification to the landing deck were yet not completed. No actual hazard as the device was not in operation at the time of inspection. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Landing_Deck.png | file://x:/photopub/docs/0000000439/d3dd0385-a62a-48e4-b7f6-626598b67c20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a064d184_ba6a_4d1b_b145_6e315e0e4f02
BPVIN-575678-2016 | BPV-067062-2013 | 6/6/2016 9:05:40 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. During an inspection of a HP Steam Boiler I found the Safety Valve overdue from 2002 and it showed signs of leaking. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Overdue_and_leaking_SV.png | file://x:/photopub/docs/0000000434/19b93c75-4a2f-4ed1-ba48-de7828e795c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52da3ea7_c7eb_41bc_a8d4_3485ed5b5f56
GAIN-587771-2016 | GA-342016-2016 | 6/14/2016 10:09:36 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Hotsy requires 24" clearance to combustibles. Installed tight to wall. Propane is not connected. | 3 | Clearance to combustible not met | Hotsy.png | file://x:/photopub/docs/0000000444/c6502723-f319-41e3-8323-e0c255b67c93.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2dd15dfb_19f5_4ada_ba32_969cb15a5205
ELIN-593692-2016 | EL-157742-2014 | 6/15/2016 5:57:38 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | The existing main panel sub feeds existing wiring not disconnected/removed by contractor with a 40 amp 120/240 volt feed leaving exposed energized hazards to persons, this is a shock hazard | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | GFCI_receptacle_under_mobile.png | file://x:/photopub/docs/0000000444/005774fc-1501-4a4a-a358-3fc63d16f9e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bda674c3_a40b_493e_bf4f_2b630cf56f90
ELIN-583898-2016 | EL-385051-2016 | 5/31/2016 8:44:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 2 | The hazard of leaving a incomplete installation is that certain items such as bonding may be forgotten. This could create a shock hazard if not completed at rough wire stage. | 3 | Continuity Bonding; method for equipment is not adequate. | Telephone_missing__6_bonding_conductor.png | file://x:/photopub/docs/0000000436/421e425c-0ef8-42ae-bd86-88b6f7908e54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5386bad2_cb3c_4a79_8baf_6e04ab47be65
ELIN-583898-2016 | EL-385051-2016 | 5/31/2016 8:44:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 2 | The hazard of leaving a incomplete installation is that certain items such as bonding may be forgotten. This could create a shock hazard if not completed at rough wire stage. | 3 | Continuity Bonding; method for equipment is not adequate. | Splice_not_complete_.png | file://x:/photopub/docs/0000000436/1581a34b-51e5-4b67-9a14-00da314c5d19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5386bad2_cb3c_4a79_8baf_6e04ab47be65
ELIN-583898-2016 | EL-385051-2016 | 5/31/2016 8:44:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 2 | The hazard of leaving a incomplete installation is that certain items such as bonding may be forgotten. This could create a shock hazard if not completed at rough wire stage. | 3 | Continuity Bonding; method for equipment is not adequate. | Panel_not_finished.png | file://x:/photopub/docs/0000000436/9c78773f-0559-4cd0-af32-2c7c5886dd29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5386bad2_cb3c_4a79_8baf_6e04ab47be65
ELIN-584095-2016 | EL-391857-2016 | 5/30/2016 11:24:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | 200 amp, 120/240 volt underground service has service conductors installed which have an ampacity rating less then the service size rating. This is a thermal issue. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Conductor_feeding_200A_main_distribution.png | file://x:/photopub/docs/0000000435/a4c9f3dd-7713-443b-b08a-686021788eb5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eeac94ff_776a_4452_8500_ce3aad71128c
ELIN-572292-2016 | EL-335240-2016 | 6/1/2016 2:33:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL143 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | 3 | 3 | Outlet box has exceeded the maximum number of conductors allowed. This could be a fire hazard if due to the conductors overheating from being in close proximity of each other. | 3 | Installation of electrical equipment Inadequate wiring or bending space provided for conductors inside boxes or cabinets | Box_fill.png | file://x:/photopub/docs/0000000437/2db6cab1-600a-474c-8f71-027511f452f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e78f029_b3a2_4996_bdd8_63a19623dfe1
ELIN-582804-2016 | EL-391108-2016 | 6/1/2016 4:44:40 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | Protection has not been installed for non metallic sheathed cable below 1.5m therefore cable jacket could be subjected to damage. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Loadcenter.png | file://x:/photopub/docs/0000000437/4d8f4c12-237b-4ced-aa34-d4d8c25fb648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d41102a_c4d3_4753_b222_1546de579507
ELIN-582804-2016 | EL-391108-2016 | 6/1/2016 4:44:40 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | Protection has not been installed for non metallic sheathed cable below 1.5m therefore cable jacket could be subjected to damage. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Exposed_NMSC.png | file://x:/photopub/docs/0000000437/a93ae87f-c6af-4e8e-b271-a87cc379ce4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d41102a_c4d3_4753_b222_1546de579507
BPVIN-580491-2016 | BPV-027196-2013 | 5/26/2016 12:25:15 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | During the inspection of a High Pressure Steam Boiler I found that the Safety Valve was leaking from the body drain hole. This can cause the Safety Valve to seize and not protect the boiler in case of overpressure. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leaking_SV.png | file://x:/photopub/docs/0000000434/d31c0091-1b79-4964-9639-f043b8ae8cc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20150139_0ab7_4c47_867b_861259c25979
ELIN-583969-2016 | EL-390370-2016 | 5/30/2016 10:39:07 AM | ASSESS: EL: Service Connection | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Where interior metal gas lines are used in buildings serviced with electricity the lines must be bonded to ground to avoid accidentally energizing them. In this installation a service upgrade was being done on a 50 year old house. The installer did not notice the gas line had never been bonded. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Plate_but_no_connection_to_gas_line.png | file://x:/photopub/docs/0000000435/0fa85fb7-6b93-4388-8bf6-2615b999f862.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a191ac5c_0858_45c7_8d44_d09c62421abf
ELIN-581795-2016 | EL-387028-2016 | 5/30/2016 6:25:58 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Smoke alarm was installed on furnace disconnect. Smoke alarm needs to be installed on a general lighting circuit to prevent dwelling unit persons from permanently turning off the circuit due to annoyance alarms tripping. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Smoke_alarm_on_with_furnace_disconnect.png | file://x:/photopub/docs/0000000436/02703567-2775-4a0a-8eb2-4c7cd82fd47d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__049fe65a_0cb7_422e_a877_8dc9a4f92c73
ELIN-576133-2016 | EL-274800-2015 | 5/31/2016 8:42:33 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacle located within 1.5 meters of kitchen sink are not ground fault circuit interruptor protected. This is could be shock hazard to persons who are plugging in electrical equipment while using the kitchen sink. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | None_gfci_receptacle.png | file://x:/photopub/docs/0000000436/9203755e-9948-4a50-be3e-79fa2bb1cf72.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77f175ca_1b8c_47d6_9c26_28b34b3996d3
BPVOP-584114-2016 | 4357706 | 5/27/2016 12:35:48 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 100 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Service_plate_valve_.png | file://x:/photopub/docs/0000000434/5235fa86-673f-4390-9262-4b34d408ccf3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc0df892_334c_41e4_a0dc_def28a7e4c4c
ELIN-578230-2016 | EL-241393-2015 | 5/24/2016 11:48:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found the main consumer's 200 amp service does not have any service grounding conductor with electrode installed and grounding conductor is not connected to neutral conductor bus bar in main service compartment as required at each individual service. When main service power supply system is not grounded with grounding conductor and electrode and if there is a fault on the system, the fault condition might not effectively and immediately trip over-current device as required for protection and the system could become an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_done_at_meterbase_but_main_service_is_not_grounded_at_all_2.png | file://x:/photopub/docs/0000000434/c8f9a5f0-9e2c-4b20-b208-62b9b52077b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed51629f_cae3_4271_8c38_24d2cd347e41
GAIN-474654-2015 | GA-306847-2015 | 6/3/2016 11:06:07 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Type G copper installed from propane tank to the building and buried and not sleeved. This is a hazard as general G copper not rated for underground use, and could get pinched or damaged during leak gas. | 3 | Non-compliant material/fittings installed | Likely1.png | file://x:/photopub/docs/0000000438/19e1171e-eeb7-4b54-8430-305253d9d11f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af11d9ca_6e4a_4f5b_a15e_4f65f338ccdb
GAIN-474654-2015 | GA-306847-2015 | 6/3/2016 11:06:07 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Type G copper installed from propane tank to the building and buried and not sleeved. This is a hazard as general G copper not rated for underground use, and could get pinched or damaged during leak gas. | 3 | Non-compliant material/fittings installed | Likely2.png | file://x:/photopub/docs/0000000438/6a32c982-7c26-47dc-8839-997a0cabebe8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af11d9ca_6e4a_4f5b_a15e_4f65f338ccdb
ELIN-587668-2016 | EL-390899-2016 | 6/3/2016 2:13:14 PM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | Low voltage wire used outside this wire is not approved to be used outside | 0 | No Created Hazard Identified | LVT_exposed_to_weather.png | file://x:/photopub/docs/0000000438/d5769625-baab-4257-8238-1f36e1dd85f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e85f1fcf_4e15_4001_9247_cb93f17daac5
ELIN-578230-2016 | EL-241393-2015 | 5/24/2016 11:48:54 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found the main consumer's 200 amp service does not have any service grounding conductor with electrode installed and grounding conductor is not connected to neutral conductor bus bar in main service compartment as required at each individual service. When main service power supply system is not grounded with grounding conductor and electrode and if there is a fault on the system, the fault condition might not effectively and immediately trip over-current device as required for protection and the system could become an electrical fire or shock hazard to people and property. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Grounding_done_at_meterbase_but_main_service_is_not_grounded_at_all_1.png | file://x:/photopub/docs/0000000434/9a90c804-ba84-4616-9f88-72e619d9a982.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed51629f_cae3_4271_8c38_24d2cd347e41
ELIN-581288-2016 | EL-390126-2016 | 5/24/2016 9:04:48 AM | ASSESS: EL: Service Connection | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 |  | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Six_zones__six_zones_of_irrigation_control_wiring_installed_no_electrical_permit_has_been_obtained_and_caution_warning_tape_not_installed.png | file://x:/photopub/docs/0000000433/b6411bfa-7eaa-4fc2-9514-963f143f3fc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57713a94_d6fe_47bb_bcfa_f5c1685e7dc1
ELIN-560434-2016 | EL-375799-2016 | 10/31/2016 12:50:07 PM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | An electric sign operating at 120 volts on a 15 amp circuit was found lacking electrical characteristics label and evidence of approval. Installers of electrical equipment need access to nominal voltage and amperage to safely connect electrical equipment. Evidence of approval verifies the equipment is safe for connection to a source of electricity. Equipment can be hazardous when connected to incorrect voltages and equipment that is not approved may be a source of electric shock or property damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Pet_valu_sign_no_labels_visible_after_installation.png | file://x:/photopub/docs/0000000433/cf947f9c-5033-4fa2-add8-8357ce7c0b97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69927d1f_f4a8_430a_b280_305d1fcbfad4
ELIN-584631-2016 | EL-390738-2016 | 5/30/2016 2:27:27 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Bond strap is not removed from sub distribution panel. Bonding straps are to be removed in all sub distribution panels unless grounding is re-established. If a electrical fault were to occur the bond strap would provide a path for stray currents to exist, thus not having the over current protection act as it should to clear the fault. This may result in shock or fire to persons or property. | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Bond_strap_not_removed_in_sub_panel_.png | file://x:/photopub/docs/0000000435/1e140961-d7e9-4403-857d-1f6159a1f34e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51360aff_f274_4dae_aab4_4bd3e06d031a
ELIN-585482-2016 | EL-342906-2016 | 6/3/2016 8:06:21 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | A 20A kitchen receptacle has been installed within 1.5m of the kitchen sink without GFCI protection, this poses a shock hazard and possible equipment damage. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Kitchen_receptacle.png | file://x:/photopub/docs/0000000438/3467ae4a-e0a5-48ab-b54f-f84b78c0fe1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40761441_ef7b_49f8_9437_1fcb0a4f750c
ELIN-586804-2016 | EL-290394-2015 | 6/1/2016 2:07:31 PM | ASSESS: EL: Final | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | View01_site_services.png | file://x:/photopub/docs/0000000437/ba7622be-206e-4f9d-8a92-eba5424b523e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd415026_d836_48de_8a98_b0c831886f45
BPVOP-584114-2016 | 4357706 | 5/27/2016 12:35:48 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 100 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valves_.png | file://x:/photopub/docs/0000000434/5dda3d52-18b0-42db-b3c9-0e0921842e00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cc0df892_334c_41e4_a0dc_def28a7e4c4c
BPVIN-584970-2016 | BPV-383528-2016 | 5/30/2016 8:52:44 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | EXPANSION_TANK_NOT_BUILT_AND_STAMPED_TO_ASME_CODE.png | file://x:/photopub/docs/0000000436/6e60d64b-706a-475c-9ecf-12a4f77bfd51.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ad970c9_9a7d_4ea5_b055_0bfb6f57e62e
BPVIN-584970-2016 | BPV-383528-2016 | 5/30/2016 8:52:44 PM | ASSESS: BPV IN: Installation Boiler | png | #asFound | BP106 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | 2 | 2 |  | 2 | 3.0.1 Safeties will not function - Pressure Relief Device Relief valve for boilers installed with spindle horizontal | SAFETY_RELIEF_VALVE_SPINDLE_HORIZONTAL.png | file://x:/photopub/docs/0000000436/729ae67c-31bd-43c4-8f34-786627fb5d18.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ad970c9_9a7d_4ea5_b055_0bfb6f57e62e
BPVOP-584584-2016 | 4770182 | 5/27/2016 9:48:50 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that vertical air receiver (1.8m long and 0.50m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 5year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000436/d1093923-a7ab-4afd-90f3-86666b10aac5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad1ac75a_3bc4_4035_8049_849b7f9e3436
BPVOP-584583-2016 | 3868002 | 5/27/2016 10:31:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that machine mounted horizontal air receiver (1.8m long and 0.6m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 3year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE.png | file://x:/photopub/docs/0000000436/1d489a11-e384-46cc-9138-cd9493bef50f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4efe980c_61cb_4353_a790_643fa1055a7e
ELIN-582037-2016 | EL-390282-2016 | 5/31/2016 11:30:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL089 | Continuity Bonding; conductor is not properly sized. | 3 | 3 | 200 amp, 347/600 volt over head dip service has a #6 copper insulated bond conductor installed with #350 aluminum feeder conductors. The #6 copper bond conductor is sized smaller then what is required. This is a shock hazard. | 2 | Continuity Bonding; conductor is not properly sized. | Bond_conductor_sized_wrong_and_terminated_on_neutral.png | file://x:/photopub/docs/0000000436/c1234bc7-dba1-4e06-960b-85f386eb59eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87948360_9afe_4065_97ce_50c2e98f6ab0
GAIN-585748-2016 | GA-326871-2015 | 6/2/2016 2:32:27 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Found regulator vent opening installed 1" away from combustion air inlet to RTU. If the regulator relieves or fails, raw gas could enter into heat exchanger resulting in an explosion. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Relief_clearance.png | file://x:/photopub/docs/0000000437/60cc4611-de62-4a67-947a-10bf284995ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3a55e90_63e4_42c5_b014_ac66b5eefbe9
ELOP-413356-2015 | 1101 | 6/3/2016 1:48:26 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL015 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | 3 | 3 | Boxes and equipment stored in front and around electrical equipment can delay a person being able to de-energize a circuit during a fault or shock event. | 3 | Placement of equipment does not allow for adequate access or egress. Working space or clearances around equipment are inadequate | PGSS.png | file://x:/photopub/docs/0000000439/bc9312c9-f125-4e4a-bc0e-4f13c4e20bb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a28eb42_0bc7_4170_a0ef_f6f1ccd28d9b
ELIN-587759-2016 | EL-378928-2016 | 6/6/2016 11:49:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | A 200 amp 240 volt residential service cable lacking effective overcurrent protection enters a dwelling with cable well in excess of the length of cable required to connect panel. Inadequately protected service cables can be damaged after construction and because they lack effective overcurrent protection present a risk for damage to property and injury to persons | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Service_cable_not_close_as_practicable.png | file://x:/photopub/docs/0000000439/5d5ceafd-254a-4e0d-8136-607a825562fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3a99f4f2_3543_4e0d_9b28_9968b98f00d9
ELIN-578012-2016 | EL-314753-2015 | 6/6/2016 2:07:36 PM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | An armoured cable operating at20 amps and 240 volts is terminated in a pump controller using a connector that is not adequately sized to properly bond armor or protect conductors where thy issue for the connector. This can lead to property damage or injury to persons | 3 | Conductors Equipment is not approved for the specific use. | Cable_connector_not_approved.png | file://x:/photopub/docs/0000000439/2b0dc7e3-241d-4d9b-ae0a-1a5bd85e8628.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3677b87d_58db_48e7_a8a2_0140016bc3ab
ELIN-585385-2016 | EL-335642-2016 | 6/7/2016 1:55:27 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Residential cables must be afforded mechanical protection she run lower than 1.5 m above the ground. In this residential shop the branch circuitry had not been completed and the cables were below the minimum height. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Unfinished.png | file://x:/photopub/docs/0000000439/4a583e22-a66e-40e7-b298-4583708359a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c057bc6_93e0_4e31_9c90_f0ac22b607ff
ELIN-585385-2016 | EL-335642-2016 | 6/7/2016 1:55:27 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Residential cables must be afforded mechanical protection she run lower than 1.5 m above the ground. In this residential shop the branch circuitry had not been completed and the cables were below the minimum height. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Ceiling_fixtures_missing.png | file://x:/photopub/docs/0000000439/5d63357e-99a9-4833-8275-546d85e5904c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c057bc6_93e0_4e31_9c90_f0ac22b607ff
ELIN-585385-2016 | EL-335642-2016 | 6/7/2016 1:55:27 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Residential cables must be afforded mechanical protection she run lower than 1.5 m above the ground. In this residential shop the branch circuitry had not been completed and the cables were below the minimum height. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | No_switches.png | file://x:/photopub/docs/0000000439/5942d3e0-a1ae-4f20-b878-d591d12a3696.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c057bc6_93e0_4e31_9c90_f0ac22b607ff
BPVOP-593360-2016 | 2287907 | 6/14/2016 10:50:01 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. Devices must be installed according to all applicable standards. During the inspection of a Hot Water Storage Tank with MAWP of 125 psig found that the T&P valve had no tag. This was found on an 2009 inspection also. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | No_tag.png | file://x:/photopub/docs/0000000443/6fb2ab74-990a-4d70-afe7-15e3bbbc79a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__272a757a_ea39_4167_b6b8_6cdaa8fb0521
ELIN-585892-2016 | EL-389620-2016 | 6/1/2016 11:54:43 AM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | There is an open splice in the crawlspace. This is a possible fire hazard. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Open_splice_in_crawlspace.png | file://x:/photopub/docs/0000000436/b5c1dd27-4b53-4128-b861-88fb9d232b45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__624589ab_db57_45d4_9967_2672bd0a0588
ELIN-582168-2016 | EL-373331-2016 | 5/27/2016 11:51:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Twin services are not acceptable to Supply Utility | 3 | Category 1 Equipment is not approved for the specific use or location. | 2_separate_services_on_same_building_1.png | file://x:/photopub/docs/0000000435/84f99961-2d42-47d7-9144-d401ae700120.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3088c5b_b3fe_4fbe_8343_a0f7cccf284d
ELIN-582168-2016 | EL-373331-2016 | 5/27/2016 11:51:28 AM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 3 | Twin services are not acceptable to Supply Utility | 3 | Category 1 Equipment is not approved for the specific use or location. | 2 separate_services_on_same_building2.png | file://x:/photopub/docs/0000000435/a5ba62a2-6d5b-4f42-9885-780c3db148fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3088c5b_b3fe_4fbe_8343_a0f7cccf284d
BPVOP-589160-2016 | 2253745 | 6/6/2016 10:22:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Boiler heat exchange surfaces should be clear from scale and other deposits that could impair thermal heat transfer. I found excessive scale and deposits on the water side fire tubes on a high pressure steam boiler operating at 100psi. This can lead to over heating and failure of the boiler tubes | 0 | No Created Hazard Identified | Hand_hole_fire_tubes_.png | file://x:/photopub/docs/0000000439/ecd4a934-a050-48e9-bb57-50719f9e9460.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d80f13c_11bc_4e6c_9e1d_3eb1b504d935
BPVOP-589160-2016 | 2253745 | 6/6/2016 10:22:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Boiler heat exchange surfaces should be clear from scale and other deposits that could impair thermal heat transfer. I found excessive scale and deposits on the water side fire tubes on a high pressure steam boiler operating at 100psi. This can lead to over heating and failure of the boiler tubes | 0 | No Created Hazard Identified | Man_hole_fire_tubes_.png | file://x:/photopub/docs/0000000439/6b989a59-ce9d-4735-b068-86b077bc1434.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d80f13c_11bc_4e6c_9e1d_3eb1b504d935
BPVOP-581986-2016 | 2288733 | 6/9/2016 10:57:51 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Scale_deposit.png | file://x:/photopub/docs/0000000440/461ddc7f-a625-4c36-b890-460ce8eb0b45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b45d753e_3515_4fde_b165_bd8bee893cff
GAIN-585748-2016 | GA-326871-2015 | 6/2/2016 2:32:27 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Found regulator vent opening installed 1" away from combustion air inlet to RTU. If the regulator relieves or fails, raw gas could enter into heat exchanger resulting in an explosion. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Street90.png | file://x:/photopub/docs/0000000437/8667a0ba-8060-46dd-a2da-f1a6b966ce73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d3a55e90_63e4_42c5_b014_ac66b5eefbe9
ELOP-462926-2015 | 3845 | 6/2/2016 8:27:59 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | 15A 120V AC90 branch wiring run exposed outside to the weather, this poses possible damage to equipment and also a shock hazard to persons maintaining the equipment. | 3 | Conductors Equipment is not approved for the specific use. | AC90.png | file://x:/photopub/docs/0000000437/5e5c0a9e-c05b-4aa3-b8ac-36f46b82f661.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92754e73_0019_4ac2_b07b_05abad5ca842
GAIN-591065-2016 | GA-395464-2016 | 6/9/2016 12:09:52 PM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Found return air ducting installed incorrectly according to manufacturers instructions. This could result in reduced air flow through furnace and overheating of the heat exchanger, leading to a cracked heat exchanger and carbon monoxide entering the occupied space. | 3 | Appliance not installed according to installation instructions | Return_ait.png | file://x:/photopub/docs/0000000441/b5d53fe4-ea18-4c56-b99d-80028872d36c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f2793b1_9500_42f3_a76a_b47447331729
GAIN-591065-2016 | GA-395464-2016 | 6/9/2016 12:09:52 PM | ASSESS: GA: Rough-In | png | #asFound | GA140 | Appliance not installed according to installation instructions | 3 | 3 | Found return air ducting installed incorrectly according to manufacturers instructions. This could result in reduced air flow through furnace and overheating of the heat exchanger, leading to a cracked heat exchanger and carbon monoxide entering the occupied space. | 3 | Appliance not installed according to installation instructions | Return_ducting.png | file://x:/photopub/docs/0000000441/7afb8c3e-35a2-47b0-bc05-ff793d739d0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f2793b1_9500_42f3_a76a_b47447331729
GAIN-590246-2016 | GA-395440-2016 | 6/9/2016 9:39:12 AM | ASSESS: GA: Final | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 | Found generator installed on driveway with no protective barriers around it. A moving vehicle could hit the appliance causing it to shift from its position, breaking the gas line and causing a substantial gas leak resulting in an fire. | 2 | Appliance installed in a proposed hazardous location | Generac_on_driveway.png | file://x:/photopub/docs/0000000441/7bcf5d02-7ccb-46e2-9dc5-6cf1a372367f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b85717a_fbc4_4973_93dc_23de5975f9a0
BPVIN-586735-2016 | UW-393975-2016 | 6/1/2016 3:47:20 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Pressure relief device shall be in a perfect working order with no sign of leakage. I found that a pressure relief device on a hot water boiler (high pressure, 150 PSI) was leaking water. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leaky_pressure_relief_device_.png | file://x:/photopub/docs/0000000437/69d64421-5aab-470b-9f34-1d1a78217c0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__738929ba_fac6_4464_b678_ff93f9eb102f
ELIN-582817-2016 | EL-316610-2015 | 5/31/2016 1:02:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Switches are wired in an unapproved manner such that a person would believe the fuses are de- energized when they are still energized ie: line to load and load to line | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Switch_wired_backward.png | file://x:/photopub/docs/0000000438/3c5256c8-0118-4f38-86c6-815d8de07ded.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de05b880_19f9_42f3_ae33_ff4bb8035a6c
ELIN-582817-2016 | EL-316610-2015 | 5/31/2016 1:02:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Switches are wired in an unapproved manner such that a person would believe the fuses are de- energized when they are still energized ie: line to load and load to line | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Meter_wired_line_to_load.png | file://x:/photopub/docs/0000000438/44968337-6e38-4145-b285-9bbddcb1e421.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de05b880_19f9_42f3_ae33_ff4bb8035a6c
ELIN-582817-2016 | EL-316610-2015 | 5/31/2016 1:02:27 PM | ASSESS: EL: Service Connection | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Switches are wired in an unapproved manner such that a person would believe the fuses are de- energized when they are still energized ie: line to load and load to line | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Switch_wired_backwards_2.png | file://x:/photopub/docs/0000000438/807d996d-c8f4-447b-ac5a-3b6f186c6024.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__de05b880_19f9_42f3_ae33_ff4bb8035a6c
ELIN-574379-2016 | EL-385120-2016 | 5/31/2016 10:21:23 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | HV and High capacity services must not be installed unless planning, engineering and commissioning studies have been performed | 0 | No Created Hazard Identified | New_12500_7200V_3_ph_load_break_switch.png | file://x:/photopub/docs/0000000438/eb18b7f1-6745-4a45-a6c3-75d4fe152cfb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4874ac3_280f_4458_b319_cba5caca988d
ELIN-574379-2016 | EL-385120-2016 | 5/31/2016 10:21:23 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | HV and High capacity services must not be installed unless planning, engineering and commissioning studies have been performed | 0 | No Created Hazard Identified | Specifications_on_LB_Switch_handle.png | file://x:/photopub/docs/0000000438/000fe05e-443d-4e9c-a67b-2c464afcef66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4874ac3_280f_4458_b319_cba5caca988d
ELIN-574379-2016 | EL-385120-2016 | 5/31/2016 10:21:23 AM | ASSESS: EL: Final | png | #asFound | EL000 | No Created Hazard Identified | 0 | 1 | HV and High capacity services must not be installed unless planning, engineering and commissioning studies have been performed | 0 | No Created Hazard Identified | New_UG_ductwork.png | file://x:/photopub/docs/0000000438/20ea148f-ec79-47fd-8f28-86718455a96a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4874ac3_280f_4458_b319_cba5caca988d
ELIN-585123-2016 | EL-392056-2016 | 6/2/2016 2:54:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 270 V DC supply voltages may be accessible without proper lockout | 3 | General Equipment is not approved for the specific use | Exterior_mounted_power_conditioner.png | file://x:/photopub/docs/0000000438/b13adc33-a6db-4622-9a11-f3c2195a697d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c12671ff_667b_4b76_90df_83d1b8d89adc
ELIN-585123-2016 | EL-392056-2016 | 6/2/2016 2:54:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 270 V DC supply voltages may be accessible without proper lockout | 3 | General Equipment is not approved for the specific use | DC_supply_circuits_from_roof_top.png | file://x:/photopub/docs/0000000438/292ca101-1429-44dd-8b2f-91862ceeac17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c12671ff_667b_4b76_90df_83d1b8d89adc
ELIN-591129-2016 | EL-396207-2016 | 6/10/2016 4:46:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL106 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | 2 | 2 | Existing consumer service mast is bent and will over time have the potential to damage the unfused consumer conductors inside the service mast. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear and will need to be either replaced or repaired. | Bent_existing_mast.png | file://x:/photopub/docs/0000000441/6b08fc9c-5ce8-4a1e-8509-f56ee0479ae4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__873eebb7_57da_4cb2_ac26_5f593f7935e8
ELHE-583512-2016 | HE-391529-2016 | 5/31/2016 3:24:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Main 200 amp, 240 v switch not approved for location or protected from weather can be opened while energized exposing live parts; accidental contact may result in shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | mtn_holdings_1.png | file://x:/photopub/docs/0000000436/463f19d1-9ebc-46e8-9505-191f0003c913.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f644e9a1_5cd4_4206_8644_0c491a66615b
ELHE-583512-2016 | HE-391529-2016 | 5/31/2016 3:24:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Main 200 amp, 240 v switch not approved for location or protected from weather can be opened while energized exposing live parts; accidental contact may result in shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Mtn_2.png | file://x:/photopub/docs/0000000436/bf5bb228-a9c4-43ba-b631-e1e1c607b074.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f644e9a1_5cd4_4206_8644_0c491a66615b
ELHE-583512-2016 | HE-391529-2016 | 5/31/2016 3:24:22 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Main 200 amp, 240 v switch not approved for location or protected from weather can be opened while energized exposing live parts; accidental contact may result in shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Mtn_3.png | file://x:/photopub/docs/0000000436/ef412861-c6d3-4659-af6d-90af53749760.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f644e9a1_5cd4_4206_8644_0c491a66615b
ELIN-588223-2016 | EL-393709-2016 | 6/6/2016 11:45:52 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt underground temporary service not located in a weatherproof enclosure. Meter base and main distribution installed on a partial wall that has no support. Wall may fall over. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Panel_location.png | file://x:/photopub/docs/0000000439/e3d1f974-e497-4248-bc0d-71705c05a026.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78fc1fc0_450c_4ba4_b78a_86a40a454833
ELIN-588114-2016 | EL-390696-2016 | 6/6/2016 2:19:05 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 3 | 15 amp, 120 volt device boxes that are greater then 100 millimetre are supported on one side only. This is a the ram effect. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Boxes_greater_then_100mm_supported_on_one_side_only.png | file://x:/photopub/docs/0000000439/ff5eda72-b156-454f-a187-b9120b1b1561.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e79985a1_1226_441c_8ce5_301a894584c3
ELIN-593692-2016 | EL-157742-2014 | 6/15/2016 5:57:38 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | The existing main panel sub feeds existing wiring not disconnected/removed by contractor with a 40 amp 120/240 volt feed leaving exposed energized hazards to persons, this is a shock hazard | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 100_amp_panel.png | file://x:/photopub/docs/0000000444/22dbe369-49dc-421d-808a-312e90d2f876.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bda674c3_a40b_493e_bf4f_2b630cf56f90
ELIN-593692-2016 | EL-157742-2014 | 6/15/2016 5:57:38 PM | ASSESS: EL: Final | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | The existing main panel sub feeds existing wiring not disconnected/removed by contractor with a 40 amp 120/240 volt feed leaving exposed energized hazards to persons, this is a shock hazard | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Damaged_energized_cable.png | file://x:/photopub/docs/0000000444/7c13f50a-3e83-43ef-b280-80b91114860c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bda674c3_a40b_493e_bf4f_2b630cf56f90
ELIN-486871-2015 | 5400439 | 6/10/2016 10:14:18 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 120v 15 amp receptacles located at kitchen and bathroom counters, within 1.5 meters of a sink, are not approved for use in these areas. They must be ground fault (G.F.C.I.) protected to minimize the likelihood of exposure to prolonged electrical shock. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Exposed_wiring.png | file://x:/photopub/docs/0000000441/5ea11eea-89bf-4de4-b898-20464b6b1f61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9dfd2d78_b340_435b_a91e_9b015288dd31
ELIN-486871-2015 | 5400439 | 6/10/2016 10:14:18 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 120v 15 amp receptacles located at kitchen and bathroom counters, within 1.5 meters of a sink, are not approved for use in these areas. They must be ground fault (G.F.C.I.) protected to minimize the likelihood of exposure to prolonged electrical shock. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Receptacle_at_kitchen_counter_near_sink.png | file://x:/photopub/docs/0000000441/ecc7fcbd-a5be-4eee-858c-ce5b564ab199.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9dfd2d78_b340_435b_a91e_9b015288dd31
ELIN-586550-2016 | EL-330378-2015 | 6/2/2016 3:50:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Service bonding issues | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Service_mast.png | file://x:/photopub/docs/0000000437/601a630f-cfd8-4343-9e5a-b7719173c45d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__110eb902_5268_4bf7_973e_8d68f34c0bc1
ELIN-586550-2016 | EL-330378-2015 | 6/2/2016 3:50:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL071 | Effective bonding and grounding Bonding is not provided or unacceptable. | 3 | 3 | Service bonding issues | 3 | Effective bonding and grounding Bonding is not provided or unacceptable. | Service_raceway.png | file://x:/photopub/docs/0000000437/8281c534-f670-42ca-892a-df2c86ea7981.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__110eb902_5268_4bf7_973e_8d68f34c0bc1
ELIN-593906-2016 | EL-382976-2016 | 6/16/2016 9:08:09 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 4 | A service upgrade from 100 amps to 200 amps 250 volts to a residence has been authorized to the utility for utility connection. The main system ground was not connected to the system neutral as required. Inadequate grounding on an electrical system can cause unpredictable reaction of overcurrent devices that can lead to property damage or injury to persons | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Main_ground_in_meter_base.png | file://x:/photopub/docs/0000000444/abca3ed3-c1a7-4d9f-91eb-52ba727d2fbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fd791a5_8e1a_41ff_9490_276fbe6d7a8b
ELIN-587902-2016 | EL-378656-2016 | 6/3/2016 2:21:26 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The 15 amp 120 volt branch wiring is in contact with the heat source, this is a thermal hazard | 3 | Conductors, No expansion joint or not installed correctly. | NMSC_to_heat_source.png | file://x:/photopub/docs/0000000438/457170e8-28ad-4852-ae9f-e042cf02e085.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01437369_06f9_4d0a_96eb_f68a01722a7c
ELIN-589232-2016 | EL-394552-2016 | 6/7/2016 12:07:53 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Cover plate for duplex receptacle was not installed. This could be shock hazed if a person was to touch the open sides. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | No__cover_plate.png | file://x:/photopub/docs/0000000440/98872e57-b008-40bf-9bc6-b8d0cb6414e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a22d14b_f9ef_4075_9022_1b1cff8d0e9e
ELOP-367901-2015 | 6353 | 6/8/2016 9:54:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | The 15 amp 120 volt spray equipment is located inside a spray booth where on occasion flammable paints are applied. The equipment is not rated to be located within the hazardous location and this is a thermal issue. | 0 | No Created Hazard Identified | Spray_booth.png | file://x:/photopub/docs/0000000440/97982beb-b4f0-4c4a-a6d0-dc9527a3b486.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b317480c_9240_49b1_a35d_88ef92952aab
ELIN-587302-2016 | EL-262688-2015 | 6/8/2016 12:46:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The local 200 amp 120/240 volt power in the mechanical room is in near vicinity of copper waterlines installed for the geo thermos system installation, this is a shock issue. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Copper_waterlines.png | file://x:/photopub/docs/0000000440/e4cd3f64-dfcc-40eb-8c08-6dc5500a6137.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe88c797_b619_4974_9be0_c41c78f6dcf6
ELIN-587302-2016 | EL-262688-2015 | 6/8/2016 12:46:57 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The local 200 amp 120/240 volt power in the mechanical room is in near vicinity of copper waterlines installed for the geo thermos system installation, this is a shock issue. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Copper_Waterlines.png | file://x:/photopub/docs/0000000440/3da073c7-3d93-4dff-85f9-5ee4111e7cc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe88c797_b619_4974_9be0_c41c78f6dcf6
ELOP-367901-2015 | 6353 | 6/8/2016 9:54:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | The 15 amp 120 volt spray equipment is located inside a spray booth where on occasion flammable paints are applied. The equipment is not rated to be located within the hazardous location and this is a thermal issue. | 0 | No Created Hazard Identified | Spray_equipment_1.png | file://x:/photopub/docs/0000000440/578beddc-1ce3-46f7-9414-6b8b5440ece6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b317480c_9240_49b1_a35d_88ef92952aab
ELOP-367901-2015 | 6353 | 6/8/2016 9:54:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | The 15 amp 120 volt spray equipment is located inside a spray booth where on occasion flammable paints are applied. The equipment is not rated to be located within the hazardous location and this is a thermal issue. | 0 | No Created Hazard Identified | Spray_equipment_2.png | file://x:/photopub/docs/0000000440/16558d4b-6e7c-44d6-98b0-59d5f15a3d24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b317480c_9240_49b1_a35d_88ef92952aab
ELOP-226664-2014 | 6074 | 5/31/2016 4:15:29 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical equipment must be kept in safe working order. In this exterior sign installation a fixture had failed and the photocell controlling it was overheated. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Inteerior.png | file://x:/photopub/docs/0000000436/858af58a-4b85-4327-af72-501557c1547e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__52ebf2a5_0469_4a7e_9e09_d024471417c4
ELOP-381974-2015 | 5024940 | 5/31/2016 10:13:23 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 4 | Where private high lines provide electrical service attention is required from the owner to ensure the lines are cleared of brush and accessible. In this installation a section of high line was found overgrown. A large fire had passed close to this area 10 months earlier. | 4 | General Location of equipment does not allow for proper access to disconnecting means | High_line_at_disconnect.png | file://x:/photopub/docs/0000000436/cd69bcc4-ced4-4900-a2ef-5c66eb56b032.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cfa5ec1f_a84f_4387_a1e8_a85e1b3b0b93
ELOP-226608-2014 | 6063 | 5/31/2016 12:09:37 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL189 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | 3 | 3 | Electrical equipment must be maintained in safe working order. In this sewage lift station a large transformer was installed in a metal grate enclosure which made it difficult to inspect. It had been heated while in use to the point that the exterior cabinet was destroyed. | 3 | Installation of electrical equipment • Equipment is showing signs of deterioration; and • repairs or maintenance required. | Hot_tranny.png | file://x:/photopub/docs/0000000436/a683a3e1-3184-4bbd-8eb0-1369c1199c06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b06fa7d_0f14_41df_8920_3d0003cbdfcb
ELIN-582775-2016 | EL-385307-2016 | 5/27/2016 5:18:52 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | This assessment found fixtures mounted on wood without boxes. There is a fire hazard without the wires being contained in an approved box | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Burnt_outlet.png | file://x:/photopub/docs/0000000435/9e6952d4-ff33-44d2-95ec-91b6d59957ae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f35f1b39_faff_4cd6_aabe_f25fa17cd91f
ELIN-582775-2016 | EL-385307-2016 | 5/27/2016 5:18:52 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | This assessment found fixtures mounted on wood without boxes. There is a fire hazard without the wires being contained in an approved box | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Light.png | file://x:/photopub/docs/0000000435/10ad86ff-895a-4592-8d53-88941031532d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f35f1b39_faff_4cd6_aabe_f25fa17cd91f
ELIN-582775-2016 | EL-385307-2016 | 5/27/2016 5:18:52 PM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | This assessment found fixtures mounted on wood without boxes. There is a fire hazard without the wires being contained in an approved box | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Fixture.png | file://x:/photopub/docs/0000000435/7aa3bf82-34f3-4d86-b5ff-03f160a25581.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f35f1b39_faff_4cd6_aabe_f25fa17cd91f
ELIN-588145-2016 | EL-386450-2016 | 6/13/2016 9:10:55 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The 20 amp 120 volt Air Conditioning air handling unit has no disconnect provided and is missing the cover plate along with all nameplate information. The unit is located underneath the mobile home and exposes the energized wiring to accidental contact to persons, this is a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Air_conditioning_unit.png | file://x:/photopub/docs/0000000442/67c7f96c-d666-4746-b960-376b5275680e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40a204b9_ffcc_4a56_a687_0f6fbaeb7f1e
ELIN-582391-2016 | EL-390789-2016 | 5/26/2016 11:37:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | And exhaust fan has been added to a bathroom of an existing dwelling. An SOW flexible cord has been installed from the junction box to the fan. The SOW cable is not approved as a permanent wiring method and the insulation can break down overtime and likely causing a fire. | 4 | Conductors, Misuse of flexible cords. | Protection_required___protection_required_for_nonmetallic_sheath_cable.png | file://x:/photopub/docs/0000000434/5dc231a7-d0d6-4be7-9dfc-04bb39a44924.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f8bd52a_ee8c_4bc2_8e93_f54b19a32902
ELIN-582391-2016 | EL-390789-2016 | 5/26/2016 11:37:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | And exhaust fan has been added to a bathroom of an existing dwelling. An SOW flexible cord has been installed from the junction box to the fan. The SOW cable is not approved as a permanent wiring method and the insulation can break down overtime and likely causing a fire. | 4 | Conductors, Misuse of flexible cords. | Picture_of.png | file://x:/photopub/docs/0000000434/4e19475e-fa0b-4b6c-9019-8b12f6908b50.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f8bd52a_ee8c_4bc2_8e93_f54b19a32902
ELIN-582391-2016 | EL-390789-2016 | 5/26/2016 11:37:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | And exhaust fan has been added to a bathroom of an existing dwelling. An SOW flexible cord has been installed from the junction box to the fan. The SOW cable is not approved as a permanent wiring method and the insulation can break down overtime and likely causing a fire. | 4 | Conductors, Misuse of flexible cords. | Heating_leads__heating_leads_require_EMT_conduit_support.png | file://x:/photopub/docs/0000000434/69d36e72-9f1d-480e-853e-f4bb75cd7fbc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f8bd52a_ee8c_4bc2_8e93_f54b19a32902
ELIN-582391-2016 | EL-390789-2016 | 5/26/2016 11:37:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | And exhaust fan has been added to a bathroom of an existing dwelling. An SOW flexible cord has been installed from the junction box to the fan. The SOW cable is not approved as a permanent wiring method and the insulation can break down overtime and likely causing a fire. | 4 | Conductors, Misuse of flexible cords. | Outdoor_receptacl__outdoor_receptacle_must_be_on_its_own_circuit.png | file://x:/photopub/docs/0000000434/9d603204-5ddd-4970-97fb-3757995ce6e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4f8bd52a_ee8c_4bc2_8e93_f54b19a32902
ELHE-587926-2016 | HE-394771-2016 | 6/3/2016 9:01:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Overhead service conductors are within reach of a door. The connection crimps are exposed and the attachment point to the building has been removed suspending the conductors on the weather head. Potential for stock or fire. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Load_side_of_service_at_meter_removed_while_energized.png | file://x:/photopub/docs/0000000438/f95114bd-341e-4d63-9569-dd3d0d8520f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f393b7d_4ae1_4bbd_858e_289a2d753f62
ELHE-587926-2016 | HE-394771-2016 | 6/3/2016 9:01:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Overhead service conductors are within reach of a door. The connection crimps are exposed and the attachment point to the building has been removed suspending the conductors on the weather head. Potential for stock or fire. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Exposed_hydro_connection_within_1m_of_door.png | file://x:/photopub/docs/0000000438/a5845440-79a4-4077-82de-4a79a86aa9c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f393b7d_4ae1_4bbd_858e_289a2d753f62
ELHE-587926-2016 | HE-394771-2016 | 6/3/2016 9:01:50 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Overhead service conductors are within reach of a door. The connection crimps are exposed and the attachment point to the building has been removed suspending the conductors on the weather head. Potential for stock or fire. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Attachment_point_removed.png | file://x:/photopub/docs/0000000438/868274eb-40cc-4366-89f5-be92bd5d6f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f393b7d_4ae1_4bbd_858e_289a2d753f62
ELOP-191431-2014 | 4558641 | 6/14/2016 10:26:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The high voltage switch handle ground is not sufficient enough to to limit the possible voltage potential to a safe level for the person operating the switch. This could create a possible shock hazard to the operator of the switch. | 3 | Continuity Bonding; method for equipment is not adequate. | No_private_fuse.png | file://x:/photopub/docs/0000000443/4eb08d95-ee8d-4880-9848-2113f5b6bd09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3080929c_6229_41aa_9893_dd26b99dc4eb
ELOP-191431-2014 | 4558641 | 6/14/2016 10:26:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The high voltage switch handle ground is not sufficient enough to to limit the possible voltage potential to a safe level for the person operating the switch. This could create a possible shock hazard to the operator of the switch. | 3 | Continuity Bonding; method for equipment is not adequate. | Switch_ground.png | file://x:/photopub/docs/0000000443/e5fd3d2c-0343-4dcd-bc46-940c905fa555.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3080929c_6229_41aa_9893_dd26b99dc4eb
ELOP-191446-2014 | 4527123 | 6/14/2016 11:33:57 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The HV switch ground has only one conductor going to the ground mat. This could create a shock hazard for a person opening the switch if the voltage potential is not limited by the proper ground conductor size. | 3 | Continuity Bonding; method for equipment is not adequate. | Switch_mat_ground.png | file://x:/photopub/docs/0000000443/7a169a66-9366-41bb-b490-d9c1652a4126.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__473322cc_8e7c_46b1_bd59_397b4f61ce26
ELOP-191446-2014 | 4527123 | 6/14/2016 11:33:57 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The HV switch ground has only one conductor going to the ground mat. This could create a shock hazard for a person opening the switch if the voltage potential is not limited by the proper ground conductor size. | 3 | Continuity Bonding; method for equipment is not adequate. | Groundmat.png | file://x:/photopub/docs/0000000443/74c406e9-2fe4-4e39-8967-0ccc08d9e316.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__473322cc_8e7c_46b1_bd59_397b4f61ce26
GAUP-586552-2016 | UW-393192-2016 | 6/15/2016 8:47:57 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Venting must be S636 certified to prevent failure and possible leaking of flue products into living space and causing illness | 3 | Unapproved venting material | Un-approved_vent_material.png | file://x:/photopub/docs/0000000443/5ec004dd-e9b7-415f-9b30-21edf4e736bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e506e800_8946_4af1_8de9_0f622c375d46
ELIN-566189-2016 | EL-378459-2016 | 5/31/2016 10:38:38 AM | ASSESS: EL: Service Connection | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Addition_.png | file://x:/photopub/docs/0000000436/5436b998-cecf-442e-a2d5-97cfbf016fdc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29d09c25_c8e5_4ee3_a117_5cd152ff76b4
ELOP-195885-2014 | 2316 | 6/16/2016 11:16:31 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL167 | Protection and control Controller is not of proper type. | 3 | 3 | The compressor starter has two openings on the cabinet that expose the live terminals inside to contact, if a person was to insert a tool or finger inside the openings there is a risk of shock or arc fault damage. | 3 | Protection and control Controller is not of proper type. | CompressorStarter.png | file://x:/photopub/docs/0000000444/521eeefa-5f5d-4bdf-8b36-fbbcfec03fd1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8812bfe8_63cb_49a4_bee6_cf723bec160f
BPVOP-590732-2016 | 4399354 | 6/8/2016 10:33:26 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 90psi jacketed steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data.png | file://x:/photopub/docs/0000000440/ae5e17ef-46a0-431f-b0ee-84f42bc16601.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d474aae0_0cb7_493f_9d14_69155a805e3a
BPVOP-590732-2016 | 4399354 | 6/8/2016 10:33:26 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 90psi jacketed steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Steam_kettle_1_steam_line_.png | file://x:/photopub/docs/0000000440/aa6f1720-0849-41dc-b6e9-a0bed10ff04c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d474aae0_0cb7_493f_9d14_69155a805e3a
ELIN-592040-2016 | EL-396838-2016 | 6/13/2016 5:12:16 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Newly installed receptacle are required to be tamper resistant. This is required to prevent shock hazards to persons from inserting objects or fingers into receptacle openings. This installation has two newly installed 15A, 120V receptacles installed on the exterior of a mobile home. The receptacles are non-tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if objects or persons contact the energized openings of receptacles. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | New_receptacle_installed_on_existing_box_at_front_entrance.png | file://x:/photopub/docs/0000000442/62f9f541-531b-49b4-adc1-d5ab72bfac1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cb01a96_b5c7_4603_a247_b9b2836fac5d
ELIN-592040-2016 | EL-396838-2016 | 6/13/2016 5:12:16 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Newly installed receptacle are required to be tamper resistant. This is required to prevent shock hazards to persons from inserting objects or fingers into receptacle openings. This installation has two newly installed 15A, 120V receptacles installed on the exterior of a mobile home. The receptacles are non-tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if objects or persons contact the energized openings of receptacles. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | New_receptacle_installed_on_existing_box_on_porch.png | file://x:/photopub/docs/0000000442/72dc1129-9455-49b4-8212-e4672c5953ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cb01a96_b5c7_4603_a247_b9b2836fac5d
ELIN-592040-2016 | EL-396838-2016 | 6/13/2016 5:12:16 PM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Newly installed receptacle are required to be tamper resistant. This is required to prevent shock hazards to persons from inserting objects or fingers into receptacle openings. This installation has two newly installed 15A, 120V receptacles installed on the exterior of a mobile home. The receptacles are non-tamper resistant type receptacles. Left uncorrected this is a potential shock hazard if objects or persons contact the energized openings of receptacles. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Mobile_home_.png | file://x:/photopub/docs/0000000442/6f366e00-8304-4eb9-92dd-99a4b697d8b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cb01a96_b5c7_4603_a247_b9b2836fac5d
ELIN-594309-2016 | EL-355891-2016 | 6/14/2016 1:38:11 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary construction service not built to temporary construction standard. Electrical panel exposed directly to weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_service_enclosure.png | file://x:/photopub/docs/0000000443/8fa3fb31-2e02-4cf3-8b51-f78b54d7349e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7e887ae_ab8d_42a0_852d_3050fee07157
ELIN-594309-2016 | EL-355891-2016 | 6/14/2016 1:38:11 PM | ASSESS: EL IN: 180-Day Safety Check | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Temporary construction service not built to temporary construction standard. Electrical panel exposed directly to weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_construction_enclosure_exposed_to_rain.png | file://x:/photopub/docs/0000000443/bfe1202a-3b2b-4a95-bd2e-b896f885b8d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f7e887ae_ab8d_42a0_852d_3050fee07157
ELIN-594312-2016 | EL-301860-2015 | 6/14/2016 4:20:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Panel-board exposed to direct weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temporary_enclosure_damaged.png | file://x:/photopub/docs/0000000443/15e7c66f-6e3b-40ae-8351-ff3466ab0c8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__598396be_7a32_43e8_91f9_17e3d740215b
BPVSP-257703-2014 | 2303384 | 5/27/2016 4:00:00 PM | ASSESS: BPV SP: General Supervision | png | #asFound | BP108 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | 3 | 3 | ASME Sec.VIII states no intervening shutoff valves between the Safety Relief valve. A closed shut off valve on the inlet or discharge piping would isolate the SRV from discharging if there was a system over pressure. The Tank would not be able to discharge the pressure and would result in a catastrophic result. | 3 | 3.0.1 Safeties will not function - Safety Devices installed contrary to the manufacturer instructions and or applicable standards | Tolko_air_tank_sv.png | file://x:/photopub/docs/0000000443/a7a46631-5407-464b-a469-a763369731c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff3da8e1_eaff_444e_9019_4e693839cf56
ELIN-583354-2016 | EL-391215-2016 | 6/3/2016 12:34:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found service grounding conductor was not installed properly to code for grounding service system within service compartment as per approved use of electrical equipment. When electrical system is not grounded as required by code the installation may become an electrical fire or shock hazard in the event of an electrical fault condition on the system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 19.png | file://x:/photopub/docs/0000000438/6df9d305-5271-406f-afe2-c6687c689b97.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96104cdb_bcdd_4975_b749_c713fcb64cee
ELIN-589162-2016 | EL-387917-2016 | 6/7/2016 10:23:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | An AC system grounded at the wrong location may not provide a fault path sufficient for operation of the Overcurrent devices. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Service_box_and_neutral_conductor_not_grounded.png | file://x:/photopub/docs/0000000439/c1ee2809-30a6-463c-b3f9-a914723d1d8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32d79885_7495_4b47_9e34_1dbe89e99cd0
ELIN-589162-2016 | EL-387917-2016 | 6/7/2016 10:23:11 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 2 | An AC system grounded at the wrong location may not provide a fault path sufficient for operation of the Overcurrent devices. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Service_box_and_neutral_not_grounded_2.png | file://x:/photopub/docs/0000000439/7e6964d4-51a9-4483-9e35-56acbf986880.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32d79885_7495_4b47_9e34_1dbe89e99cd0
ELIN-589697-2016 | EL-352263-2016 | 6/7/2016 11:11:24 AM | ASSESS: EL: Final | png | #asFound | EL126 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | 3 | 3 | A new residence has been constructed without providing a receptacle accessible from grade on a dedicated circuit for use outdoors. Residents may resort to using extension cords from receptacles located inside the dwelling and flexibl cord can be damaged when misused or fed through windows and doorways. Additionally, the circuit which may not be dedicated is not robust enough to reliably operate outdoor equipment that can put strain on a circuit that may be feeding other electrical equipment in the dwelling. This can result in either property damage or potential for injury to persons and damage to electrical equipment | 3 | Installation of electrical equipment Residential: general use receptacles are not properly spaced. | No_receptacle_on_dedicated_circuit_at_grade_new_dwelling.png | file://x:/photopub/docs/0000000440/20ce3f95-6613-42f8-a00a-c4dd220d7d42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e51b86d8_aa61_4dd9_8982_67e936b5670b
GAOP-366545-2015 | GA-130568-2014 | 6/13/2016 12:33:40 PM | ASSESS: GA OP: Periodic | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | The as found hazard was a liquid propane supply line serving a remote vehicle refuelling station which had a leak on a threaded joint. This is a hazard because if the gas were to be ignited there is a risk of fire and/or explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Leak_2.png | file://x:/photopub/docs/0000000444/93427781-abbc-4123-978a-54e1e05cf787.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0c9b744_aff3_47d4_b7fa_5555f75fc142
GAOP-366545-2015 | GA-130568-2014 | 6/13/2016 12:33:40 PM | ASSESS: GA OP: Periodic | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | The as found hazard was a liquid propane supply line serving a remote vehicle refuelling station which had a leak on a threaded joint. This is a hazard because if the gas were to be ignited there is a risk of fire and/or explosion. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Leak_1.png | file://x:/photopub/docs/0000000444/1f249111-f4b8-4ed5-a572-027afdf60d29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0c9b744_aff3_47d4_b7fa_5555f75fc142
GAIN-572459-2016 | GA-379550-2016 | 6/16/2016 1:52:00 PM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | Appliance air intake is approximately 2 feet horizontally and 3 feet vertically from meter regulator relief opening. I have asked and have still not been given an explanation as to what the hazard is. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 1683_happyvale.png | file://x:/photopub/docs/0000000444/1a7b7241-7fb8-4bc8-af70-26b226f67e43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7d7ee67_a631_4dc7_9f30_b40ff6d99db9
GAIN-595840-2016 | GA-035710-2013 | 6/16/2016 12:41:05 PM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | 510_amess.png | file://x:/photopub/docs/0000000444/68f5a871-8afb-4b35-b409-f80b7bedc63e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9eb69693_f10c_4564_ba01_41862b955083
EDIN-582601-2016 | ED-250493-2015 | 5/12/2016 6:46:00 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED012 | Oil/Water/Other Debris found that: Does not present a fire hazard and is not likely to progress | 2 | 2 |  | 2 | Oil/Water/Other Debris found that: Does not present a fire hazard and is not likely to progress | Wet_pit.png | file://x:/photopub/docs/0000000438/cc0b0579-3b77-4617-8216-1de8b2ca9658.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1376db20_f52a_4f9b_9866_e6ca84480916
ELIN-583354-2016 | EL-391215-2016 | 6/3/2016 12:34:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found service grounding conductor was not installed properly to code for grounding service system within service compartment as per approved use of electrical equipment. When electrical system is not grounded as required by code the installation may become an electrical fire or shock hazard in the event of an electrical fault condition on the system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 20.png | file://x:/photopub/docs/0000000438/73cd7968-118d-4acb-a56b-8a48f2ff26eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96104cdb_bcdd_4975_b749_c713fcb64cee
ELIN-583354-2016 | EL-391215-2016 | 6/3/2016 12:34:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found service grounding conductor was not installed properly to code for grounding service system within service compartment as per approved use of electrical equipment. When electrical system is not grounded as required by code the installation may become an electrical fire or shock hazard in the event of an electrical fault condition on the system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 18.png | file://x:/photopub/docs/0000000438/547f69af-f4ea-4cc8-9ee8-55c06b40994a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96104cdb_bcdd_4975_b749_c713fcb64cee
ELIN-583354-2016 | EL-391215-2016 | 6/3/2016 12:34:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found service grounding conductor was not installed properly to code for grounding service system within service compartment as per approved use of electrical equipment. When electrical system is not grounded as required by code the installation may become an electrical fire or shock hazard in the event of an electrical fault condition on the system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 17.png | file://x:/photopub/docs/0000000438/4135a5ba-cce7-4c68-9bb2-d86365314bec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96104cdb_bcdd_4975_b749_c713fcb64cee
ELIN-583354-2016 | EL-391215-2016 | 6/3/2016 12:34:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found service grounding conductor was not installed properly to code for grounding service system within service compartment as per approved use of electrical equipment. When electrical system is not grounded as required by code the installation may become an electrical fire or shock hazard in the event of an electrical fault condition on the system. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 21.png | file://x:/photopub/docs/0000000438/5bf66b13-d26b-41fe-922b-22505579cbf0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__96104cdb_bcdd_4975_b749_c713fcb64cee
EDOP-573037-2016 | 2050657 | 6/7/2016 4:09:30 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | When access to the machine room is over the roof, a clear path is to be provided with a hand rail if there is no parapet on the edge of the roof. This is to prevent a fall in dim lighting or adverse weather conditions. No hand rail was installed, and the roof has no parapet. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 2nd_view__no_rail.png | file://x:/photopub/docs/0000000439/79299692-48b9-4378-bab0-b928b1209b54.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d4376d1_d2e2_47e1_9ea5_bce4d19c88b0
EDOP-573037-2016 | 2050657 | 6/7/2016 4:09:30 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | When access to the machine room is over the roof, a clear path is to be provided with a hand rail if there is no parapet on the edge of the roof. This is to prevent a fall in dim lighting or adverse weather conditions. No hand rail was installed, and the roof has no parapet. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Roof_path__no_rail.png | file://x:/photopub/docs/0000000439/2fbd36f0-1c2f-48aa-83d4-ca87aeb38b14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d4376d1_d2e2_47e1_9ea5_bce4d19c88b0
EDOP-573037-2016 | 2050657 | 6/7/2016 4:09:30 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | When access to the machine room is over the roof, a clear path is to be provided with a hand rail if there is no parapet on the edge of the roof. This is to prevent a fall in dim lighting or adverse weather conditions. No hand rail was installed, and the roof has no parapet. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3rd_view__two_level_roof__no_rail.png | file://x:/photopub/docs/0000000439/06da9838-3314-489a-9e2c-0bf151a3d58a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d4376d1_d2e2_47e1_9ea5_bce4d19c88b0
ELIN-594163-2016 | UW-398440-2016 | 6/13/2016 12:28:38 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | NMD90 household wiring was run along the ground to feed outside lights. This type of wire is not approved for use in areas where it is exposed to the weather or in areas where it is subject to mechanical damage. Use of this type of wire in those locations could result in damage and degradation of the wire, leading to potential shock and fire hazards. | 3 | Conductors Equipment is not approved for the specific use. | Ftgp.png | file://x:/photopub/docs/0000000443/09934e9c-d8fd-4cef-af34-51cb88d5b423.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af2e14e2_0846_4627_b4e2_f20dde038386
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Storage.png | file://x:/photopub/docs/0000000443/12c98198-3b5a-4ac5-94b4-9db16b2a7bbf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Const_serv.png | file://x:/photopub/docs/0000000443/409ded90-4a61-496e-b656-98e4581b43fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Branch_circuits.png | file://x:/photopub/docs/0000000443/8b3ff4ef-305e-4410-ba81-ce7f8d7f52de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Access.png | file://x:/photopub/docs/0000000443/e0582b42-6e2b-4623-aa86-f24efe745e66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Transformer.png | file://x:/photopub/docs/0000000443/625d1160-96e3-42e7-92fb-575b755a0c3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 1_screw.png | file://x:/photopub/docs/0000000443/86cd7b53-2ecd-4ddb-be39-beb497d97835.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-594434-2016 | UW-398612-2016 | 6/14/2016 3:00:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Extensive Unpermitted work appears to have been done over the years by unqualified persons resulting in extensive unsafe conditions in publicly accessible areas | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Corrosion_ac90.png | file://x:/photopub/docs/0000000443/4ed0d87c-be79-4137-896e-861c2b6de052.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2eb462e5_bf58_412a_b445_1eecf41436c8
ELIN-584579-2016 | EL-237786-2015 | 6/7/2016 5:40:05 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Overcurrent device is oversized to conductor. Possibility for fire in fault conditions. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Lighting_not_installed.png | file://x:/photopub/docs/0000000439/5a988cc3-bf87-4268-8ee7-7b33edeee821.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6a51af_29b3_4864_8f72_3a3858ca4820
ELIN-584579-2016 | EL-237786-2015 | 6/7/2016 5:40:05 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Overcurrent device is oversized to conductor. Possibility for fire in fault conditions. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Type_r2_panel_in_damp_location.png | file://x:/photopub/docs/0000000439/a2eee58e-6b3c-4933-b4bd-1650cfb6fd9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6a51af_29b3_4864_8f72_3a3858ca4820
ELIN-584579-2016 | EL-237786-2015 | 6/7/2016 5:40:05 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Overcurrent device is oversized to conductor. Possibility for fire in fault conditions. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 2_Circuits_on_1breaker.png | file://x:/photopub/docs/0000000439/51048b3c-17e0-4e6b-8bf6-2f92c8e3b010.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6a51af_29b3_4864_8f72_3a3858ca4820
ELIN-584579-2016 | EL-237786-2015 | 6/7/2016 5:40:05 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Overcurrent device is oversized to conductor. Possibility for fire in fault conditions. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Floor_receptacle_facing_upwards.png | file://x:/photopub/docs/0000000439/41a8ecd6-52c3-4d99-92af-a6097fa50f3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6a51af_29b3_4864_8f72_3a3858ca4820
ELIN-584579-2016 | EL-237786-2015 | 6/7/2016 5:40:05 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Overcurrent device is oversized to conductor. Possibility for fire in fault conditions. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 100Amp_circuit_breaker.png | file://x:/photopub/docs/0000000439/db7d2a10-5374-4a2a-b5c8-64ed0d75d91f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6a51af_29b3_4864_8f72_3a3858ca4820
ELIN-584579-2016 | EL-237786-2015 | 6/7/2016 5:40:05 PM | ASSESS: EL: Final | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | Overcurrent device is oversized to conductor. Possibility for fire in fault conditions. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Devices_not_installed.png | file://x:/photopub/docs/0000000439/7e1d4bac-6d77-45fd-a1a2-6c0c66d98968.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba6a51af_29b3_4864_8f72_3a3858ca4820
ELOP-591247-2016 | 4248 | 6/11/2016 8:09:40 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | A 400A 208V panel has been temporarily fed. The connections have been made directly to the bus lugs without fittings or the panel cover in place, the cables runs through the door of the room so access to the energized equipment has not been provided or restricted. This could result in a shock hazard and equipment damage. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Panel_Connection.png | file://x:/photopub/docs/0000000442/5328ef76-886b-445e-9425-9f2e9f11cf52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c110affe_7820_4046_ba33_c567ef7a88ac
ELIN-589864-2016 | EL-395778-2016 | 6/8/2016 10:11:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unfused consumer service conductors are not permitted to exceed 1.5 m in length inside a building without being encased in concrete. In this installation a service connection request had been submitted before the building contractor had added the concrete required. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | At_meter_base.png | file://x:/photopub/docs/0000000440/899701eb-3981-46cd-9a5f-5231f88f3228.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13a9a996_0038_41ed_bced_e1e5ba44a915
ELIN-589864-2016 | EL-395778-2016 | 6/8/2016 10:11:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Unfused consumer service conductors are not permitted to exceed 1.5 m in length inside a building without being encased in concrete. In this installation a service connection request had been submitted before the building contractor had added the concrete required. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | At_panel.png | file://x:/photopub/docs/0000000440/e005e67a-b6ad-4ebb-b10c-b9483e58fe1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13a9a996_0038_41ed_bced_e1e5ba44a915
ELIN-585097-2016 | EL-359403-2016 | 6/1/2016 12:07:12 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | The conduit runs for the 600 volt 3 phase feed to the transformer have field bends made and are kinked which could likely affect the installation of the cabling. This is an equipment damage issue. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 600_volt_duct_bank_2.png | file://x:/photopub/docs/0000000437/ceb22f48-fbe0-4932-a2f8-3d3d8cee07e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f81fc31_dade_4942_8b9b_e7595e7f8882
ELIN-585097-2016 | EL-359403-2016 | 6/1/2016 12:07:12 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | The conduit runs for the 600 volt 3 phase feed to the transformer have field bends made and are kinked which could likely affect the installation of the cabling. This is an equipment damage issue. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 600_volt_duct_bank.png | file://x:/photopub/docs/0000000437/e34c4629-5842-4c1c-9476-82ba7baf6b4b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f81fc31_dade_4942_8b9b_e7595e7f8882
GAIN-572688-2016 | GA-371344-2016 | 6/8/2016 3:58:10 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | 1) A burner shall be monitored or requires a flame safety safeguard system 2) The fire table burner does not have a flame safety system. 3) A Burner with out a flame safety system could allow gas to flow uncontrolled in the event of flame loss during operation. | 4 | Missing mandatory safety controls | Appliance_shut_down_no_burner_safety_control.png | file://x:/photopub/docs/0000000440/da8573d3-4dd3-4a5e-aba4-0c7227538f70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d030773_1cab_40ad_8b6e_6f6c819c8231
GAIN-572688-2016 | GA-371344-2016 | 6/8/2016 3:58:10 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | 1) A burner shall be monitored or requires a flame safety safeguard system 2) The fire table burner does not have a flame safety system. 3) A Burner with out a flame safety system could allow gas to flow uncontrolled in the event of flame loss during operation. | 4 | Missing mandatory safety controls | Custom_fire_table_no_certification__.png | file://x:/photopub/docs/0000000440/91169879-83e6-4f7a-b799-58d614e19a02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d030773_1cab_40ad_8b6e_6f6c819c8231
GAIN-572688-2016 | GA-371344-2016 | 6/8/2016 3:58:10 PM | ASSESS: GA: Final | png | #asFound | GA144 | Missing mandatory safety controls | 4 | 4 | 1) A burner shall be monitored or requires a flame safety safeguard system 2) The fire table burner does not have a flame safety system. 3) A Burner with out a flame safety system could allow gas to flow uncontrolled in the event of flame loss during operation. | 4 | Missing mandatory safety controls | Fire_table_Burner_.png | file://x:/photopub/docs/0000000440/e4c3f3fd-8bbd-4442-a53e-c8d777f7a68e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d030773_1cab_40ad_8b6e_6f6c819c8231
ELHE-595093-2016 | HE-398995-2016 | 6/16/2016 7:04:09 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 4 | An indoor use gardening tent assembly of electrical equipment for operation on 120 volts and 15 amps was being offered for sale. The fixture, fan speed controls, lamps, and circulating fan did not bear evidence of approval. Failure of the uncertified fan, or other components, would lead to extreme temperatures in the vicinity of the lamp which could cause damage to property or injury to persons | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Fixture_portion_of_tent_assembly.png | file://x:/photopub/docs/0000000444/80dfdf59-a0f2-4e36-8be1-be9edce61c0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85c0c77d_c477_4117_b02f_e61b65febd28
ELOP-250235-2014 | 3338337 | 6/16/2016 12:00:49 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | High voltage lines must be kept clear of objects below. In this remote installation a pole had been struck by a tree. It's guy line broke and the pole was listing. This created slack in the wires between poles. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Two_poles.png | file://x:/photopub/docs/0000000444/4f5f06fc-1adb-43d9-b6fe-44f6bb80fe89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40d8c98c_9b20_4f9e_a05c_efa7a15376c6
ELOP-250241-2014 | 5179344 | 6/16/2016 12:14:48 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords cannot be used as a replacement for permanent wiring. In this installation a flexible cord was run through interior walls and one exterior wall where it was coiled on the ground. | 4 | Conductors, Misuse of flexible cords. | Source.png | file://x:/photopub/docs/0000000444/7d0edd4b-591c-461b-b56f-cbdd5924380c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65b546f6_adc0_4bdd_962d_e78d6cd738fd
ELOP-250235-2014 | 3338337 | 6/16/2016 12:00:49 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | High voltage lines must be kept clear of objects below. In this remote installation a pole had been struck by a tree. It's guy line broke and the pole was listing. This created slack in the wires between poles. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Could_guy_this.png | file://x:/photopub/docs/0000000444/7beefbcf-3cb2-4fa2-b269-1959cd6c8221.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40d8c98c_9b20_4f9e_a05c_efa7a15376c6
ELOP-250243-2014 | 1979 | 6/16/2016 11:54:41 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 | A minimum of 1 m clear working pace must be maintained around electrical equipment. In this school a large amount of cardboard was stored in front of an electrical panel. | 1 | General Working space or dedicated space is being used for storage | Storage_area.png | file://x:/photopub/docs/0000000444/d090a795-a653-47cf-828f-6dd85d242528.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1dc30434_b026_4675_9f58_062d736c639b
ELOP-250241-2014 | 5179344 | 6/16/2016 12:14:48 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords cannot be used as a replacement for permanent wiring. In this installation a flexible cord was run through interior walls and one exterior wall where it was coiled on the ground. | 4 | Conductors, Misuse of flexible cords. | Terminus.png | file://x:/photopub/docs/0000000444/be5c5adc-d617-49bb-8b8a-65ba72c6ce0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65b546f6_adc0_4bdd_962d_e78d6cd738fd
BPVOP-589991-2016 | 2283810 | 6/7/2016 10:01:42 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound PRD mounted horizontally and is past service interval. | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 |  | Safety relief valve may not operate as intended, allowing system pressure to exceed boiler MAWP. This can cause the boiler to rupture and release scalding water which can cause personal injury and property damage. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | HW80123_PRD.png | file://x:/photopub/docs/0000000439/98890604-0c51-4a2d-8cd5-f7b56b8c3de9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1180be7b_5ed0_481d_9f5c_fd7c110c384b
ELIN-588957-2016 | EL-209894-2015 | 6/15/2016 9:06:23 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | Exposed ends of insulated conductors must be protected from contact by entering them into a junction box or other acceptable method. The white and red wires are not rated to for underground installations. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000443/5a848a68-ed38-4930-96fe-7f75e419400f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7cdb5d16_22e7_4e6b_9f81_8750e202200a
ELIN-588957-2016 | EL-209894-2015 | 6/15/2016 9:06:23 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 2 | Exposed ends of insulated conductors must be protected from contact by entering them into a junction box or other acceptable method. The white and red wires are not rated to for underground installations. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000443/78085370-c3f9-4b0e-9265-9e7033b0e4e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7cdb5d16_22e7_4e6b_9f81_8750e202200a
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Main_distribution_1.png | file://x:/photopub/docs/0000000444/e69b5290-e45e-4aed-9c88-96f6022ab90e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Open_junction_boxes_typical.png | file://x:/photopub/docs/0000000444/7c335c49-14b7-440d-8b20-f7ad8ec9fbba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Distribution_2.png | file://x:/photopub/docs/0000000444/1ef7d084-fb4b-462d-8e5b-54846f7f27f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | AC_cable_in_damp_areas.png | file://x:/photopub/docs/0000000444/20157323-a074-4c08-b7a4-f8eb9e066b64.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Distribution_panel_and_branch_circuits.png | file://x:/photopub/docs/0000000444/ef54ab5f-77df-4d50-87e0-a172904c4149.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Distribution_panel_3.png | file://x:/photopub/docs/0000000444/8595ae73-ae35-4ce9-ba1d-2f10a04d92e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Micro_wave_receptacle_and_branch_ccts.png | file://x:/photopub/docs/0000000444/33ec4233-c03c-4c87-87e4-295eec7d3902.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
ELIN-590231-2016 | UW-396011-2016 | 6/8/2016 8:35:43 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unauthorized and non compliant work has resulted in exposed electrical conductors in several locations. This has resulted in shock hazard and fire hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_energized_motor_connections.png | file://x:/photopub/docs/0000000444/fc4d7bd7-5875-428e-94e1-11e8d5c7cf80.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c7edfb4_bc7e_46d4_83a5_d2fbe2d3a1b8
BPVOP-593960-2016 | 2295987 | 6/14/2016 9:42:36 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP068 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | 1 | 1 |  | 1 | 1.2.3 Boiler construction - Minor scale or deposits on boiler heat exchange surfaces | Boiler_scale.png | file://x:/photopub/docs/0000000442/b44f72d6-ac23-4cda-ba0c-680d64fd443d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3f8c1fc3_9f34_4066_842d_56d33492fefb
ELIN-593916-2016 | EL-391591-2016 | 6/15/2016 8:45:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | 3 switch box not fastened on two sides. Larger boxes may move during installation of switches and drying of lumber. | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | Multi_gangbox.png | file://x:/photopub/docs/0000000444/f8148f01-b08c-4201-8769-a8a63c86ad90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7fe92ff2_6cca_4cae_98db_59ab371c1ec3
ELIN-593976-2016 | EL-398270-2016 | 6/15/2016 1:53:16 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Hazelton.png | file://x:/photopub/docs/0000000444/52ff094f-727d-4a12-92ba-96d53692fda4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feb3e379_1578_43a2_b7ff_154796c0b9ff
ELIN-589369-2016 | EL-319371-2015 | 6/15/2016 2:52:26 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles beside kitchen sink are not GFCI protected | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Daycare.png | file://x:/photopub/docs/0000000444/34b8a766-a448-4125-91fc-898f49e4cb5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69f8a8ad_1e70_45bc_90aa_2de167674127
ELIN-590209-2016 | EL-383744-2016 | 6/21/2016 1:33:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Haz_prv.png | file://x:/photopub/docs/0000000444/d223b6c1-ee91-458c-9dc9-f8c3b0a72648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad988b14_1e7c_47db_99ac_97a9f4e52315
ELIN-590417-2016 | 3901937 | 6/9/2016 12:18:52 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The metallic sheath bond and mechanical continuity must be maintained for the entire cable length. In this installation plastic fittings had been used instead of metal fittings and the continuity was lost. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Marked_as_12c12_TECK_90.png | file://x:/photopub/docs/0000000441/1804a6d5-b860-4b8f-9d1c-65fbb7ce26bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2667426_6ed6_4bfa_9272_c12cb6e65eff
ELIN-590417-2016 | 3901937 | 6/9/2016 12:18:52 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | The metallic sheath bond and mechanical continuity must be maintained for the entire cable length. In this installation plastic fittings had been used instead of metal fittings and the continuity was lost. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | TECK_cable_terminates_in_PVC_fittings.png | file://x:/photopub/docs/0000000441/c4d18174-d2b4-42a1-844e-48430c2cd15b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2667426_6ed6_4bfa_9272_c12cb6e65eff
ELOP-335141-2015 | 7119 | 6/9/2016 3:05:59 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Electrical enclosures housing energized wiring must be closed with an approved cover. In this installation a fan motor switch and cover had been left open after service. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Fan_motor_switch.png | file://x:/photopub/docs/0000000441/4b8334ec-4026-4c93-9ffe-5fa2cdddc1ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__707a5e2e_27b8_41d4_bd93_0d8dfb7a83f5
AMOP-577541-2016 | 2053156 | 5/16/2016 3:25:46 PM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Deck joint plate fasteners which prevent the pie shaped sections of the rotating deck from separating when rotating have broken or pulled out at multiple locations. The separating gaps in the rotating deck could present a pinching hazard to persons standing on the deck (eg the heel of a lady's high heel shoe). | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Deck_joint_plate_missing_fasteners.png | file://x:/photopub/docs/0000000442/716e1dd5-579d-454e-af07-5543feebf4fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__53c27381_1260_455d_83ea_f327f2ad414b
AMIN-590328-2016 | UW-396052-2016 | 6/3/2016 3:47:22 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM050 | Anchoring is not installed as per manufacturers requirements but unit is not in operation Baffling is not present and unit is in operation | 4 | 3 | None of the unit attachment points were anchored at the time of inspection, however the unit was not in operation at the time of inspection. There is hazard in which there is a risk the device could rollover or move out of position in a high wind condition. | 4 | Anchoring is not installed as per manufacturers requirements but unit is not in operation Baffling is not present and unit is in operation | Unit_not_anchored.png | file://x:/photopub/docs/0000000442/216aa416-a03d-46c9-9883-44686c315490.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8651ec32_5689_42da_b470_e6417f84e0b3
ELIN-594697-2016 | EL-382284-2016 | 6/15/2016 2:57:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Consumer service/distribution equipment not adequately protected from effects of weather during construction stage of installation. This significantly increases the risk of personal injury (shock) or property damage (thermal event) due to equipment failure from exposure to water. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_rear_of_main_distribution.png | file://x:/photopub/docs/0000000443/e45a97fe-18a6-4df4-a186-342b955c8c13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff7274a6_535d_4440_bb83_3dceb5018cb1
ELHE-595430-2016 | HE-399192-2016 | 6/16/2016 12:33:40 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | The damaged and energized teck cable is hanging on pole accessible to persons, this cable is protected by the 40 amp 240 volt breaker at the main panel that feeds the overhead wiring to the south of the panel, this is a shock hazard | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_cable.png | file://x:/photopub/docs/0000000444/f6905447-0195-428a-a687-9f8802736c46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e9fdb62_d7f5_4f0d_b53d_2b14a343f61e
ELIN-591413-2016 | EL-326615-2015 | 6/16/2016 10:58:07 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 480 volt 30 amp feeder cable to the pivot units is laying on grade surface at the building and pivot units with no mechanical protection. This is a shock hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Pivot_1.png | file://x:/photopub/docs/0000000444/1d3e2148-340d-4bae-927d-81f9aabad665.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3118bf79_59bf_4ce4_8ad1_959c71c75898
BPVOP-583668-2016 | 2289131 | 6/16/2016 10:39:45 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP133 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | 3 | 3 | During the inspection of an Ammonia refrigeration System of 125 kW, 400 lbs of ammonia and a system pressure of 250 psig I found 3 Pressure Relief Device's (PRD's) overdue as per CSA B52. In case of system overpressure this can cause the PRD's not to function and piping or pressure vessels rupture can occur. | 3 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | Overdue_PRD.png | file://x:/photopub/docs/0000000444/6cd96813-5980-47de-96a4-fc90de1da556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6af61c27_43f6_4abf_91d3_a31bfaa6020c
BPVOP-592325-2016 | 2279159 | 6/10/2016 2:00:06 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety valve appears damaged. Air receiver tank more than 20 years old. Compliance with Safety Order required failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Pressure_indicator_damaged.png | file://x:/photopub/docs/0000000441/88aa6beb-e467-4d46-bd56-898d8b056946.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4d3d91_9b88_4e19_9495_594385265fe5
BPVOP-592325-2016 | 2279159 | 6/10/2016 2:00:06 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety valve appears damaged. Air receiver tank more than 20 years old. Compliance with Safety Order required failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | tank_safety_valve.png | file://x:/photopub/docs/0000000441/86cb80d2-48f6-4d9c-b436-2bf2d945a190.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4d3d91_9b88_4e19_9495_594385265fe5
BPVOP-592325-2016 | 2279159 | 6/10/2016 2:00:06 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety valve appears damaged. Air receiver tank more than 20 years old. Compliance with Safety Order required failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_receiver_end_view.png | file://x:/photopub/docs/0000000441/8d22a2dc-cca4-4a9c-bad3-2aef29f7ed03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4d3d91_9b88_4e19_9495_594385265fe5
BPVOP-592325-2016 | 2279159 | 6/10/2016 2:00:06 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety valve appears damaged. Air receiver tank more than 20 years old. Compliance with Safety Order required failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Supply_line_gauge_damaged.png | file://x:/photopub/docs/0000000441/e5160a49-a592-4c97-bac6-4afd6b932557.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4d3d91_9b88_4e19_9495_594385265fe5
BPVOP-592325-2016 | 2279159 | 6/10/2016 2:00:06 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | No evidence of regular maintenance on this machine-mounted air receiver. Broken pressure indicator dials. Safety valve appears damaged. Air receiver tank more than 20 years old. Compliance with Safety Order required failure to do so may result in an incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_receiver_nameplate.png | file://x:/photopub/docs/0000000441/65b85b9c-344c-45ff-b679-f6fc3288250b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce4d3d91_9b88_4e19_9495_594385265fe5
GAIN-592359-2016 | GA-331648-2016 | 6/14/2016 3:23:47 PM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 4 | The gas venting was glued using the incorrect glue. The venting is graded the wrong way so that the condensate in the vent will not drain properly. | 5 | Special venting system not glued or connected as per certified instructions | Rjgas1.png | file://x:/photopub/docs/0000000443/777a4477-4083-41ef-ab2b-577fe5edd1c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cce7b499_b39f_4333_babb_a71096971dc6
GAIN-592359-2016 | GA-331648-2016 | 6/14/2016 3:23:47 PM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 4 | The gas venting was glued using the incorrect glue. The venting is graded the wrong way so that the condensate in the vent will not drain properly. | 5 | Special venting system not glued or connected as per certified instructions | Rjgas.png | file://x:/photopub/docs/0000000443/2e8e1903-1d1b-4ae2-adca-588c48982ee8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cce7b499_b39f_4333_babb_a71096971dc6
GAIN-592433-2016 | GA-392797-2016 | 6/14/2016 10:27:38 AM | ASSESS: GA: Final | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Thin walled bushing used for piping size change. Bushing may crack when piping is stressed during settling or movement. | 3 | Non-compliant material/fittings installed | 195Surrey.png | file://x:/photopub/docs/0000000443/ae958c7b-6328-43fb-9b6a-087c00d260c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5bf23c4_d002_48f3_8dea_9aedc1272046
ELIN-588131-2016 | EL-393968-2016 | 6/14/2016 7:19:09 AM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | None of the park sub feeds to the mobiles are marked to identify which service feeds which mobile. The subs are mounted two to a pole and the wrong home could be disconnected by mistake. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Park_Sub.png | file://x:/photopub/docs/0000000442/1a124fb3-3d4f-4a1e-ba11-70146f24ab00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a14b6f78_1e7d_4a14_bd86_d4366475012c
GAIN-588338-2016 | GA-392999-2016 | 6/16/2016 2:43:31 PM | ASSESS: GA: Final | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 4 | Water heater installed and running with no vent connected to the appliance. This is hazard as venting designed to remove the products of combustion and protect the water heater from water damage down the flue. | 5 | Venting system not connected or dislodged from energized appliance | Watson1.png | file://x:/photopub/docs/0000000444/6fa94ab1-59a0-460f-94a2-241461e2dc00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57e2052c_9b87_4f19_8523_34d2f8c24e59
GAIN-588338-2016 | GA-392999-2016 | 6/16/2016 2:43:31 PM | ASSESS: GA: Final | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 4 | Water heater installed and running with no vent connected to the appliance. This is hazard as venting designed to remove the products of combustion and protect the water heater from water damage down the flue. | 5 | Venting system not connected or dislodged from energized appliance | Watson2.png | file://x:/photopub/docs/0000000444/dc923ee6-a0fa-445d-818a-a4b93efa2f03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__57e2052c_9b87_4f19_8523_34d2f8c24e59
GAIN-585313-2016 | GA-386940-2016 | 6/16/2016 1:27:42 PM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | Clearance between service regulator relief opening and mechanical air intake not maintained. Natural gas could be drawn into mechanical air intake to burner if regulator failure occurred causing explosion or fire. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Meter_clearance_not_maintained_.png | file://x:/photopub/docs/0000000444/8993903d-a8a3-4518-bc2a-ddcf8da7db2b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0817a0e2_8ada_4210_a353_effbe0b34e31
GAIN-511945-2016 | GA-288753-2015 | 6/6/2016 1:49:13 PM | ASSESS: GA: Final | png | #asFound | GA141 | Missing make up air exhaust interlocks | 3 | 3 | The bypassed interlock would allow the make up air to fire without an operational exhaust system. Products of combustion would be discharged into the occupied building creating a hazard to the occupants. | 3 | Missing make up air exhaust interlocks | Bypassed_interlock.png | file://x:/photopub/docs/0000000439/dc74d3dc-e261-4208-857c-d3c03030d710.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a715e7e_cdf5_4d62_a763_bc954c17e42c
GAIN-511945-2016 | GA-288753-2015 | 6/6/2016 1:49:13 PM | ASSESS: GA: Final | png | #asFound | GA141 | Missing make up air exhaust interlocks | 3 | 3 | The bypassed interlock would allow the make up air to fire without an operational exhaust system. Products of combustion would be discharged into the occupied building creating a hazard to the occupants. | 3 | Missing make up air exhaust interlocks | Bypassed_interlock__2.png | file://x:/photopub/docs/0000000439/81b6ef85-d905-4717-81c4-564c88e53626.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a715e7e_cdf5_4d62_a763_bc954c17e42c
ELIN-423924-2015 | 3799831 | 6/15/2016 10:04:12 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Electrical cables must be terminated in approved enclosures to protect persons from accidentally coming into contact with energized parts. In this floating camp installation the exterior fixtures had not all been installed but the conductors had been left exposed. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Loomex_under_eave.png | file://x:/photopub/docs/0000000443/71789a41-f3e7-4723-9b27-ed5c5a6e2251.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__35559aaa_f4ed_4fad_b5bf_aa321e241a7a
ELIN-585581-2016 | EL-392440-2016 | 6/6/2016 10:59:49 AM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | NMW cable is exposed to mechanical damage as it is on the ground where the Pedestrian traffic may step on it The hazard would be created from the damage done to the cable which would create an eventual shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 120_volt_conductor_is__conductor_is_subject_to_mechanical_damage_.png | file://x:/photopub/docs/0000000439/8263d7e0-1602-4577-9b2e-13e3c2f12448.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12d044c2_b113_4cf4_8432_d8c1effcefef
ELIN-586855-2016 | EL-393887-2016 | 6/9/2016 9:23:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Incomplete circuits energized by using an extension cord are potential fire and shock hazards | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | AC_cable_in_NMD_type_box.png | file://x:/photopub/docs/0000000441/de2b3a76-88f6-45ee-a976-c7b85b654dd6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db4235c9_a9ab_4aa2_ad82_b533b42fffd2
ELIN-586855-2016 | EL-393887-2016 | 6/9/2016 9:23:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Incomplete circuits energized by using an extension cord are potential fire and shock hazards | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | CMG_cable_in_same_box_as_line_voltage_cable.png | file://x:/photopub/docs/0000000441/fcd0339c-453a-4a60-b169-7e4b6922c90d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db4235c9_a9ab_4aa2_ad82_b533b42fffd2
ELIN-586855-2016 | EL-393887-2016 | 6/9/2016 9:23:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Incomplete circuits energized by using an extension cord are potential fire and shock hazards | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Warehouse_lighting_energized_from_temp_service_.png | file://x:/photopub/docs/0000000441/ba83d755-28af-461e-9e02-ac0c92a83a2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db4235c9_a9ab_4aa2_ad82_b533b42fffd2
ELIN-586855-2016 | EL-393887-2016 | 6/9/2016 9:23:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Incomplete circuits energized by using an extension cord are potential fire and shock hazards | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Cable_terminations_as_found.png | file://x:/photopub/docs/0000000441/00987b69-c24b-4262-a62e-ea6f0a48973a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db4235c9_a9ab_4aa2_ad82_b533b42fffd2
ELIN-593250-2016 | EL-360415-2016 | 6/14/2016 12:59:33 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | This assessment found the infloor heating leads being installed without the required conduit. There is a risk of damaging the cable and a hazard of losing the heating system or starting a fire. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Heating_leads.png | file://x:/photopub/docs/0000000443/9a559cd8-cd66-4503-8f3b-4a535a996d49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a1da4949_f92c_49e5_a52a_a8ea8b9c1077
ELHE-593336-2016 | HE-397901-2016 | 6/14/2016 1:24:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | When connecting aluminum to copper wiring specific wire connectors approved for this purpose are required. This is required to provide for a solid connection between conductors made of different materials that expand and contract at different rates and can oxidize and corrode. This installation at a 15 unit town house complex has aluminum to copper connections made in outlet boxes that are not approved for aluminum to copper connections. Left uncorrected this is a potential fire hazard if the connections fail due to conductor expansion and contraction, or corrosion and oxidization of the conductors within the unapproved connectors currently installed. | 3 | Conductors Equipment is not approved for the specific use. | Town_house_complex_were_inspection_occurred_.png | file://x:/photopub/docs/0000000443/4adddc09-c1f2-479a-bd28-02fb8570fd1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebb9f665_73b4_4737_a1c7_265f3efd25e0
ELHE-593336-2016 | HE-397901-2016 | 6/14/2016 1:24:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | When connecting aluminum to copper wiring specific wire connectors approved for this purpose are required. This is required to provide for a solid connection between conductors made of different materials that expand and contract at different rates and can oxidize and corrode. This installation at a 15 unit town house complex has aluminum to copper connections made in outlet boxes that are not approved for aluminum to copper connections. Left uncorrected this is a potential fire hazard if the connections fail due to conductor expansion and contraction, or corrosion and oxidization of the conductors within the unapproved connectors currently installed. | 3 | Conductors Equipment is not approved for the specific use. | Incorrect_wire_connectors_observed_on_fire_damaged_wiring_-_wire_connectors_not_related_to_incident.png | file://x:/photopub/docs/0000000443/aa2c43c8-9354-4e80-8028-208ab1cc01ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebb9f665_73b4_4737_a1c7_265f3efd25e0
ELHE-593336-2016 | HE-397901-2016 | 6/14/2016 1:24:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | When connecting aluminum to copper wiring specific wire connectors approved for this purpose are required. This is required to provide for a solid connection between conductors made of different materials that expand and contract at different rates and can oxidize and corrode. This installation at a 15 unit town house complex has aluminum to copper connections made in outlet boxes that are not approved for aluminum to copper connections. Left uncorrected this is a potential fire hazard if the connections fail due to conductor expansion and contraction, or corrosion and oxidization of the conductors within the unapproved connectors currently installed. | 3 | Conductors Equipment is not approved for the specific use. | Marrette_number_35_connectors_installed_on_aluminum_to_copper_wiring.png | file://x:/photopub/docs/0000000443/a249be37-5dcf-4248-868b-1d726bdb7495.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebb9f665_73b4_4737_a1c7_265f3efd25e0
ELHE-593336-2016 | HE-397901-2016 | 6/14/2016 1:24:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | When connecting aluminum to copper wiring specific wire connectors approved for this purpose are required. This is required to provide for a solid connection between conductors made of different materials that expand and contract at different rates and can oxidize and corrode. This installation at a 15 unit town house complex has aluminum to copper connections made in outlet boxes that are not approved for aluminum to copper connections. Left uncorrected this is a potential fire hazard if the connections fail due to conductor expansion and contraction, or corrosion and oxidization of the conductors within the unapproved connectors currently installed. | 3 | Conductors Equipment is not approved for the specific use. | Main_floor_hallway_receptacle_sampled.png | file://x:/photopub/docs/0000000443/9a892a93-22dd-4b8f-91bc-fd1a19b4cb30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebb9f665_73b4_4737_a1c7_265f3efd25e0
ELHE-593336-2016 | HE-397901-2016 | 6/14/2016 1:24:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | When connecting aluminum to copper wiring specific wire connectors approved for this purpose are required. This is required to provide for a solid connection between conductors made of different materials that expand and contract at different rates and can oxidize and corrode. This installation at a 15 unit town house complex has aluminum to copper connections made in outlet boxes that are not approved for aluminum to copper connections. Left uncorrected this is a potential fire hazard if the connections fail due to conductor expansion and contraction, or corrosion and oxidization of the conductors within the unapproved connectors currently installed. | 3 | Conductors Equipment is not approved for the specific use. | Unapproved_wire_connectors_observed_on_aluminum_to_copper_fire_damaged_wiring_-_unapproved_wire_connectors_not_related_to_fire_cause_but_non-compliant.png | file://x:/photopub/docs/0000000443/49467453-30d0-4ff9-bf63-1bf1e258bad3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebb9f665_73b4_4737_a1c7_265f3efd25e0
ELHE-593336-2016 | HE-397901-2016 | 6/14/2016 1:24:37 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | When connecting aluminum to copper wiring specific wire connectors approved for this purpose are required. This is required to provide for a solid connection between conductors made of different materials that expand and contract at different rates and can oxidize and corrode. This installation at a 15 unit town house complex has aluminum to copper connections made in outlet boxes that are not approved for aluminum to copper connections. Left uncorrected this is a potential fire hazard if the connections fail due to conductor expansion and contraction, or corrosion and oxidization of the conductors within the unapproved connectors currently installed. | 3 | Conductors Equipment is not approved for the specific use. | Aluminum_to_copper_wiring_spliced_using_unapproved_wire_connectors.png | file://x:/photopub/docs/0000000443/e8fd4158-98b4-4489-baba-2abe5d7963b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebb9f665_73b4_4737_a1c7_265f3efd25e0
ELIN-594861-2016 | UW-398836-2016 | 6/15/2016 9:47:22 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | New_three___New_three_gang_wall_switches_installed.png | file://x:/photopub/docs/0000000443/facd5f9e-f001-425e-be8e-0975d62393a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23d00a82_fc59_4a2f_a9d6_ae23b78294e9
ELIN-594861-2016 | UW-398836-2016 | 6/15/2016 9:47:22 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | One_of__One_of_six_pot_lights_installed_in_living_room_and_MD-90_finished_through_Joyce_s.png | file://x:/photopub/docs/0000000443/0683c2e5-7523-461e-9d33-f4013b6c62e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23d00a82_fc59_4a2f_a9d6_ae23b78294e9
ELIN-594861-2016 | UW-398836-2016 | 6/15/2016 9:47:22 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Nonmetallic_sheath__nonmetallic_sheath_cable_installed_behind_crown_moulding.png | file://x:/photopub/docs/0000000443/c04d57ff-8b8a-459f-9d6c-7ea01569367c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__23d00a82_fc59_4a2f_a9d6_ae23b78294e9
ELIN-586039-2016 | EL-386042-2016 | 6/2/2016 1:35:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Panel_not_installed_in_weather_proof_enclosure.png | file://x:/photopub/docs/0000000438/49e8d438-58f5-4a96-b304-d1ca4fe54c3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7863d3f9_07fb_4786_8217_34775d8b9920
ELIN-586036-2016 | EL-386116-2016 | 6/2/2016 1:38:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Main_distribution_not_installed_in_weatherproof_enclosure.png | file://x:/photopub/docs/0000000438/21392e8d-b6c1-4544-a051-41b4b82be802.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28709ebc_cc60_4dcc_a51c_b375f644087e
ELIN-576423-2016 | EL-303532-2015 | 5/24/2016 5:02:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | The 120/240volt 200 Amp main consumer service conductors pass through the branch circuit compartment of a combination panel. These conductors if energized have no overcurrent protection and should be terminated behind the main service compartment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Main_ground_termination.png | file://x:/photopub/docs/0000000433/f1c4f670-3648-47a6-9e10-b9fb62748a91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c26d4f1b_2888_4f10_a9ff_6003f074d995
ELIN-576423-2016 | EL-303532-2015 | 5/24/2016 5:02:04 PM | ASSESS: EL: Service Connection | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | The 120/240volt 200 Amp main consumer service conductors pass through the branch circuit compartment of a combination panel. These conductors if energized have no overcurrent protection and should be terminated behind the main service compartment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | Consumer_service_conductors.png | file://x:/photopub/docs/0000000433/aec751ec-bec5-4d81-aff3-125610896ab1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c26d4f1b_2888_4f10_a9ff_6003f074d995
BPVIN-581276-2016 | BPV-390122-2016 | 5/23/2016 1:20:53 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | External_corrosoin.png | file://x:/photopub/docs/0000000433/677c315c-7eaa-45b3-81dc-c1c38409a355.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b6924b6_afac_4df7_a1f4_6964f74ebc15
ELIN-589592-2016 | EL-390418-2016 | 6/8/2016 10:59:15 AM | ASSESS: EL: Final | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | 20 amp male receptacle being used on a 30A circuit. This could result in overheating. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Truck_gone_at_time_of_report.png | file://x:/photopub/docs/0000000440/8f26fe71-00f7-4eb5-aa7d-3ce1175ed9a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ff3446c_49de_4815_b765_615ae32af700
ELIN-590869-2016 | UW-391795-2016 | 6/8/2016 4:03:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Permit EL-391858-2016 generated after UW-391795-2016 assigned to Proworks Electric Ltd. after being identified by the General Contractor by telephone. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Overhead.png | file://x:/photopub/docs/0000000440/22db4fb6-96a5-45d9-ab61-c1fb93f8b33e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cc3a1a8_faf2_49d8_9922_c0c01319f7cd
ELIN-590869-2016 | UW-391795-2016 | 6/8/2016 4:03:45 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Permit EL-391858-2016 generated after UW-391795-2016 assigned to Proworks Electric Ltd. after being identified by the General Contractor by telephone. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Disconnect.png | file://x:/photopub/docs/0000000440/fa89187d-69ca-4789-9c52-089273d007fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4cc3a1a8_faf2_49d8_9922_c0c01319f7cd
GAUP-582681-2016 | UW-391029-2016 | 6/8/2016 9:07:21 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 4 | Factory flue assembly not installed correctly that the inner exhaust pipe is too big and not sealed and products of combustion leaking into combustion air and creating condensate. This is a hazard as products of combustion air not leaving outdoors in a safe matter and products of combustion are entering the house. | 5 | Vent sizing causing spillage | 2202-4.png | file://x:/photopub/docs/0000000440/96380b4e-1cad-4f9f-9c30-ea108c1e2099.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8954f5d_33a9_4308_b9d2_6732d416ef5b
GAUP-582706-2016 | UW-391041-2016 | 6/8/2016 10:14:03 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA122 | Combustion air supply missing | 4 | 4 | Furnace drawing air from basement, basement under construction and no combustion or dilution air into building. This creates a hazard as the home can become negative | 4 | Combustion air supply missing | Quesn1.png | file://x:/photopub/docs/0000000440/b3420652-07bf-48ae-8898-2faa43fae656.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ee6e360_9670_4c8b_a1a2_88c5803ef2ee
GAUP-582681-2016 | UW-391029-2016 | 6/8/2016 9:07:21 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 4 | Factory flue assembly not installed correctly that the inner exhaust pipe is too big and not sealed and products of combustion leaking into combustion air and creating condensate. This is a hazard as products of combustion air not leaving outdoors in a safe matter and products of combustion are entering the house. | 5 | Vent sizing causing spillage | 22012-2.png | file://x:/photopub/docs/0000000440/82c13e8b-610a-444e-91df-1c934c4a3b5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8954f5d_33a9_4308_b9d2_6732d416ef5b
GAUP-582681-2016 | UW-391029-2016 | 6/8/2016 9:07:21 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 4 | Factory flue assembly not installed correctly that the inner exhaust pipe is too big and not sealed and products of combustion leaking into combustion air and creating condensate. This is a hazard as products of combustion air not leaving outdoors in a safe matter and products of combustion are entering the house. | 5 | Vent sizing causing spillage | 2202-1.png | file://x:/photopub/docs/0000000440/0020da37-a63b-45ef-80b0-dc9edd44f1c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8954f5d_33a9_4308_b9d2_6732d416ef5b
GAUP-582681-2016 | UW-391029-2016 | 6/8/2016 9:07:21 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA115 | Vent sizing causing spillage | 5 | 4 | Factory flue assembly not installed correctly that the inner exhaust pipe is too big and not sealed and products of combustion leaking into combustion air and creating condensate. This is a hazard as products of combustion air not leaving outdoors in a safe matter and products of combustion are entering the house. | 5 | Vent sizing causing spillage | 2202-3.png | file://x:/photopub/docs/0000000440/a9256d90-9853-42fb-b250-0204f75e3589.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8954f5d_33a9_4308_b9d2_6732d416ef5b
BPVOP-581346-2016 | 4249978 | 5/18/2016 10:21:20 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water storage tank with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Working Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating pressure exceeds MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000433/e6e2057c-f4b5-40d8-afc6-03e0b7357f9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff9f4b1_b8ae_4e0a_ad0d_01191f37e621
BPVOP-581346-2016 | 4249978 | 5/18/2016 10:21:20 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water storage tank with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Working Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating pressure exceeds MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Valve.png | file://x:/photopub/docs/0000000433/a1fe8aa7-09f8-45cd-9b69-46db26d0013f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5ff9f4b1_b8ae_4e0a_ad0d_01191f37e621
BPVOP-581345-2016 | 4249979 | 5/18/2016 11:03:10 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of hot water storage tank with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Working Temperature (MAWT) of 210*Fahrenheit, it was determined that safety relief valve has exceeded the required 3year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating pressure exceeds MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE.png | file://x:/photopub/docs/0000000433/7d0150e6-ac7a-4af7-8657-030a6623bb61.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f777c86f_1bb1_4483_afe1_9b9129e2bab2
BPVIN-589554-2016 | BPV-344117-2016 | 2/3/2016 4:00:24 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 0 | Slight leakage on gage glass observed and operator notified. | 0 | No Created Hazard Identified | Leaking_Gage_Glass.png | file://x:/photopub/docs/0000000439/190ab6d3-4009-47c5-a2a9-c4b2495a8e75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5358c615_9605_41a1_9412_81e0ca9fe508
ELIN-581291-2016 | EL-390125-2016 | 5/24/2016 9:58:16 AM | ASSESS: EL: Service Connection | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 |  | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | Extra_low-volta__extra_low_voltage_irrigation_control_wiring_installed_without_a_permit.png | file://x:/photopub/docs/0000000433/4644d1c9-4c4c-456a-a824-05b84edf31d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7165aa41_15b0_4a93_9682_4e3602473b13
BPVOP-588765-2016 | 2254449 | 6/4/2016 9:48:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP071 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | EXISTING_SHROUD.png | file://x:/photopub/docs/0000000438/76609bd2-680d-4ee4-b9a0-d93d25dad899.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e089626a_1acf_45ba_b4ca_c7ef50ad60d5
BPVOP-588765-2016 | 2254449 | 6/4/2016 9:48:08 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP071 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Damaged insulation which could allow the ingress of moisture making the pressure retaining component susceptible to corrosion under insulation. | PROPER_SHROUD.png | file://x:/photopub/docs/0000000438/378d1a6f-2061-46a9-916a-27e845184c95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e089626a_1acf_45ba_b4ca_c7ef50ad60d5
ELIN-580683-2016 | EL-349017-2016 | 5/24/2016 10:10:56 AM | ASSESS: EL: Service Connection | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Dry type outlet box is exposed to the weather. This could result in possible shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outlet_boxes_exposed_to_weather.png | file://x:/photopub/docs/0000000433/0b7b0621-f1fc-45bf-b066-9159a819cca7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c3c1b5a5_d405_4eb1_aff1_290f5f2fc4fd
AMOP-583869-2016 | AM-019499-2013 | 5/27/2016 12:01:34 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | Waterslide water inlet ports were found to be sharp presenting a cut hazard for riders. This hazard is reasonably detectable by maintenance and is unlikely to propagate. The waterslide was not yet in operation for the season. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Water_inlets.png | file://x:/photopub/docs/0000000434/209a5252-f08e-4ac1-88c5-3051ce1fe499.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad1b0ff7_5366_4da4_9bb8_a55538f43ff3
ELIN-577845-2016 | EL-387558-2016 | 5/26/2016 3:18:55 PM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a routine Silver Label inspection, the main 100amp 120/240volt switch was found with the identified conductor in the system not grounded. This could lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_switch.png | file://x:/photopub/docs/0000000434/2d192fd9-41d3-4688-9ee9-e39d3c0fb80a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1150a892_31f8_490f_b35c_c0e20424b799
BPVIN-573429-2016 | BPV-159908-2014 | 5/26/2016 3:24:34 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP117 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | 4 | 4 | A Hot Water Boiler was designed for a maximum allowable working pressure of 30 psi. The pressure relief valve installed was set at 45 psi. The boiler could be subjected to a higher working pressure than what it was designed for and has the potential of a major failure. | 4 | 3.0.1 Safeties will not function - Pressure Relief Device set pressure over required to provide over pressure protection | Working_Pressure_30.png | file://x:/photopub/docs/0000000434/f378ef23-9a93-4c8a-903b-dc17174f928d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__079c87e0_434e_4755_a692_b1ac1370b94c
ELIN-582805-2016 | EL-309401-2015 | 6/6/2016 8:51:30 AM | ASSESS: EL: Final | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Non metallic sheathed cable is located below 1.5 meters in garage area. This could become a shock hazard to persons if the wire is damaged. Non metallic sheathed cable is not made to be unprotected from mechanical damage. | 3 | Conductors Equipment is not approved for the specific use. | NMD_located_below_1_5_meters.png | file://x:/photopub/docs/0000000439/1a9604d2-89ae-470c-986d-3b19eb3a91e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba69c3ef_2a8b_4f05_ba61_42e87161ad90
ELIN-581796-2016 | EL-389719-2016 | 5/25/2016 12:08:34 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | A span of greater than 38 m has being installed between a machine shop and the electrical room. The stress from the extra weight of the cable will cause the points of attachment to pull away from the support and possibly causing a short circuit and electrical fire at a later point in time | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Span_of__span_of_triplex_between_electrical_room_and_barn.png | file://x:/photopub/docs/0000000433/122a844c-9280-4044-906a-36ffcd3b1fc7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ee24466b_6669_48cc_ae7f_667d25ae1fc0
ELIN-581002-2016 | EL-385253-2016 | 5/27/2016 10:11:12 AM | ASSESS: EL: Service Connection | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | In a new single family dwelling a 200amp 120/240volt 1phase electrical service was found installed using the wire size to small for the installation. This could lead to a thermal effect. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Wire_size.png | file://x:/photopub/docs/0000000434/fdc1b117-3bac-48fc-97c6-f2e9d1a4e947.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__abe5f74b_5bd8_476a_aacf_7d9e70ba02c8
ELIN-585429-2016 | EL-391738-2016 | 6/1/2016 1:03:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Type R2 Temporary service not built for construction weatherproofing. See bulletin IB-EL-2016-03 | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Back_of_service_distribution_exposed_to_weather.png | file://x:/photopub/docs/0000000436/b6213e19-6446-40da-85de-69442df9a3ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8c8dfa0_df0e_4aa2_a6ec_dec9fb0f764c
BPVIN-553699-2016 | BPV-369383-2016 | 5/25/2016 1:37:00 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP205 | 5.1.0 In service proc/process - Housekeeping of boiler or machinery rooms not compliant personal safety, and general safety etc. | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Housekeeping of boiler or machinery rooms not compliant personal safety, and general safety etc. | Machine_room_.png | file://x:/photopub/docs/0000000434/1a0b99e8-481b-40f4-9859-23fb6ce746bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cac886d5_a886_4f3f_ab1b_b5c1942f1026
ELIN-582583-2016 | EL-279339-2015 | 5/27/2016 12:46:27 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service cable damage may result in shock and fire hazard at the service pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_pole.png | file://x:/photopub/docs/0000000435/ee95d480-2081-464d-9307-98b295846e58.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9040fe1e_3574_49e6_b2f4_e250249ba8e6
ELIN-582583-2016 | EL-279339-2015 | 5/27/2016 12:46:27 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service cable damage may result in shock and fire hazard at the service pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Panel2.png | file://x:/photopub/docs/0000000435/c37f31f2-9a30-4923-8219-ee818cd0bd4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9040fe1e_3574_49e6_b2f4_e250249ba8e6
ELIN-582583-2016 | EL-279339-2015 | 5/27/2016 12:46:27 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service cable damage may result in shock and fire hazard at the service pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Panel1.png | file://x:/photopub/docs/0000000435/384d69ed-9be3-4a81-b4cc-ee609a8e5568.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9040fe1e_3574_49e6_b2f4_e250249ba8e6
ELIN-582583-2016 | EL-279339-2015 | 5/27/2016 12:46:27 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service cable damage may result in shock and fire hazard at the service pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Counter2.png | file://x:/photopub/docs/0000000435/c99003b2-1892-49a7-89b5-667fbf503133.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9040fe1e_3574_49e6_b2f4_e250249ba8e6
ELIN-582583-2016 | EL-279339-2015 | 5/27/2016 12:46:27 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service cable damage may result in shock and fire hazard at the service pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Counter.png | file://x:/photopub/docs/0000000435/03c137ec-c92c-436a-a9f0-22124e3aab44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9040fe1e_3574_49e6_b2f4_e250249ba8e6
ELIN-582583-2016 | EL-279339-2015 | 5/27/2016 12:46:27 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service cable damage may result in shock and fire hazard at the service pole. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Counter_receptacles.png | file://x:/photopub/docs/0000000435/42593622-6680-48ee-ad2d-df25793e3f5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9040fe1e_3574_49e6_b2f4_e250249ba8e6
AMOP-586792-2016 | 2041833 | 6/1/2016 1:41:48 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | Flume support blocking overhead of flume no longer properly secured. This presents a hazard as a piece of blocking could fall into the flume and contact a rider. | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Blocking.png | file://x:/photopub/docs/0000000436/fae369ed-1ce3-46e9-b1f8-8c2464395793.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea838cd9_15e3_4303_a087_f821d8bc15bd
ELHE-584979-2016 | HE-392374-2016 | 5/30/2016 12:30:53 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 5 | In an existing single family dwelling a 15amp 120volt outlet in the garage, is the suspected source of where this garage fire started. This is a shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Location_of_fire.png | file://x:/photopub/docs/0000000435/00808e84-c95b-4b6c-876e-91b213b8b4b4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6566e3d5_283d_4906_84ca_dd6c6e817088
ELIN-576851-2016 | EL-387233-2016 | 5/27/2016 2:09:09 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Service conductors not adequately buried. This is a hazard as the exposed raceway could become damaged and cause a fire or shock. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000434/53b98a2a-0e8c-4b3e-932b-ca08f4cc2e6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61ec7e18_0fe9_42a1_8fc2_25b214d12e4d
ELIN-580046-2016 | UW-356404-2016 | 5/20/2016 11:33:48 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Home owner has installed a wood cover over the exposed branch breaker portion of the main panel. This panel cover is not approved as there are gaps between the cover and the breaker terminals, which are energized. A risk of shock or fire is present to persons and property. Original branch breaker portion cover is lost. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Non_approved_panel_cover_installed_over_branch_breakers.png | file://x:/photopub/docs/0000000433/ed8bc1f9-c2d4-4b86-9ef9-3eb0f45edf76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd49f145_01f6_4711_9422_cd04722d116c
ELIN-580046-2016 | UW-356404-2016 | 5/20/2016 11:33:48 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | Home owner has installed a wood cover over the exposed branch breaker portion of the main panel. This panel cover is not approved as there are gaps between the cover and the breaker terminals, which are energized. A risk of shock or fire is present to persons and property. Original branch breaker portion cover is lost. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Branch_breakers_inaccessible_with_non_approved_cover.png | file://x:/photopub/docs/0000000433/453da025-2228-42af-90f4-5a745b9fa63c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd49f145_01f6_4711_9422_cd04722d116c
ELOP-306689-2015 | EL-203882-2015 | 5/20/2016 3:46:09 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Sub distribution in green houses left energized without covers and protection in place. Energized equipment poses a risk of fire and shock to persons and property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_equipment_left_exposed.png | file://x:/photopub/docs/0000000433/64048542-8b35-40fe-9a76-48ecc637ba33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34d595b9_1237_4516_8118_512e8358273c
ELIN-584832-2016 | EL-370135-2016 | 5/31/2016 1:02:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Parallel service conduits installed in Hydro pull box, bonding jumpers not installed on conduits. Bonding jumpers provide a path for fault currents, thus reducing the amount of current that the service neutral conductor would have to carry back to the service providers over current device. Reducing damage to equipment and property in the case of an electrical fault. | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | Bonding_jumpers_not_in_place_at_service_equipment.png | file://x:/photopub/docs/0000000436/edd3642b-a670-4bd1-82af-223f523b9a3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__30c2799f_b51e_47e7_8749_1ecdc912d870
ELIN-588156-2016 | EL-347473-2016-1 | 6/7/2016 11:22:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The 15 and 20 amp 120/240 volt NMSC branch circuits are in contact with the heating ducts. This is a Thermal hazard. | 3 | Conductors, No expansion joint or not installed correctly. | Heating_source_2.png | file://x:/photopub/docs/0000000439/bd984ca7-8a5e-418d-b703-daac88f225cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63d69ead_7d74_451d_8c81_c6d6126f5180
ELIN-588156-2016 | EL-347473-2016-1 | 6/7/2016 11:22:35 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The 15 and 20 amp 120/240 volt NMSC branch circuits are in contact with the heating ducts. This is a Thermal hazard. | 3 | Conductors, No expansion joint or not installed correctly. | Heating_source_1.png | file://x:/photopub/docs/0000000439/90a2aa7c-fc1b-4b6f-9831-c50f75d42258.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__63d69ead_7d74_451d_8c81_c6d6126f5180
ELIN-571351-2016 | EL-383086-2016 | 5/26/2016 9:22:18 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Enclosure not built to weatherproof temporary construction standard. Rain can easily penetrate equipment causing damage or shock potential. Receptacles not readily accessible with door closed. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Non-weatherproof_enclosure.png | file://x:/photopub/docs/0000000434/5b254c48-8178-41be-b142-dd9f47e61ef7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1fe7bd20_bd9a_4b98_bb92_f738289ae3cc
ELIN-577592-2016 | EL-322809-2015 | 5/27/2016 11:06:33 AM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Use of plumbing adapter not approved for electrical use. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Plumbing_adapter_used_for_electrical_service.png | file://x:/photopub/docs/0000000434/edf5ecce-74e6-495a-8adb-791eea53ee01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a3ec03d_0346_45a1_83c2_55c5d1b732c7
BPVOP-584022-2016 | 4398890 | 5/27/2016 11:24:39 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 125 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data_.png | file://x:/photopub/docs/0000000434/6b53788c-c400-4f70-852c-5c014a09ba83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdc546a1_c943_40be_b9b1_3de65708e061
BPVOP-584022-2016 | 4398890 | 5/27/2016 11:24:39 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 125 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_.png | file://x:/photopub/docs/0000000434/8c1ae68c-7a4d-4327-b26b-eb4993e47604.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdc546a1_c943_40be_b9b1_3de65708e061
ELIN-580618-2016 | EL-298975-2015 | 5/24/2016 12:31:16 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | And exposed cable is energized and not terminated. this is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed__energized_cable.png | file://x:/photopub/docs/0000000433/ed99664d-7027-46ed-9990-b6f6fc5a908c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b25c7c3_52ac_4fbf_99dc_f890e90d83ae
ELIN-586701-2016 | EL-350607-2016 | 6/3/2016 11:15:26 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Open breaker space. | 0 | No Created Hazard Identified | Space-1.png | file://x:/photopub/docs/0000000438/0665c512-3cda-4108-9904-1fdbfb63772d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46af0f01_019a_485c_93ae_854e942fb558
AMOP-586790-2016 | 2050549 | 6/1/2016 2:06:25 PM | ASSESS: AM OP: Periodic | png | #asFound | AM014 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Damaged flume entrance railing and guard board. Waterslide maintenance still underway at the time of the inspection. | 2 | Wear or defects that are: Reasonably detectable by maintenance program Likely to propagate | Railing_.png | file://x:/photopub/docs/0000000436/19cbcba9-8074-4c54-b95f-840a936bf2de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6b46150_ee3f_4533_a409_22e15b54a796
EDOP-586061-2016 | 2055115 | 5/31/2016 3:46:53 PM | ASSESS: ED OP: Regular/Periodic | png | #asFound | ED014 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 3 | 3 | The pits of elevators are to remain dry at all times. This pit has had water in it for many years. This water is causing the pit equipment to corrode which will result in a failure if not corrected | 3 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | Pit_9286.png | file://x:/photopub/docs/0000000436/bb539df5-6461-418e-bf15-819614ee951f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea0e03e8_6a23_4b0a_9d32_955aa7ad45d5
ELIN-582270-2016 | EL-349126-2016 | 5/30/2016 2:22:25 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The 100 amp 240 volt service does not include the required bonding to the copper (sprinkler) waterline, this is a shock hazard | 3 | Equipment Gas line, cast or water pipe has not been bonded | Water.png | file://x:/photopub/docs/0000000435/88529fda-432d-414d-9385-048e277de6db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__450a2c5a_a18f_47c6_800d_955ea55f40cf
ELIN-582976-2016 | EL-349118-2016 | 5/30/2016 12:56:37 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | The 200 amp 120/240 volt service to residence does not include bonding of the copper waterlines and communications system to the service equipment. This is a shock hazard | 3 | Equipment Gas line, cast or water pipe has not been bonded | Waterline.png | file://x:/photopub/docs/0000000435/e0aab82a-0e09-4e03-8a4d-91a9ec5227aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__16a10e87_c2da_4038_938a_e63040f5b875
ELIN-587015-2016 | EL-394139-2016 | 6/2/2016 2:29:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The 15 amp 120 volt NMSC feeder to shed is exposed to mechanical damage and this is both a shock NMD thermal hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | No_mechanical_protection.png | file://x:/photopub/docs/0000000437/6f397ae9-ae77-4e3c-aac1-cf003652d9a3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0129f1cc_e589_42fe_b84a_14040d4ad2d9
ELIN-582076-2016 | EL-353179-2016 | 5/27/2016 12:09:45 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | This assessment found cables running across the joists in the attic without the required protection. There is a fire hazard should the cables become damaged from somebody walking on them while in the attic. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_attic.png | file://x:/photopub/docs/0000000434/d1bc293e-af42-467e-9e7b-7e4bfecc0a03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e99c5ab_bb61_4f18_92fd_cb5135b48716
ELIN-587699-2016 | EL-352801-2016 | 6/6/2016 1:59:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Distribution panels are typeR2 and not weatherproofed for temporary construction. Possibility for equipment damage due to rain | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Not_weatherproofed_2.png | file://x:/photopub/docs/0000000439/547702d4-e5b1-42f5-8867-4f91563fa606.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f7c09f7_898f_4b24_ac91_d2ea71f70872
ELIN-587699-2016 | EL-352801-2016 | 6/6/2016 1:59:48 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Distribution panels are typeR2 and not weatherproofed for temporary construction. Possibility for equipment damage due to rain | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Not_weatherproofed.png | file://x:/photopub/docs/0000000439/9ae841f9-a9d2-47c4-842a-4242a3886bce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f7c09f7_898f_4b24_ac91_d2ea71f70872
ELIN-588495-2016 | EL-394727-2016 | 6/6/2016 12:45:40 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Energized receptacles did not have cover plates installed. This exposes occupants to a potential shock hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 962Surfside_.png | file://x:/photopub/docs/0000000439/8d0f1cdf-1dc7-41a4-b63b-b592718ca99d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af0db007_f6f5_4af0_885f_496bebdefee7
GAIN-536731-2016 | GA-301386-2015 | 6/8/2016 11:34:04 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The gas regulator is not protected from contamination from the black piping. The regulator vent limiter will not operate in the horizontal position. This could cause the regulator to fail and over pressure the appliance causing an over fired condition. | 2 | Not installed according to certified installation instructions | Regulator_not_installed_properly.png | file://x:/photopub/docs/0000000440/56c4f192-b514-4285-b5a4-85aec4c1c6e8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f219f4_0817_4e62_89bd_9c05a4cc7517
GAIN-536731-2016 | GA-301386-2015 | 6/8/2016 11:34:04 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | The gas regulator is not protected from contamination from the black piping. The regulator vent limiter will not operate in the horizontal position. This could cause the regulator to fail and over pressure the appliance causing an over fired condition. | 2 | Not installed according to certified installation instructions | Gas_piping_not_properly_labled.png | file://x:/photopub/docs/0000000440/be37059c-2175-4315-a040-6c80528879eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__56f219f4_0817_4e62_89bd_9c05a4cc7517
GAIN-575964-2016 | GA-386704-2016 | 6/8/2016 7:16:28 PM | ASSESS: GA: Final | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 |  | 2 | Container not set upon compliant base | Inadequate_hose_used.png | file://x:/photopub/docs/0000000440/7d282e8a-ee2d-44b7-8bf2-5bf4aa89c7b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7df48c4_757d_4159_8f84_f446893dc055
GAIN-575964-2016 | GA-386704-2016 | 6/8/2016 7:16:28 PM | ASSESS: GA: Final | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 |  | 2 | Container not set upon compliant base | Tank_on_wood_planks.png | file://x:/photopub/docs/0000000440/934e6d4b-0e53-4e8d-83b0-3d26392791ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7df48c4_757d_4159_8f84_f446893dc055
GAIN-519821-2016 | GA-278085-2015 | 6/8/2016 5:17:19 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Boiler_gas_valve_missing.png | file://x:/photopub/docs/0000000440/d629e645-086b-4d20-81bd-b3f107af0bef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46475c8c_1203_4cfa_9e80_0a02ae2a4d12
GAIN-575964-2016 | GA-386704-2016 | 6/8/2016 7:16:28 PM | ASSESS: GA: Final | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 |  | 2 | Container not set upon compliant base | Regulator_not_mounted.png | file://x:/photopub/docs/0000000440/26bfd8c6-eda5-4fb5-bca4-f6a007e6b11c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7df48c4_757d_4159_8f84_f446893dc055
GAIN-519821-2016 | GA-278085-2015 | 6/8/2016 5:17:19 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Pipe_sleeves_missing.png | file://x:/photopub/docs/0000000440/784c814e-9902-4f0b-b741-dc92df4d2735.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46475c8c_1203_4cfa_9e80_0a02ae2a4d12
GAIN-519821-2016 | GA-278085-2015 | 6/8/2016 5:17:19 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Low_water_cut_off_missing.png | file://x:/photopub/docs/0000000440/7b671534-52a6-410c-b756-939e002afb57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46475c8c_1203_4cfa_9e80_0a02ae2a4d12
GAIN-519821-2016 | GA-278085-2015 | 6/8/2016 5:17:19 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Dirt_pocket_missing_bushing_used.png | file://x:/photopub/docs/0000000440/7f28c75a-2308-49ae-81c9-343db4c16db3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46475c8c_1203_4cfa_9e80_0a02ae2a4d12
GAIN-575964-2016 | GA-386704-2016 | 6/8/2016 7:16:28 PM | ASSESS: GA: Final | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 |  | 2 | Container not set upon compliant base | Gas_pipe_not_bonded.png | file://x:/photopub/docs/0000000440/6b1b8e02-c7b1-43ca-8f21-eb6ec342e3ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7df48c4_757d_4159_8f84_f446893dc055
GAIN-575964-2016 | GA-386704-2016 | 6/8/2016 7:16:28 PM | ASSESS: GA: Final | png | #asFound | GA006 | Container not set upon compliant base | 2 | 2 |  | 2 | Container not set upon compliant base | Pipe_not_protected.png | file://x:/photopub/docs/0000000440/10a15b96-de2b-46df-aaea-92d48dd0e66d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7df48c4_757d_4159_8f84_f446893dc055
GAIN-571149-2016 | GA-382125-2016 | 6/8/2016 3:21:13 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Wrong_connector_on_deep_fryer_No_restraint_on_deep_fryer.png | file://x:/photopub/docs/0000000440/d41821e2-9287-4200-98e4-0e95eb62e650.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94c12d13_7b0e_436b_a32b_f7e625d059e9
GAIN-519821-2016 | GA-278085-2015 | 6/8/2016 5:17:19 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Meters_not_identified.png | file://x:/photopub/docs/0000000440/981ff30f-b7c5-4e72-bf92-cf2f75d80fb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46475c8c_1203_4cfa_9e80_0a02ae2a4d12
GAIN-519821-2016 | GA-278085-2015 | 6/8/2016 5:17:19 PM | ASSESS: GA: Commissioning Approval | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 |  | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Regulator_vents_not_painted_missing_screen.png | file://x:/photopub/docs/0000000440/53751e12-4daf-4920-bcb3-ee6b4f74cd11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46475c8c_1203_4cfa_9e80_0a02ae2a4d12
GAIN-571149-2016 | GA-382125-2016 | 6/8/2016 3:21:13 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Cylinder_must_be_secured_with_metal_system.png | file://x:/photopub/docs/0000000440/05514fb5-6e4e-4e27-80fc-885a746ca1a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94c12d13_7b0e_436b_a32b_f7e625d059e9
ELIN-587757-2016 | EL-353876-2016 | 6/9/2016 8:10:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unapproved meter jumpers, unapproved meter base cover, openings in service equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Service_equipment_enclosure.png | file://x:/photopub/docs/0000000440/bc391aa5-d06e-4c50-af7e-e78953319ddf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d226510_cd35_4df5_a0d6_388a65230d32
ELIN-587757-2016 | EL-353876-2016 | 6/9/2016 8:10:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unapproved meter jumpers, unapproved meter base cover, openings in service equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Spare_meter_base.png | file://x:/photopub/docs/0000000440/dc28d519-1ffe-465d-bd10-08c607093b19.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d226510_cd35_4df5_a0d6_388a65230d32
ELIN-587757-2016 | EL-353876-2016 | 6/9/2016 8:10:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unapproved meter jumpers, unapproved meter base cover, openings in service equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Breakers.png | file://x:/photopub/docs/0000000440/84083dce-7c5e-4be5-8eed-dde21685fffd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d226510_cd35_4df5_a0d6_388a65230d32
ELIN-587757-2016 | EL-353876-2016 | 6/9/2016 8:10:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unapproved meter jumpers, unapproved meter base cover, openings in service equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Meter_cover.png | file://x:/photopub/docs/0000000440/0f5ebbd9-803e-4e82-9c64-7d379b660026.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d226510_cd35_4df5_a0d6_388a65230d32
ELIN-587757-2016 | EL-353876-2016 | 6/9/2016 8:10:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Unapproved meter jumpers, unapproved meter base cover, openings in service equipment. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Panel.png | file://x:/photopub/docs/0000000440/ed358e2d-ad53-4a1f-96a2-020711e31360.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d226510_cd35_4df5_a0d6_388a65230d32
ELIN-591009-2016 | EL-208856-2015 | 6/9/2016 11:11:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | The exterior jackets on the parallel cable runs have been damaged due to poor installation. The damage cable jacket means the cable does not have a flame temperature spread rating and the original CSA certification has been voided because of the cable damage. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Photo_to__Photo_too_damaged_exterior_insulation_on_cables.png | file://x:/photopub/docs/0000000440/2e7d15c6-53ca-4c5f-a4c6-546e3edc0eed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21d1c571_c3ad_451b_9a22_93e73f25a80e
ELIN-591009-2016 | EL-208856-2015 | 6/9/2016 11:11:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | The exterior jackets on the parallel cable runs have been damaged due to poor installation. The damage cable jacket means the cable does not have a flame temperature spread rating and the original CSA certification has been voided because of the cable damage. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Photo_one__Photo_one_view_of_damaged_exterior_insulation_on_cables.png | file://x:/photopub/docs/0000000440/1e968dff-1227-4fcb-8d40-7b0f9cabfc46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21d1c571_c3ad_451b_9a22_93e73f25a80e
ELIN-591009-2016 | EL-208856-2015 | 6/9/2016 11:11:34 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | The exterior jackets on the parallel cable runs have been damaged due to poor installation. The damage cable jacket means the cable does not have a flame temperature spread rating and the original CSA certification has been voided because of the cable damage. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | Photo_three__Photo_three_damaged_insulation_on_cable.png | file://x:/photopub/docs/0000000440/d773155f-505e-44b3-b88b-7ffe2f10ad45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__21d1c571_c3ad_451b_9a22_93e73f25a80e
BPVOP-591370-2016 | 2252864 | 6/9/2016 9:46:45 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 3 | An emergency shutdown switch shall be installed at an accessible location so the boiler can be safely shutdown in the event of an emergency. I found that there was no remote shutdown switch provided for a 150 psi high pressure steam boiler. Potential exists for an incident due to missing remote emergency control | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | Existing_disconnect_switch_.png | file://x:/photopub/docs/0000000440/15007376-eaa4-444f-9c67-579cc2a07bf3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90b18b90_2207_48d1_8cc8_5a0086c51566
BPVOP-591379-2016 | 2298355 | 6/9/2016 11:41:09 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP042 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | 1 | 1 |  | 1 | 1.2.0 Corrosion/PSI Retention - Inactive local or general corrosion or erosion that has caused thinning of a pressure retaining component but has not reduced the corrosion allowance or the thickness below minimum design thickness | Blowoff_tank.png | file://x:/photopub/docs/0000000440/3af6871b-e731-4dff-9c83-93fcbd6942ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__522664bc_2860_4eff_949f_d674b625f7f3
ELIN-582298-2016 | EL-384167-2016 | 6/8/2016 10:46:07 AM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | In a single wide mobile home, a 30amp 120/240volt outlet was found energized and mounted to the wood paneling of the laundry room with no junction box in place. This could lead to a thermal effect. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Dryer_recep_without_a_box.png | file://x:/photopub/docs/0000000440/24a0914d-7e5e-489e-aa47-a5dc28df6000.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40edf359_2c5e_4711_b094_e6c4335ffa22
ELIN-586196-2016 | EL-393133-2016 | 6/2/2016 10:23:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL096 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | 3 | 3 | Service equipment not bonded | 3 | Effective bonding and grounding Bonding jumper or panel screw at service equipment, distribution centre or load centre has; not been installed or has been removed; or remains installed and is providing multiple paths to the system's grounded point. | His_electric.png | file://x:/photopub/docs/0000000439/08e62016-5e7f-4e5b-bec6-ff841982ecbd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1dfe0375_e734_408a_bc90_981d8b251b77
ELIN-586195-2016 | EL-393133-2016 | 6/2/2016 11:04:30 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL131 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | 3 | 2 | Dryer box not securely fastened,may move while plugging or unplugging dryer | 3 | Installation of electrical equipment General: boxes or cabinets are not secured properly. | His_Electric_2.png | file://x:/photopub/docs/0000000439/ce64b84b-20c1-4971-9c31-79d5c47ef8bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd4ec795_fa53_40b3_8d3f_68e27ef26d0e
ELIN-580959-2016 | EL-389850-2016 | 6/3/2016 9:42:45 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Service mast to short and clearance for conductors is reduced | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Gitanyow.png | file://x:/photopub/docs/0000000439/456709c6-d5f8-49a6-9d80-9aff1c0e19d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__28c96a69_d4e3_4dd7_9c2f_28851c016276
BPVIN-582478-2016 | UW-390859-2016 | 5/25/2016 1:00:22 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Every pressure retaining component of a regulated equipment or pressure piping must be provided with a suitable pressure relief device in order to protect from over pressurization and possible rupture. I Found that the pressure relief valve was leaking at the discharge Of a liquid oxygen vessel. Potential exists for an incident due to a faulty overpressure protection device. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Pressur_relief_device_.png | file://x:/photopub/docs/0000000435/c9d57922-2280-419a-9de6-9c2d6c7654c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d0b0afad_33ec_4a38_97dd_9aba0896cb14
ELIN-589813-2016 | EL-345962-2016 | 6/10/2016 10:50:42 AM | ASSESS: EL: Final | png | #asFound | EL068 | Protection and control Loading of distribution equipment exceeded | 3 | 3 | 100A 240V 3PH Panel is being fed from a 200A 240V Switch fused at 150A, this could result in equipment damage and a shock hazard. | 3 | Protection and control Loading of distribution equipment exceeded | Panel_C.png | file://x:/photopub/docs/0000000441/79eb0fcd-b415-4ee5-8fdb-653e1e59c6fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41eb14f5_fda6_443e_8e3b_23d2f0c8d6eb
ELIN-587645-2016 | EL-382068-2016 | 6/8/2016 2:29:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL250 | Category 1 Equipment is not approved for the specific use or location. | 3 | 2 | This assessment found indoor receptacle equipment to be installed outdoors. When this equipment becomes wet there is a shock hazard. | 3 | Category 1 Equipment is not approved for the specific use or location. | Outlet_boxes.png | file://x:/photopub/docs/0000000440/75310846-5945-46f8-8262-db619867d613.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebf7b10a_1f61_4e28_a429_3fc53d008572
ELIN-591203-2016 | EL-390696-2016 | 6/9/2016 9:41:20 AM | ASSESS: EL: Service Connection | png | #asFound | EL155 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | 3 | 2 | Low energy communication cable encased in concrete. Communication cable not rated to be encased in concrete. This could cause equipment damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use or location. Examples may be enviromental, mounting means, ventilation, etc. | Communication_cable_encased_in_concrete.png | file://x:/photopub/docs/0000000441/530a1654-dc4e-4d6b-a94e-2af2f90f27c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d5bef1b_6951_482f_a29a_576c7c1ea7f1
ELIN-569448-2016 | EL-327354-2015 | 6/2/2016 4:59:23 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles installed in exterior locations on residential properties are required to be ground fault circuit interrupter protected (GFCI) when installed within 2.5M of grade. This is required to protect persons from electrical shocks when using portable appliances and electrical equipment outdoors. This installation has a 15A, 120V exterior receptacle that is located on a residential property. The receptacle is not GFCI protected and is within 2.5M of grade. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 15A__120V_receptacle_installed_in_an_exterior_location_without_GFCI_protection.png | file://x:/photopub/docs/0000000437/3c00a8b9-d03b-4d2d-9300-ea83d63b6069.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__181431c3_7d8f_4d45_9fc3_4650e9f38e4b
ELIN-569448-2016 | EL-327354-2015 | 6/2/2016 4:59:23 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles installed in exterior locations on residential properties are required to be ground fault circuit interrupter protected (GFCI) when installed within 2.5M of grade. This is required to protect persons from electrical shocks when using portable appliances and electrical equipment outdoors. This installation has a 15A, 120V exterior receptacle that is located on a residential property. The receptacle is not GFCI protected and is within 2.5M of grade. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | front_of_new_house.png | file://x:/photopub/docs/0000000437/50e0dc31-f62a-4f76-8c5a-62b632939e42.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__181431c3_7d8f_4d45_9fc3_4650e9f38e4b
ELIN-583443-2016 | EL-390867-2016 | 6/2/2016 12:41:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL019 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | 3 | 3 | The 200 amp 120/240 volt main distribution panel has an opening not filled, this can lead to a thermal hazard due to missing metal barrier protection from combustible materials | 3 | Damage to equipment may result in overheating. Unused openings in enclosures have not been closed Location of equipment does not allow for proper access to disconnecting means | Missing_ko_filler.png | file://x:/photopub/docs/0000000437/f981cf2d-d26a-4310-9d87-ef1553c0bc5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54744307_fe88_46e6_aae1_22cfc485b5eb
BPVIN-590126-2016 | BPV-395945-2016 | 6/7/2016 2:40:47 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP142 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | 3 | 3 | Upon assessment of potable hot water storage tank (Length-1.8m, Diameter-0.70m) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Working Temperature (MAWT) of 210*Fahrenheit, it is determined that there is no thermometer at or near the outlet of storage tank. There is no way to detect and take subsequent corrective action in the event of water temperature above operating range or even MAWT, caused by mal-function of controls , which may lead to incident. | 3 | 4.0.1 Incorrect readings/alarms - Code or manufacturer required instrumentation or alarms not provided | DHW_STORAGE_TANK_2_WITHOUT_THERMOMETER_AT_OUTLER.png | file://x:/photopub/docs/0000000441/06349815-97fd-4544-82ce-eddb41e14ea8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82703b5e_0f7d_48a4_875a_1dc9453bc6ed
BPVIN-590147-2016 | BPV-395965-2016 | 6/7/2016 8:33:56 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP116 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | 4 | 3 | Upon assessment of heat exchanger (1m long and 0.3m wide) with Maximum Allowable Working Pressure (MAWP) of 150psig and Maximum Allowable Water Temperature (MAWT) of 220*Fahrenheit, is determined that there is no pressure relief device installed on the side receiving heat. Inadvertent operation of heat exchanger with secondary side (side receiving heat) valves shut may subject vessel pressure above MAWP. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.0.1 Safeties will not function - Pressure Relief Device not provided or non functioning | Heat_exchanger_without_pressure_relief_valve.png | file://x:/photopub/docs/0000000441/59f76895-0c14-494b-b664-247d1c52d8b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9107da1_47c6_45af_aaab_d6a3ce7ba132
ELIN-586855-2016 | EL-393887-2016 | 6/9/2016 9:23:43 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 4 | Incomplete circuits energized by using an extension cord are potential fire and shock hazards | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Poor_cable_work.png | file://x:/photopub/docs/0000000441/f6cfae51-4d9c-4ce4-934f-d93cf4f4488c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__db4235c9_a9ab_4aa2_ad82_b533b42fffd2
ELIN-585198-2016 | EL-391716-2016 | 6/10/2016 2:42:37 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles and switches are required to have cover plates in place to prevent persons and objects from contacting exposed energized terminals and to contain thermal energy in the event of an electrical fault or failure on the device or wiring inside the outlet box. This is required to prevent electric shock and fire hazards. This installation has several switches and receptacles that do not have the required covers in place. Left uncorrected this is a potential shock and fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_missing_from_receptacle.png | file://x:/photopub/docs/0000000442/299e69c1-3dca-4470-840d-09c77cb3fe68.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10124802_7053_47b0_a9cf_5622015e08e7
ELIN-585378-2016 | EL-388526-2016 | 6/3/2016 11:23:07 AM | ASSESS: EL: Final | png | #asFound | EL154 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | 2 | 2 |  | 2 | Installation of electrical equipment Equipment is approved, and installation instructions have not been satisfied. Examples may be enviromental, mounting means, ventilation, etc. | AC_switch.png | file://x:/photopub/docs/0000000438/672bf2a8-8380-4039-b6f5-c01ace94505a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f1d4636a_6308_492c_9e24_32d8aca80b84
GAIN-487915-2015 | GA-318029-2015 | 6/2/2016 11:16:47 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 2 | The radiant heater during extended operation could cause the combustible materials to get to the point of combustion if the metal roofing material were not to act as a heat shield. | 3 | Clearance to combustible not met | Meters_not_identified.png | file://x:/photopub/docs/0000000438/f5436084-c5db-45c5-804f-126153d6b53b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5089725d_8e0f_4e33_9532_65889dd3975f
GAIN-487915-2015 | GA-318029-2015 | 6/2/2016 11:16:47 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 2 | The radiant heater during extended operation could cause the combustible materials to get to the point of combustion if the metal roofing material were not to act as a heat shield. | 3 | Clearance to combustible not met | Pipe_hung_from_pipe.png | file://x:/photopub/docs/0000000438/3a01af34-c7b0-412d-ab10-9f0b12efa406.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5089725d_8e0f_4e33_9532_65889dd3975f
GAIN-487915-2015 | GA-318029-2015 | 6/2/2016 11:16:47 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 2 | The radiant heater during extended operation could cause the combustible materials to get to the point of combustion if the metal roofing material were not to act as a heat shield. | 3 | Clearance to combustible not met | Appliance_with_out_accessible_isolation_valve.png | file://x:/photopub/docs/0000000438/b1f11e61-17e2-435a-b895-e046b3f44692.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5089725d_8e0f_4e33_9532_65889dd3975f
GAIN-487915-2015 | GA-318029-2015 | 6/2/2016 11:16:47 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 2 | The radiant heater during extended operation could cause the combustible materials to get to the point of combustion if the metal roofing material were not to act as a heat shield. | 3 | Clearance to combustible not met | Regulator_not_installed_correct.png | file://x:/photopub/docs/0000000438/78ec016b-ab54-4233-9c77-df05cb115cae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5089725d_8e0f_4e33_9532_65889dd3975f
GAIN-487915-2015 | GA-318029-2015 | 6/2/2016 11:16:47 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 2 | The radiant heater during extended operation could cause the combustible materials to get to the point of combustion if the metal roofing material were not to act as a heat shield. | 3 | Clearance to combustible not met | Pipe_not_painted.png | file://x:/photopub/docs/0000000438/afa75866-2ea1-40dd-a84f-8fdd6b1519ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5089725d_8e0f_4e33_9532_65889dd3975f
GAIN-487915-2015 | GA-318029-2015 | 6/2/2016 11:16:47 AM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 2 | The radiant heater during extended operation could cause the combustible materials to get to the point of combustion if the metal roofing material were not to act as a heat shield. | 3 | Clearance to combustible not met | Heater_installed_without_required_clearances.png | file://x:/photopub/docs/0000000438/60c2bab7-b55a-4df8-a9cd-c8862798c3a4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5089725d_8e0f_4e33_9532_65889dd3975f
ELIN-576253-2016 | EL-386859-2016 | 6/3/2016 8:26:22 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Energized sub-distribution equipment, accessible to general public is exposed to the effects of weather because of roof membrane of structure is not intact. This presents a serious risk of personal injury (shock) and property damage (thermal event) due to water contacting energized systems. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | View01_sub_distribution.png | file://x:/photopub/docs/0000000438/51ac5327-3697-4f9a-bedf-3f19769607f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a69762d_eae0_40d6_85e2_ff4f0d546f8c
ELHE-590936-2016 | HE-396423-2016 | 6/8/2016 1:54:06 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 60 amp power pedestals in city park, energized and damaged, accessible to general public | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Pedestals_hit_by_vehicles__energized.png | file://x:/photopub/docs/0000000440/5b7a54e0-2b3c-4103-9989-0c1c835b9ac4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec75037d_f93a_474e_879a_1b1819ee13fb
ELHE-590936-2016 | HE-396423-2016 | 6/8/2016 1:54:06 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 60 amp power pedestals in city park, energized and damaged, accessible to general public | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Loose_access_cover_on_pedestal__energized_terminals_exposed.png | file://x:/photopub/docs/0000000440/61b216db-1f09-4f9d-8a4e-cab6068c0534.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec75037d_f93a_474e_879a_1b1819ee13fb
ELHE-590936-2016 | HE-396423-2016 | 6/8/2016 1:54:06 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 60 amp power pedestals in city park, energized and damaged, accessible to general public | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Pedestals_loose_on_base_impact_damage.png | file://x:/photopub/docs/0000000440/892daae4-52b2-4fe5-960e-1bf40b3a4917.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec75037d_f93a_474e_879a_1b1819ee13fb
ELHE-590936-2016 | HE-396423-2016 | 6/8/2016 1:54:06 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | 60 amp power pedestals in city park, energized and damaged, accessible to general public | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Missing_KO_filler.png | file://x:/photopub/docs/0000000440/88e54000-6db2-43a5-8216-07ad55440874.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec75037d_f93a_474e_879a_1b1819ee13fb
ELIN-581610-2016 | EL-303059-2015 | 6/8/2016 1:35:43 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The island receptacle is mounted close to the kitchen sink. This could become a shock hazard to someone working around the sink if an appliance faulted when plugged into this receptacle. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | kitchen_plug.png | file://x:/photopub/docs/0000000440/704393c2-307c-4a4a-a194-bbcc6bd11899.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d4f4c7e_02c3_4021_80f2_c930156b4d4b
GAIN-550630-2016 | GA-368557-2016 | 6/3/2016 11:10:27 AM | ASSESS: GA: Final | png | #asFound | GA047 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | 2 | 2 |  | 2 | Damage to natural gas or propane distribution systems due to unsafe work practices no release of gas | Kinked_copper.png | file://x:/photopub/docs/0000000439/4c0c5452-9785-4e4d-859e-5241de5ff98f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e787ddd0_c52a_4fec_9412_800a23e86379
ELIN-586544-2016 | EL-387064-2016 | 6/2/2016 11:36:01 AM | ASSESS: EL: Final | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | A new commercial 200 amp 240 volt service feeder cable is installed and is settled out f connector. Inadequate provision for settling of cable below grade can result in property damage or injury to persons | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | ACWU_feeder_pulled_from_connector.png | file://x:/photopub/docs/0000000438/58fe25ae-36a3-48ef-97f5-302b5463b720.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__952ddfde_546f_4c09_acde_cdbe700f76ff
ELIN-581610-2016 | EL-303059-2015 | 6/8/2016 1:35:43 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The island receptacle is mounted close to the kitchen sink. This could become a shock hazard to someone working around the sink if an appliance faulted when plugged into this receptacle. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Island_plug.png | file://x:/photopub/docs/0000000440/d28dfb92-5165-40ca-a8c4-fcac020f60a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0d4f4c7e_02c3_4021_80f2_c930156b4d4b
ELIN-585198-2016 | EL-391716-2016 | 6/10/2016 2:42:37 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles and switches are required to have cover plates in place to prevent persons and objects from contacting exposed energized terminals and to contain thermal energy in the event of an electrical fault or failure on the device or wiring inside the outlet box. This is required to prevent electric shock and fire hazards. This installation has several switches and receptacles that do not have the required covers in place. Left uncorrected this is a potential shock and fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_broken_and_missing_from_receptacle.png | file://x:/photopub/docs/0000000442/a34571e4-ffaa-4136-9de9-8a3239b23bfc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10124802_7053_47b0_a9cf_5622015e08e7
ELIN-585198-2016 | EL-391716-2016 | 6/10/2016 2:42:37 PM | ASSESS: EL: Final | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Receptacles and switches are required to have cover plates in place to prevent persons and objects from contacting exposed energized terminals and to contain thermal energy in the event of an electrical fault or failure on the device or wiring inside the outlet box. This is required to prevent electric shock and fire hazards. This installation has several switches and receptacles that do not have the required covers in place. Left uncorrected this is a potential shock and fire hazard. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Cover_plate_missing_from_two_gang_switch_box.png | file://x:/photopub/docs/0000000442/957c402e-45a0-4216-834b-9bc5981dae3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__10124802_7053_47b0_a9cf_5622015e08e7
ELIN-484697-2015 | EL-275308-2015 | 6/9/2016 9:38:15 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Baseboard heater was not installed, residence was unoccupied as it is a seasonal retreat. If residence had been attended and conductor energized this might create a shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Existing_heater_removed_for_floor_installation.png | file://x:/photopub/docs/0000000441/2d31d207-f412-4e61-bb57-f5698fca21bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd5efca_1952_4a7c_a593_0dddb0a53837
ELIN-582752-2016 | EL-353752-2016 | 6/9/2016 2:50:19 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Main distribution and sub distribution are both bonded, the hazard could result from a more desired current flow through another path creating a difference in potential between equipment . The hazard of shock & thermal conditions would be present. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Sub_panel_bonded.png | file://x:/photopub/docs/0000000441/353efc67-a06d-4478-a5b2-f66acd40f801.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e9ae4e4_0816_40bf_9d6d_f672fa2f0a5d
ELIN-585995-2016 | EL-380526-2016 | 6/2/2016 1:10:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | A new 400 amp 240 volt one phase service has been installed. No main system ground was installed . Persons or property can be damaged should a fault occur in the electrical system and no main ground is present | 3 | Installation Grounding; Electrode or grounding conductor are not present. | No_main_ground_installed_authorized_for_connection.png | file://x:/photopub/docs/0000000438/111dcb8f-0d5a-49b1-9efc-18c187921146.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__71b73193_c88e_4a1c_ad68_9ec6a2bb3892
GAIN-584103-2016 | GA-371310-2016 | 6/3/2016 3:39:48 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Furnace.png | file://x:/photopub/docs/0000000438/c9a48c64-8de1-4aaf-9adf-a135bebdfbd4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__104962f7_6e54_47ee_b640_3991a214c710
ELIN-588308-2016 | EL-341050-2016 | 6/7/2016 6:18:12 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Energized consumer service cabling exceeds 1.5m of unprotected length inside structure. This poses a risk of personal injury (shock) or property damage (thermal event) due to possibility of mechanical damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | View01_suite_panel_.png | file://x:/photopub/docs/0000000439/f5a8dd18-662d-4130-8789-64e803062d4f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bdf9178a_ca41_4bd0_8b23_9b5be9ce0618
ELOP-446309-2015 | 17 | 6/7/2016 8:32:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The ground conductor on a transformer sub feed has been severed and could become a shock hazard to people if a lighting circuit should fault. | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Ground_conductor.png | file://x:/photopub/docs/0000000439/6ff89686-882a-4677-a2cb-1b519d9b0d8c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e3df035_6c24_46ae_993e_de824a6366a7
BPVIN-592513-2016 | UW-397491-2016 | 6/10/2016 5:16:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP037 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | 2 | 2 | This low pressure fluid (glycol) boiler has safety relief valves set at 50 psi. This expansion tank is not constructed to the ASME Section VIII Div.1 code of construction. CSA-B51 indicates that expansion tanks operating above 30 psi shall conform to the ASME Code. | 2 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | Expansion_tank_label_photo1.png | file://x:/photopub/docs/0000000441/87d636b4-758c-4768-af17-ce83c6d6b719.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e48478a_d9a0_4d12_83bd_511ab3dfd193
BPVIN-592513-2016 | UW-397491-2016 | 6/10/2016 5:16:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP037 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | 2 | 2 | This low pressure fluid (glycol) boiler has safety relief valves set at 50 psi. This expansion tank is not constructed to the ASME Section VIII Div.1 code of construction. CSA-B51 indicates that expansion tanks operating above 30 psi shall conform to the ASME Code. | 2 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | Safety_valve_set_pressure.png | file://x:/photopub/docs/0000000441/7d132764-d8be-4382-9f7a-974a9b0ad9b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e48478a_d9a0_4d12_83bd_511ab3dfd193
BPVIN-592513-2016 | UW-397491-2016 | 6/10/2016 5:16:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP037 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | 2 | 2 | This low pressure fluid (glycol) boiler has safety relief valves set at 50 psi. This expansion tank is not constructed to the ASME Section VIII Div.1 code of construction. CSA-B51 indicates that expansion tanks operating above 30 psi shall conform to the ASME Code. | 2 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | Expansion_tank_overview.png | file://x:/photopub/docs/0000000441/4625555e-f008-4414-8f66-27272e51676b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e48478a_d9a0_4d12_83bd_511ab3dfd193
BPVIN-592513-2016 | UW-397491-2016 | 6/10/2016 5:16:19 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP037 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | 2 | 2 | This low pressure fluid (glycol) boiler has safety relief valves set at 50 psi. This expansion tank is not constructed to the ASME Section VIII Div.1 code of construction. CSA-B51 indicates that expansion tanks operating above 30 psi shall conform to the ASME Code. | 2 | 1.1.0 Material use/application - Identified material which conforms to a non-ASME (American Society of Mechanical Engineers) standard | Expansion_tank_label_photo2.png | file://x:/photopub/docs/0000000441/ec17dcab-9db9-4a82-b0fc-332c39b3336f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e48478a_d9a0_4d12_83bd_511ab3dfd193
GAIN-576708-2016 | GA-320761-2015 | 6/13/2016 2:18:11 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 3 | Piping requires vehicle protection. Roof top units require fall protection. Meter piping requires connection above ground. | 2 | Physical protection of piping and tubing absent. | Clearance.png | file://x:/photopub/docs/0000000442/175ab45b-e02b-4a11-b122-7e89afde3c95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b9af501_ab35_4735_bb7c_c698fac07399
GAIN-576708-2016 | GA-320761-2015 | 6/13/2016 2:18:11 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 3 | Piping requires vehicle protection. Roof top units require fall protection. Meter piping requires connection above ground. | 2 | Physical protection of piping and tubing absent. | Piping.png | file://x:/photopub/docs/0000000442/646082a8-cdc8-4546-900e-6f114577790b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b9af501_ab35_4735_bb7c_c698fac07399
GAIN-576708-2016 | GA-320761-2015 | 6/13/2016 2:18:11 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 3 | Piping requires vehicle protection. Roof top units require fall protection. Meter piping requires connection above ground. | 2 | Physical protection of piping and tubing absent. | Protection.png | file://x:/photopub/docs/0000000442/a7a20c0c-4f2a-4234-addc-ccfab97b2280.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8b9af501_ab35_4735_bb7c_c698fac07399
GAIN-586747-2016 | GA-393976-2016 | 6/3/2016 11:25:01 AM | ASSESS: GA: Rough-In | png | #asFound | GA054 | Code prohibited practices or materials | 3 | 3 | The Code stipulates that the final gas connection to the appliance is the only joint or connection permitted inside a food truck. The gas piping inside the food truck has multiple joints and connections. | 3 | Code prohibited practices or materials | Food_truck.png | file://x:/photopub/docs/0000000438/9f4e6b40-e79a-49e9-891a-f3382e09ff3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__152831a1_4299_4d19_a600_080b4ff24baf
ELIN-587622-2016 | EL-386564-2016 | 6/6/2016 10:29:57 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 200A 240V Main Panel cover is removed and the panel is energized, this poses a shock hazard to persons who may accidentally come in contact with energized components. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel.png | file://x:/photopub/docs/0000000439/7f52b927-7530-48b8-9fa1-e97c3c3130c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b6c5b255_61ec_4d00_8285_a91435f75c21
ELIN-590262-2016 | EL-392709-2016 | 6/10/2016 11:04:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | Main distribution panel and sub distribution panels were found energized, at a rough wire assessment request. BC Hydro meter clip was removed and placed on top of meter. Incoming " line" side of meter base remains energized without meter installed. Complete disconnection of energized electrical equipment is required prior to executing work on said equipment. A risk of shock, and fire would be present to persons and property if accidental contact was made with energized equipment. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Main_panel_energized.png | file://x:/photopub/docs/0000000442/ab6c26e9-5e59-4c39-a706-27ade966953d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b42d90b_7d66_4a5a_9261_0570c2a22f39
ELIN-590262-2016 | EL-392709-2016 | 6/10/2016 11:04:06 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | Main distribution panel and sub distribution panels were found energized, at a rough wire assessment request. BC Hydro meter clip was removed and placed on top of meter. Incoming " line" side of meter base remains energized without meter installed. Complete disconnection of energized electrical equipment is required prior to executing work on said equipment. A risk of shock, and fire would be present to persons and property if accidental contact was made with energized equipment. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | Hydro_meter_installed_with_out_clip.png | file://x:/photopub/docs/0000000442/220a26e1-f587-4284-aa02-5dce7ffc467e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b42d90b_7d66_4a5a_9261_0570c2a22f39
GAIN-584545-2016 | GA-373011-2016 | 6/8/2016 12:07:20 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | No_dirt_pocket_or_shut_off_upstream_of_regulator.png | file://x:/photopub/docs/0000000442/1f375a05-2a8b-421a-9d29-2f4b9fd4585c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4766416f_3e0a_4e3a_bed0_89ecb43a0848
GAIN-584545-2016 | GA-373011-2016 | 6/8/2016 12:07:20 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Common_venting_of_Cat_4_appliance.png | file://x:/photopub/docs/0000000442/c9501ce9-f31b-44d2-8e24-fede1002fa11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4766416f_3e0a_4e3a_bed0_89ecb43a0848
GAIN-584545-2016 | GA-373011-2016 | 6/8/2016 12:07:20 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 |  | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Metallic_fittings_in_condensate_drain.png | file://x:/photopub/docs/0000000442/ec8e9748-a6a2-4ff1-bf40-c894e34af1d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4766416f_3e0a_4e3a_bed0_89ecb43a0848
ELOP-591245-2016 | 5076521 | 6/10/2016 1:36:00 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15A 120V receptacle located by sink is not GFCI protected, this poses a shock hazard and possible damage to equipment. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Wash_Basin_Receptacle.png | file://x:/photopub/docs/0000000442/f1a6f6c7-2df8-49cb-bbd3-efc87533a2b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f9afd96_1402_41c7_bc9a_7d12b5c642c8
ELOP-226569-2014 | 3818876 | 6/15/2016 4:30:02 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | Electrical systems which require a connection from neutral to ground must be connected by a grounding conductor with no mechanical splices. In this installation a generator system was grounded with a copper conductor containing two mechanical splices. | 4 | Installation Grounding; conductor is not continuous. | Ground_conductor_spliced.png | file://x:/photopub/docs/0000000443/23645290-e23a-4d5a-bdd4-935c7811e46d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ceb85600_3470_4f69_90bd_2efd203e7185
BPVOP-588298-2016 | BPV-163635-2014 | 6/3/2016 10:10:07 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 1 | Boiler is inoperable at this time due to building fire and will require a full inspection before being restarted. | 0 | No Created Hazard Identified | Removed_controls.png | file://x:/photopub/docs/0000000438/d8c6f5a9-a9ad-418c-8dcd-5c8ce6487d71.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e6ae8ed_a62c_4dde_bc58_3993a985628e
BPVOP-588298-2016 | BPV-163635-2014 | 6/3/2016 10:10:07 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP000 | No Created Hazard Identified | 0 | 1 | Boiler is inoperable at this time due to building fire and will require a full inspection before being restarted. | 0 | No Created Hazard Identified | Boiler.png | file://x:/photopub/docs/0000000438/53b2f414-04e8-4136-a2d7-96d4ecd5f1fb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e6ae8ed_a62c_4dde_bc58_3993a985628e
ELIN-591188-2016 | EL-192257-2014 | 6/9/2016 9:37:08 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 volt dishwasher circuits not capped off or terminated in box: potential shock or fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Service.png | file://x:/photopub/docs/0000000440/b170b772-f990-485e-8007-ab414024e3f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a838227_fd51_4109_85dd_369774f6ae2e
ELIN-591188-2016 | EL-192257-2014 | 6/9/2016 9:37:08 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 volt dishwasher circuits not capped off or terminated in box: potential shock or fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel.png | file://x:/photopub/docs/0000000440/50283d1e-9361-41ed-979c-8aac1b7e432c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a838227_fd51_4109_85dd_369774f6ae2e
ELIN-591188-2016 | EL-192257-2014 | 6/9/2016 9:37:08 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 volt dishwasher circuits not capped off or terminated in box: potential shock or fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Panel_unit_26.png | file://x:/photopub/docs/0000000440/0629b786-3188-4700-9404-d2404aeacf1f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a838227_fd51_4109_85dd_369774f6ae2e
ELIN-591188-2016 | EL-192257-2014 | 6/9/2016 9:37:08 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 volt dishwasher circuits not capped off or terminated in box: potential shock or fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Dishw.png | file://x:/photopub/docs/0000000440/63f88c43-9868-4e93-8c34-ac7caa70d1de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a838227_fd51_4109_85dd_369774f6ae2e
ELIN-591188-2016 | EL-192257-2014 | 6/9/2016 9:37:08 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 120 volt dishwasher circuits not capped off or terminated in box: potential shock or fire hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Dish.png | file://x:/photopub/docs/0000000440/4ba259ed-4dfb-4662-b471-5446d70ad73d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7a838227_fd51_4109_85dd_369774f6ae2e
ELIN-591122-2016 | EL-378836-2016 | 6/9/2016 6:58:53 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Flexible_cord_to_generator_panel.png | file://x:/photopub/docs/0000000442/0a8adac7-a775-4de8-9c4a-e2909c7eb155.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0dd5da62_e5a5_4c3c_aa70_72c73c3ba6eb
PRIN-575858-2016 | PR-386618-2016 | 5/18/2016 12:37:22 AM | ASSESS: PR IN: Acceptance | png | #asFound | PR011 | Small defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Guarding for station acceleration deceleration equipment has been removed. Entrapment hazard with rotating machinery. | 1 | Small defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Tire_bank_guarding_not_installed.png | file://x:/photopub/docs/0000000443/a58d2ba5-d3b8-402c-9d66-c2edb56bcd7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ee2c949_4e17_4843_b1b1_4d7282afafc0
PRIN-575861-2016 | PR-386513-2016 | 5/18/2016 12:44:02 AM | ASSESS: PR IN: Acceptance | png | #asFound | PR011 | Small defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 1 | 1 | Guarding for station acceleration and deceleration equipment had been removed. Entrapment hazard with rotating machinery. | 1 | Small defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Guarding_for_tire_banks_not_installed.png | file://x:/photopub/docs/0000000443/55e15863-71b3-4e53-aef2-c83ba7d14f32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__966cf6cd_798f_43ae_9668_27f266e7898a
ELIN-594318-2016 | EL-346857-2016 | 6/14/2016 5:05:41 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Main temporary construction service panel exposed to weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_panel_exposed_to_weather.png | file://x:/photopub/docs/0000000443/a9c36418-93f0-4f6f-b515-f5a6624f1557.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7816bd5f_c452_41db_afed_da238d1512f9
ELIN-592409-2016 | EL-396238-2016 | 6/13/2016 11:27:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL246 | All locations Minor maintenance required | 2 | 2 |  | 2 | All locations Minor maintenance required | Photo_to__Photo_to_new_cabinetry_instal_in_front_of_electrical_equipment.png | file://x:/photopub/docs/0000000442/bd6458e9-152f-45c4-8376-6054c511aeaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c4bb08b_4f54_41bc_92ef_8957dafa8d38
ELIN-592409-2016 | EL-396238-2016 | 6/13/2016 11:27:52 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL246 | All locations Minor maintenance required | 2 | 2 |  | 2 | All locations Minor maintenance required | New_cabinetry__New_cabinetry_installed_in_front_of_existing_electrical_panel.png | file://x:/photopub/docs/0000000442/118c2c78-3e56-4c27-b945-9c80f22c824d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c4bb08b_4f54_41bc_92ef_8957dafa8d38
BPVOP-593348-2016 | 5361922 | 6/15/2016 11:33:05 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | During the inspection of a Hot Water Boiler with the MAWP of 160 psig I found that the Safety Relief Valve was not replaced within the interval specified in the CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve__.png | file://x:/photopub/docs/0000000443/61655de7-b812-49bb-b829-5f48083c3a57.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__97d21fb0_1f2b_4235_adad_5ceecf06cf0c
ELIN-593536-2016 | EL-346462-2016 | 6/15/2016 1:29:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non-compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Main.png | file://x:/photopub/docs/0000000443/cacdc541-ecfd-4abf-a85d-8f591a0baaca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea5e339f_ec87_48dc_aba0_711b331fb0b1
ELIN-593536-2016 | EL-346462-2016 | 6/15/2016 1:29:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non-compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Closet.png | file://x:/photopub/docs/0000000443/51a6d9a4-9078-46e0-95db-8ffae0ac5132.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea5e339f_ec87_48dc_aba0_711b331fb0b1
ELIN-593536-2016 | EL-346462-2016 | 6/15/2016 1:29:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non-compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 70A.png | file://x:/photopub/docs/0000000443/2996b1ce-46c7-4f42-8945-afa6c658352a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea5e339f_ec87_48dc_aba0_711b331fb0b1
ELIN-593536-2016 | EL-346462-2016 | 6/15/2016 1:29:14 PM | ASSESS: EL: Service Connection | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Service non-compliances | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Pnl.png | file://x:/photopub/docs/0000000443/0b0b8f14-d5e5-45df-ad94-0c34d8781cce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ea5e339f_ec87_48dc_aba0_711b331fb0b1
ELIN-593150-2016 | UW-397790-2016 | 6/13/2016 11:12:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Multiple locations of exposed energized terminations of branch circuit wiring, receptacles, lighting, hot water tank termination and (removed) oil furnace location. Not able to determine complete scope of work completed as drywall has been re-installed. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | DHW_tank.png | file://x:/photopub/docs/0000000442/ab84cfd9-b43b-4715-a2f2-614f586b6556.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2ded4_5f26_401f_b5fe_b735d3d18ef2
ELIN-593150-2016 | UW-397790-2016 | 6/13/2016 11:12:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Multiple locations of exposed energized terminations of branch circuit wiring, receptacles, lighting, hot water tank termination and (removed) oil furnace location. Not able to determine complete scope of work completed as drywall has been re-installed. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Receptacle_.png | file://x:/photopub/docs/0000000442/ff5a6061-6921-43c1-8ae1-3e928ac4364d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2ded4_5f26_401f_b5fe_b735d3d18ef2
ELIN-593150-2016 | UW-397790-2016 | 6/13/2016 11:12:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Multiple locations of exposed energized terminations of branch circuit wiring, receptacles, lighting, hot water tank termination and (removed) oil furnace location. Not able to determine complete scope of work completed as drywall has been re-installed. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Ceiling_fixture.png | file://x:/photopub/docs/0000000442/d0d678ba-d4d0-4403-b381-6d6ac4efb372.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2ded4_5f26_401f_b5fe_b735d3d18ef2
ELIN-593150-2016 | UW-397790-2016 | 6/13/2016 11:12:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Multiple locations of exposed energized terminations of branch circuit wiring, receptacles, lighting, hot water tank termination and (removed) oil furnace location. Not able to determine complete scope of work completed as drywall has been re-installed. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Light_switches.png | file://x:/photopub/docs/0000000442/607c8ba5-b76d-4e0e-b440-8ac853b186df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2ded4_5f26_401f_b5fe_b735d3d18ef2
ELIN-593150-2016 | UW-397790-2016 | 6/13/2016 11:12:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Multiple locations of exposed energized terminations of branch circuit wiring, receptacles, lighting, hot water tank termination and (removed) oil furnace location. Not able to determine complete scope of work completed as drywall has been re-installed. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Wall_removal.png | file://x:/photopub/docs/0000000442/58aed2d9-4795-4e45-a385-2abbe17ee1e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2ded4_5f26_401f_b5fe_b735d3d18ef2
ELIN-593150-2016 | UW-397790-2016 | 6/13/2016 11:12:35 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Multiple locations of exposed energized terminations of branch circuit wiring, receptacles, lighting, hot water tank termination and (removed) oil furnace location. Not able to determine complete scope of work completed as drywall has been re-installed. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | furnace_circuit.png | file://x:/photopub/docs/0000000442/926d84d0-a82e-423d-b1f2-4b2ae24b77db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6f2ded4_5f26_401f_b5fe_b735d3d18ef2
ELOP-190934-2014 | 5298315 | 6/3/2016 3:11:02 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL139 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | 3 | 3 | Receptacles installed in wet areas must be GFCI protected to prevent shock. In this fish processing facility GFCI protection was omitted at sinks, water troughs, and wet working areas. | 3 | Installation of electrical equipment Residential: receptacle has not been provided within 1 m of a sink. | Wet_zone.png | file://x:/photopub/docs/0000000438/9afaaec9-4b59-479f-bca8-5b46f448de12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e8c8ad85_cc3e_467b_bf80_83f8941fb749
ELIN-584404-2016 | EL-382609-2016 | 5/30/2016 11:41:35 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Exposed_cable_.png | file://x:/photopub/docs/0000000435/7f15aadf-3c0e-47f2-a83a-6d2b948abe24.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18b236c8_c1fe_4d61_a0a0_ccee4019a89b
ELIN-584404-2016 | EL-382609-2016 | 5/30/2016 11:41:35 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Meter_location.png | file://x:/photopub/docs/0000000435/04b27b72-a533-42c4-9522-f3af5fbba1ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18b236c8_c1fe_4d61_a0a0_ccee4019a89b
ELIN-584404-2016 | EL-382609-2016 | 5/30/2016 11:41:35 AM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Panel_location.png | file://x:/photopub/docs/0000000435/88dd4236-3f32-46e2-aa76-cc817da4c68c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18b236c8_c1fe_4d61_a0a0_ccee4019a89b
ELIN-587082-2016 | EL-391757-2016 | 6/2/2016 2:38:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Service conductor is undersized for 200amp | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Cable_repaired_with_a_tar_like_substance.png | file://x:/photopub/docs/0000000437/3995fc1b-1ca5-4f2a-8c87-9935bf357cdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd9ace6f_0a24_43ad_ae0e_62d3b27ace34
ELIN-587082-2016 | EL-391757-2016 | 6/2/2016 2:38:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Service conductor is undersized for 200amp | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Steel_screws_on_treated_pole.png | file://x:/photopub/docs/0000000437/a9904605-a74c-45db-817d-fb37afd3392c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd9ace6f_0a24_43ad_ae0e_62d3b27ace34
ELIN-587082-2016 | EL-391757-2016 | 6/2/2016 2:38:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Service conductor is undersized for 200amp | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_exposed.png | file://x:/photopub/docs/0000000437/fac3705a-959d-4a5a-abf8-c18eba4ebae2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd9ace6f_0a24_43ad_ae0e_62d3b27ace34
ELIN-587082-2016 | EL-391757-2016 | 6/2/2016 2:38:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Service conductor is undersized for 200amp | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Cables_buried_without_declaration_.png | file://x:/photopub/docs/0000000437/5d6a26be-8408-4b34-9560-df44ab80c999.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd9ace6f_0a24_43ad_ae0e_62d3b27ace34
ELIN-587082-2016 | EL-391757-2016 | 6/2/2016 2:38:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 3 | Service conductor is undersized for 200amp | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Service_cable_is_4o_AWG_al_distance_is_118ft.png | file://x:/photopub/docs/0000000437/6ad5437c-6be3-42e9-91e7-5dd04bb006ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd9ace6f_0a24_43ad_ae0e_62d3b27ace34
BPVOP-579404-2016 | BPV-082121-2014 | 5/18/2016 1:33:57 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Air_receiver_clearances_.png | file://x:/photopub/docs/0000000433/07d68d51-827c-4203-b11f-d869738658d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fcd0bb98_5a78_41ee_86c0_6d0f35fec7cb
ELIN-573061-2016 | EL-382315-2016 | 5/26/2016 3:27:25 PM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | A 3 phase 4 wire cable was energized with a 3 pole 60 Amp breaker and only protected by wire nuts. This was located in an area (Under counter) that would not be regularly accessible by public and a hidden risk for staff. The risk of electrocution would be greatly increased over time as the unsecured and unprotected conductors would accidentally tugged or hit with supplies or body parts. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_energized_conductor_.png | file://x:/photopub/docs/0000000435/7743e949-c45f-4074-b21e-f878f0c88058.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5155829d_79f4_4332_9784_74f22c1b8add
ELOP-226624-2014 | 6053 | 5/31/2016 11:23:39 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL173 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical equipment must be maintained in good working order. This sewage lift station is old and near the water. It is starting to deteriorate and replacement parts are difficult to locate. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Oldie.png | file://x:/photopub/docs/0000000436/5abcadc9-8c19-477f-971f-5e44923b5603.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8ef67a4_7b62_4819_b23f_12befcd01ea8
ELOP-381967-2015 | 6062 | 5/31/2016 11:33:54 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL245 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | 4 | 4 | Electrical equipment must be maintained in safe working order. In this sewage lift station the ventilation fan had failed making it possible for corrosive gases to accumulate in the enclosure. | 4 | All locations • Equipment is damaged and needs to be either replaced or repaired; and • not suitable for continued use. | Listing.png | file://x:/photopub/docs/0000000436/1d122457-3f87-4a94-8153-92ed67c120c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eeadbd2_4c3f_4f2f_994b_e5a8eac0e836
ELIN-582991-2016 | EL-324029-2015 | 5/27/2016 7:53:15 AM | ASSESS: EL: Final | png | #asFound | EL146 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 15A 120V Exposed light bulbs have been installed in a location only 3' from the floor, this poses a shock hazard and possible equipment damage to the lamp holder and bulb. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Lamp_Holders.png | file://x:/photopub/docs/0000000434/d44c139d-781f-4cec-aec0-22a26b6f90c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__02c1522e_cc9f_433b_83d3_4a2c7d990a24
ELIN-582515-2016 | EL-375315-2016 | 5/27/2016 10:50:02 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | 15A 120V light fixture is incomplete missing the lamp and cover, the energized socket is exposed which poses a shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Jam_Jar.png | file://x:/photopub/docs/0000000434/236a6ac2-dd0f-423a-ab51-6b8dc824bc49.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55a691a0_dfc4_44b5_8290_2452da2f538b
ELIN-580018-2016 | EL-389159-2016 | 5/31/2016 11:18:03 AM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | A water system pump operating at 15 amps 120 volts is wired with flexible cord and cord cap. Flexible cord is not designed to be used as a permanent wiring method. It can deteriorate and lead to a potential for property damage or injury to persons. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_wiring_existing_cabin_water_system.png | file://x:/photopub/docs/0000000436/73dd0292-8103-4261-9eb7-a3b721a8dec7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2114de6b_71d3_43bc_af18_4559a12fe1cd
AMOP-583868-2016 | AM-019500-2013 | 5/27/2016 10:24:44 AM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Fibreglass drain grating slat was found to be cracked and raised. This condition could cause damage to the raft that riders occupy. This hazard is reasonably detectable by maintenance and likely to propagate. The waterslide was not yet in operation for the season and annual maintenance is still underway. | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Drain_grate_slat.png | file://x:/photopub/docs/0000000434/50423d32-0025-416f-bc51-80270c87ccde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__992c25ea_0226_499e_ba8f_845ae68a211e
ELIN-582659-2016 | UW-391001-2016 | 5/26/2016 11:04:15 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | A 60 amp rated conductor operating at 240 volts was terminated on a 100 amp breaker which was providing overcurrent protection for the 60 amp cable. The panel board was found energized with no covers on and combustibles in contact with internal panel components. Panel was not provided bonding to ground or a neutral conductor. Accidental contact by persons could result in injury to persons and was made more hazardous with lno effective grounding, bonding and installation of neutral conductor. A real potential for fire due to contact with combustibles was also present. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Energized_panel_in_closet_no_cover__combustibles_in_contact_with_live_equipment.png | file://x:/photopub/docs/0000000434/e1ea1f66-7dab-492f-9a60-f0e2d5172022.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65db0da6_9a6a_4903_9885_d3bba613bafc
ELIN-581470-2016 | EL-389167-2016 | 5/26/2016 12:46:45 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | The 120/240 volt 100 amp feeder cable to the trailer is subject to mechanical damage, this can lead to a shock and equipment damage hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Service_cable_feeder.png | file://x:/photopub/docs/0000000434/bb35bd38-6a07-404d-94a9-5b53b01443d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1eabf7c4_e17d_4a93_993e_7f9996f59263
AMOP-574331-2016 | 2053351 | 5/10/2016 2:08:14 PM | ASSESS: AM OP: Periodic | png | #asFound | AM036 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | 3 | 3 | It was observed that components of 2 of the personnel carrying unit (PCU) are making contact with the sweep arm when rotated. It is not known with certainty, but it may be possible that during the ride cycle this condition could result in a hazard in which the rotating PCU could come to a sudden jarring stop which could cause damage to the PCU and injure the rider/s. Also, wear in the spindle configuration may indicate that the structural strength of the spindle configuration is compromised and therefore over a period of time there is a risk that,during the ride cycle, the PCU could become detached from the sweep arm with it occupied by a rider. | 3 | Defects that: May not be reasonably detectable by maintenance program Likely to propagate | PCU_contact_with_Sweep_Arm.png | file://x:/photopub/docs/0000000436/a8e28346-9ed2-45c0-8418-40b595ca6809.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__691b5f01_8761_43aa_8527_ebc6294e6f37
AMOP-574340-2016 | 2050474 | 5/10/2016 2:04:10 PM | ASSESS: AM OP: Periodic | png | #asFound | AM008 | Small misalignments that are: Reasonably detectable by maintenance program Unlikely to result in rapid wear or deropement | 1 | 1 | Although the the ride operates without issues within the clearance perimeter that is provided the ride clearance perimeter is suspected of being inadequate. The operating contractor was unable to determine the manufacturer's minimum clearance perimeter. | 1 | Small misalignments that are: Reasonably detectable by maintenance program Unlikely to result in rapid wear or deropement | Ride_perimeter_suspect.png | file://x:/photopub/docs/0000000436/b95d92d3-03ef-4905-8960-51abd12a40cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__60e267fc_14e7_43c6_bafb_8ddf7fa874ad
ELIN-581698-2016 | UW-390296-2016 | 5/24/2016 4:10:16 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL252 | Category 2 Equipment is not approved for the specific use or location. | 3 | 3 | No approval marks on equipment. This regulation is in place to protect consumers from shoddy equipment. | 3 | Category 2 Equipment is not approved for the specific use or location. | C.png | file://x:/photopub/docs/0000000433/7fd5a40c-ad36-4c71-b979-7c4156febcc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__307fb77e_a98c_4978_8537_82b6dab9bae3
ELIN-581751-2016 | EL-377073-2016 | 5/25/2016 3:10:16 PM | ASSESS: EL: Final | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | Ground fault circuit interrupters for hot tubs are required to be 3 meters away from the hot tub. This is required to prevent the breaker from getting damaged from exposure to water and chlorine. This is also required to prevent persons in close proximity or occupants of the tub from contacting energized parts of the electrical system. This installation has a hot tub GFCI breaker located adjacent to the tub and within 300mm of the tub. Left uncorrected this is a potential shock hazard for persons contacting this equipment and a potential fire hazard if equipment and connections become corroded. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Hot_tub_and_breaker_location.png | file://x:/photopub/docs/0000000433/9ae66983-5ddd-4c04-b828-857b529a2a23.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658d7b97_1154_468c_8c35_020c1b9cbaad
ELIN-583984-2016 | EL-290394-2015 | 5/31/2016 11:56:28 AM | ASSESS: EL: Final | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 |  | 2 | Equipment is not marked / identified Multiple service boxes not marked. | View01_meter_bases.png | file://x:/photopub/docs/0000000436/90c10a28-56ea-40a6-847e-380fa7b5261b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__067d3ebd_330b_470d_b94f_f91069cdeb2d
GAIN-561478-2016 | GA-268426-2015 | 5/25/2016 9:23:35 AM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 | If the regulator relief vents raw gas it could be ignited by the operating burner causing an uncontrolled burning of the escaping gas. | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | RTU_12.png | file://x:/photopub/docs/0000000434/53431c33-db22-4d34-891e-4c08384d0066.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7bb7ade_8975_42a6_bd0e_374ecd92bad0
BPVOP-585056-2016 | BPV-163635-2014 | 6/8/2016 3:49:51 PM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | Boiler is inoperable due to fire damage of enclosure. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Roof_where_fire_appears_to_have_started.png | file://x:/photopub/docs/0000000438/636d8c0c-b5f3-4d88-9d18-24b2ec6f2cb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a317b2a8_e58e_423b_a7e3_db0789735aca
BPVOP-585056-2016 | BPV-163635-2014 | 6/8/2016 3:49:51 PM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | Boiler is inoperable due to fire damage of enclosure. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Wiring_and_controls_removed.png | file://x:/photopub/docs/0000000438/e0e4d101-de88-4104-9aef-9f49ff9bc940.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a317b2a8_e58e_423b_a7e3_db0789735aca
BPVOP-585056-2016 | BPV-163635-2014 | 6/8/2016 3:49:51 PM | ASSESS: BPV OP: Incident Boiler | png | #asFound | BP099 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | 5 | 5 | Boiler is inoperable due to fire damage of enclosure. | 5 | 2.0.1 Control system may overrun - Safety devices not functional, by-passed or missing with no back up corresponding safety device | Building_damage.png | file://x:/photopub/docs/0000000438/e1b32c5d-6295-4193-a867-df406dcb7283.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a317b2a8_e58e_423b_a7e3_db0789735aca
ELIN-581751-2016 | EL-377073-2016 | 5/25/2016 3:10:16 PM | ASSESS: EL: Final | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | Ground fault circuit interrupters for hot tubs are required to be 3 meters away from the hot tub. This is required to prevent the breaker from getting damaged from exposure to water and chlorine. This is also required to prevent persons in close proximity or occupants of the tub from contacting energized parts of the electrical system. This installation has a hot tub GFCI breaker located adjacent to the tub and within 300mm of the tub. Left uncorrected this is a potential shock hazard for persons contacting this equipment and a potential fire hazard if equipment and connections become corroded. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Hot_tub_and_breaker_enclosure_location.png | file://x:/photopub/docs/0000000433/97b77214-541e-4637-b2b8-f125fe13a41c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658d7b97_1154_468c_8c35_020c1b9cbaad
ELIN-581751-2016 | EL-377073-2016 | 5/25/2016 3:10:16 PM | ASSESS: EL: Final | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | Ground fault circuit interrupters for hot tubs are required to be 3 meters away from the hot tub. This is required to prevent the breaker from getting damaged from exposure to water and chlorine. This is also required to prevent persons in close proximity or occupants of the tub from contacting energized parts of the electrical system. This installation has a hot tub GFCI breaker located adjacent to the tub and within 300mm of the tub. Left uncorrected this is a potential shock hazard for persons contacting this equipment and a potential fire hazard if equipment and connections become corroded. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Exterior_of_the_house.png | file://x:/photopub/docs/0000000433/677f54c3-ca14-4aa9-b736-16c74a8ea863.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658d7b97_1154_468c_8c35_020c1b9cbaad
ELIN-581751-2016 | EL-377073-2016 | 5/25/2016 3:10:16 PM | ASSESS: EL: Final | png | #asFound | EL265 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | 3 | 3 | Ground fault circuit interrupters for hot tubs are required to be 3 meters away from the hot tub. This is required to prevent the breaker from getting damaged from exposure to water and chlorine. This is also required to prevent persons in close proximity or occupants of the tub from contacting energized parts of the electrical system. This installation has a hot tub GFCI breaker located adjacent to the tub and within 300mm of the tub. Left uncorrected this is a potential shock hazard for persons contacting this equipment and a potential fire hazard if equipment and connections become corroded. | 3 | Pools, Spas and Hot Tubs Protection; equipment within the classified area is not acceptable. | Hot_tub_and_breaker_location__.png | file://x:/photopub/docs/0000000433/36cfe218-c19e-4d7f-81a8-c94a1e17afb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__658d7b97_1154_468c_8c35_020c1b9cbaad
ELIN-582139-2016 | EL-374319-2016 | 5/25/2016 1:14:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Outlet boxes installed of the support of ceiling fans are required to be approved and marked for fan support. This is required so that the box is able to properly support the ceiling fan and prevent the box and the fan from vibrating loose from its supports after installation. This installation has a regular "pan" type box installed to support a ceiling fan in a new home under construction. Left uncorrected this is a shock, fire, and dropping hazard should the fan or fan/box come loose and fall causing damage to wiring and or fall on some one. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | New_house_under_construction.png | file://x:/photopub/docs/0000000433/38cf77d7-3bde-4cdf-83ef-bc40e6ee44ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8687303_ffe6_402f_8a8f_f75788e8714a
ELIN-582139-2016 | EL-374319-2016 | 5/25/2016 1:14:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Outlet boxes installed of the support of ceiling fans are required to be approved and marked for fan support. This is required so that the box is able to properly support the ceiling fan and prevent the box and the fan from vibrating loose from its supports after installation. This installation has a regular "pan" type box installed to support a ceiling fan in a new home under construction. Left uncorrected this is a shock, fire, and dropping hazard should the fan or fan/box come loose and fall causing damage to wiring and or fall on some one. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Box_installed_for_the_ceiling_fan.png | file://x:/photopub/docs/0000000433/e065a092-4e96-456f-8d16-d71f8886b84f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8687303_ffe6_402f_8a8f_f75788e8714a
ELIN-582139-2016 | EL-374319-2016 | 5/25/2016 1:14:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 2 | Outlet boxes installed of the support of ceiling fans are required to be approved and marked for fan support. This is required so that the box is able to properly support the ceiling fan and prevent the box and the fan from vibrating loose from its supports after installation. This installation has a regular "pan" type box installed to support a ceiling fan in a new home under construction. Left uncorrected this is a shock, fire, and dropping hazard should the fan or fan/box come loose and fall causing damage to wiring and or fall on some one. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Family_room_ceiling.png | file://x:/photopub/docs/0000000433/7db57a26-c661-4899-bb8e-eebd55241c0b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d8687303_ffe6_402f_8a8f_f75788e8714a
BPVOP-543753-2016 | 4060892 | 5/18/2016 4:24:29 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Electric Steam Boiler with heating surface of 4 square meters and Maximum Allowable Working Pressure (MAWP) of 100psig, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, steam or flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | Boiler_without_remote_emergency_shutdown_switch.png | file://x:/photopub/docs/0000000433/bd5bd3f9-f207-4f75-b1bc-346d776c5bc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87E175D2_BB8D_46B0_A5BE_92988D3A9225
BPVOP-543753-2016 | 4060892 | 5/18/2016 4:24:29 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Electric Steam Boiler with heating surface of 4 square meters and Maximum Allowable Working Pressure (MAWP) of 100psig, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, steam or flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_Remote_Emergency_Shutdown_Switch.png | file://x:/photopub/docs/0000000433/305fd0b7-1f62-4bd3-b1e9-9e949d4f144a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87E175D2_BB8D_46B0_A5BE_92988D3A9225
ELIN-516750-2016 | EL-157822-2014 | 6/1/2016 6:56:33 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Overhead power cables must be separated from other utility lines (telephone, cable) to stop radio interference and to provide adequate limits of approach for utility workers. In this remote installation power cables which had been disconnected from mobile homes which were relocated had been coiled and tied with light duty twine high on the poles. Telus refused to work on their lines because of the danger. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Typical_coil.png | file://x:/photopub/docs/0000000437/6a682511-a08a-4adc-8616-d58135ac8f4a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e58ad28b_7415_4375_96c8_c4728316b7af
ELIN-516750-2016 | EL-157822-2014 | 6/1/2016 6:56:33 AM | ASSESS: EL: Final | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Overhead power cables must be separated from other utility lines (telephone, cable) to stop radio interference and to provide adequate limits of approach for utility workers. In this remote installation power cables which had been disconnected from mobile homes which were relocated had been coiled and tied with light duty twine high on the poles. Telus refused to work on their lines because of the danger. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Coils_along_main_street.png | file://x:/photopub/docs/0000000437/128feccc-d8d0-49aa-a832-516e728c5893.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e58ad28b_7415_4375_96c8_c4728316b7af
ELIN-485216-2015 | EL-270383-2015 | 6/1/2016 7:10:58 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 3 | Electrical cables must be sized for the overcurrent protection installed to protect them. In this generator replacement installation a larger generator was installed with a circuit breaker rated larger than the capacity of the existing cable. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Nameplate.png | file://x:/photopub/docs/0000000437/5fd6fd0f-1199-40d8-8dfb-f2d64097c2a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5336afb2_ede5_477b_bcb4_623f17568028
GAUP-582689-2016 | UW-391036-2016 | 6/2/2016 10:29:46 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | Flue connection on furnace leaking, flue ran into existing single wall vent and not terminated through the existing cap or sealed and leaking into the building. This is a hazard as products of combustion are entering the building. | 3 | Leaking or failing special venting system (Minor) | 4.png | file://x:/photopub/docs/0000000437/877c6ef8-6e61-4a81-9ae1-92ff49825fe8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c77a6cb_8b6d_404d_9573_ff29ac5e8780
GAUP-582689-2016 | UW-391036-2016 | 6/2/2016 10:29:46 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | Flue connection on furnace leaking, flue ran into existing single wall vent and not terminated through the existing cap or sealed and leaking into the building. This is a hazard as products of combustion are entering the building. | 3 | Leaking or failing special venting system (Minor) | 3.png | file://x:/photopub/docs/0000000437/d409bf6c-fe9d-4e74-a327-6176c93edf7a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c77a6cb_8b6d_404d_9573_ff29ac5e8780
GAUP-582689-2016 | UW-391036-2016 | 6/2/2016 10:29:46 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | Flue connection on furnace leaking, flue ran into existing single wall vent and not terminated through the existing cap or sealed and leaking into the building. This is a hazard as products of combustion are entering the building. | 3 | Leaking or failing special venting system (Minor) | 2.png | file://x:/photopub/docs/0000000437/4a5dd494-be64-4e41-a4b0-1c271b2dbaba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c77a6cb_8b6d_404d_9573_ff29ac5e8780
GAUP-582689-2016 | UW-391036-2016 | 6/2/2016 10:29:46 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA104 | Leaking or failing special venting system (Minor) | 3 | 3 | Flue connection on furnace leaking, flue ran into existing single wall vent and not terminated through the existing cap or sealed and leaking into the building. This is a hazard as products of combustion are entering the building. | 3 | Leaking or failing special venting system (Minor) | 1.png | file://x:/photopub/docs/0000000437/d42d9350-66ca-4155-89a8-d44763bb1ef0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c77a6cb_8b6d_404d_9573_ff29ac5e8780
GAUP-582725-2016 | UW-391052-2016 | 6/2/2016 11:46:03 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Black iron and fittings installed underground, couldn't find where piping enters the building. This is a hazard as black iron will corrode underground, and threaded fittings not approved underground. | 2 | Physical protection of piping and tubing absent. | 1872_crystal.png | file://x:/photopub/docs/0000000437/f6db15fb-3a5d-427d-9ded-bb8bcde36936.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4611dd4_008a_404f_967d_c5f674963f35
BPVOP-583182-2016 | 2266678 | 5/26/2016 10:00:35 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP109 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | 3 | 3 | Upon assessment of Hot Water Boiler with Heating Surface (HS) of 9.0 square meters, Maximum Allowable Working Pressure (MAWP) of 30psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that the lockable remote shutdown switch is not installed at the boiler room entrance. In the event of failure of boiler pressure retaining components, the flashing hot water can make it impossible to shutdown boiler from local control panel and can lead to a severe incident. | 3 | 3.0.1 Safeties will not function - Safety Devices not providing the intended control, e.g. - emergency disconnect switch not provided. | No_Remote_Emergency_Shutdown_Switch.png | file://x:/photopub/docs/0000000434/d3166664-eb35-4241-8703-6898a6086d43.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3ed34812_615d_48d4_b218_5b17f934b42e
BPVOP-583335-2016 | 2285549 | 5/26/2016 11:20:27 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that horizontal air receiver (1.0m long and 0.41m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 5 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVE.png | file://x:/photopub/docs/0000000434/4a272207-cf01-4a49-a9ee-0cd4f4eb5874.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6f17232_fcc3_4a33_aa91_8c0a05a36ad1
BPVOP-583752-2016 | 4578056 | 5/26/2016 10:55:32 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment it is determined that vertical air receiver (2.0m long and 0.70m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, has a safety valve that exceeded the required 5 year interval for servicing or replacement. Failure to have safety valve serviced or replaced as required may subject vessel to pressure above MAWP if operating control fails to shut down compressor. This could result in failure of pressureboundary (shell, head, nozzle, longitudinal or circular seam welds etc. of vessel) with rapid release of compressed air and shooting/rocketing effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Valve.png | file://x:/photopub/docs/0000000434/d05e5f5e-df8a-486c-bf8a-4b6264553670.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8d24659f_e6b6_4c64_bf87_3cb5d83b8a7b
ELIN-567779-2016 | 4949896 | 5/20/2016 11:58:31 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Branch circuit for sleeping areas are not protected by an arc fault circuit interrupting breaker. This is could be a fire hazard if there was an arc producing over time that a regular breaker cannot detect. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | No_arc_fault_breakers_installed.png | file://x:/photopub/docs/0000000435/40c47a6e-327a-4f4b-a7f2-5ddac950d115.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cc259b8_3d0d_4984_9695_71d98cde9b80
BPVOP-584058-2016 | 4357708 | 5/27/2016 12:02:58 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP133 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 100 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | Safety_valves_.png | file://x:/photopub/docs/0000000434/4fb63ace-96eb-410f-8964-53a68f9947ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e59defa3_c70b_4d6c_89ad_c1c593445218
BPVOP-584058-2016 | 4357708 | 5/27/2016 12:02:58 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP133 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 100 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - AMMONIA -Risk Registry BPV-19 No maintenance or servicing and testing scheduled Service and maintenance completed as per CSA B-52 | SV_data_.png | file://x:/photopub/docs/0000000434/9fed8147-a8cb-429c-aaa5-869819971ce8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e59defa3_c70b_4d6c_89ad_c1c593445218
BPVOP-584149-2016 | 4357698 | 5/27/2016 1:11:15 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 100 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safet_valves_.png | file://x:/photopub/docs/0000000434/4a26218a-98d7-4c90-a7ae-12f265dd8f3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6733f621_dcf0_43e0_b4b4_f5c7f87db095
BPVOP-584149-2016 | 4357698 | 5/27/2016 1:11:15 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | All pressure relief devices require periodic inspection, testing and service. I found no record of service or replacement for safety valves on a 100 psi steam kettle for the last 6 years. Potential exists for a safety valve not functioning properly in a critical situation due to being inadequately serviced. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve_data_x2.png | file://x:/photopub/docs/0000000434/1af4b180-c2ae-429a-b02e-61ae4fec79db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6733f621_dcf0_43e0_b4b4_f5c7f87db095
GAUP-587392-2016 | UW-391931-2016 | 5/27/2016 | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | The plastic vent pipe for the furnace was not secured to the appliance flue outlet. The pipe was able detach from the furnace with slight pressure. If the pipe became separated from the furnace during operation the flue gas would enter the living space potentially causing carbon monoxide poisoning to the occupants. | 5 | Special venting system not glued or connected as per certified instructions | Unsecured_furnace_venting.png | file://x:/photopub/docs/0000000437/6bb6ca27-2b6a-4212-8966-c78f08f7fa04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__960dcac6_cd12_4c04_b458_46fee08b14ed
ELIN-580904-2016 | UW-389928-2016 | 5/24/2016 4:17:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Arc fault circuit interrupters are required. These breakers provide a higher degree of protection from fires due to arcing. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | A.png | file://x:/photopub/docs/0000000433/f69c37b4-927f-43da-848c-6107782c5d5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__19f23747_0951_47df_884f_7f629e1f19ca
ELIN-581690-2016 | UW-390295-2016 | 5/24/2016 1:48:53 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Hot water tank connection not made in a junction box. This is a shock hazard as somebody could accidentally contact the conductors. It is also a fire hazard, if the connections are disturbed a hot spot could develop. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000433/321caaa9-7329-47ba-a4ee-293835858802.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__889d5f90_8e49_4001_9f46_b59202c3a022
ELIN-583584-2016 | EL-367186-2016 | 6/1/2016 1:56:01 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL115 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | 3 | 4 | A new home is having branch circuit wiring installed for circuits up to 40 amps operating at 240 volts. The installer has bundled up to 14 multi conductor cables in lengths in excess of 600 mm and in some cases in lengths as much as 10 meters. When multi conductor cables are bundled a potential for overheating of the cables causing damage to both the jacket and conductor insulation which could lead to damage to property or injury to persons | 3 | Conductors, Cables, Raceways or conductors are not suitably sized for their intended use. | Cable_bundling_example_photo_14_-_16_cables_in_contact_extra_low_voltage_in_bundle_as_well.png | file://x:/photopub/docs/0000000437/f5f702ec-7fed-4afa-82a7-58ddb28d54a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__62658ddc_eab6_4661_8bdc_25c1b39d85c5
ELIN-581088-2016 | EL-152047-2014 | 5/27/2016 11:29:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL092 | Continuity Bonding conductor is not observed or broken | 4 | 4 | Bonding conductor is not installed in rigid pvc installation. Bonding conductors are required in a pvc type systems to provide a path for accidental electrical faults to reach the system ground, as well it will allow the over current device to act and clear the fault. Systems without adequate bonding provide a risk for shock and fire for persons and property. | 3 | Continuity Bonding conductor is not observed or broken | Bonding_conductor_not_installed_in_rigid_pvc_.png | file://x:/photopub/docs/0000000434/8281255d-240e-40f3-b4ac-9f037c0b8f83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d714ae2_e9b6_439a_8c67_19da6f3fe0b5
ELIN-584857-2016 | EL-226852-2015 | 5/31/2016 2:32:00 PM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 20 amp duplex receptacles located within 1.5 meters of sink are not approved for application. They need to be ground fault circuit interruptor protected to prevent possible shock to persons. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | None_gfci.png | file://x:/photopub/docs/0000000437/3755c88a-8965-4ef5-bd02-2baf1b2802c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__460c2de9_e17d_4a06_8f81_6e801e840060
BPVOP-584576-2016 | 2261992 | 5/27/2016 12:20:43 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 |  | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Malleable_iron_fittings_in_blowoff_line.png | file://x:/photopub/docs/0000000435/611ac1a3-0351-44d8-9254-892ec46b83b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__267a4535_4f19_4478_bdd0_14032d68540c
ELIN-569334-2016 | EL-345677-2016 | 5/25/2016 4:39:54 PM | ASSESS: EL: Final | png | #asFound | EL023 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 4 | 4 | Electrical services and sub services for row housing and carriage houses require that special attention be paid when one service feeds more than one residence. In this installation the responsible individual made a computational error when calculating service size. | 4 | Overcurrent devices do not adequately protect conductors Conductor ampacity is not adequate for the connected load | 125_amp_panel_with_2_100_amp_subs.png | file://x:/photopub/docs/0000000433/132b2d18-e9c4-4fdd-a3f9-5c24e3bf8d5d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7522419c_940a_4c40_b1c7_b28aa27e64be
ELIN-582402-2016 | UW-382231-2016 | 5/25/2016 10:40:26 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Metal electrical conduit has had a steel garage door cable rub a hole into the conduit. Door moving up and down rubs the cable into the conduit and a hole has worn into the conduit. If not replaced ,the steel cable will cut into the conductors inside the conduit. A risk of shock or fire to persons or property exists if steel cable comes in contact with energized conductors. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | Damaged_conduit_by_steel_garage_cable__.png | file://x:/photopub/docs/0000000434/fd98ff5c-b3bf-4dd2-b030-f3a7a5aa9ff9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80c451c8_8d16_4c73_bb87_1f34e66fd37b
ELOP-434505-2015 | 5393753 | 6/1/2016 6:39:53 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Overhead electrical services must be maintained in safe working order. In this remote installation a service drop was damaged when a piece of equipment contacted and pulled an overhead line. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Big_house_mast.png | file://x:/photopub/docs/0000000437/26318548-a5f4-46e8-8373-8217d1483a1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__490dc30b_5563_47b8_b388_207eae9c5311
ELIN-563118-2016 | EL-295116-2015 | 5/30/2016 12:48:01 PM | ASSESS: EL: Final | png | #asFound | EL118 | Conductors Identified conductor or neutral conductor has not been properly identified | 1 | 1 | 2 20 amp a circuit court 240 volt hot water tanks were connected to the identified conductor used for one side of the line voltage connection. The identified conductor was not identified other than white at both the panel and hot water tank ends of the circuits. By jus can cause injuries to persons performing maintenance or alteration to these circuits | 1 | Conductors Identified conductor or neutral conductor has not been properly identified | Line_voltage_on_neutral_no_id.png | file://x:/photopub/docs/0000000435/d0428e5b-7171-4265-b620-15b2dde8350c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e7f02a28_f0f3_454a_b36e_891b67e61366
ELIN-583440-2016 | EL-374416-2016 | 5/30/2016 3:03:49 PM | ASSESS: EL: Final | png | #asFound | EL174 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | A 240 volt 15 amp residential swimming pool pump was found in service and it did not bear an approval label for electrical characteristics. Electrical equipment that is marked as certified by a recognized certification body may be unsafe and cause damage to property or injury to persons | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Motor_pool_pump_no_certification_label_.png | file://x:/photopub/docs/0000000435/f8c12642-0d9f-4c70-9b3b-6de20a64c4c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b23954f_4c46_4695_89b8_a2c222664abc
GAIN-586122-2016 | GA-339752-2016 | 6/1/2016 1:45:21 PM | ASSESS: GA: Final | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Found regulator for generator installed and in operation with relief vent opening 2 ' away from generator air inlet. If regulator begins to vent, raw gas could enter generator and cause explosion/fire. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Regulator_clearance.png | file://x:/photopub/docs/0000000437/c73f5aa6-8c92-41ab-9ae0-ea6ee0089d90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7df2e145_45c3_4d53_9f74_c2ff8789124e
BPVOP-583760-2016 | 2285550 | 5/26/2016 12:21:55 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Upon assessment of machine mounted horizontal air receiver (1.5m long and .5m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, it was determined that vessel has exceeded 20 years of service life without having complete examination (complete examination for vessel over 20 years shall include the use of surface and volumetric NDE testing as applicable, to determine thickness and identify defects such as cracking, corrosion and pitting). Minimum thickness of pressure boundary (shell, nozzle, weld etc.) determines the MAWP and presence of corrosion, cracking and pitting may cause failure of pressure boundary at a pressure well below MAWP. In the event of failure of pressure boundary, shooting/propelling effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Safety_order_not_followed.png | file://x:/photopub/docs/0000000435/ec4334bd-c73f-4c70-8cb9-e51c99cf5402.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69b56e45_e514_40dc_84c2_f4fd2533b940
BPVOP-583760-2016 | 2285550 | 5/26/2016 12:21:55 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Upon assessment of machine mounted horizontal air receiver (1.5m long and .5m diameter pressure vessel) with Maximum Allowable Working Pressure (MAWP) of 200psig, it was determined that vessel has exceeded 20 years of service life without having complete examination (complete examination for vessel over 20 years shall include the use of surface and volumetric NDE testing as applicable, to determine thickness and identify defects such as cracking, corrosion and pitting). Minimum thickness of pressure boundary (shell, nozzle, weld etc.) determines the MAWP and presence of corrosion, cracking and pitting may cause failure of pressure boundary at a pressure well below MAWP. In the event of failure of pressure boundary, shooting/propelling effect of flying object (caused by uncontrolled release of compressed air) may cause a severe incident. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Safety_valve.png | file://x:/photopub/docs/0000000435/2f8aabb8-8aaa-4341-904e-1658af63f63a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__69b56e45_e514_40dc_84c2_f4fd2533b940
ELIN-579566-2016 | EL-178081-2014 | 5/25/2016 9:17:40 AM | ASSESS: EL: Final | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 3 | This assessment found the service mast to be improperly bonded. There is a shock hazard should the mast become energized as the fault may not clear. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Mast_not_bonded.png | file://x:/photopub/docs/0000000434/d24c0839-cd16-4294-8541-89b9b7403273.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b2a669d_a67d_4d02_aab4_ad35e92c0b6b
ELIN-579633-2016 | EL-388499-2016 | 5/25/2016 2:33:17 PM | ASSESS: EL: Service Connection | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | This Assessment found a temporary service cable running across the sidewalk through the garden to the house. This cable comes directly from BC Hydro and is considered hazardous because it is unfused. There is a shock hazard should this cable become damaged | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cable_on_sidewalk.png | file://x:/photopub/docs/0000000434/888a56ed-16b7-4e4c-a303-54232277abaf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6f1b2f7b_244c_49c6_b2bb_43e372b8350f
GAIN-563942-2016 | GA-283673-2015 | 5/26/2016 9:50:44 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Dawson_COOP_RTU.png | file://x:/photopub/docs/0000000435/3cb8692b-f9eb-4577-b322-c67634a7aa5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2e1bb25_9418_4267_a827_4b82bc9d25d9
AMOP-586949-2016 | 2042524 | 6/1/2016 4:35:03 PM | ASSESS: AM OP: Periodic | png | #asFound | AM015 | Required operational strength does not exist. | 5 | 4 | It was observed that a structural ground cable has become disconnected. This creates a shock hazard in the case of a ground fault condition. | 5 | Required operational strength does not exist. | Disconnected_structural_ground.png | file://x:/photopub/docs/0000000437/5c5cbe63-1c59-461a-8449-efcbd3090171.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__17b3aaff_ec8f_49b0_828e_35993a081c10
ELIN-598140-2016 | EL-399838-2016 | 6/23/2016 12:49:18 PM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 3 | Existing service conductors intended to be re connected were deteriorated to the point that the insulation was missing on the red conductor where the Utility connects. This condition could result in potential shock and fire hazards. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | Exposed_conductor.png | file://x:/photopub/docs/0000000447/21298284-6797-46af-96f0-ff772b5d5701.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__81f25aca_a870_4a94_8ffd_54c7e9b7f29c
ELIN-597832-2016 | EL-374229-2016 | 6/23/2016 11:35:33 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | The wire used in the conduit is not an approved type for a wet location and therefore the insulation jacket will deteriorate to a failed state over a period of time. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | NMD_in_slab_on_grade_conduit.png | file://x:/photopub/docs/0000000447/c836f53e-fca0-4d6f-8857-74c862a2a517.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6bee5091_eb9b_4c69_b10b_6b273547984f
BPVOP-597643-2016 | 2281068 | 6/21/2016 | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | The discharge capacity of the safety valves was less than the required minimum relief capacity of the hot water boiler with a maximum allowable working pressure of 160psig and maximum allowable working temperature of 250 Fahrenheit. If left unchanged, this could result in subsequent series damage to the equipment and personal injury. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_valve.png | file://x:/photopub/docs/0000000446/5c112ee7-d2b0-4973-9c7a-ff815c3d5567.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82562807_00b6_4795_8a17_c6773282c7f3
ELIN-596252-2016 | EL-399577-2016 | 6/23/2016 1:37:53 PM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The service panel is not rated as weatherproof and it is in a cabinet with no bottom. This will allow water to get into the panel and corrode the parts inside. This damage may effect the operation of the over current device and create a shock hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Service_panel.png | file://x:/photopub/docs/0000000447/974f54ab-e157-4426-a1b7-88d26add6788.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__caccb61d_3092_4a9d_b456_3a649f8b3919
ELIN-596748-2016 | UW-399954-2016 | 6/23/2016 9:16:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The service distribution covers are missing and have been replaced with plywood. This cover is not appropriate and can be damaged very easily. This would expose the energized conductors and create a shock hazard for maintenance people. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Meter_stack.png | file://x:/photopub/docs/0000000447/64d84352-c4e3-40bb-bfdb-bb2d8e3854a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1e7043e_8aa9_469a_a3d1_245825df59b0
ELIN-596748-2016 | UW-399954-2016 | 6/23/2016 9:16:06 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | The service distribution covers are missing and have been replaced with plywood. This cover is not appropriate and can be damaged very easily. This would expose the energized conductors and create a shock hazard for maintenance people. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Storage.png | file://x:/photopub/docs/0000000447/9d3067d8-9fee-42c2-83ab-bc7685486ced.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e1e7043e_8aa9_469a_a3d1_245825df59b0
BPVOP-595794-2016 | 2271917 | 6/17/2016 12:45:28 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 |  | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Staining.png | file://x:/photopub/docs/0000000444/10f73f30-88d5-427b-94b9-2ee2955dd375.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__466b5b06_63e3_4a41_8264_babef6f8ab61
BPVOP-596224-2016 | 3060583 | 6/17/2016 10:29:58 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Ammonia Receiver with MAWP of 250 psig, was found that the PRD was installed in June 2009 and was overdue as per CSA B52. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_.png | file://x:/photopub/docs/0000000444/53b659d4-099b-4f99-ae60-cdb5c3df2cc5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b77ec1f8_0c3b_461f_bf7e_058cb98f643a
BPVIN-595835-2016 | BPV-399407-2016 | 6/17/2016 10:06:15 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Ammonia Heat Recovery Condenser with MAWP of 250 psig, it was found that the Pressure Relief Device was installed in June 2009 and is currently overdue for servicing as per the requirements in the CSA B52 code. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD.png | file://x:/photopub/docs/0000000444/a4f8cf47-7cf8-49be-bd2b-c62dd3487f7c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a7d70f20_e5b8_4e41_91c8_e6efdd000651
ELIN-594382-2016 | EL-386798-2016 | 6/17/2016 2:36:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The service ground conductor is not terminated on the neutral bus. This could possibly create a shock hazard during a fault. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_plate_conductor.png | file://x:/photopub/docs/0000000444/0e484b74-a87a-4bff-b706-396837a32c44.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3dc236bc_c2fc_4136_94fc_5bdf354bb29f
ELIN-594382-2016 | EL-386798-2016 | 6/17/2016 2:36:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The service ground conductor is not terminated on the neutral bus. This could possibly create a shock hazard during a fault. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Receptacles_covers_missing.png | file://x:/photopub/docs/0000000444/885073f0-7f73-4f41-bd17-e480b4941d76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3dc236bc_c2fc_4136_94fc_5bdf354bb29f
ELIN-594382-2016 | EL-386798-2016 | 6/17/2016 2:36:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The service ground conductor is not terminated on the neutral bus. This could possibly create a shock hazard during a fault. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Receptacles.png | file://x:/photopub/docs/0000000444/36dc7d1b-44af-4bcd-9a0e-35ae97f5fb95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3dc236bc_c2fc_4136_94fc_5bdf354bb29f
ELIN-594382-2016 | EL-386798-2016 | 6/17/2016 2:36:05 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 3 | The service ground conductor is not terminated on the neutral bus. This could possibly create a shock hazard during a fault. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_conductor_on_bond.png | file://x:/photopub/docs/0000000444/1ab5ef98-0cab-4ad5-a98f-c5ee868c3475.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3dc236bc_c2fc_4136_94fc_5bdf354bb29f
ELIN-593437-2016 | EL-395459-2016 | 6/16/2016 2:33:54 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | This Solar assessment found Solar panels rated maximum 20A tied into 30A breakers. Also these breakers are required to be located at the opposite end of the main breaker; instead they were adjacent. There is a risk of overloading the wires at the solar panels and the busbar in the electrical panel; therefore presenting a fire hazard. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | 30A_breakers.png | file://x:/photopub/docs/0000000444/c223281b-c4e1-4def-b3fa-bb91959e2c92.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4f1eeba_76bf_4c75_b4a1_9928cdcba0c5
ELIN-593437-2016 | EL-395459-2016 | 6/16/2016 2:33:54 PM | ASSESS: EL: Final | png | #asFound | EL055 | Protection and control Overcurrent devices do not adequately protect conductors | 4 | 4 | This Solar assessment found Solar panels rated maximum 20A tied into 30A breakers. Also these breakers are required to be located at the opposite end of the main breaker; instead they were adjacent. There is a risk of overloading the wires at the solar panels and the busbar in the electrical panel; therefore presenting a fire hazard. | 4 | Protection and control Overcurrent devices do not adequately protect conductors | Label.png | file://x:/photopub/docs/0000000444/fe74c48f-2cd9-42a6-ab30-e56b7abde6d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c4f1eeba_76bf_4c75_b4a1_9928cdcba0c5
GAHE-597636-2016 | HE-400596-2016 | 6/21/2016 9:53:18 AM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | While inspecting a unit heater in warehouse I noticed that on another unit heater the vent is dislodged. Gas is still connected to appliance. Appliance can be turned on and the products of combustion will be vented into warehouse space, workers on warehouse will be breathing in products of combustion with possible CO Poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Dislodged_vent.png | file://x:/photopub/docs/0000000445/474217de-3ddf-4e28-9e00-359244f858c2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3e6603fa_c17b_4377_b386_111e81c7e3d0
ELIN-468017-2015 | EL-267641-2015 | 10/29/2015 11:41:20 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Db2 used above ground. This type of conduit is easily damaged and is not permitted to be used above ground. This is a shock and fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000445/aad1777c-c11c-489a-9ea2-39c593aa9675.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ad258bc_b28d_404a_8215_6f9f0154ed1f
ELIN-594228-2016 | EL-342503-2016 | 6/16/2016 1:02:14 PM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | 15 amp, 120 volt armoured cable not terminated in box. This is a thermal issue. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | AC90_not_terminated_in_box.png | file://x:/photopub/docs/0000000444/fed4d754-7a50-4058-825d-54d73c2bf573.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c41a4a1a_216a_4ea9_8b24_23e2eb93cd39
ELHE-597183-2016 | HE-400227-2016 | 6/20/2016 10:29:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Motel unit in general disrepair with emphasis on secondary overhead distribution. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Main_service_pole_in_poor_condition.png | file://x:/photopub/docs/0000000445/0586f8c2-d2ac-42ce-8ad7-042b421cfb0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9b3921a_e21a_4dc2_b5bc_67fc0cfc3ab5
ELHE-597183-2016 | HE-400227-2016 | 6/20/2016 10:29:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Motel unit in general disrepair with emphasis on secondary overhead distribution. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Secondary_pole_2_falling_down.png | file://x:/photopub/docs/0000000445/52e162a1-f1b1-440c-b27f-b0cb3e155c0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9b3921a_e21a_4dc2_b5bc_67fc0cfc3ab5
ELHE-597183-2016 | HE-400227-2016 | 6/20/2016 10:29:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Motel unit in general disrepair with emphasis on secondary overhead distribution. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Overhead_clearances.png | file://x:/photopub/docs/0000000445/95947c52-d938-4f3a-93dd-f290711b6932.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9b3921a_e21a_4dc2_b5bc_67fc0cfc3ab5
ELHE-597183-2016 | HE-400227-2016 | 6/20/2016 10:29:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Motel unit in general disrepair with emphasis on secondary overhead distribution. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Frontage_of_hotel_unit.png | file://x:/photopub/docs/0000000445/405b3c03-9f52-4207-a28e-6ebe82923c9d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9b3921a_e21a_4dc2_b5bc_67fc0cfc3ab5
ELHE-597183-2016 | HE-400227-2016 | 6/20/2016 10:29:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Motel unit in general disrepair with emphasis on secondary overhead distribution. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Secondary_pole_3_poor_condition.png | file://x:/photopub/docs/0000000445/0a24a552-7018-44a5-9274-3bb0fab7e5aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9b3921a_e21a_4dc2_b5bc_67fc0cfc3ab5
ELIN-597290-2016 | EL-396256-2016 | 6/20/2016 2:22:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Electrical cables not approved for the location may corrode and create a fire or shock hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Residential_range_plug_and_receptacle_without_WP_covers.png | file://x:/photopub/docs/0000000445/c4e84605-e9d7-4447-84ee-bc26d34f7403.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25e46c5f_9c5a_427f_b9d1_eaf6f99b06aa
ELIN-597290-2016 | EL-396256-2016 | 6/20/2016 2:22:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Electrical cables not approved for the location may corrode and create a fire or shock hazard | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | AC90_cable_in_damp_locations.png | file://x:/photopub/docs/0000000445/88da7e8b-bac4-4aa1-aa25-6e9238b34fdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__25e46c5f_9c5a_427f_b9d1_eaf6f99b06aa
ELIN-595992-2016 | EL-353908-2016 | 6/20/2016 2:25:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 3 | This assessment found the lower half of the house to be wired and plumbed in a manner consistent with a suite. Panels are required to be installed in each unit or common area so the each can be disconnected without affecting the other. There is a hazard that the unit without access to its breakers might be unable to reset lost power to essential equipment, including smoke detectors. In an emergency there may not be access to shut the power off. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Kitchen.png | file://x:/photopub/docs/0000000445/3e8bd93b-b4c7-4a10-a7c7-edee1fa1fe46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42fcfc1b_a198_41cb_b4de_7880050da3df
ELIN-595992-2016 | EL-353908-2016 | 6/20/2016 2:25:30 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL063 | General Location of equipment does not allow for proper access to disconnecting means | 4 | 3 | This assessment found the lower half of the house to be wired and plumbed in a manner consistent with a suite. Panels are required to be installed in each unit or common area so the each can be disconnected without affecting the other. There is a hazard that the unit without access to its breakers might be unable to reset lost power to essential equipment, including smoke detectors. In an emergency there may not be access to shut the power off. | 4 | General Location of equipment does not allow for proper access to disconnecting means | Suite.png | file://x:/photopub/docs/0000000445/aa1dee6a-514f-41a3-b824-53336ce8c9ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__42fcfc1b_a198_41cb_b4de_7880050da3df
ELIN-596154-2016 | UW-399600-2016 | 6/16/2016 7:12:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | HV equipment not maintained presents an increased chance of switch failure during normal operation and during switching operations. Hedging which grows up into lines presents a fire and shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Hedge_and_load_break_switch.png | file://x:/photopub/docs/0000000445/cd7cfaa4-501f-41b3-a346-e02f53cf129d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0786d2aa_1972_49e4_a80e_b4d64447d59f
ELIN-596154-2016 | UW-399600-2016 | 6/16/2016 7:12:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | HV equipment not maintained presents an increased chance of switch failure during normal operation and during switching operations. Hedging which grows up into lines presents a fire and shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Close_up_load_break_switch_assembly.png | file://x:/photopub/docs/0000000445/cc120d1a-c48a-40e2-ad30-8e0f396427fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0786d2aa_1972_49e4_a80e_b4d64447d59f
ELIN-596154-2016 | UW-399600-2016 | 6/16/2016 7:12:17 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | HV equipment not maintained presents an increased chance of switch failure during normal operation and during switching operations. Hedging which grows up into lines presents a fire and shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Closeup_load_break_Sw_and_metering_equipment.png | file://x:/photopub/docs/0000000445/f7d8490f-6b1d-4838-a2c7-ef52fa68d976.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0786d2aa_1972_49e4_a80e_b4d64447d59f
ELIN-583500-2016 | EL-376467-2016 | 6/20/2016 8:35:16 AM | ASSESS: EL: Final | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Conductive armour jackets which could become energized are not bonded to ground. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Fuel_dispenser_wiring.png | file://x:/photopub/docs/0000000445/f922691b-92a0-48e6-b235-2d4c5bebc9de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b24d0978_621c_4d90_a89f_638f5208207c
ELIN-583500-2016 | EL-376467-2016 | 6/20/2016 8:35:16 AM | ASSESS: EL: Final | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Conductive armour jackets which could become energized are not bonded to ground. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Insufficient_marking_at_distribution_panels.png | file://x:/photopub/docs/0000000445/1b770261-e70d-4426-9e2b-024b449b6ac6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b24d0978_621c_4d90_a89f_638f5208207c
ELIN-583500-2016 | EL-376467-2016 | 6/20/2016 8:35:16 AM | ASSESS: EL: Final | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Conductive armour jackets which could become energized are not bonded to ground. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Storage_building_wiring.png | file://x:/photopub/docs/0000000445/a9acd6ef-5cb5-4051-8697-7c63df01fbcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b24d0978_621c_4d90_a89f_638f5208207c
ELIN-583500-2016 | EL-376467-2016 | 6/20/2016 8:35:16 AM | ASSESS: EL: Final | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | Conductive armour jackets which could become energized are not bonded to ground. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Armoured_cable_termination_in_PVC_box.png | file://x:/photopub/docs/0000000445/c4aa9693-e10b-4195-bcbb-c0ca5237af4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b24d0978_621c_4d90_a89f_638f5208207c
BPVIN-546035-2016 | BPV-366966-2016 | 6/21/2016 10:17:50 AM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 | Upon assessment it is determined that Tridicator pressure and temperature range is above code specified but within operating range. There is no way to verify abnormal operating condition with accuracy required to take timely action. | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | TRIDICATOR.png | file://x:/photopub/docs/0000000445/028b8a9f-f047-4081-a300-f57f4a9e50ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2302ada_792b_4689_8596_90e5203ea8fd
BPVOP-598029-2016 | 2885658 | 6/21/2016 1:12:54 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP111 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | 3 | 3 | During the inspection of a Hot Water Boiler with MAWP of 160 Psig was found that the minimum required safety relief capacity is 1,750,000 BTU/HR and the Actual Safety Relief Valve capacity is 1,682,000 BTU/hr. In case of a failure the SRV will not be able to relief all the hot water with the burners firing. | 3 | 3.0.1 Safeties will not function - Pressure Relief Device under capacity | Safety_Relief_Valve_under_capacity.png | file://x:/photopub/docs/0000000445/9cc2f47c-7121-48ed-a7b7-824cbc6051fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8058b77a_94c2_4ef9_b21f_1c4ffea5aa93
BPVOP-598027-2016 | 2296022 | 6/21/2016 1:43:26 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a Hot Water Boiler with MAWP of 160 psig, was found that the Safety Relief Valve was installed in Oct 2008 and was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_Relief_Valve_.png | file://x:/photopub/docs/0000000445/3e69ea96-c2ca-4fd5-bfef-f0bc0a7345a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75016c8f_8abd_4084_8654_a6b0fb6300bb
ELIN-597401-2016 | EL-399481-2016 | 6/22/2016 8:02:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found existing connected and energized 120/240 volt 70 amp combination panelboard removed from its existing location hanging unsupported with panelboard cover off leaving exposed energized conductors and bus bars. When panelboard is energized and not supported with panel cover off, the exposed energized conductors and bus bars are an electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Energized_panel_hanging_unsupported_with_cover_missing_3.png | file://x:/photopub/docs/0000000446/03155ef1-5050-4fb7-b5e4-b390ec43bc09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae97218_0b25_4ce4_9502_a5f012d50fc0
ELIN-597401-2016 | EL-399481-2016 | 6/22/2016 8:02:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found existing connected and energized 120/240 volt 70 amp combination panelboard removed from its existing location hanging unsupported with panelboard cover off leaving exposed energized conductors and bus bars. When panelboard is energized and not supported with panel cover off, the exposed energized conductors and bus bars are an electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Energized_panel_hanging_unsupported_with_cover_missing_filler_plates_where_breaker_missing.png | file://x:/photopub/docs/0000000446/d6178939-7b79-490c-be5b-405278cbe0e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae97218_0b25_4ce4_9502_a5f012d50fc0
ELIN-597401-2016 | EL-399481-2016 | 6/22/2016 8:02:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found existing connected and energized 120/240 volt 70 amp combination panelboard removed from its existing location hanging unsupported with panelboard cover off leaving exposed energized conductors and bus bars. When panelboard is energized and not supported with panel cover off, the exposed energized conductors and bus bars are an electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Energized_panel_hanging_unsupported_with_cover_missing_2.png | file://x:/photopub/docs/0000000446/59b5a8de-72cd-4cde-ae4c-1e68018661cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae97218_0b25_4ce4_9502_a5f012d50fc0
ELIN-597401-2016 | EL-399481-2016 | 6/22/2016 8:02:22 AM | ASSESS: EL: Service Connection | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found existing connected and energized 120/240 volt 70 amp combination panelboard removed from its existing location hanging unsupported with panelboard cover off leaving exposed energized conductors and bus bars. When panelboard is energized and not supported with panel cover off, the exposed energized conductors and bus bars are an electrical shock or fire hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Energized_panel_hanging_unsupported_with_cover_missing_1.png | file://x:/photopub/docs/0000000446/eaa5dd4a-08c2-48e2-a91a-5b9bf6b061cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8ae97218_0b25_4ce4_9502_a5f012d50fc0
ELIN-597644-2016 | EL-329823-2015 | 6/21/2016 11:30:00 AM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | Potential stray voltage can raise the voltage potential level on the conductive metal piping therefore creating a shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_piping_bond_incomplete.png | file://x:/photopub/docs/0000000445/aff25125-5d59-418b-90d3-cc8949f80941.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80e6230d_b9fc_43a7_a370_751970118726
GAOP-353700-2015 | 2170978 | 6/17/2016 8:56:58 PM | ASSESS: GA OP: Periodic | png | #asFound | GA026 | No protection high traffic | 5 | 5 | With no protection from vehicle traffic the propane tank could be hit by a vehicle causing damage and leaks of propane. Leaking propane could cause a fire and loss of property and or life. | 5 | No protection high traffic | Tank_to_close_to_fuel_tanks_.png | file://x:/photopub/docs/0000000445/31d55ca6-4772-4882-ab3f-c90cd5056147.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feaea4be_b9e0_4d69_a768_352910ea71cc
GAIN-540709-2016 | GA-343686-2016 | 6/17/2016 6:07:57 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | The first stage propane regulator is not mounted above the liquid level of the tank. This could allow liquid to enter the regulator causing it to fail and damage the equipment it serves. The damage could cause the equipment to over fire creating a fire hazard. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Piping_not_protected_from_snow_or_traffic_damage_.png | file://x:/photopub/docs/0000000445/3ecc3375-4f84-4324-9682-402650d9721e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bf846ca_fbd5_4eb6_83f6_72a8e155b84b
GAIN-540709-2016 | GA-343686-2016 | 6/17/2016 6:07:57 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | The first stage propane regulator is not mounted above the liquid level of the tank. This could allow liquid to enter the regulator causing it to fail and damage the equipment it serves. The damage could cause the equipment to over fire creating a fire hazard. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | No_proper_swing_joint_or_valve.png | file://x:/photopub/docs/0000000445/1e353ae9-6330-4a61-892d-07a8397943e9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bf846ca_fbd5_4eb6_83f6_72a8e155b84b
GAIN-540709-2016 | GA-343686-2016 | 6/17/2016 6:07:57 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | The first stage propane regulator is not mounted above the liquid level of the tank. This could allow liquid to enter the regulator causing it to fail and damage the equipment it serves. The damage could cause the equipment to over fire creating a fire hazard. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Regulator_mounted_below_liquid_level_of_tank.png | file://x:/photopub/docs/0000000445/885ef1e2-c10c-495e-a932-b7ae9d45cc17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bf846ca_fbd5_4eb6_83f6_72a8e155b84b
GAOP-353700-2015 | 2170978 | 6/17/2016 8:56:58 PM | ASSESS: GA OP: Periodic | png | #asFound | GA026 | No protection high traffic | 5 | 5 | With no protection from vehicle traffic the propane tank could be hit by a vehicle causing damage and leaks of propane. Leaking propane could cause a fire and loss of property and or life. | 5 | No protection high traffic | No_protection_of_propane_tank_.png | file://x:/photopub/docs/0000000445/5043d3b0-3bf6-48e5-8bd4-d10a49e06a6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feaea4be_b9e0_4d69_a768_352910ea71cc
GAIN-540709-2016 | GA-343686-2016 | 6/17/2016 6:07:57 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | The first stage propane regulator is not mounted above the liquid level of the tank. This could allow liquid to enter the regulator causing it to fail and damage the equipment it serves. The damage could cause the equipment to over fire creating a fire hazard. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Pipe_not_supported_.png | file://x:/photopub/docs/0000000445/8b7c10b2-e071-4f56-9b2f-a47329720b11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bf846ca_fbd5_4eb6_83f6_72a8e155b84b
GAOP-538090-2016 | 3038859 | 6/17/2016 8:05:28 PM | ASSESS: GA OP: Periodic | png | #asFound | GA025 | Inadequate protection high traffic | 4 | 4 | The protective posts around the propane tank are damaged and do not protect the tank from vehicle traffic. Moving vehicles could damage or rupture the tank or piping causing a propane leak and possible fire. | 4 | Inadequate protection high traffic | Damaged_protection_posts_and_truck_traffic_.png | file://x:/photopub/docs/0000000445/d9206b68-bc67-426d-9d23-b8772324cec6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bb481a76_da97_49e8_9582_9bf886b55f32
GAOP-353700-2015 | 2170978 | 6/17/2016 8:56:58 PM | ASSESS: GA OP: Periodic | png | #asFound | GA026 | No protection high traffic | 5 | 5 | With no protection from vehicle traffic the propane tank could be hit by a vehicle causing damage and leaks of propane. Leaking propane could cause a fire and loss of property and or life. | 5 | No protection high traffic | No_protection_from_vehicle_traffic_.png | file://x:/photopub/docs/0000000445/2de9fe34-3580-495c-984f-e8878a041e1a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feaea4be_b9e0_4d69_a768_352910ea71cc
GAIN-540709-2016 | GA-343686-2016 | 6/17/2016 6:07:57 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 3 | The first stage propane regulator is not mounted above the liquid level of the tank. This could allow liquid to enter the regulator causing it to fail and damage the equipment it serves. The damage could cause the equipment to over fire creating a fire hazard. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | Pipe_not_painted_No_valve_or_dirt_pocket_upstream_of_regulator_.png | file://x:/photopub/docs/0000000445/8d22e6f2-7329-40ce-a967-5b62c55edcb6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bf846ca_fbd5_4eb6_83f6_72a8e155b84b
GAOP-353700-2015 | 2170978 | 6/17/2016 8:56:58 PM | ASSESS: GA OP: Periodic | png | #asFound | GA026 | No protection high traffic | 5 | 5 | With no protection from vehicle traffic the propane tank could be hit by a vehicle causing damage and leaks of propane. Leaking propane could cause a fire and loss of property and or life. | 5 | No protection high traffic | Tank_supported_on_wood_blocks_.png | file://x:/photopub/docs/0000000445/22b97fbc-5160-4b00-83f3-30fbc99ba60a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feaea4be_b9e0_4d69_a768_352910ea71cc
GAOP-353700-2015 | 2170978 | 6/17/2016 8:56:58 PM | ASSESS: GA OP: Periodic | png | #asFound | GA026 | No protection high traffic | 5 | 5 | With no protection from vehicle traffic the propane tank could be hit by a vehicle causing damage and leaks of propane. Leaking propane could cause a fire and loss of property and or life. | 5 | No protection high traffic | Improper_electrical_connection_.png | file://x:/photopub/docs/0000000445/5abf7893-c710-4c60-bf58-8d56d02b661f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__feaea4be_b9e0_4d69_a768_352910ea71cc
ELHE-596570-2016 | HE-399846-2016 | 6/17/2016 2:46:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage electrical equipment. such as high voltage 14.4 KV rated power poles and overhead conductors, are not supported adequately and poles are damaged and rotted and could fall down to earth. When high voltage electrical equipment is damaged and is not maintained the electrical equipment could fall down to earth and could come into contact with people or property and could become an electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Pole_rotted_out_and_non-compliant_and_unsafe_.png | file://x:/photopub/docs/0000000444/435db2a4-79ea-42f1-942d-84a4a3f94587.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__979db999_df56_4f1a_845c_a5390a8251b9
ELHE-596570-2016 | HE-399846-2016 | 6/17/2016 2:46:35 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL013 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | 5 | 5 | Found high voltage electrical equipment. such as high voltage 14.4 KV rated power poles and overhead conductors, are not supported adequately and poles are damaged and rotted and could fall down to earth. When high voltage electrical equipment is damaged and is not maintained the electrical equipment could fall down to earth and could come into contact with people or property and could become an electrical fire or shock hazard to people and property. | 5 | Conductors are exposed to accidental contact by persons Overhead high voltage conductors are not attached or supported adequately; Clearances are not adequate. | Pole_leaning_to_possibly_fall_over.png | file://x:/photopub/docs/0000000444/8aaa0a95-e429-40aa-ab67-3702814915be.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__979db999_df56_4f1a_845c_a5390a8251b9
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Space4.png | file://x:/photopub/docs/0000000445/74fa3610-79ab-4be6-bed3-acf86a6230c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Space1.png | file://x:/photopub/docs/0000000445/3e444070-9b64-4ee4-9c45-7cee5a847777.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Space2.png | file://x:/photopub/docs/0000000445/3f407ee6-252c-4fab-b0e1-d63e257355ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Space3.png | file://x:/photopub/docs/0000000445/7f79cd3a-6dce-46ec-a8f0-61c2247e58b8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Opening3.png | file://x:/photopub/docs/0000000445/d17b2982-6f16-46d9-8bdb-b822de4a0f7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Opening1.png | file://x:/photopub/docs/0000000445/c5299a1d-be2f-4549-ace2-4286c0c4d4d6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Service.png | file://x:/photopub/docs/0000000445/96bd3719-3c54-4b87-8e62-63dcf48f19a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
ELOP-346726-2015 | 3997666 | 6/20/2016 3:58:19 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Opening2.png | file://x:/photopub/docs/0000000445/5cbcb31b-695b-42f5-9927-95f0b1b8e7e5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78161443_a830_4c27_81ed_dfb145a2240e
BPVOP-598754-2016 | 2288754 | 6/22/2016 10:23:26 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP065 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | 4 | 4 | During the inspection of an air receiver manufactured in 1955 and with MAWP of 200 psig was found a 15 mm long crack at the toe of the weld between the shell and the leg. This crack can propagate into the shell and result in fracture and a rapid release of air pressure. | 4 | 1.2.2 Boiler leakage: procedure - Boiler tube-sheet or ligaments cracks which are leaking. | Crack.png | file://x:/photopub/docs/0000000446/94d93fec-7002-4ae6-a111-6ec65919c052.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7d88ce0_ee06_4f6c_afe1_49728c1fdb37
BPVOP-576305-2016 | 2252867 | 6/22/2016 10:01:44 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of a High Pressure Steam Boiler with MAWP of 150 psig, was found that the Safety Relief Valve was installed in April 2009 and was overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Overdue_SV_.png | file://x:/photopub/docs/0000000446/504b1795-1793-4911-ad13-3c1649e16609.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51c74e32_8d7b_4845_b778_e56b58b2a6f8
ELIN-595698-2016 | EL-399300-2016 | 6/22/2016 4:55:58 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The attachment clevis for the feeder wiring to the workshop is threaded into a tree. This would allow for the clevis to loosen over time when the tree expands due to growth and the feeder wiring falling to the ground. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Attachment_clevis_location.png | file://x:/photopub/docs/0000000446/9774edf7-867f-4d31-aea3-83f655480523.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11cbf582_2c97_49ae_b537_4376052c6106
ELIN-595698-2016 | EL-399300-2016 | 6/22/2016 4:55:58 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The attachment clevis for the feeder wiring to the workshop is threaded into a tree. This would allow for the clevis to loosen over time when the tree expands due to growth and the feeder wiring falling to the ground. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Branch_cct_wiring_NMD.png | file://x:/photopub/docs/0000000446/a879762e-0cd4-4c38-9242-872a71a16584.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11cbf582_2c97_49ae_b537_4376052c6106
BPVOP-594052-2016 | 3097998 | 6/17/2016 9:36:17 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scaling.png | file://x:/photopub/docs/0000000444/a9ca1677-1864-4d2d-b97f-f527db6b0b12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95c8d675_ba76_4485_8002_87bd82c9e983
ELIN-597258-2016 | UW-400272-2016 | 6/16/2016 11:18:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | This assessment was on a commercial site and found un-permitted electrical wiring being installed into the main service panel. The panels cover was missing and according to the owner is lost. The exposed energized buss presents a shock and fire hazard. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Underground_shallow.png | file://x:/photopub/docs/0000000445/272a184a-3e9d-48bb-a66c-123d23177342.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba3141e_f68d_4e52_87da_b2b26ef035c0
ELIN-597258-2016 | UW-400272-2016 | 6/16/2016 11:18:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | This assessment was on a commercial site and found un-permitted electrical wiring being installed into the main service panel. The panels cover was missing and according to the owner is lost. The exposed energized buss presents a shock and fire hazard. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Underground_not_to_depth.png | file://x:/photopub/docs/0000000445/3f0ff95b-d55f-4f69-b489-d37c00fbf36e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba3141e_f68d_4e52_87da_b2b26ef035c0
ELIN-597258-2016 | UW-400272-2016 | 6/16/2016 11:18:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | This assessment was on a commercial site and found un-permitted electrical wiring being installed into the main service panel. The panels cover was missing and according to the owner is lost. The exposed energized buss presents a shock and fire hazard. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Panel_no_cover.png | file://x:/photopub/docs/0000000445/67927163-b520-43e0-9825-4333bc527fb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba3141e_f68d_4e52_87da_b2b26ef035c0
ELIN-597258-2016 | UW-400272-2016 | 6/16/2016 11:18:56 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL018 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | 4 | 4 | This assessment was on a commercial site and found un-permitted electrical wiring being installed into the main service panel. The panels cover was missing and according to the owner is lost. The exposed energized buss presents a shock and fire hazard. | 4 | Equipment may not contain thermal energy during fault or overheating event. Covers are not properly installed | Service_cover_missing.png | file://x:/photopub/docs/0000000445/78384717-d650-4097-af3d-dd84d9a6ca9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba3141e_f68d_4e52_87da_b2b26ef035c0
BPVOP-596397-2016 | 3098002 | 6/17/2016 10:19:32 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scaling.png | file://x:/photopub/docs/0000000444/4dbae266-391d-4511-813e-ccaa9296e191.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c112675_c751_4aa6_af0f_7a9afe60231e
ELOP-529959-2016 | EL-347462-2016 | 6/20/2016 4:14:49 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Permanent structures are not permitted to be built below overhead lines. In this rural campground installation a washroom facility was constructed by a previous owner under a BC Hydro high voltage line. The facility has been closed to the public but cannot be left in its current location. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | High_voltage_line_over_washroom.png | file://x:/photopub/docs/0000000445/b17ceb34-e98a-4153-9738-f3582918db83.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf22de50_4803_4ee6_afc5_2a2c0c633279
ELIN-423925-2015 | 4064840 | 6/17/2016 4:14:07 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | Electrical fixtures must installed over junction boxes to reduce the chance of accidental contact by persons or objects. In this floating camp a few temporary fixtures had been installed and the permanent fixtures never replaced them at the end of the job. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Out_of_reach.png | file://x:/photopub/docs/0000000446/06d0776b-3171-4f04-8a16-c4c3a1205c9b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eceaf83_82e9_43ef_a293_cbadf0e50364
GAIN-594921-2016 | GA-219439-2015 | 6/20/2016 10:03:40 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Seven of eight tube heaters connected with metallic gas connectors, during the life of the installation the movement of the tube heaters will cause fatigue on the metal connecter causing a gas leak and potential fire or explosion | 2 | Certified appliance connector installed but not approved for application | KMS_1.png | file://x:/photopub/docs/0000000445/f87f7ec3-327e-4354-a1ed-3a5f58daa609.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fde5acc6_7674_49c0_becb_2f62a02949a5
GAIN-594921-2016 | GA-219439-2015 | 6/20/2016 10:03:40 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Seven of eight tube heaters connected with metallic gas connectors, during the life of the installation the movement of the tube heaters will cause fatigue on the metal connecter causing a gas leak and potential fire or explosion | 2 | Certified appliance connector installed but not approved for application | KMS_2.png | file://x:/photopub/docs/0000000445/dd509882-06e5-4212-9343-1956e92ec932.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fde5acc6_7674_49c0_becb_2f62a02949a5
GAIN-595689-2016 | GA-382076-2016 | 6/20/2016 3:09:22 PM | ASSESS: GA: Final | png | #asFound | GA137 | Clearance to combustible not met | 3 | 3 | Clearance to combustible material not met. Certified outdoor BBQ not rated for use under a combustible structure, installed under a combustible roof, could cause a fire. | 3 | Clearance to combustible not met | 1780_mills_rd1.png | file://x:/photopub/docs/0000000445/4254cd84-75e3-4325-818b-1bbb9feeab14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da88001f_5f21_4ae5_bc48_32d882ee0e29
ELHE-596131-2016 | HE-399578-2016 | 6/20/2016 9:30:55 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL193 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | 5 | 5 | The start/stop control for the booster pump fed from the 60 amp 240 volt breaker is not mounted within the enclosure and is exposed to accidental contact to personnel operating the equipment. This is a shock hazard | 5 | Site condition, Risk Reg EL-26-2017 Energized, no qualified person, energized parts. | Booster_starter.png | file://x:/photopub/docs/0000000445/7d72b08b-3a00-4d08-bef0-070196e63b21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__13d0eb9b_55a3_4b53_9879_49eb6a78939a
ELIN-594364-2016 | EL-383831-2016 | 6/20/2016 10:07:25 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | A 20A 120V GFCI receptacle is being fed from a 15A 1P breaker. A 20A rated cord connected device could be used in this outlet over loading the 15A wiring and breaker, this could result in equipment damage. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | GFCI.png | file://x:/photopub/docs/0000000445/b777f41c-db98-4ed2-b3ab-13141275e5b9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__34fab582_b351_47fd_b8ee_ad3305913610
ELIN-488959-2015 | EL-267651-2015 | 6/16/2016 8:05:15 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Db2 containing Service conductors installed above ground. This is a hazard as this type of conduit is easily damaged and is not permitted to be installed above ground. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | D.png | file://x:/photopub/docs/0000000445/db92564d-2f8f-4584-bc20-af57c982a5de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b7a5632_6d33_43c0_aebd_f54c05a68014
ELIN-589737-2016 | EL-394453-2016 | 6/17/2016 11:11:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Covers are required to be installed on energized electrical panels. This is required to prevent accidental contact with energized parts of the panel, to prevent mechanical damage to the internal components of the panel, and to contain thermal energy from a fault within the panel. This installation of a service panel in a shop on a residential property has a service panel that does not have the cover installed on the branch circuit section of the panel. This has left open bus bars accessible to contact. The main circuit breaker was turned off at the time of the inspection however the breaker was not locked off and was in a location accessible to persons. This is a potential shock and fire hazard should the breaker be turned on and a person or object contacts the exposed energized parts. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_panel_bus_bars_in_shop.png | file://x:/photopub/docs/0000000445/28620604-b03b-408d-ba43-a225eb7d6637.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af81b801_4ab7_45dc_adc1_165902d7755b
ELIN-589737-2016 | EL-394453-2016 | 6/17/2016 11:11:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Covers are required to be installed on energized electrical panels. This is required to prevent accidental contact with energized parts of the panel, to prevent mechanical damage to the internal components of the panel, and to contain thermal energy from a fault within the panel. This installation of a service panel in a shop on a residential property has a service panel that does not have the cover installed on the branch circuit section of the panel. This has left open bus bars accessible to contact. The main circuit breaker was turned off at the time of the inspection however the breaker was not locked off and was in a location accessible to persons. This is a potential shock and fire hazard should the breaker be turned on and a person or object contacts the exposed energized parts. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Shop_service_meter_installed.png | file://x:/photopub/docs/0000000445/d9d2514b-dcb4-4c33-afa2-1ef63ee376ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af81b801_4ab7_45dc_adc1_165902d7755b
ELIN-589737-2016 | EL-394453-2016 | 6/17/2016 11:11:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Covers are required to be installed on energized electrical panels. This is required to prevent accidental contact with energized parts of the panel, to prevent mechanical damage to the internal components of the panel, and to contain thermal energy from a fault within the panel. This installation of a service panel in a shop on a residential property has a service panel that does not have the cover installed on the branch circuit section of the panel. This has left open bus bars accessible to contact. The main circuit breaker was turned off at the time of the inspection however the breaker was not locked off and was in a location accessible to persons. This is a potential shock and fire hazard should the breaker be turned on and a person or object contacts the exposed energized parts. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_bus_bars_of_service_panel_-_main_breaker_turned_off.png | file://x:/photopub/docs/0000000445/cd4591b4-1a1f-49ff-a873-7ac3fda0d680.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af81b801_4ab7_45dc_adc1_165902d7755b
ELIN-589737-2016 | EL-394453-2016 | 6/17/2016 11:11:37 AM | ASSESS: EL: Service Connection | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Covers are required to be installed on energized electrical panels. This is required to prevent accidental contact with energized parts of the panel, to prevent mechanical damage to the internal components of the panel, and to contain thermal energy from a fault within the panel. This installation of a service panel in a shop on a residential property has a service panel that does not have the cover installed on the branch circuit section of the panel. This has left open bus bars accessible to contact. The main circuit breaker was turned off at the time of the inspection however the breaker was not locked off and was in a location accessible to persons. This is a potential shock and fire hazard should the breaker be turned on and a person or object contacts the exposed energized parts. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exterior_of_shop.png | file://x:/photopub/docs/0000000445/d44ec71d-e526-4f8a-b932-a2852da888a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af81b801_4ab7_45dc_adc1_165902d7755b
BPVOP-597470-2016 | 2303204 | 6/22/2016 11:47:02 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Safety relief valves on air systems must be tested annually and serviced or replaced every 5 years. There is no tag on this valve to show last service date. To date I have not received any proof that it was changed out. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | In_place_safety.png | file://x:/photopub/docs/0000000446/3d02c157-e8f0-4908-b073-9bbccddf9275.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__18844e27_f5c2_4690_ba03_1983444fc71f
ELIN-593867-2016 | EL-398215-2016 | 6/16/2016 9:16:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service conductors are not mechanical protected from damage and more then 1.5 meters have entered the building. This could become unsafe if the conductors were to be damaged. These conductors are over fused from the supply service due to multiple houses being on the same fusing. If the conductors were damaged they could cause a fire/shock to persons or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Exposed_service__conductors.png | file://x:/photopub/docs/0000000444/7ccaf187-0075-4653-945b-352e3fc2dfed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a9aff19_eb73_4478_a557_e67882b19bec
ELIN-593867-2016 | EL-398215-2016 | 6/16/2016 9:16:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service conductors are not mechanical protected from damage and more then 1.5 meters have entered the building. This could become unsafe if the conductors were to be damaged. These conductors are over fused from the supply service due to multiple houses being on the same fusing. If the conductors were damaged they could cause a fire/shock to persons or property. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Exposed_service_conductors.png | file://x:/photopub/docs/0000000444/7ce7bf79-348a-4024-8bef-d759dfb7eb6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2a9aff19_eb73_4478_a557_e67882b19bec
ELIN-594157-2016 | EL-383990-2016 | 6/21/2016 2:18:46 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Non-compliances noted in previous inspections remain | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Enclosure.png | file://x:/photopub/docs/0000000446/d23aaedb-926e-474f-a4ed-75c70b7bf18b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4513f406_1870_464a_8d26_f3892ea43721
ELIN-594157-2016 | EL-383990-2016 | 6/21/2016 2:18:46 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Non-compliances noted in previous inspections remain | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Filler.png | file://x:/photopub/docs/0000000446/f2bbad15-0186-4bdb-8af9-8c23b1b0be08.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4513f406_1870_464a_8d26_f3892ea43721
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_installed_in_foam_formed_walls_.png | file://x:/photopub/docs/0000000446/07fc1f11-3c20-4c77-8a45-9eebb4ebf335.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_passing_through_members_in_foam_formed_walls_less_than_32mm_from_face_of_wall.png | file://x:/photopub/docs/0000000446/b8c72936-1080-44fa-9ee1-622451689bb4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_foam_formed_walls___.png | file://x:/photopub/docs/0000000446/a22c3730-3a15-4417-a005-15672a392389.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_foam_formed_walls__.png | file://x:/photopub/docs/0000000446/039fa07c-a967-4eec-9902-46006f120b5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
GAIN-592968-2016 | GA-395999-2016 | 6/20/2016 3:48:06 PM | ASSESS: GA: Rough-In | png | #asFound | GA059 | Underground piping entering a building below grade (unapproved) | 3 | 3 | If a leak was to develop in the under ground portion of the gas line,fuel could enter the crawl space of the structure Explosion and or fire hazard. | 3 | Underground piping entering a building below grade (unapproved) | Gray.png | file://x:/photopub/docs/0000000445/9b37a364-eeb7-48fb-ae81-8a8d589ad9c3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__80dfa706_0648_4034_8d99_1a0ca6ce9d3b
ELIN-595296-2016 | EL-328558-2015 | 6/21/2016 9:17:31 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Ground fault circuit breaker protecting the bathroom receptacle circuit is not able to be reset. When breaker handle is operated the breaker trips and remains in the "trip position". Malfunctioning and defective breakers may accidentally remain in an energized state and not provide overcurrent protection that they are rated for, which may result in shock or fire to persons or property. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | GFCI_breaker_will_not_reset__.png | file://x:/photopub/docs/0000000446/3d54d94a-7641-4229-b502-1eae5a0634ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9e4b8fc4_f996_46f8_9aa3_041aa5d83dbb
BPVOP-593819-2016 | 5078516 | 6/22/2016 2:08:10 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP199 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | 2 | 2 | The annual manual lift test as mandated by CSA-B51 (2014) was not conducted and evidence was not available to safety officer of any such test conducted. | 2 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | PSV.png | file://x:/photopub/docs/0000000446/0750e672-6d7d-4da4-a8d4-b9b2890a45c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__FE54D549_36F6_475C_B7A7_94E5B698A137
PRIN-593263-2016 | PR-386840-2016 | 6/16/2016 1:38:32 PM | ASSESS: PR IN: Acceptance | png | #asFound | PR026 | Fall safety devices inadequate for hazards in area. | 3 | 2 | A rolling staircase that is to be utilized in allowing the public to access the cabin roof deck had not had a design review conducted on it by a P.Eng. It therefore is not possible to be confident that the staircase is suitable for that use. There could be a risk of the staircase toppling, causing the user to fall. Or the staircase becomes get entangled with moving ropeway equipment. | 3 | Fall safety devices inadequate for hazards in area. | Rolling_staircase_at_top_station.png | file://x:/photopub/docs/0000000446/e0e9a3e2-53a0-42b7-b1ea-5085499eea37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__12e1b839_8865_47a5_af5d_790c26c2889f
ELIN-581290-2016 | EL-390116-2016 | 6/23/2016 11:38:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | Flexible cord has been used to feed receptacles and enters a panel board. Flexible cord is not designed or approved for installation as a general wiring method to fixed equipment. Subject to oxidation and other factors flexible cord used in this fashion can result in damage to property or injury to persons. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_as_a_substitute_for_permanent_wiring_method_enters_panel__breaker__receptacle.png | file://x:/photopub/docs/0000000447/aa896c83-14d4-4046-bea6-cffca67ed25e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba1e4f1_4700_48a0_b462_cab369463082
ELIN-598169-2016 | EL-397563-2016 | 6/23/2016 12:30:16 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 2 | A new 200 amp 240 volt residential service has been installed. The consumer service conductors are at the same height as the utility attachment. When proper orientation is not provided to ensure a minimum of 150 mm and a maximum of 300 mm for service conductors above the point of utility attachment, water damage to electrical equipment can occur | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Insulator_level_with_service_conductor_emergenc.png | file://x:/photopub/docs/0000000447/100d2223-5d4f-4b29-a424-adb511e89a4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c6a200b_fe1e_458d_b2f2_c66e574f5106
ELIN-581290-2016 | EL-390116-2016 | 6/23/2016 11:38:27 AM | ASSESS: EL: Service Connection | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | Flexible cord has been used to feed receptacles and enters a panel board. Flexible cord is not designed or approved for installation as a general wiring method to fixed equipment. Subject to oxidation and other factors flexible cord used in this fashion can result in damage to property or injury to persons. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_used_to_feed_fixed_receptacles__in_use_covers_not_extra_duty.png | file://x:/photopub/docs/0000000447/bd1afa8d-ecaf-4936-9d61-d4291a0d6019.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ba1e4f1_4700_48a0_b462_cab369463082
ELOP-315407-2015 | 3904 | 6/21/2016 12:03:17 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL053 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | 4 | 3 | 480 Volt, 200 Amp, 3 phase, 3 wire service has no ground fault detection. This is a shock hazard. | 4 | Protection and control Ground-fault protection has not been provided at equipment rated >150 volts to ground and 1000 A or more; or 150 volts to ground or less and 2000 A or more. | Compressor_and_old_sawmill_building_480V_3_wire_service_no_ground_fault_detection_.png | file://x:/photopub/docs/0000000446/077ca407-3ddc-4902-9af0-f2be9e54a561.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__41a1ade9_073e_43c6_ac8d_7225686d3e5b
ELIN-594604-2016 | EL-398702-2016 | 6/21/2016 3:12:19 PM | ASSESS: EL: Final | png | #asFound | EL032 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | 3 | 3 | 120/240 volt, 100 amp. Branch circuit conductors pass through the main service conductor compartment of the combination panel. Equipment damage condition. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors other than service conductors pass through service box. Service conductors are not isolated from distribution equipment, feeder or branch circuit conductors. | EL032__branch_circuit_conductors_passing_through_service_conductor_compartment_.png | file://x:/photopub/docs/0000000446/51ddd93b-3108-440a-808f-abb57985bad2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c77325ed_c5ae_45d8_8123_7db0d52d7dbd
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cord.png | file://x:/photopub/docs/0000000448/ae0901a2-ffbe-4fee-8c60-3e1c9726868c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Feeder.png | file://x:/photopub/docs/0000000448/8b83ca2a-6aa4-4ad9-aaea-93d6bd38d278.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Receptacles.png | file://x:/photopub/docs/0000000448/45eaab44-79ec-4ef9-ae27-181189e401a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
AMIN-588227-2016 | AM-391870-2016 | 6/3/2016 1:56:51 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 2 | None of the attachment point on this inflatable amusement device where anchored at the time of inspection. This would result in a hazard in which a high wind condition could cause the device to be blown over or out of position. It should be realized that the device was not open for public at the time of inspection and the hazard level would be lower then had there been participants on the device. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | No_attachment_points_anchored.png | file://x:/photopub/docs/0000000445/977be07b-28c7-429b-a37b-37dbdfec4940.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b332b310_e824_4d78_8306_c1a94f94020c
AMIN-588221-2016 | AM-391869-2016 | 6/3/2016 1:33:04 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 2 | None of the attachment point on this inflatable amusement device where anchored at the time of inspection. This would result in a hazard in which a high wind condition could cause the device to be blown over or out of position. It should be realized that the device was not open for public at the time of inspection and the hazard level would be lower then had there been participants on the device. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Example_of_non_anchored_attachment_point.png | file://x:/photopub/docs/0000000445/0d3f0a10-e319-479b-bdec-483ff21eee1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b26ba46_7cc0_4ed3_95f9_230d35fd4e6b
AMIN-588250-2016 | AM-391872-2016 | 6/3/2016 3:37:29 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 2 | None of the attachment point on this inflatable amusement device where anchored at the time of inspection. This would result in a hazard in which a high wind condition could cause the device to be blown over or out of position. It should be realized that the device was not open for public at the time of inspection and the hazard level would be lower then had there been participants on the device. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Attachment_point_not_anchored.png | file://x:/photopub/docs/0000000445/e41ca9cf-7fe4-4f57-b908-c373ae5ad146.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9533bb74_7790_4010_8f0c_65f7999792d1
AMIN-588209-2016 | AM-391861-2016 | 6/3/2016 2:35:44 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 2 | None of the attachment point on this inflatable amusement device where anchored at the time of inspection. This would result in a hazard in which a high wind condition could cause the device to be blown over or out of position. It should be realized that the device was not open for public at the time of inspection and the hazard level would be lower then had there been participants on the device. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Missing_anchor_points.png | file://x:/photopub/docs/0000000445/7ebd23da-eb06-488e-aec6-c974ee4d8288.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ddf7156_3a74_4419_9086_5d413a3f329e
AMIN-588214-2016 | AM-391867-2016 | 6/3/2016 2:20:16 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 2 | None of the attachment point on this inflatable amusement device where anchored at the time of inspection. This would result in a hazard in which a high wind condition could cause the device to be blown over or out of position. It should be realized that the device was not open for public at the time of inspection and the hazard level would be lower then had there been participants on the device. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Example_of_attachment_points_not_anchored.png | file://x:/photopub/docs/0000000445/5378ffea-a93f-4430-b7e7-b05c71160005.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01551806_5385_4009_802d_e4038c70034f
EDMA-597507-2016 | ED-372781-2016 | 6/16/2016 10:43:36 AM | ASSESS: ED MA: Acceptance | png | #asFound | ED000 | No Created Hazard Identified | 0 | 0 | Safeties | 0 | No Created Hazard Identified | Safety.png | file://x:/photopub/docs/0000000446/3e7482b5-58ef-47a6-a199-7ebe96a500cd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1117b1c0_78a3_40c5_bfa9_cdb57500c152
GAWP-598417-2016 | GA-222607-2015 | 6/21/2016 5:08:09 PM | ASSESS: GA Work In Progress | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Clearance from propane relief to mechanical air intake to appliance not met. Propane could be drawn into mechanical air intake if relief valve opened causing fire or explosion. | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Clearance_to_combustion_air_not_met.png | file://x:/photopub/docs/0000000446/c8ce8f3d-ffa8-4dc6-acc5-8b5e02a541ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d7390db_2238_445b_b039_6a42f7a7c18c
GAWP-598419-2016 | GA-400096-2016 | 6/21/2016 4:30:00 PM | ASSESS: GA Work In Progress | png | #asFound | GA012 | Clearance to combustibles not maintained | 3 | 3 | Clearance to combustibles not met. Ignition of propane could occur if relief valve on propane cylinder released propane. | 3 | Clearance to combustibles not maintained | Clearance_to_combustibles_not_met_.png | file://x:/photopub/docs/0000000446/bdf67d45-feae-4e2c-950c-027bbf1e507d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1c54dae4_ae31_4e67_b540_d0a624d2d70e
GAIN-593456-2016 | GA-397982-2016 | 6/21/2016 3:27:38 PM | ASSESS: GA: Final | png | #asFound | GA016 | Ignition sources present with-in minimum distance required | 4 | 4 | Vent termination installed less than the minimum required distance to the liquid level gauge. Propane vapour would be present during tank filling that could enter the combustion chamber of the water heater. Possible fire hazard if unit was in use during the filling operation. | 4 | Ignition sources present with-in minimum distance required | JV_9425.png | file://x:/photopub/docs/0000000446/c8a158ad-13f2-4ea1-ac59-fc885dde01ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5c748564_a912_4089_b215_ccd0e396f370
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_foam_formed_walls_.png | file://x:/photopub/docs/0000000446/da39ef35-77a8-468b-b6c9-19c174bdafd9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Front_of_house_under_construction.png | file://x:/photopub/docs/0000000446/b5c9b67b-c607-4b35-9cd2-0432cc0db472.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
GAIN-595798-2016 | GA-035710-2013 | 6/20/2016 11:25:49 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | Vent to close to vented soffit, will cause water damage and allow products of combustion to enter attic space | 2 | Side wall vent termination not compliant with installation instructions | 510_Amess.png | file://x:/photopub/docs/0000000445/1b121973-0446-4e30-9e06-a3bdd23044bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdb4364c_da59_4d64_a129_366bbcf73f14
ELIN-579024-2016 | EL-257814-2015 | 5/18/2016 4:51:34 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Db2 conduit installed above ground. This type of conduit can be easily damaged and is not permitted to used in exposed installations. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | C.png | file://x:/photopub/docs/0000000444/4d5defa6-3f98-4620-836c-bff86414d046.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__83515658_7343_4533_ac4a_be88d39e2ddd
ELIN-425575-2015 | EL-251509-2015 | 8/20/2015 7:42:58 AM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Db2 conduit used above ground. This type of conduit is easily damaged and is not permitted to be used above ground. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | D.png | file://x:/photopub/docs/0000000444/29dec087-0c27-477a-a7ea-128af3aedcf5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da406d99_8606_42de_9095_04ed980d1495
ELIN-596031-2016 | EL-397092-2016 | 6/21/2016 3:55:07 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pole_meter_mounting.png | file://x:/photopub/docs/0000000446/2c6ac97e-65ab-401a-b963-9aedaed71b65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a5960365_d785_4e45_bba9_7b699ce9238f
ELIN-601430-2016 | EL-269970-2015 | 6/27/2016 11:22:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Non-compliant support for service conductors | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Poa.png | file://x:/photopub/docs/0000000448/54da656c-036c-4c45-a949-7b2c9e740f1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75b582b5_4803_4a26_9454_2ca68ecd0796
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Panel.png | file://x:/photopub/docs/0000000448/de94c4c2-244e-474a-b962-f0a0d7b8b3bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cordend.png | file://x:/photopub/docs/0000000448/f5b01ff5-240d-42b9-a3fb-bbcfd458bb9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Panel_connect.png | file://x:/photopub/docs/0000000448/dcd75ad3-47af-4d52-a0be-924f6bca5f31.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cord_end.png | file://x:/photopub/docs/0000000448/35dff619-31dc-4b54-aadb-3d5746630239.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Receptacle.png | file://x:/photopub/docs/0000000448/b22b4448-f7b1-4b14-bd03-ec801ede6af3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Cord_connect.png | file://x:/photopub/docs/0000000448/19c9bbb0-1d71-4515-9048-8b7c89b8bc3c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
ELIN-601443-2016 | EL-383747-2016 | 6/27/2016 10:24:40 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Hazardous equipment accessible to non-qualified personnel | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | Temp_panel.png | file://x:/photopub/docs/0000000448/3c5be900-1631-4590-80e6-be5f745a7b3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f82c138_3af6_4973_9416_be6c51185794
GAIN-585619-2016 | GA-379659-2016 | 6/21/2016 11:59:00 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | 1)All installed gas piping shall be leak tight and tested 2) detected door and found gas leak at furnace supply gas piping. 3) A small gas leak undetected could possibly become larger or the leaking fuel could collect in an enclosed area and possibly become ignited by an unknown source of ignition. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Water_heater_vent_support_and_no_slope.png | file://x:/photopub/docs/0000000447/7e8ebcfa-2b98-4b5a-9498-a373d0a0611d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdb80a87_380f_451a_9945_9f9310f487ab
GAIN-585619-2016 | GA-379659-2016 | 6/21/2016 11:59:00 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | 1)All installed gas piping shall be leak tight and tested 2) detected door and found gas leak at furnace supply gas piping. 3) A small gas leak undetected could possibly become larger or the leaking fuel could collect in an enclosed area and possibly become ignited by an unknown source of ignition. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Gas_leak_.png | file://x:/photopub/docs/0000000447/7902f9ac-74d4-4eac-a35b-56d11afc3d87.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdb80a87_380f_451a_9945_9f9310f487ab
GAIN-585619-2016 | GA-379659-2016 | 6/21/2016 11:59:00 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | 1)All installed gas piping shall be leak tight and tested 2) detected door and found gas leak at furnace supply gas piping. 3) A small gas leak undetected could possibly become larger or the leaking fuel could collect in an enclosed area and possibly become ignited by an unknown source of ignition. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | No_Water_heater_T_P_relief_pipe__.png | file://x:/photopub/docs/0000000447/59a128f2-e36e-4ddc-b18d-166fad9c715d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdb80a87_380f_451a_9945_9f9310f487ab
GAIN-585619-2016 | GA-379659-2016 | 6/21/2016 11:59:00 AM | ASSESS: GA: Final | png | #asFound | GA066 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | 3 | 3 | 1)All installed gas piping shall be leak tight and tested 2) detected door and found gas leak at furnace supply gas piping. 3) A small gas leak undetected could possibly become larger or the leaking fuel could collect in an enclosed area and possibly become ignited by an unknown source of ignition. | 3 | Gas leak detected very minor odor present, able to pinpoint and isolate locally | Condensate_power_wire_protection_required__.png | file://x:/photopub/docs/0000000447/8aa2b88d-2415-4d87-89d3-90bb2d892bb2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__cdb80a87_380f_451a_9945_9f9310f487ab
GAIN-585659-2016 | GA-384541-2016 | 6/22/2016 9:32:49 AM | ASSESS: GA: Final | png | #asFound | GA138 | Equipment unserviceable due to lack of clearance. | 3 | 3 | 1)All installed appliances require 24" minimum clearance for service. 2) furnace front installed to close to structure and combustibles. Blower cannot be removed from furnace. 3) The furnace blower section cannot be maintained or repaired. A dirt plugged blower could lead to the furnace running at excessive temperatures possibly causing cycling on the high temp safety control system. | 3 | Equipment unserviceable due to lack of clearance. | Vent_and_intake_termination_clearance_.png | file://x:/photopub/docs/0000000447/5253f6c6-3e3b-4d17-811a-749536a04f06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ca3dbee_06da_4adb_9af4_295f85924735
GAIN-585659-2016 | GA-384541-2016 | 6/22/2016 9:32:49 AM | ASSESS: GA: Final | png | #asFound | GA138 | Equipment unserviceable due to lack of clearance. | 3 | 3 | 1)All installed appliances require 24" minimum clearance for service. 2) furnace front installed to close to structure and combustibles. Blower cannot be removed from furnace. 3) The furnace blower section cannot be maintained or repaired. A dirt plugged blower could lead to the furnace running at excessive temperatures possibly causing cycling on the high temp safety control system. | 3 | Equipment unserviceable due to lack of clearance. | No_front_service_clearance.png | file://x:/photopub/docs/0000000447/f29e4d38-b598-41ba-ab5f-75ee88d1c593.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7ca3dbee_06da_4adb_9af4_295f85924735
ELIN-593221-2016 | EL-396991-2016 | 6/23/2016 9:46:22 AM | ASSESS: EL: Final | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | In a routine silver label re-certification at a single wide mobile home, a 120volt 15amp GFCI receptacle was found under the mobile unit for use of the heating cable. This may lead to a Power Supply System Interruption. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | GFCI_under_unit_.png | file://x:/photopub/docs/0000000447/8485e44a-152b-4c23-8aba-b61d8ae608c4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dddaf57a_068e_4db5_9b7b_e13c6f265106
ELIN-595697-2016 | EL-395713-2016 | 6/21/2016 8:51:58 AM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | In a double wide modular home, a routine Silver Label inspection found the 120/240volt 100amp feeder cable is bonded incorrectly in the modular house panel. This could lead to a Shock Hazard. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Bond_conductor_in_neutral_buss.png | file://x:/photopub/docs/0000000446/69690608-12e6-4e25-874f-3e84090a5879.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__77eb199a_2a5a_4abf_80d2_bce56f179098
ELIN-599946-2016 | UW-401895-2016 | 6/23/2016 2:22:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head high voltage power lines are required to have acceptable clearances from trees and their branches. This is required to prevent the power line from contacting the tree and completing a circuit to ground creating a hazard. This installation of a 14.4KV high voltage over head power line on private property is installed in contact with tree branches. The installation was not energized yet but a service connection inspection had been requested. Left uncorrected this is shock and fire hazard if the line becomes energized, is in contact with the tree branches, and a person or object comes in contact with the energized tree. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | High_voltage_switch_pole.png | file://x:/photopub/docs/0000000447/2372d34f-951e-4874-b331-cb42f17d1ab1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06bc0096_9c5d_4a4e_b56d_1084e4859aac
ELIN-596451-2016 | EL-259284-2015 | 6/17/2016 4:33:28 PM | ASSESS: EL: Final | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | Db2 housing service conductors installed above ground. This is a fire hazard. This type of conduit is easily damaged and is not permitted to be installed above ground. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | B.png | file://x:/photopub/docs/0000000445/3ce63caa-562a-45a8-856a-dd0653b58bec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f9419726_c2f1_43df_a304_8e086f41a737
ELIN-596432-2016 | EL-330930-2016 | 6/20/2016 1:01:35 PM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Db2 housing service conductors installed above ground. This type of conduit can be easily damaged and is not permitted to be installed above ground. This is a fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | C.png | file://x:/photopub/docs/0000000445/80e6626f-5d33-4c9d-93f1-20e493b97312.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8e79944f_a9dc_450a_a205_71ee2431dffe
ELIN-420144-2015 | EL-214736-2015 | 8/12/2015 5:04:22 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Hot tub feeder not supported or properly housed in a suitable enclosure. This is a shock and fire hazard as the cable could short out to the metal sidings sharp edge. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000445/d605b88c-7c7d-4f7b-aab2-0bacda5d1c4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dcc8876f_b656_4714_8dca_13e45625083e
ELIN-592807-2016 | EL-397597-2016 | 6/20/2016 12:19:22 PM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | A secondary entrance was added to a dwelling. No light fixture was installed at the entrance. Persons can be hurt exiting dwellings where adequate lighting has been omitted. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | Entrance_to_dwelling_no_light.png | file://x:/photopub/docs/0000000445/a34cccee-865a-4ff4-81d1-54756d143034.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f68155aa_6a0e_4160_ab7e_494f8ed3a502
ELIN-594298-2016 | EL-370311-2016 | 6/20/2016 1:27:27 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuits feeding newly added kitchen appliances pass through a 125 amp 240 volt main disconnect portion of a service panel board. The main service compartment is designed to be used for service conductors, and main service grounding and is rated to contain fault current for that condition. Branch circuits passing through the main distribution portion of the panel could compromise the panels ability to operate as approved under fault conditions for either the two added branch circuits or the main service conductors | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Branch_circuits_pass_through_main_service_compartment.png | file://x:/photopub/docs/0000000445/2f72fe82-d544-4a76-a80e-320acffe6b6c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0e2580a0_5454_444b_9f14_c96957076494
ELIN-600189-2016 | EL-352809-2016 | 6/24/2016 2:02:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | 125 amp, 240 volt residential service not grounded and bonded properly; shock and thermal hazard to persons and equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | P1.png | file://x:/photopub/docs/0000000447/9f9b1b17-7cac-4ba5-bd3f-f601289e6220.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31b71593_bf71_4864_9014_396fe0bd5db0
ELIN-596503-2016 | EL-267651-2015 | 6/17/2016 4:06:06 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Db2 conduit installed above ground. This type of conduit can be easily damaged and is not permitted to be installed in exposed installations. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | I.png | file://x:/photopub/docs/0000000444/841547d8-3218-4a7f-ace7-fef7e095c4f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2937a90d_3857_4bdb_8f15_4bc29a738d4b
ELIN-596509-2016 | EL-274905-2015 | 6/17/2016 12:51:12 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Exposed live parts of lighting switches and control transformer in a pool mechanical room. This is a shock hazard as an individual could accidentally come into contact with these parts. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000444/3a060e50-c7d8-4cd1-aa25-bc6b4457ff5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3025e0dd_7aa0_4159_b41f_6f5c862e5136
ELIN-596503-2016 | EL-267651-2015 | 6/17/2016 4:06:06 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Db2 conduit installed above ground. This type of conduit can be easily damaged and is not permitted to be installed in exposed installations. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | H.png | file://x:/photopub/docs/0000000444/9cf50055-5316-416a-9a1d-2df4f8477c06.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2937a90d_3857_4bdb_8f15_4bc29a738d4b
ELIN-596509-2016 | EL-274905-2015 | 6/17/2016 12:51:12 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Exposed live parts of lighting switches and control transformer in a pool mechanical room. This is a shock hazard as an individual could accidentally come into contact with these parts. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000444/0358082f-bd76-4744-86ae-9b9b5d715b70.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3025e0dd_7aa0_4159_b41f_6f5c862e5136
ELIN-596522-2016 | EL-300390-2015 | 6/17/2016 3:24:22 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | DB2 conduit installed above ground and not buried to the correct depth. This type of conduit is not permitted to be installed above ground because it can be easily damaged, creating a shock and fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | F.png | file://x:/photopub/docs/0000000444/f4bd692b-f098-47b1-9c49-5294ee700b7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f53d81d_5905_4b09_8a46_4cac953db092
ELIN-596522-2016 | EL-300390-2015 | 6/17/2016 3:24:22 PM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | DB2 conduit installed above ground and not buried to the correct depth. This type of conduit is not permitted to be installed above ground because it can be easily damaged, creating a shock and fire hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | G.png | file://x:/photopub/docs/0000000444/eb7f60ca-91a5-4c6b-b4eb-b9ea0c73d390.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5f53d81d_5905_4b09_8a46_4cac953db092
ELIN-438779-2015 | EL-238178-2015 | 9/10/2015 8:46:29 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Consumer service conductor not adequately protected. This could cause damage to the cab,e and potentially a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | E.png | file://x:/photopub/docs/0000000444/f8f30d7a-ccb0-4e5e-af85-be4bc589f5ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8fb7723b_6d61_4359_91df_537a1df51760
GAIN-572455-2016 | GA-379545-2016 | 6/21/2016 7:26:35 AM | ASSESS: GA: Final | png | #asFound | GA075 | Required clearances not met | 2 | 2 | Appliance vent outlet and appliance air intake are located within 3 feet horizontally of the meters regulator relief outlet. The appliance vent outlet requires a 3 foot clearance horizontally from the relief outlet for a vertical distance of 15 feet. The appliance air intake requires a 10 foot clearance horizontally from the relief outlet for a vertices distance of 15 feet. | 2 | Required clearances not met | Appliance_air_intake_and_vent_outlet_clearances_.png | file://x:/photopub/docs/0000000445/3a3f9ebd-87de-41d5-9669-021b01e5c04f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__930a81a0_c5e7_43d5_b63d_5e3da4765fea
ELHE-598990-2016 | HE-400969-2016 | 6/21/2016 12:47:46 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL061 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | 3 | 3 | During a site visit with the local utility, the 200amp 120/240volt electrical service panel was found in a most undesirable location. This can directly affect the system operation. | 3 | Placement of equipment does not allow for adequate access or egress. Entrance to or egress from working space has not been adequately provided. | Panel_location.png | file://x:/photopub/docs/0000000446/72936b27-2451-432f-b93d-93ebe953a803.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__eb323755_66bd_4ced_8c60_6abea1e5339e
ELIN-599946-2016 | UW-401895-2016 | 6/23/2016 2:22:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head high voltage power lines are required to have acceptable clearances from trees and their branches. This is required to prevent the power line from contacting the tree and completing a circuit to ground creating a hazard. This installation of a 14.4KV high voltage over head power line on private property is installed in contact with tree branches. The installation was not energized yet but a service connection inspection had been requested. Left uncorrected this is shock and fire hazard if the line becomes energized, is in contact with the tree branches, and a person or object comes in contact with the energized tree. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | High_voltage_line_installed_in_contact_with_tree_branches_.png | file://x:/photopub/docs/0000000447/ce77c9b3-9c59-42a8-a8bc-d91db4c732c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06bc0096_9c5d_4a4e_b56d_1084e4859aac
ELIN-599946-2016 | UW-401895-2016 | 6/23/2016 2:22:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head high voltage power lines are required to have acceptable clearances from trees and their branches. This is required to prevent the power line from contacting the tree and completing a circuit to ground creating a hazard. This installation of a 14.4KV high voltage over head power line on private property is installed in contact with tree branches. The installation was not energized yet but a service connection inspection had been requested. Left uncorrected this is shock and fire hazard if the line becomes energized, is in contact with the tree branches, and a person or object comes in contact with the energized tree. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Switch_pole.png | file://x:/photopub/docs/0000000447/ef7bad85-2d85-464a-a845-8f6f31ed4044.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06bc0096_9c5d_4a4e_b56d_1084e4859aac
ELIN-599946-2016 | UW-401895-2016 | 6/23/2016 2:22:25 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Over head high voltage power lines are required to have acceptable clearances from trees and their branches. This is required to prevent the power line from contacting the tree and completing a circuit to ground creating a hazard. This installation of a 14.4KV high voltage over head power line on private property is installed in contact with tree branches. The installation was not energized yet but a service connection inspection had been requested. Left uncorrected this is shock and fire hazard if the line becomes energized, is in contact with the tree branches, and a person or object comes in contact with the energized tree. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Second_pole.png | file://x:/photopub/docs/0000000447/4a998f56-a48d-4118-9aa2-100b864f95bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__06bc0096_9c5d_4a4e_b56d_1084e4859aac
ELIN-593396-2016 | EL-395316-2016 | 6/21/2016 11:05:30 AM | ASSESS: EL: Final | png | #asFound | EL117 | Conductors, No expansion joint or not installed correctly. | 3 | 3 | The 15 amp 120 volt NMSC circuit does not include a junction box as required,this is a thermal issue | 3 | Conductors, No expansion joint or not installed correctly. | no_junction_box.png | file://x:/photopub/docs/0000000447/75b67bf9-6a5c-4807-989f-a4b4b4d0774e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bec602dc_5578_4ae8_91c4_c255dabd1d55
BPVOP-481526-2015 | BPV-247831-2015 | 6/20/2016 9:58:56 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP195 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | 3 | 3 | Waterside of the boiler surfaces shall be kept free of scale and sludge. I found siginficant amount of scale on the waterside surfaces of the boiler tubes and in the bottom of the boiler. Scale has thermal insulating effect and may lead to boiler metal weakening due to overheating because of loss of heat transfer. | 3 | 5.1.0 In service proc/process - Scale, sludge and sediment build up on waterside of boiler | Bottom_handhole_plugged_.png | file://x:/photopub/docs/0000000445/2448f8f7-e8cf-4b85-89e2-4c718c38d976.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__61c71fdc_1b0a_4748_85ec_659608df0dcf
GAUP-571039-2016 | UW-382812-2016 | 6/21/2016 5:37:08 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Physical protection of corrugated stainless steel tubing absent. Tubing must by protected from damage to prevent uncontrolled release of gas in the event of damage to tubing. | 2 | Physical protection of piping and tubing absent. | 9663_3rd1.png | file://x:/photopub/docs/0000000445/5b57c3e1-0eb2-4433-a9a8-bcbe3d397904.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d43bdb9_c7b7_43af_b365_861c9bd07928
BPVOP-481524-2015 | 5288374 | 6/22/2016 10:01:55 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale.png | file://x:/photopub/docs/0000000446/73a85be6-892b-4c7c-9d37-a9836daef0a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a76c0a90_cd08_434c_8439_e452b865e2a2
BPVOP-593817-2016 | 5085326 | 6/22/2016 2:20:02 PM | ASSESS: BPV OP: RAP (for recert insp) Boiler | png | #asFound | BP199 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | 2 | 2 | The annual manual lift test as mandated by CSA B51 (2014) was not conducted and evidence was not available to safety officer for any such test conducted. | 2 | 5.1.0 In service proc/process - Inspection and service intervals requirements not met | Safety_Relief_Valve.png | file://x:/photopub/docs/0000000447/74c921ab-b94b-46f1-803c-e3790bb5a9ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4C0FB3EA_4DDF_4B29_A26C_78424D6B17A6
ELIN-412684-2015 | EL-216764-2015 | 6/16/2016 8:42:26 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Large rocks placed against db2 service conduit have damaged the raceway. The rocks are part of a retaining wall that was built to raise the grade in the vicinity of the conduit. This is a hazard as the service conductors could be damaged by the collapsing conduit. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | A.png | file://x:/photopub/docs/0000000447/5301e689-db09-4804-81a0-d4e9ecdf548e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0db0ddfb_e105_4241_80a9_27ef02b0cdb6
ELIN-412684-2015 | EL-216764-2015 | 6/16/2016 8:42:26 AM | ASSESS: EL: Final | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Large rocks placed against db2 service conduit have damaged the raceway. The rocks are part of a retaining wall that was built to raise the grade in the vicinity of the conduit. This is a hazard as the service conductors could be damaged by the collapsing conduit. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | B.png | file://x:/photopub/docs/0000000447/3295afe0-e651-45f4-a383-12d16eddecd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0db0ddfb_e105_4241_80a9_27ef02b0cdb6
GAIN-598007-2016 | GA-394507-2016 | 6/27/2016 10:39:45 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Found moisture exhaust ducting on commercial dryers installed with 0" clearance to combustibles. This could lead to a fire hazard. | 3 | Non compliant Type C Vent clearance | Venting_clearances_.png | file://x:/photopub/docs/0000000448/0dc6c044-dc1b-497b-aba0-b1ef3df663ea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b8a226a2_8050_4a50_957d_5574f74c00fe
ELIN-600501-2016 | EL-402157-2016 | 6/27/2016 10:52:17 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Panel boards are not permitted to be installed in bathrooms. This is because bathrooms are typically moist environments which can negatively affect the panel board and circuit breakers causing rust or corrosion and premature failure. Also occupants of the bathrooms are typically wet and in bare feet. Contact with or operation of the panel board and circuit breakers when persons are wet may pose a shock hazard. This installation of a new bathroom installed at a house has a 30A, 120/240V load center (panel board) installed inside the bathroom. Left uncorrected this is a potential shock hazard if wet persons in bare feet contact the panel and electrical breakers. This may also be a fire hazard if over time the panel, circuit breakers, or terminations rust or corrode and fail. | 3 | General Equipment is not approved for the specific use | New_bathroom_installed_in_the_back_yard_beside_a_hot_tub.png | file://x:/photopub/docs/0000000448/c4607701-77a1-4604-bc9b-86e037e81de3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc96a32_b4fa_44a6_ab7a_d5b0abde763e
ELIN-600501-2016 | EL-402157-2016 | 6/27/2016 10:52:17 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Panel boards are not permitted to be installed in bathrooms. This is because bathrooms are typically moist environments which can negatively affect the panel board and circuit breakers causing rust or corrosion and premature failure. Also occupants of the bathrooms are typically wet and in bare feet. Contact with or operation of the panel board and circuit breakers when persons are wet may pose a shock hazard. This installation of a new bathroom installed at a house has a 30A, 120/240V load center (panel board) installed inside the bathroom. Left uncorrected this is a potential shock hazard if wet persons in bare feet contact the panel and electrical breakers. This may also be a fire hazard if over time the panel, circuit breakers, or terminations rust or corrode and fail. | 3 | General Equipment is not approved for the specific use | Panel_board_in_bathroom_.png | file://x:/photopub/docs/0000000448/407b7c73-3f92-4cbc-aa0e-5756d29bc41b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc96a32_b4fa_44a6_ab7a_d5b0abde763e
ELIN-600501-2016 | EL-402157-2016 | 6/27/2016 10:52:17 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Panel boards are not permitted to be installed in bathrooms. This is because bathrooms are typically moist environments which can negatively affect the panel board and circuit breakers causing rust or corrosion and premature failure. Also occupants of the bathrooms are typically wet and in bare feet. Contact with or operation of the panel board and circuit breakers when persons are wet may pose a shock hazard. This installation of a new bathroom installed at a house has a 30A, 120/240V load center (panel board) installed inside the bathroom. Left uncorrected this is a potential shock hazard if wet persons in bare feet contact the panel and electrical breakers. This may also be a fire hazard if over time the panel, circuit breakers, or terminations rust or corrode and fail. | 3 | General Equipment is not approved for the specific use | New_sub-panel_installed_in_the_bathroom.png | file://x:/photopub/docs/0000000448/5f34c40d-05c1-4974-a321-6b99eb54c688.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc96a32_b4fa_44a6_ab7a_d5b0abde763e
ELIN-585773-2016 | EL-274113-2015 | 6/23/2016 8:58:12 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 3 | During a renovation, a short length of extension cord was spliced to an existing circuit which had been cut in order to open a wall. The cord was plugged in to an energized outlet to power the cut circuit. The open splice could pose a shock hazard to those in the home. Flexible cord is not approved to be used in this manner. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Flexible_cord_open_splice_to_power_existing_circuit.png | file://x:/photopub/docs/0000000447/32f551ec-657a-4ace-91e3-a247cfb098a5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3902b124_4d67_45d7_aff2_da0b9cea0875
ELIN-597113-2016 | EL-384768-2016 | 6/17/2016 12:14:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | 200 amp, 240 volt residential service energized and not located or protected adequately as declared permanent in nature: shock and fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Petit2.png | file://x:/photopub/docs/0000000445/cf401d53-7913-4ca1-b0b7-c8fc135785c0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55c72550_90c0_445e_b14b_726921e30c4c
ELIN-597113-2016 | EL-384768-2016 | 6/17/2016 12:14:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | 200 amp, 240 volt residential service energized and not located or protected adequately as declared permanent in nature: shock and fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Petit_1.png | file://x:/photopub/docs/0000000445/6c37c5d4-ef68-403f-a8f9-c3e0b155a9b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55c72550_90c0_445e_b14b_726921e30c4c
ELIN-597113-2016 | EL-384768-2016 | 6/17/2016 12:14:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | 200 amp, 240 volt residential service energized and not located or protected adequately as declared permanent in nature: shock and fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Petit5.png | file://x:/photopub/docs/0000000445/1170a89f-dd6d-4080-866f-8e39e5328b88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55c72550_90c0_445e_b14b_726921e30c4c
ELIN-597113-2016 | EL-384768-2016 | 6/17/2016 12:14:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | 200 amp, 240 volt residential service energized and not located or protected adequately as declared permanent in nature: shock and fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Petit_4.png | file://x:/photopub/docs/0000000445/014a8647-a0ef-4ecf-bccc-9c4b6d127992.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55c72550_90c0_445e_b14b_726921e30c4c
ELIN-597113-2016 | EL-384768-2016 | 6/17/2016 12:14:21 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 5 | 200 amp, 240 volt residential service energized and not located or protected adequately as declared permanent in nature: shock and fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Petit_3.png | file://x:/photopub/docs/0000000445/7e50590e-986d-4254-9039-511c05ad4ef2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__55c72550_90c0_445e_b14b_726921e30c4c
ELIN-597136-2016 | EL-351510-2016 | 6/21/2016 10:47:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | 200 amp, 120/240 volt type 1 main distribution panel installed were main distribution panel maybe be subject to exterior weather conditions. This could cause equipment damage. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Non_weather_proof_enclosure.png | file://x:/photopub/docs/0000000445/bd284a6a-8d9f-44e7-ac53-96b5f05c01c9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b7209ca5_2f91_4c33_ac98_26555ba411e1
GAOP-538977-2016 | GA-227594-2015 | 6/20/2016 7:32:41 AM | ASSESS: GA OP: Periodic | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | The propane tank was set on wood planks set in loose gravel. The tank when filled has caused the planks to break and result in an unstable tank. The unsupported tank can shift with the ground movement and cause leaks in the piping system. The tank will settle as the wood planks rot and become unstable possibly tipping over. In the event of a fire the planks will burn causing the tank to become unstable and possibly rolling over. | 4 | Tank saddles/support failing | Broken_planks_under_tank_skids_.png | file://x:/photopub/docs/0000000447/a0172b67-5384-40ca-8ff5-101852b64f30.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e193fb0d_0a19_4370_9280_6bce0ee3ab08
GAOP-538977-2016 | GA-227594-2015 | 6/20/2016 7:32:41 AM | ASSESS: GA OP: Periodic | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | The propane tank was set on wood planks set in loose gravel. The tank when filled has caused the planks to break and result in an unstable tank. The unsupported tank can shift with the ground movement and cause leaks in the piping system. The tank will settle as the wood planks rot and become unstable possibly tipping over. In the event of a fire the planks will burn causing the tank to become unstable and possibly rolling over. | 4 | Tank saddles/support failing | Piping_that_needs_painted_.png | file://x:/photopub/docs/0000000447/764b545d-4369-4407-9ba0-c9df9390c0fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e193fb0d_0a19_4370_9280_6bce0ee3ab08
GAOP-538977-2016 | GA-227594-2015 | 6/20/2016 7:32:41 AM | ASSESS: GA OP: Periodic | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | The propane tank was set on wood planks set in loose gravel. The tank when filled has caused the planks to break and result in an unstable tank. The unsupported tank can shift with the ground movement and cause leaks in the piping system. The tank will settle as the wood planks rot and become unstable possibly tipping over. In the event of a fire the planks will burn causing the tank to become unstable and possibly rolling over. | 4 | Tank saddles/support failing | Gas_pipe_that_needs_a_sleeve_.png | file://x:/photopub/docs/0000000447/1582a0e8-ba2a-4708-830b-c53b4f44c4bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e193fb0d_0a19_4370_9280_6bce0ee3ab08
GAOP-538977-2016 | GA-227594-2015 | 6/20/2016 7:32:41 AM | ASSESS: GA OP: Periodic | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | The propane tank was set on wood planks set in loose gravel. The tank when filled has caused the planks to break and result in an unstable tank. The unsupported tank can shift with the ground movement and cause leaks in the piping system. The tank will settle as the wood planks rot and become unstable possibly tipping over. In the event of a fire the planks will burn causing the tank to become unstable and possibly rolling over. | 4 | Tank saddles/support failing | IBC_Boiler_relief_valve_.png | file://x:/photopub/docs/0000000447/62532759-e0ab-4571-8f99-e6e17a7371a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e193fb0d_0a19_4370_9280_6bce0ee3ab08
GAOP-538977-2016 | GA-227594-2015 | 6/20/2016 7:32:41 AM | ASSESS: GA OP: Periodic | png | #asFound | GA017 | Tank saddles/support failing | 4 | 4 | The propane tank was set on wood planks set in loose gravel. The tank when filled has caused the planks to break and result in an unstable tank. The unsupported tank can shift with the ground movement and cause leaks in the piping system. The tank will settle as the wood planks rot and become unstable possibly tipping over. In the event of a fire the planks will burn causing the tank to become unstable and possibly rolling over. | 4 | Tank saddles/support failing | Unsupported_tank_skid.png | file://x:/photopub/docs/0000000447/59223b9d-7c4d-4847-8ac3-b0160377e4fd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e193fb0d_0a19_4370_9280_6bce0ee3ab08
GAOP-353607-2015 | 2171036 | 6/23/2016 7:34:03 AM | ASSESS: GA OP: Periodic | png | #asFound | GA025 | Inadequate protection high traffic | 4 | 4 | The missing barricades could allow vehicles to hit the dispenser causing damage and or leaks leading to possible fire and property damage. | 4 | Inadequate protection high traffic | Missing_barricades_to_protect_the_dispenser_.png | file://x:/photopub/docs/0000000447/99f11118-8d48-46d6-a2e5-e0bbcfd9b76e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__514ca2b2_a792_461b_b461_d54a379f3566
GAOP-353607-2015 | 2171036 | 6/23/2016 7:34:03 AM | ASSESS: GA OP: Periodic | png | #asFound | GA025 | Inadequate protection high traffic | 4 | 4 | The missing barricades could allow vehicles to hit the dispenser causing damage and or leaks leading to possible fire and property damage. | 4 | Inadequate protection high traffic | Barricades_and_signage_missing.png | file://x:/photopub/docs/0000000447/7ee301d6-dea0-4c87-b5e1-1840d61374ee.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__514ca2b2_a792_461b_b461_d54a379f3566
BPVIN-525238-2016 | BPV-329479-2015 | 6/15/2016 12:12:35 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Grrtgrtg | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Sv.png | file://x:/photopub/docs/0000000446/24bbd3da-aa5d-4463-8c73-3513bde8a916.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3957b8ea_ef07_43c7_a72c_90e1df818a36
GAIN-585590-2016 | GA-379568-2016 | 6/27/2016 1:17:30 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Single wall vent pipe and fittings require a minimum clearance of 6" to combustible. The single wall vent pipe from the water heater was less than 1" from a combustible surface. This could cause the combustible surface to over heat and possibly ignite. | 3 | Non compliant Type C Vent clearance | Simply_Green_installation.png | file://x:/photopub/docs/0000000448/eb045914-cd36-43f0-bfa8-265e5d4ae53d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e18c3d9c_5071_4c11_9555_5b0402cf59c4
GAIN-585590-2016 | GA-379568-2016 | 6/27/2016 1:17:30 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Single wall vent pipe and fittings require a minimum clearance of 6" to combustible. The single wall vent pipe from the water heater was less than 1" from a combustible surface. This could cause the combustible surface to over heat and possibly ignite. | 3 | Non compliant Type C Vent clearance | S636_vent_pipe_from_furnace.png | file://x:/photopub/docs/0000000448/e0722e33-ba75-47b3-a384-9b1fefdc96b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e18c3d9c_5071_4c11_9555_5b0402cf59c4
GAIN-585590-2016 | GA-379568-2016 | 6/27/2016 1:17:30 PM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | Single wall vent pipe and fittings require a minimum clearance of 6" to combustible. The single wall vent pipe from the water heater was less than 1" from a combustible surface. This could cause the combustible surface to over heat and possibly ignite. | 3 | Non compliant Type C Vent clearance | Hole_patch_in_single_wall_vent_pipe.png | file://x:/photopub/docs/0000000448/2b2d0383-2446-4f29-88e1-d6bef1758985.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e18c3d9c_5071_4c11_9555_5b0402cf59c4
ELIN-592388-2016 | EL-396433-2016 | 6/24/2016 12:10:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Where consumer service neutral conductors are spliced at connection points between cables on poles and over head wiring between poles and structures, compression type connections are required. This is required because the neutral conductor is the grounded circuit conductor and is typically the fault path that current will follow in order to trip over current devices. Compression type connections are considered to be better than other mechanical type connectors. This installation of a 200A, 120/240V service upgrade on a residential property has consumer service neutral conductors that are spliced at pole tops using mechanical type connections. This is a shock and fire hazard if the connections fail and equipment either becomes energized or the failed connections produce excess thermal heating. Also an unbalanced three wire electrical system can cause an over voltage condition damaging circuits and equipment which is also a fire hazard. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Front_of_property.png | file://x:/photopub/docs/0000000447/d1ac33c2-10e9-4448-8969-3e1a89cef4a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11eea243_731d_4ec6_9b58_30dff74964d9
ELIN-592388-2016 | EL-396433-2016 | 6/24/2016 12:10:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Where consumer service neutral conductors are spliced at connection points between cables on poles and over head wiring between poles and structures, compression type connections are required. This is required because the neutral conductor is the grounded circuit conductor and is typically the fault path that current will follow in order to trip over current devices. Compression type connections are considered to be better than other mechanical type connectors. This installation of a 200A, 120/240V service upgrade on a residential property has consumer service neutral conductors that are spliced at pole tops using mechanical type connections. This is a shock and fire hazard if the connections fail and equipment either becomes energized or the failed connections produce excess thermal heating. Also an unbalanced three wire electrical system can cause an over voltage condition damaging circuits and equipment which is also a fire hazard. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Connections_at_pole_top.png | file://x:/photopub/docs/0000000447/1196c0e7-f294-4768-af2e-22fe928f8ea7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11eea243_731d_4ec6_9b58_30dff74964d9
ELIN-592388-2016 | EL-396433-2016 | 6/24/2016 12:10:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Where consumer service neutral conductors are spliced at connection points between cables on poles and over head wiring between poles and structures, compression type connections are required. This is required because the neutral conductor is the grounded circuit conductor and is typically the fault path that current will follow in order to trip over current devices. Compression type connections are considered to be better than other mechanical type connectors. This installation of a 200A, 120/240V service upgrade on a residential property has consumer service neutral conductors that are spliced at pole tops using mechanical type connections. This is a shock and fire hazard if the connections fail and equipment either becomes energized or the failed connections produce excess thermal heating. Also an unbalanced three wire electrical system can cause an over voltage condition damaging circuits and equipment which is also a fire hazard. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Service_pole.png | file://x:/photopub/docs/0000000447/9f28a7ec-aa9b-4807-8ca0-71c28956e966.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11eea243_731d_4ec6_9b58_30dff74964d9
ELIN-592388-2016 | EL-396433-2016 | 6/24/2016 12:10:55 PM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Where consumer service neutral conductors are spliced at connection points between cables on poles and over head wiring between poles and structures, compression type connections are required. This is required because the neutral conductor is the grounded circuit conductor and is typically the fault path that current will follow in order to trip over current devices. Compression type connections are considered to be better than other mechanical type connectors. This installation of a 200A, 120/240V service upgrade on a residential property has consumer service neutral conductors that are spliced at pole tops using mechanical type connections. This is a shock and fire hazard if the connections fail and equipment either becomes energized or the failed connections produce excess thermal heating. Also an unbalanced three wire electrical system can cause an over voltage condition damaging circuits and equipment which is also a fire hazard. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Connections_at_top_of_second_pole.png | file://x:/photopub/docs/0000000447/a649db97-a136-44c2-a3a9-ec377f07fdb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11eea243_731d_4ec6_9b58_30dff74964d9
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Basement_exterior_foam_formed_walls.png | file://x:/photopub/docs/0000000446/4859d16b-e7e4-43c9-b72a-06dcf71a60f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_in_foam_formed_walls.png | file://x:/photopub/docs/0000000446/57cb4d32-3e60-4f8a-9be5-6462984a0f76.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
GAIN-595853-2016 | GA-399414-2016 | 6/22/2016 2:59:03 PM | ASSESS: GA: Final | png | #asFound | GA078 | Relief style regulator/device terminated outdoors but not in a compliant manner | 2 | 2 |  | 2 | Relief style regulator/device terminated outdoors but not in a compliant manner | 7060_forest.png | file://x:/photopub/docs/0000000447/1ab57571-5542-482f-ab6b-2c2d06b9aee9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__557718b3_a78a_499c_ab44_3b38e8a460fa
GAIN-586169-2016 | GA-392581-2016 | 6/22/2016 3:28:42 PM | ASSESS: GA: Final | png | #asFound | GA081 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 3 | 2 | Liquid propane could enter the regulator which has a vapour rating only. Damage to the regulator could result in excessive downstream pressure. Possible downstream equipment damage resulting in fire and or carbon monoxide risk due to upset condition. | 3 | Propane system regulator installed in a non-compliant manner which allows for re-liquefaction | 213_tal.png | file://x:/photopub/docs/0000000447/b82d04cf-6876-4060-982d-172eb2fbbe3b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5d779a6_9718_47de_84e4_143c17e98b03
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Service_panel_at_shop.png | file://x:/photopub/docs/0000000447/0cce5436-e58c-45ee-9d8e-918b2f891c12.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Neutral_termination_at_meter_base.png | file://x:/photopub/docs/0000000447/a25c0352-8b3a-40c1-8200-18f44d072730.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Panel_in_temporary_enclosure.png | file://x:/photopub/docs/0000000447/d4f219ba-a08f-49cf-a532-5b626a2e55f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
BPVOP-596493-2016 | 3605075 | 6/23/2016 10:08:24 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP054 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | 2 | 2 |  | 2 | 1.2.2 Boiler leakage: procedure - Weeping, or staining from flanges or hand whole covers. | Outlet_flange_corrosion.png | file://x:/photopub/docs/0000000447/3c0d05ce-1a7c-4e6d-8f3b-125f5622305e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5714dff9_d5bb_4301_87aa_969903472d52
ELIN-594411-2016 | EL-336649-2016 | 6/22/2016 1:22:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables (NMSC) are required to be installed 32mm from the face of structural members when they pass through them. This is required to prevent damage to the cables from nails and screws both during and after construction. This installation of wiring for a new house has NMSC installed less than 32mm from the face of structural members where they pass through them. The branch circuit wiring passes through the vertical members of foam formed walls flush with the face of the wall. This is a shock and fire hazard if wiring is damaged by nails, screws, or other fasteners secured to the walls either during or after construction. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Wiring_installed_in_foam_formed_walls.png | file://x:/photopub/docs/0000000446/75e63a37-8fe0-462d-b876-97077072949a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__560e6b5e_237e_4096_83c5_9c2190b48d1f
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Label_showing_conductor_ranges_for_meter_base.png | file://x:/photopub/docs/0000000447/7e3324a1-896a-457a-8a89-d2ae4aadf64a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Terminations_in_meter_base.png | file://x:/photopub/docs/0000000447/e6e15a43-1c31-4e8f-8e74-a1cb1da336cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Label_on_panel_cover_showing_conductor_size_range_permitted.png | file://x:/photopub/docs/0000000447/236bd916-46b5-4507-860a-3dc908cd42b7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Conductor_terminations_at_shop.png | file://x:/photopub/docs/0000000447/128a4fb9-9e87-4304-9a83-0a3861fa1be0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | terminations_at_meter_base.png | file://x:/photopub/docs/0000000447/f20044cc-18ca-4824-9649-1fa75acf67ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Meter_bases_on_pole.png | file://x:/photopub/docs/0000000447/3fc367ec-188e-42eb-bf44-1f63f9d6da45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
ELIN-599286-2016 | EL-355781-2016 | 6/22/2016 9:31:59 AM | ASSESS: EL: Service Connection | png | #asFound | EL021 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | 3 | 3 | Conductors connected to termination lugs are required to meet the specifications of the equipment manufacturer with regards to the proper conductor size range. This is required so that the integrity of the connection is solid providing a safe termination that will allow for thermal expansion of a loaded conductor. This new installation of a 200A service on a residential property has service conductors terminated to termination lugs at a meter base and service panel. The conductors are sized at 350 Kcmil and terminated to lugs that are rated for a maximum size of 250 Kcmil. This is a potential fire hazard if the connections are not solid or if the conductors need to expand under load and damage the termination lugs. | 3 | Improper terminations or splices may result in overheating of conductors Joint or splice in consumer service conductor | Marking_on_service_cable_showing_size.png | file://x:/photopub/docs/0000000447/c74e1e1b-d99b-422c-9946-89e4bd71333e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11ec36f2_c645_49d0_8b9d_d1a1b501ab72
GAIN-594209-2016 | GA-398174-2016 | 6/23/2016 2:20:40 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 | Certified appliance connector not approved for use. Appliance connectors are not designed for vibration elimination. Hose can be damaged and fail due to prolonged vibration. | 2 | Certified appliance connector installed but not approved for application | Connector_not_certified_for_use_.png | file://x:/photopub/docs/0000000447/f5f875c2-864e-4768-bc18-18b7c08d65ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fced697d_9287_4f53_9aca_f06ae91f24ae
GAIN-595880-2016 | GA-397932-2016 | 6/23/2016 10:52:32 AM | ASSESS: GA: Rough-In | png | #asFound | GA000 | No Created Hazard Identified | 0 | 0 | No hazard as gas piping not connected to gas meter or furnace at this time. | 0 | No Created Hazard Identified | Clearance_not_mainained_.png | file://x:/photopub/docs/0000000447/04ca45b6-da4a-4808-bbda-7da007132f1b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b0d6b0f8_88e2_4b3b_bd89_af20b709dcf3
GAIN-598107-2016 | GA-400862-2016 | 6/22/2016 8:17:45 AM | ASSESS: GA: Final | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 | Inadequate vehicle protection. Propane tank could be damaged by vehicles on driveway. | 2 | Inadequate protection Low traffic | Inadequate_vehicle_protection.png | file://x:/photopub/docs/0000000447/d1fbd47c-51ad-41b5-acf7-b18073c8efc3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a16cb105_10d5_4a70_8910_ea89f2e7ec3e
GAIN-584013-2016 | GA-380139-2016 | 6/22/2016 2:56:02 PM | ASSESS: GA: Final | png | #asFound | GA024 | No protection Low traffic | 3 | 2 | Gas meter not protected in Driveway, homeowner or visitor could hit meter with vehicle causing damage to meter in turn possible gas leak or fire may may occur | 3 | No protection Low traffic | Gas_meter.png | file://x:/photopub/docs/0000000446/d2722842-979b-4a83-8844-5cac3abfc7cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d4a1cb71_793a_446b_807e_0ca4d188dc0c
BPVOP-598983-2016 | 2285313 | 6/22/2016 12:51:07 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Boiler fire tubes should have clear passage for the flue gas to transfer heat to surrounding fluid. I found a lake in one of the tubes of a 30psi hot water boiler. This can lead to corrosion and damage to the tubes. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | Tube_leak_.png | file://x:/photopub/docs/0000000447/cdd0d408-1605-4f99-9e5c-57b343513672.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d02c2f03_0735_4624_8d68_7ca5da3a2a80
BPVOP-598983-2016 | 2285313 | 6/22/2016 12:51:07 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Boiler fire tubes should have clear passage for the flue gas to transfer heat to surrounding fluid. I found a lake in one of the tubes of a 30psi hot water boiler. This can lead to corrosion and damage to the tubes. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | _Tube_sheet_Front.png | file://x:/photopub/docs/0000000447/456ed81d-9fe1-4a0e-be1e-a3c5f22d9298.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d02c2f03_0735_4624_8d68_7ca5da3a2a80
ELIN-591654-2016 | EL-392412-2016 | 6/23/2016 3:15:43 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Temp_wiring.png | file://x:/photopub/docs/0000000447/5ecb1e87-2605-457d-ab06-0cf053da668d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5104b57c_e6f2_49f1_a161_5a72358fa38e
ELIN-601683-2016 | EL-310393-2015 | 6/27/2016 2:59:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service is not grounded. Potential for electric shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Servicmast_with_two_clamps_and_ground_not_buried_energized_service.png | file://x:/photopub/docs/0000000448/fb731194-286c-432e-a04b-d281656b672e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c40bbd_dcf3_4d11_8a85_594e223aa111
ELIN-601683-2016 | EL-310393-2015 | 6/27/2016 2:59:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service is not grounded. Potential for electric shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Light_circuit_energized.png | file://x:/photopub/docs/0000000448/9af22a91-d1dc-4189-b106-83a0f04c7487.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c40bbd_dcf3_4d11_8a85_594e223aa111
ELIN-601683-2016 | EL-310393-2015 | 6/27/2016 2:59:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service is not grounded. Potential for electric shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Lighting_circuit_tagged_in_off_position.png | file://x:/photopub/docs/0000000448/ebaed7d8-3d7d-43a1-8de8-fe922a677903.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c40bbd_dcf3_4d11_8a85_594e223aa111
ELIN-601683-2016 | EL-310393-2015 | 6/27/2016 2:59:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service is not grounded. Potential for electric shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Lighting_circuits_were_energized.png | file://x:/photopub/docs/0000000448/5c7aff46-542c-458d-acd2-0222b676f622.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c40bbd_dcf3_4d11_8a85_594e223aa111
ELIN-601683-2016 | EL-310393-2015 | 6/27/2016 2:59:38 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Service is not grounded. Potential for electric shock. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Branch_circuits_tagged_off.png | file://x:/photopub/docs/0000000448/19cc19cc-2f6c-4ba4-b123-425b9de85aeb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32c40bbd_dcf3_4d11_8a85_594e223aa111
ELIN-600800-2016 | EL-283838-2015 | 6/27/2016 2:45:55 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | This assessment found the gas pipe installed without the required bond jumper. There is a risk of the pipe becoming energized from internal circuits or lightening; thereby presenting a fire and shock hazard. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Gas_pipe.png | file://x:/photopub/docs/0000000448/7324ca52-636b-4f83-806d-4cfb3ee28313.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fba67977_9048_4391_9e03_db8d58b2379b
ELIN-600932-2016 | EL-375818-2016 | 6/27/2016 12:22:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | This assessment found that the load on the mobile home exceeds the rating of the service. There is a risk of the high load overhearing wire terminations presenting a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Furnace.png | file://x:/photopub/docs/0000000448/2ad9426c-9f29-46e7-b98a-e72c66b31be5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c720b2b_00bd_4604_8cf1_bc1ced0d8142
ELIN-600932-2016 | EL-375818-2016 | 6/27/2016 12:22:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | This assessment found that the load on the mobile home exceeds the rating of the service. There is a risk of the high load overhearing wire terminations presenting a fire hazard. | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Panel.png | file://x:/photopub/docs/0000000448/82e232c4-7601-4aff-82ec-f33e93244dc0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0c720b2b_00bd_4604_8cf1_bc1ced0d8142
GAIN-544168-2016 | GA-228938-2015 | 6/27/2016 3:40:29 PM | ASSESS: GA: Final | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Exhaust vent of Rinnai is too close to un-dampered vent opening where exhaust gases could re-circulate into building | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_term.png | file://x:/photopub/docs/0000000448/c3e4522d-a401-4a68-a088-ba4b557a8826.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51b82c6d_1341_4987_80b3_a313694170cf
ELIN-597948-2016 | EL-399813-2016 | 6/23/2016 1:18:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 200 amp, 240 volt residential service main panel has exposed parts that if contacted may result in shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | P1.png | file://x:/photopub/docs/0000000447/afc742d7-9665-46bf-b593-bca5fe504744.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2c7d230_1460_4a62_a39a_2b549a3e5650
ELIN-597948-2016 | EL-399813-2016 | 6/23/2016 1:18:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 200 amp, 240 volt residential service main panel has exposed parts that if contacted may result in shock hazard. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | M1.png | file://x:/photopub/docs/0000000447/16aeb48f-5dc3-4798-a06d-5b000e65d599.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2c7d230_1460_4a62_a39a_2b549a3e5650
ELIN-600189-2016 | EL-352809-2016 | 6/24/2016 2:02:33 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | 125 amp, 240 volt residential service not grounded and bonded properly; shock and thermal hazard to persons and equipment. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | P2.png | file://x:/photopub/docs/0000000447/5cf2d269-da1b-44e3-97ee-6d03f5fdea17.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__31b71593_bf71_4864_9014_396fe0bd5db0
ELIN-577531-2016 | EL-360976-2016 | 6/21/2016 10:27:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Poles installed to support electrical equipment and over head wiring are required to be marked to show the class, length, type, and a gain mark to indicate the pole setting depth. This is required to ensure that the pole installed is suitable for the intended use and set to the correct depth to support itself and the equipment and wiring connected to it. This new installation of a primary (high voltage) over head power line on a private residential property has a pole installed that does not have any markings on it to indicate it is a suitable pole for this use. The installation is not currently connected but is intended to be connected using this pole. This is a potential shock and fire hazard if the pole fails and breaks, or prematurely deteriorates and falls over leaving high voltage conductors exposed to contact. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | No_markings_on_pole_.png | file://x:/photopub/docs/0000000446/7fe0dc71-479a-4c8e-b5fe-e2c4f50eea8a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d97c0578_ffeb_4fbc_ae3c_8abd4a836c0d
ELIN-577531-2016 | EL-360976-2016 | 6/21/2016 10:27:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Poles installed to support electrical equipment and over head wiring are required to be marked to show the class, length, type, and a gain mark to indicate the pole setting depth. This is required to ensure that the pole installed is suitable for the intended use and set to the correct depth to support itself and the equipment and wiring connected to it. This new installation of a primary (high voltage) over head power line on a private residential property has a pole installed that does not have any markings on it to indicate it is a suitable pole for this use. The installation is not currently connected but is intended to be connected using this pole. This is a potential shock and fire hazard if the pole fails and breaks, or prematurely deteriorates and falls over leaving high voltage conductors exposed to contact. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | No_markings_on_pole.png | file://x:/photopub/docs/0000000446/3bd3d269-e14a-4857-b10e-0198ef7f4874.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d97c0578_ffeb_4fbc_ae3c_8abd4a836c0d
ELIN-577531-2016 | EL-360976-2016 | 6/21/2016 10:27:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL027 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | 3 | 3 | Poles installed to support electrical equipment and over head wiring are required to be marked to show the class, length, type, and a gain mark to indicate the pole setting depth. This is required to ensure that the pole installed is suitable for the intended use and set to the correct depth to support itself and the equipment and wiring connected to it. This new installation of a primary (high voltage) over head power line on a private residential property has a pole installed that does not have any markings on it to indicate it is a suitable pole for this use. The installation is not currently connected but is intended to be connected using this pole. This is a potential shock and fire hazard if the pole fails and breaks, or prematurely deteriorates and falls over leaving high voltage conductors exposed to contact. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; clearances provided for overhead conductors. | Primary_pole_on_private_property.png | file://x:/photopub/docs/0000000446/4185fb22-8532-489e-86fc-85059d259b4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d97c0578_ffeb_4fbc_ae3c_8abd4a836c0d
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 3.png | file://x:/photopub/docs/0000000446/9cadf723-635a-46a2-935e-8a9346d7d596.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 1.png | file://x:/photopub/docs/0000000446/dfe5ad7b-7bf4-4c63-bd5f-d0712fa3be66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 5.png | file://x:/photopub/docs/0000000446/8ed829bc-311e-4dab-bdf0-6a8f27a7b400.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
BPVOP-599066-2016 | 2271096 | 6/22/2016 4:16:27 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP043 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | 2 | 2 | Minimum required thickness of tube determines the Maximum Allowable Working Pressure at or below which boiler can be operated safely. During inspection I found that boiler tube has nicked areas (due to corrosion and/or mechanical impact) with thickness close to minimum required for operation. Any further deterioration of tubes in theses areas may lead to tube leak with consequent downtime. | 2 | 1.2.0 Corrosion/PSI Retention - Active local or general corrosion or erosion that causes thinning of a pressure retaining component which reduces the corrosion allowance | Rear_tubesheet.png | file://x:/photopub/docs/0000000446/bedf54a1-2484-46ac-ac14-53b3df98863c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26ef5d66_b4ae_4001_a574_67e3b7fa3fc2
BPVOP-601134-2016 | 2291755 | 6/26/2016 1:34:52 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | SWEID_TF_BOILER.png | file://x:/photopub/docs/0000000448/ed6ac42a-452c-45fb-94d7-ffff0f98bf9a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bfd08e1e_1632_4b88_b6d5_49a1d3a6a830
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 7.png | file://x:/photopub/docs/0000000446/e1b167a6-e890-47c1-bcb3-52d18155bb0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 2.png | file://x:/photopub/docs/0000000446/3ff1d1dd-7d19-4b89-994a-b99c6a7d64b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 6.png | file://x:/photopub/docs/0000000446/cd9cd6a1-49cd-4d3b-856b-9a42e63db5f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
ELIN-595758-2016 | EL-388264-2016 | 6/21/2016 5:11:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found high voltage 25 KV rated 3000 KVA consumer's service pad mounted unit substation does not have service system grounded at all as required by code. Neutral bar or XO point of transformer has no system grounding conductor and is not connected directly to high voltage grounding system. If electrical system is not on equipotential grounding plane and a fault condition happens, the supply system over-current devices might not effectively operate as required to safely disconnect and eliminate electrical hazards to protect people and property from electrical fire or shock hazards. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4.png | file://x:/photopub/docs/0000000446/a1dd018a-6e7e-4d7e-b520-185a84f7e5f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__48a947b7_36fb_4ef6_8697_b5f89f625771
ELIN-601322-2016 | EL-400228-2016 | 6/27/2016 3:54:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Conduit between meter base and panel has not been bonded. Risk for electric shock if fault occurred. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond_2.png | file://x:/photopub/docs/0000000449/403f9b01-9429-448d-a71c-3809be8d3177.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46ad9027_3a40_4e29_97f1_10f74d0b759d
ELIN-601322-2016 | EL-400228-2016 | 6/27/2016 3:54:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Conduit between meter base and panel has not been bonded. Risk for electric shock if fault occurred. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Dirt_floor.png | file://x:/photopub/docs/0000000449/04e83c7b-c467-4729-8257-7935a61e19eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46ad9027_3a40_4e29_97f1_10f74d0b759d
ELIN-601322-2016 | EL-400228-2016 | 6/27/2016 3:54:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Conduit between meter base and panel has not been bonded. Risk for electric shock if fault occurred. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_bond.png | file://x:/photopub/docs/0000000449/6219cdd3-ab24-4d4d-a306-d10c36519a09.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46ad9027_3a40_4e29_97f1_10f74d0b759d
ELIN-601322-2016 | EL-400228-2016 | 6/27/2016 3:54:20 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Conduit between meter base and panel has not been bonded. Risk for electric shock if fault occurred. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Tel_cable_bond_is_bare_copper.png | file://x:/photopub/docs/0000000449/493f667f-e1bb-446c-9894-cfcab3c1bb55.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__46ad9027_3a40_4e29_97f1_10f74d0b759d
ELIN-597937-2016 | EL-392058-2016 | 6/24/2016 9:52:33 AM | ASSESS: EL: Service Connection | png | #asFound | EL042 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | 2 | 2 | A new photovoltaic system has been installed. Operating at 240 volts and 20 amps, the photo panels are accessible to the public. The panels are not marked with an installation class. If photovoltaic panels are not installed to the installation class requirements people can be injured | 2 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | No_installation_class.png | file://x:/photopub/docs/0000000448/e513d367-cb3b-44f8-bdb7-ac164f89330a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d257959f_e981_44a8_9b36_18796571f7d1
BPVOP-601133-2016 | 2259779 | 6/26/2016 3:23:38 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | The tube ends on 5 boiler tubes exhibited signs of leakage under Hydrostatic test pressure requiring them to be replaced prior to being able to safely run the boiler. The contractor had difficulty removing the damaged tubes due to excessive accumulation of hard scale on the tube outer surfaces. This accumulation is greater than what was observed during last year's annual inspection. The accumulation of hard scale on the boiler tubes will reduce the amount of heat transferred from the heat source to the fluid it is heating resulting in greater output being required from the boiler to achieve the desired setting and lowering the overall efficiency of the boiler. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | SCALE_ACCUMULATION.png | file://x:/photopub/docs/0000000448/f4965945-456c-456a-8d50-9735d6ba97d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a64e4aac_bb02_438e_ad1e_a246af7dccf0
ELIN-585381-2016 | EL-320425-2015 | 6/23/2016 6:09:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 100.png | file://x:/photopub/docs/0000000447/40e9147c-f861-44f8-933f-ed1bcec4bdbf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e128afa6_57ac_419a_a2f1_0234f654b025
ELIN-582902-2016 | EL-390170-2016 | 6/22/2016 11:14:19 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a routine mobile home Silver Label certification, a 100amp 120/240volt main service was found without an effective system ground in place. This can lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Loose_bond_connection.png | file://x:/photopub/docs/0000000446/6dfada32-558a-4a12-a935-fb3657d45376.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6324db4_55ab_49f2_9ddb_272538f427d7
ELIN-582902-2016 | EL-390170-2016 | 6/22/2016 11:14:19 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a routine mobile home Silver Label certification, a 100amp 120/240volt main service was found without an effective system ground in place. This can lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Heat_trace.png | file://x:/photopub/docs/0000000446/6c7cc7d4-f8a9-41bf-87ba-d4d938d3e21d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6324db4_55ab_49f2_9ddb_272538f427d7
ELIN-582902-2016 | EL-390170-2016 | 6/22/2016 11:14:19 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a routine mobile home Silver Label certification, a 100amp 120/240volt main service was found without an effective system ground in place. This can lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | KO_filler_missing.png | file://x:/photopub/docs/0000000446/e3de0e79-1531-42e9-b5c1-cc87fbadb263.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6324db4_55ab_49f2_9ddb_272538f427d7
ELIN-582902-2016 | EL-390170-2016 | 6/22/2016 11:14:19 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | In a routine mobile home Silver Label certification, a 100amp 120/240volt main service was found without an effective system ground in place. This can lead to a thermal effect. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Ground_connected_to_lug.png | file://x:/photopub/docs/0000000446/9698b9bf-0a56-42b6-b4ca-e87bc3a3a38f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6324db4_55ab_49f2_9ddb_272538f427d7
ELIN-582935-2016 | EL-253331-2015 | 5/26/2016 10:39:48 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Electrical equipment used sold or installed in BC must bear evidence of approval from an accredited approval agency. In this liquor store installation electric rolling shutters were installed. No certification marks were observed onsite and later discussion with the manufacturer confirmed none had been obtained. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Manufacturer_mark_on_product.png | file://x:/photopub/docs/0000000448/418847c1-c702-4c16-a52f-5e23aaff257c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__167beed1_0841_42e3_bbb9_061d4fb7d703
ELIN-585381-2016 | EL-320425-2015 | 6/23/2016 6:09:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 104.png | file://x:/photopub/docs/0000000447/b5b49d44-3a0c-4bfa-8953-63c1bd964729.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e128afa6_57ac_419a_a2f1_0234f654b025
ELIN-585381-2016 | EL-320425-2015 | 6/23/2016 6:09:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 102.png | file://x:/photopub/docs/0000000447/08e6f73b-c10b-4989-903f-798bec7844d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e128afa6_57ac_419a_a2f1_0234f654b025
ELIN-585381-2016 | EL-320425-2015 | 6/23/2016 6:09:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 101.png | file://x:/photopub/docs/0000000447/ce930018-f386-490b-8c5a-9d383fbf4526.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e128afa6_57ac_419a_a2f1_0234f654b025
ELIN-585381-2016 | EL-320425-2015 | 6/23/2016 6:09:09 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL086 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 2 | 2 |  | 2 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 103.png | file://x:/photopub/docs/0000000447/5a7be39c-8a07-4e75-8b80-03afa6f24cdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e128afa6_57ac_419a_a2f1_0234f654b025
BPVOP-599321-2016 | 2286545 | 6/24/2016 12:08:18 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety Orders must be followed. During the inspection of a machined mounted air receiver manufactured in 1992, I fund that no NDE was done as per Safety Order SO-B60505303. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | Overall___.png | file://x:/photopub/docs/0000000447/96edd4a8-2959-418e-86f5-ea3e9d93182b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ff643f4a_e5a6_45d2_b573_2cc78fafc422
ELIN-594314-2016 | EL-380309-2016 | 6/24/2016 10:35:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service conductors inside wall/unapproved point of attachment/hazardous live receptacles | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Point_of_attachment.png | file://x:/photopub/docs/0000000447/39661d10-e362-4e24-bffa-08a953b03436.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfd63251_c6c0_4549_99f3_fe07b8bfddbf
ELIN-594314-2016 | EL-380309-2016 | 6/24/2016 10:35:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service conductors inside wall/unapproved point of attachment/hazardous live receptacles | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_recessed.png | file://x:/photopub/docs/0000000447/551b8df0-c9ea-4875-adc2-a1ca1055d3fc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfd63251_c6c0_4549_99f3_fe07b8bfddbf
ELIN-594314-2016 | EL-380309-2016 | 6/24/2016 10:35:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service conductors inside wall/unapproved point of attachment/hazardous live receptacles | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Live_receptaces.png | file://x:/photopub/docs/0000000447/8a238750-f116-4071-bc50-fe8df1009153.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfd63251_c6c0_4549_99f3_fe07b8bfddbf
ELIN-594314-2016 | EL-380309-2016 | 6/24/2016 10:35:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Service conductors inside wall/unapproved point of attachment/hazardous live receptacles | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Missing_panel_fillers.png | file://x:/photopub/docs/0000000447/8ab8fcb9-b632-4ee1-a7a9-91d42e6bc479.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dfd63251_c6c0_4549_99f3_fe07b8bfddbf
ELIN-594205-2016 | 5435580 | 6/24/2016 8:53:57 PM | ASSESS: EL: Final | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | A.png | file://x:/photopub/docs/0000000448/a0968b84-30c8-4fb4-ba8b-1ddaeec2227c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__367e1ef7_e419_45f2_b91d_a00fc6d69128
ELIN-605366-2016 | EL-397563-2016 | 7/12/2016 9:00:08 AM | ASSESS: EL: Service Connection | png | #asFound | EL060 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | 2 | 2 | A residential panel board upgrade to existing dwelling 200 amp 240 volt has been installed with top overcurrent device 1.95 meters above the floor. Panel boards are to be mounted to allow average height persons reasonable safe access to panel boards and breakers. Panels mounted in excess of recommended heights an lead to safety issues for workers and operators and least to injury of persons | 2 | Improper installation or location of equipment, conductors, cables or raceways Inadequate working clearances; dedicated spaces | Panel_1_95_meters_to_top_breaker.png | file://x:/photopub/docs/0000000455/71d1e97b-de6c-4c99-bcfe-ebf543c8f180.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a78eeec3_c19c_43cd_b024_4ebb04d97c17
ELIN-606082-2016 | EL-304538-2015 | 7/12/2016 11:44:47 AM | ASSESS: EL: Final | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | 3 Dry location type 200 amp 240 volt combination panels have been mounted outdoors in a plywood enclosure. Electrical equipment that has not been installed using approved outdoor enclosures can be subject to ingress of rain and water. This can lead to property damage or injury to persons | 3 | General Equipment is not approved for the specific use | Dry_location_panels_outdoors_in_1_2_inch_plywood_enclosure.png | file://x:/photopub/docs/0000000455/681a52c4-a912-4261-ae93-3e85d3c89925.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dd9ecb43_fa6e_4fea_b35e_a259c9264606
AMOP-608353-2016 | 5371356 | 7/13/2016 12:55:59 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | This is a design flaw from the Manufacturer. A user would have the potential to fall through the opening and contacting wall resulting in the possibility of an injury. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Exposed_opening_to_adjacent_wall_.png | file://x:/photopub/docs/0000000455/da03ae75-d916-447b-8ff3-95d5eb636ea4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8776882e_fe32_42f3_ae30_4100d65348fa
ELIN-626707-2016 | EL-419004-2016 | 8/10/2016 11:24:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Thin wall plastic duct is subject to damage until encased in concrete or backfill | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Unprotected_service_ducts.png | file://x:/photopub/docs/0000000469/3e439d31-f2c7-4dd8-bc67-8f7adf437412.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fa21842_71aa_4afe_abba_56d29cef2651
ELIN-626707-2016 | EL-419004-2016 | 8/10/2016 11:24:50 AM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Thin wall plastic duct is subject to damage until encased in concrete or backfill | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | Meter_base_service_wiring.png | file://x:/photopub/docs/0000000469/90a23bfa-9c4b-4a58-941e-a346837b259a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3fa21842_71aa_4afe_abba_56d29cef2651
ELIN-621566-2016 | EL-418507-2016 | 8/2/2016 11:39:51 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Rough wired circuits are terminated on breakers that are not adequately locked out. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Duct_tape_lockout.png | file://x:/photopub/docs/0000000464/6b289450-af6b-4687-839f-eed65c2f10a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e801f95f_ce61_4850_a91a_5fc71a26ed62
ELIN-601555-2016 | EL-391824-2016 | 6/27/2016 12:32:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Hazardous service installation, no inspection requests | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Unfused_cond.png | file://x:/photopub/docs/0000000449/e26257b6-5aa1-48a5-9d9a-81068f04207b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15fb01dd_4988_45ff_82e4_19c53ee2deed
ELIN-601555-2016 | EL-391824-2016 | 6/27/2016 12:32:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Hazardous service installation, no inspection requests | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Temp_receptacles.png | file://x:/photopub/docs/0000000449/dcf3b22a-f475-4ba3-9e86-a04726d5236a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15fb01dd_4988_45ff_82e4_19c53ee2deed
ELIN-601555-2016 | EL-391824-2016 | 6/27/2016 12:32:53 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Hazardous service installation, no inspection requests | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Serv_conduit.png | file://x:/photopub/docs/0000000449/18dfdbfc-42b3-435e-a2b9-5b3a98a86ab5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__15fb01dd_4988_45ff_82e4_19c53ee2deed
ELIN-598033-2016 | EL-388113-2016 | 6/27/2016 2:54:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Incomplete non-compliant service not safe for connection | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Service_masts.png | file://x:/photopub/docs/0000000449/81bc2546-3138-425a-ada0-19be14091f16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f14403c1_bb51_4626_b6fc_b731683a555f
ELIN-598033-2016 | EL-388113-2016 | 6/27/2016 2:54:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | Incomplete non-compliant service not safe for connection | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Weather_head.png | file://x:/photopub/docs/0000000449/eb7d0736-084b-4aa0-be2a-eef9c963cfc4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f14403c1_bb51_4626_b6fc_b731683a555f
BPVOP-595663-2016 | 3093886 | 6/29/2016 3:00:18 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP019 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | 2 | 3 | Found that this expansion tank on the hot water side (200F) has no supports and can fall due to a seismic shock. | 2 | 1.0.2 Clearances/Maintenance - Foundations and supports have deterioration including spalling and cracking that are likely to propagate. | This_tall_tank_has_no_supports_.png | file://x:/photopub/docs/0000000449/80ffeb55-ac8e-4894-901e-305ffa3c3c78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9eeb398d_3e49_47d1_bedd_83ee3c4f6799
ELIN-602719-2016 | EL-374857-2016 | 6/30/2016 9:59:18 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | Cables doubled up under one cable tab are not supported from strain and abrasion | 0 | No Created Hazard Identified | 2_cables_per_box_tab.png | file://x:/photopub/docs/0000000450/466ae845-1a53-4900-a64d-ee2e4f007496.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__571cf414_3ecf_4ae0_9caf_8a66ae4eefe9
ELHE-603792-2016 | HE-404542-2016 | 6/30/2016 10:57:35 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | The ground conductor for the high voltage switch has been damaged and is cut. This has created a shock hazard if a fault occurs | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Switch_ground.png | file://x:/photopub/docs/0000000450/0c5ee6ac-415f-402c-b247-308911f28429.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__254fc482_7fc3_4f13_9c13_e1ff2406ed7a
BPVOP-538780-2016 | 4251078 | 7/7/2016 3:45:26 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP201 | 5.1.0 In service proc/process - Burner setup incorrect | 2 | 2 | Boiler HW63992 - HS = 125 M^2 MWAP = 125 psig Over due for servicing, combustion operating in the fuel rich zone, boiler has been isolated and dry stored, repair will be done before unit is returned to service. | 2 | 5.1.0 In service proc/process - Burner setup incorrect | HW63992_Tube-sheet_soot.png | file://x:/photopub/docs/0000000457/e1515c91-9a1b-405c-acf7-fc19570da603.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8efbdd5f_88e0_4f0d_b861_0dd8e0479582
BPVOP-538780-2016 | 4251078 | 7/7/2016 3:45:26 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP201 | 5.1.0 In service proc/process - Burner setup incorrect | 2 | 2 | Boiler HW63992 - HS = 125 M^2 MWAP = 125 psig Over due for servicing, combustion operating in the fuel rich zone, boiler has been isolated and dry stored, repair will be done before unit is returned to service. | 2 | 5.1.0 In service proc/process - Burner setup incorrect | HW63992_Rear_Tube_Sheet_2nd_pass_tube_leakage_site.png | file://x:/photopub/docs/0000000457/0501b499-c914-4b1f-b6d8-1b522f68a6f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8efbdd5f_88e0_4f0d_b861_0dd8e0479582
BPVOP-538780-2016 | 4251078 | 7/7/2016 3:45:26 PM | ASSESS: BPV OP: Miscellaneous Boiler | png | #asFound | BP201 | 5.1.0 In service proc/process - Burner setup incorrect | 2 | 2 | Boiler HW63992 - HS = 125 M^2 MWAP = 125 psig Over due for servicing, combustion operating in the fuel rich zone, boiler has been isolated and dry stored, repair will be done before unit is returned to service. | 2 | 5.1.0 In service proc/process - Burner setup incorrect | HWH_63992_combustion_tube.png | file://x:/photopub/docs/0000000457/080bf918-f1e4-4636-8880-c016f4ca49a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8efbdd5f_88e0_4f0d_b861_0dd8e0479582
ELIN-604852-2016 | UW-406867-2016 | 7/4/2016 12:20:13 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 | A permit is required before regulated work is done except in an emergency. In this summer residence the owner had hired a contractor to update an office space. This was done without permit. | 0 | No Created Hazard Identified | Copy_left_onsite.png | file://x:/photopub/docs/0000000451/f38f3935-cc0c-42d1-a661-4118d0abef03.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9458cf3f_f610_43b9_81d7_71fecdd12bb1
ELIN-603801-2016 | UW-404562-2016 | 6/30/2016 11:15:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL039 | Equipment is not marked / identified Multiple service boxes not marked. | 2 | 2 | The electrical vault contains high voltage switch and transformer that require maintenance to ensure proper operation. Without the maintenance the operation of the safety devices may not occurs during a fault and cause a fire. | 2 | Equipment is not marked / identified Multiple service boxes not marked. | Service_vault_disconnect.png | file://x:/photopub/docs/0000000450/21a5630a-8575-499c-bd16-6b41a0382324.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__65649225_9a79_46dc_8f80_2205b41a974d
GAIN-605854-2016 | GA-401209-2016 | 7/14/2016 10:18:10 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Flex_range.png | file://x:/photopub/docs/0000000457/85ee9e34-7800-44f2-9af3-d8e7aa2676a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cc7d2fa_01fd_4b32_9dad_5624d8f62948
GAIN-605854-2016 | GA-401209-2016 | 7/14/2016 10:18:10 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Flex_fryer.png | file://x:/photopub/docs/0000000457/9226876e-5dfe-439a-ae55-5e207de3fe2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5cc7d2fa_01fd_4b32_9dad_5624d8f62948
ELIN-603625-2016 | EL-234501-2015 | 7/21/2016 5:51:04 PM | ASSESS: EL: Final | png | #asFound | EL197 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | 5 | 5 | Certified individual observed performing regulated work to energized consumer supply service metering equipment without PPE, procedures in place and prior authorization from utility. This presented a serious and immediate hazard to certified individual and assistant on site of personal injury (shock) or catastrophic property damage (thermal event/interface fire). | 5 | Energized work by qualified persons, Risk Reg EL-26-2017 High or Low voltage: no PPE in place. | View01_energized_unguarded_meter_base.png | file://x:/photopub/docs/0000000460/43e3265f-23cd-41ef-ba04-f99859d51479.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afdad9f3_25f1_4820_9427_26872e4b9e25
ELIN-598948-2016 | EL-304571-2015 | 7/21/2016 10:37:58 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cables installed in wood construction should be protected with a minimum of 32 mm of wood or approved steel protection plates. This protects the cables from being damaged during the installation of wall finishes. During the inspection it was observed that cables had not been installed with adequate protection. This presents a possible shock hazard to the installer of the wall finishes and or a short circuit that could cause a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Haisla_center_2.png | file://x:/photopub/docs/0000000460/feb92046-dee9-4b7a-8fb7-12ef70284724.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2ef224a_e393_43d8_bd42_7479f57dfc38
ELIN-598948-2016 | EL-304571-2015 | 7/21/2016 10:37:58 AM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Cables installed in wood construction should be protected with a minimum of 32 mm of wood or approved steel protection plates. This protects the cables from being damaged during the installation of wall finishes. During the inspection it was observed that cables had not been installed with adequate protection. This presents a possible shock hazard to the installer of the wall finishes and or a short circuit that could cause a fire. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Haisla_centre_.png | file://x:/photopub/docs/0000000460/0e593c4d-cf45-4771-bf45-420e3c18e555.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d2ef224a_e393_43d8_bd42_7479f57dfc38
BPVIN-607281-2016 | BPV-403082-2016 | 7/7/2016 1:01:33 PM | ASSESS: BPV IN: Final (First Certification) Boiler | png | #asFound | BP141 | 4.0.1 Incorrect readings/alarms - Instrumentation or alarms installed contrary to manufacturer or code requirement | 2 | 2 | Upon assessment it is determined that thermometer temperature range is below code requirement but within operating range. There is no way to verify abnormal operation beyond normal operating condition with accuracy. | 2 | 4.0.1 Incorrect readings/alarms - Instrumentation or alarms installed contrary to manufacturer or code requirement | Thermometer_range_not_to_code.png | file://x:/photopub/docs/0000000453/352ec386-0ebf-4482-8f96-aa7fb4308a26.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__946b9b8a_c0cb_4864_8908_3ed5e41ea2df
EDRI-607623-2016 | ED-279916-2015 | 7/7/2016 4:53:03 PM | ASSESS: ED RI: Extension | png | #asFound | ED051 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | 4 | 4 | Access to elevator cartop available because of missing hoarding barricades | 4 | Switches / circuits controlling access point working correctly Damp/Wet/Outdoor Location Dark/unlit space Oily Surface No Fall prevention means in place | Hoarding_at_37.png | file://x:/photopub/docs/0000000453/7be9d3e5-d4ed-4cf1-af3d-d411e47a7444.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c81f195a_2165_4c55_b02f_98a4afd7f604
EDRI-607626-2016 | ED-279923-2015 | 7/7/2016 5:17:12 PM | ASSESS: ED RI: Extension | png | #asFound | ED055 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | 4 | 4 | Access to landing without fall protection | 4 | Sharp Edges Uneven Landing Surface Slipping /Tripping Hazard Dimly lit Space | Hoarding_landing_37.png | file://x:/photopub/docs/0000000453/361ddbd2-7cdc-4e30-b5ce-8ab226e01def.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__389434a1_969a_461b_bdab_5bb41c3cc577
ELIN-605104-2016 | EL-373641-2016 | 7/6/2016 9:55:58 AM | ASSESS: EL: Service Connection | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 2 | The contractor provided an inadequate attachment point for a 400 amp overhead service. This could lead to bending of the individual masts under heavy snow load or a tree falling on the supply lines. A severe bend could lead to shorting of the supply conductors within the mast causing a shock hazard. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 400_amp_point_of_attachment.png | file://x:/photopub/docs/0000000462/5c8b2137-48cd-4849-86ae-2040927aa136.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__93c4b743_d569_4374_adfd_b0f779909012
ELIN-523645-2016 | UW-133459-2014 | 7/18/2016 12:02:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermoplastic wrapped armoured cable is not intended to be permanently installed on the earths surface without adequate mechanical protection and support. In this installation a cable was installed on the ground between two buildings. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | On_surface.png | file://x:/photopub/docs/0000000458/873769e0-3419-4ce5-a4a5-5fd3b046e149.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6c584b4_1263_4718_87e1_2c3962aee850
ELOP-226735-2014 | 1023 | 7/18/2016 9:30:23 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords are not intended to be used as a replacement for permanent wiring. In this remote school installation a wood shop was powered with a flexible cord run over ground and partially buried. | 4 | Conductors, Misuse of flexible cords. | Cabtyre.png | file://x:/photopub/docs/0000000458/f94f508d-f9fa-44c2-991c-3ee8314e118d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7749d169_3bd2_42c6_aeaa_e8e712dd8d03
ELIN-523645-2016 | UW-133459-2014 | 7/18/2016 12:02:29 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermoplastic wrapped armoured cable is not intended to be permanently installed on the earths surface without adequate mechanical protection and support. In this installation a cable was installed on the ground between two buildings. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Unprotected.png | file://x:/photopub/docs/0000000458/ed226d4c-4109-4520-9d07-8d0c1d256cb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6c584b4_1263_4718_87e1_2c3962aee850
ELOP-386352-2015 | 4751406 | 7/19/2016 10:06:55 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | Receptacles within 1.5 m of sinks required GFCI protection. In this commercial bar installation undercounter receptacles beside the bar sink were not observed with GFCI protection. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Forgot_to_shoot_new_photos.png | file://x:/photopub/docs/0000000458/dc432c42-6495-402d-b6f2-f54854595191.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9dbd6892_c64d_4f2b_a342_60bd3d2ec9e1
ELIN-613667-2016 | EL-411348-2016 | 7/20/2016 10:08:46 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL136 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | 3 | 3 | 15 amp, 120 volt device box exceeds maximum box fill allowed. This is a thermal issue. | 3 | Installation of electrical equipment General: boxes do not have adequate depth for the equipment that will be installed. | Conductors_entering_device_box.png | file://x:/photopub/docs/0000000459/12a24299-b0d8-4085-abe9-c2f8a8de718e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4c499856_9198_44a5_9ef6_c42961383369
EDIN-607890-2016 | ED-346010-2016 | 7/18/2016 3:41:06 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED014 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 3 | 3 | The pit is to be dry from moisture. It was found during an acceptance inspection the pit had 2 inches of water. Water in the pit for a prolong period of time will cause corrosion of equipment in the pit and surrounding areas. Corrosion of equipment may cause failure of safety equipment when it is needed to be functional in an emergency situation. It was found the general contractor did not ensure that the sump pump is operational. This new 9 stop MRL elevator is located in a residential building. | 3 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 40458-As-Found.png | file://x:/photopub/docs/0000000457/24e2def6-d527-4c8c-afc1-6909eff0dcb3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f217f60d_2b4b_40f7_9afb_fa6a099b7237
EDIN-613809-2016 | ED-346008-2016 | 7/15/2016 | ASSESS: ED IN: Acceptance | png | #asFound | ED014 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 3 | 3 | The pit is to be dry from moisture. It was found during an acceptance inspection the pit had 2 inches of water. Water in the pit for a prolong period of time will cause corrosion of equipment in the pit and surrounding areas. Corrosion of equipment may cause failure of safety equipment when it is needed to be functional in an emergency situation. It was found the general contractor did not ensure that the sump pump is operational. This new 9 stop MRL elevator is located in a residential building. | 3 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 40457-40458-As-Found.png | file://x:/photopub/docs/0000000457/6db4add7-9268-459b-beb7-933b9cc365b0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd600da5_89e7_4924_80ab_b879a8095702
EDIN-613809-2016 | ED-346008-2016 | 7/15/2016 | ASSESS: ED IN: Acceptance | png | #asFound | ED014 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 3 | 3 | The pit is to be dry from moisture. It was found during an acceptance inspection the pit had 2 inches of water. Water in the pit for a prolong period of time will cause corrosion of equipment in the pit and surrounding areas. Corrosion of equipment may cause failure of safety equipment when it is needed to be functional in an emergency situation. It was found the general contractor did not ensure that the sump pump is operational. This new 9 stop MRL elevator is located in a residential building. | 3 | Oil/Water/Other Debris that: Does not present a fire hazard but is likely to progress | 40457-As-Found.png | file://x:/photopub/docs/0000000457/5a60cd5d-0fc6-4bcb-9731-5f3402d023c1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd600da5_89e7_4924_80ab_b879a8095702
GAIN-621939-2016 | GA-415631-2016 | 8/12/2016 2:38:05 PM | ASSESS: GA: Final | png | #asFound | GA082 | Vent limiter style regulator not installed in a ventilated space | 3 | 3 | 2 PSI regulator with vent limiter installed in unventilated space. A regulator failure would allow the build up of gas in a confined space,which could go unnoticed by the occupants. Possible fire hazard if a source of ignition was present. | 3 | Vent limiter style regulator not installed in a ventilated space | Concealed_regulator.png | file://x:/photopub/docs/0000000471/5a1e9ad2-a06e-4617-a10f-5a4c0c222e5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__09632313_0825_41f6_8bbb_87f06681e5f7
GAIN-628978-2016 | GA-423016-2016 | 8/12/2016 3:49:46 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Seven_universe.png | file://x:/photopub/docs/0000000471/328f3f4f-ecbf-4c3c-bfbb-3a5151a9537c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__192996fb_7d81_4d76_adae_09aadceb2669
ELIN-635945-2016 | EL-427439-2016 | 8/25/2016 10:33:32 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | NMSC_service_cable.png | file://x:/photopub/docs/0000000475/65cfd5aa-5ac1-4e05-8eec-56c3eb7940ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2601480_85ce_4641_93f5_7483a8c3f89f
ELIN-613325-2016 | EL-407169-2016 | 7/20/2016 2:38:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL120 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | 3 | 3 | Nonmetallic sheathed cable in slabs are not mechanically protected and can result in a shock or fire hazard | 3 | Conductors Cables, Raceways or conductors are; damaged or may become damaged; and need to be either replaced, repaired, or provided with mechanical protection. | NMD90_in_slab.png | file://x:/photopub/docs/0000000459/929358fb-a78d-41c8-9594-8e0137431d1c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a8d6ee68_cefb_406e_952d_7c16012da467
ELIN-627665-2016 | EL-407529-2016 | 8/10/2016 3:16:47 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Panel filler is missing for breaker installation. This is a shock hazard. | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Breaker_panel_filler_missing_on_energized_distribution_panel_.png | file://x:/photopub/docs/0000000469/b3fd0c32-e334-4878-9bde-18909d27be27.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c6a00c31_a888_4d08_a157_941980b6a9a4
ELIN-604657-2016 | EL-406661-2016 | 7/5/2016 2:14:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | The point of attachment for 240v single phase 100a overhead pole service supply conductors must utilize a bolt-through type insulator to minimize the likelihood of energized supply conductors detaching from the overhead service and falling to within reach of pedestrians. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Emily_knob_point_of_attachment_on_unapproved_pole.png | file://x:/photopub/docs/0000000452/055cdb0e-3b5a-4ee5-a247-2a73dcec4fab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f8503799_f54b_4fbe_8405_89f9dcf8f96e
ELIN-618784-2016 | EL-354205-2016 | 7/27/2016 1:10:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermal hazard due unprotected cable. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder2.png | file://x:/photopub/docs/0000000462/57f49605-4e74-4e9d-96bb-a8a2f5b3ad01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca4fa18_e72d_4405_a794_e1edbd334e07
ELIN-618784-2016 | EL-354205-2016 | 7/27/2016 1:10:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermal hazard due unprotected cable. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Service_panel.png | file://x:/photopub/docs/0000000462/60699d7b-4a9b-4475-9a9b-0f3170e6a8c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca4fa18_e72d_4405_a794_e1edbd334e07
ELIN-618784-2016 | EL-354205-2016 | 7/27/2016 1:10:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermal hazard due unprotected cable. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder3.png | file://x:/photopub/docs/0000000462/a3da84fc-2e57-4133-b8cd-651a2820cfd2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca4fa18_e72d_4405_a794_e1edbd334e07
ELIN-618784-2016 | EL-354205-2016 | 7/27/2016 1:10:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermal hazard due unprotected cable. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Service1.png | file://x:/photopub/docs/0000000462/bc9a63d9-d0a5-46c5-933e-1550c5ab1fae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca4fa18_e72d_4405_a794_e1edbd334e07
ELIN-618784-2016 | EL-354205-2016 | 7/27/2016 1:10:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Thermal hazard due unprotected cable. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Feeder1.png | file://x:/photopub/docs/0000000462/2dd56b30-3867-4de8-b176-8c36040cadda.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__aca4fa18_e72d_4405_a794_e1edbd334e07
ELIN-636215-2016 | EL-391537-2016 | 8/24/2016 12:32:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Outlet boxes not specifically approved for use with ceiling fans may not be capable of handling the weight associated with ceiling fans; hence, increasing the likelihood of the fan falling off the outlet box and possibly causing injury to a person. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Outlet_box_for_ceiling_fan_use.png | file://x:/photopub/docs/0000000475/4851150b-3c18-4aff-b8f3-cf36b6b4bf1d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3d0e40bf_503a_4049_9dbe_82371cbbbcae
GAIN-607097-2016 | GA-400723-2016 | 8/3/2016 4:35:14 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Gas_piping.png | file://x:/photopub/docs/0000000465/6b6b290f-ed08-41c0-bcf1-9eeabf40bea4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f961ed2_9507_4e3e_882e_9e2a16dfb73b
ELIN-600369-2016 | EL-390978-2016 | 8/4/2016 3:49:20 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuits that travel along property line and laying on ground will be damaged from pedestrian traffic stepping on them if left in the present state. The hazard would be damage to the conductors and possibly shock and fire hazards after conductor was damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Teck_branch_cucuits.png | file://x:/photopub/docs/0000000466/75e18703-e48a-438f-a47a-31de692230dc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__059ee232_7ebf_4b1a_be7d_96865ac626d1
ELIN-600369-2016 | EL-390978-2016 | 8/4/2016 3:49:20 PM | ASSESS: EL: Final | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuits that travel along property line and laying on ground will be damaged from pedestrian traffic stepping on them if left in the present state. The hazard would be damage to the conductors and possibly shock and fire hazards after conductor was damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Plywood_backing_board_.png | file://x:/photopub/docs/0000000466/2b10e488-beae-427d-a88a-fac3ed5156e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__059ee232_7ebf_4b1a_be7d_96865ac626d1
EDMA-629567-2016 | ED-399926-2016 | 8/9/2016 2:59:59 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED025 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | 3 | 3 | Electrical equipment could create a fire situation when mounted onto combustible material. During my inspection I found the elevator 240 Volts 3 phase electrical disconnect and 110 Volt 1 phase disconnect mounted onto wood. | 3 | Accessible location Preventative measure show sign of minor wear and/or damage Contact with Object/human possible Contact could result in property damage | Electrical_2-110.png | file://x:/photopub/docs/0000000469/94ddf84c-3502-4eb3-9cad-4c42d9b825bc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ce98d96_ae98_4ced_8835_be0c9ebfd3f3
GAIN-626432-2016 | GA-383502-2016 | 8/9/2016 2:05:52 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | dirt_pocket.png | file://x:/photopub/docs/0000000470/8fd796df-0c39-4a4f-828c-a9694b25b929.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e1fc430_4ff3_421c_8084_2c4240807fdd
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Electrical_equipment_inside_sewage_treatment_plant_.png | file://x:/photopub/docs/0000000471/e56962f3-f788-40b0-a587-dca5969e90ab.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Corroded_neutral_terminations_inside_panel_in_sewage_treatment_plant.png | file://x:/photopub/docs/0000000471/ef7c26eb-ce5b-4c33-9165-859c98fbf15c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Corroded_breaker_terminations_inside_sewage_treatment_plant.png | file://x:/photopub/docs/0000000471/33ddb4b5-fc48-4561-b00a-59e9b434c5fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
ELIN-627667-2016 | UW-422195-2016 | 8/15/2016 11:07:22 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Exterior receptacles for dwelling units are required to be Ground Fault Circuit Interrupter (GFCI) protected. This is required to protect people from shock hazards when plugging portable electrical equipment into exterior receptacles. This installation at a vacation cabin has exterior receptacles installed on the patio that are not GFCI protected. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_receptacle_that_is_not_GFCI_protected.png | file://x:/photopub/docs/0000000471/7cd287d3-7e90-43a0-99b8-d10e75bc8917.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__356a5652_deb7_4048_b73e_f4f2cf33560f
ELIN-627667-2016 | UW-422195-2016 | 8/15/2016 11:07:22 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Exterior receptacles for dwelling units are required to be Ground Fault Circuit Interrupter (GFCI) protected. This is required to protect people from shock hazards when plugging portable electrical equipment into exterior receptacles. This installation at a vacation cabin has exterior receptacles installed on the patio that are not GFCI protected. Left uncorrected this is a potential shock hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Exterior_of_cabin.png | file://x:/photopub/docs/0000000471/8f594af7-5b12-44bc-beea-02ef787a7620.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__356a5652_deb7_4048_b73e_f4f2cf33560f
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Sewage_treatment_plant.png | file://x:/photopub/docs/0000000471/0e52393f-1855-4016-bef1-b5dba6004381.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Evidence_from_previously_installed_and_failed_connections_to_a_sub-service_switch_in_the_sewage_treatment_plant.png | file://x:/photopub/docs/0000000471/7150403e-bb20-4581-b7d1-8db259d97796.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Corroded_connections_inside_panel_in_sewage_treatment_plant.png | file://x:/photopub/docs/0000000471/47caf014-e4e6-4a69-b49d-65bc533252a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
ELOP-191457-2014 | 196 | 8/16/2016 1:41:15 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL244 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | 3 | 3 | Electrical equipment and wiring methods installed in sewage treatment plant are required to be approved for installation in a corrosive and hazardous location. This is required to ensure that electrical equipment is not damaged by the corrosive affects of sewer gas and to ensure that explosive concentrations of sewer gases are not allowed to migrate through electrical equipment to locations where they can cause damage to equipment or be ignited causing a fire or explosion. This installation of a sewage treatment plant at a RV resort has electrical equipment that is not approved for installation in a corrosive or hazardous location. Copper conductors and terminations are corroded at grounding, bonding and sub-distribution equipment. Left uncorrected this is fire and shock hazard if electrical connections fail and over heat and at the same time grounding and bonding connections fail or are inadequate due to the effects of corrosion. | 3 | All locations • Equipment showing signs of corrosion, wear or degradation; and • repairs to be completed. | Corroded_grouning_and_bonding_conductors_and_connections.png | file://x:/photopub/docs/0000000471/dd14ecd9-1a08-4efb-971f-cb199f8a649f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f87398e5_cd64_46a1_a8ac_c45acaa3cb17
GAUP-631281-2016 | UW-424418-2016 | 8/16/2016 1:19:41 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Water heater vent termination installed too close to the perforated roofing soffit. The flue gas from the appliance could enter the attic space through the perforations possibly introducing carbon monoxide into the living space. | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Water_heater_vent_termination.png | file://x:/photopub/docs/0000000471/3228e4a8-5078-45c8-ad57-8e4dec0ac027.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b479452_9395_4c11_814a_6129a3da3db6
ELIN-627500-2016 | EL-402352-2016 | 8/9/2016 10:29:13 AM | ASSESS: EL: Final | png | #asFound | EL145 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Signs do not bear evidence of approval. This is a possible shock or fire hazard. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Uncertified_sign.png | file://x:/photopub/docs/0000000468/967eaa03-824e-447b-b604-3338259c5d7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8165cdbc_47ea_4ebe_84fb_b3d206b119c7
ELIN-602637-2016 | EL-399323-2016 | 7/4/2016 1:31:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Bare exposed wires intended to feed a receptacle. The receptacle was removed by the carpenter. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000451/2f79c39d-a88e-4f04-9860-bfb8fda1084c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9ee10f4_7dd4_409d_83a4_d782b8796c08
ELIN-602637-2016 | EL-399323-2016 | 7/4/2016 1:31:51 PM | ASSESS: EL: Service Connection | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Bare exposed wires intended to feed a receptacle. The receptacle was removed by the carpenter. This is a shock hazard. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | B.png | file://x:/photopub/docs/0000000451/1e035d8a-990f-4b46-859d-ff0b09a4a013.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9ee10f4_7dd4_409d_83a4_d782b8796c08
ELIN-624936-2016 | EL-408304-2016 | 8/4/2016 10:28:15 AM | ASSESS: EL: Service Connection | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 3 | In a new agricultural pumphouse installation, the 200amp 120/240volt 1phase panel was observed with no protective panel fillers installed. This can lead to a shock hazard. Pic attached. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_panel_fillers.png | file://x:/photopub/docs/0000000466/4b84ea8e-167f-4bf3-94a4-473b695f905b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d722697_7ea9_4cd0_bddf_cf6adc5b21ef
ELIN-612730-2016 | EL-400528-2016 | 7/18/2016 1:29:09 PM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Main distribution equipment for permanent service installation not adequately protected against the effects of weather. This poses a serious risk of personal injury (shock) or property damage (thermal damage) due to deterioration of the service equipment. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_main_distribution_1.png | file://x:/photopub/docs/0000000458/e7bf2e0c-6b40-4102-91cd-01ea1db3f828.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__95eafe63_d622_4fd6_b8fd_08c92c9bc8fa
ELIN-627582-2016 | EL-386614-2016 | 8/17/2016 1:06:31 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | View01_service_.png | file://x:/photopub/docs/0000000472/79717b39-04ca-49f5-8c34-90694246e566.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87ed3bf1_ffd0_4a3b_b15c_f1bda5a45537
ELIN-588555-2016 | EL-374663-2016 | 8/17/2016 12:52:24 PM | ASSESS: EL: Service Connection | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Consumer service raceway installed in large, angular aggregate exposing it to mechanical damage. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_meter_base.png | file://x:/photopub/docs/0000000472/8572f5e2-f93a-49da-b9d0-540e9ae74445.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__82686a6a_44b3_4e39_a6ad_a2e7253df1b7
ELIN-612208-2016 | EL-374663-2016 | 8/17/2016 1:21:35 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 |  | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Detail01_pump_feeder.png | file://x:/photopub/docs/0000000472/27b374bd-de6d-4e3e-8eee-16afd2a19bdb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__78035198_ca3f_4076_8609_db0db051d061
ELIN-630171-2016 | EL-341972-2016 | 8/15/2016 12:32:10 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Armoured cabling used for feeders is bedded in large, angular aggregate exposing feeders to mechanical damage. This poses a serious risk of personal injury (shock) or property damage (thermal event). | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | View01_feeders.png | file://x:/photopub/docs/0000000472/01a66093-ccd5-4ea3-8d92-61aa28a843cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef3251ea_c29a_404b_99d3_7a31e5f99ae3
ELIN-625976-2016 | EL-420545-2016 | 8/9/2016 8:34:49 AM | ASSESS: EL: Service Connection | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | View01_service.png | file://x:/photopub/docs/0000000468/1b146e9e-213f-49bb-abe3-5cf04869bb07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__978eba31_46a5_4213_85ed_55a56d0358ee
AMOP-637921-2016 | AM-158619-2014 | 8/25/2016 3:20:58 PM | ASSESS: AM OP: Periodic | png | #asFound | AM018 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | 2 | 2 | Material of PCU was cracked, could become a sharp hazard | 2 | Defects that are: Reasonably detectable by maintenance program Likely to propagate | Cracked_tail_pcu.png | file://x:/photopub/docs/0000000475/d8a0def6-051e-4bf2-b42e-71a9e49302d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b97b5401_bc27_4069_80bc_40d2745ffd50
AMOP-637917-2016 | AM-158618-2014 | 8/25/2016 3:32:53 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | Nut was found loose on PCU, could result in PCU coming loose of lower guide | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | PCU_connection.png | file://x:/photopub/docs/0000000475/8d5c61ee-d58a-4ffe-9a2c-60e55fbfc1db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e60cfb1_f260_4b96_b7ca_21d552ce122a
ELIN-602898-2016 | EL-403197-2016 | 7/6/2016 10:26:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | System ground conductors exposed to mechanical damage may result in creation of a shock hazard | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | Incorrect_splice_connector.png | file://x:/photopub/docs/0000000453/c7e19dac-6d06-4884-9bac-3734187b91ce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__478907de_1635_4ef6_a2e9_31cfcafbf8d1
ELIN-602898-2016 | EL-403197-2016 | 7/6/2016 10:26:44 AM | ASSESS: EL: Service Connection | png | #asFound | EL094 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | 3 | 3 | System ground conductors exposed to mechanical damage may result in creation of a shock hazard | 3 | Continuity Grounding conductor is not properly protected from mechanical damage, or is not properly secured | System_ground_conductor_location.png | file://x:/photopub/docs/0000000453/540e59bc-21f2-4c40-b524-b064d536e334.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__478907de_1635_4ef6_a2e9_31cfcafbf8d1
BPVOP-626555-2016 | 2267722 | 8/8/2016 4:30:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Crack is found in weld between tube and tubesheet. Propagation of crack may lead to expansive tubesheet repair if crack is not removed to sound metal and restored to original condition by appropriate repair. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | Crack_in_tube.png | file://x:/photopub/docs/0000000469/99d7dd2c-ee03-4dd2-b050-e93c5d79e51d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec63fbf3_6bed_4918_ac3a_c47c08fc5e2d
BPVOP-626555-2016 | 2267722 | 8/8/2016 4:30:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP057 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | 2 | 2 | Crack is found in weld between tube and tubesheet. Propagation of crack may lead to expansive tubesheet repair if crack is not removed to sound metal and restored to original condition by appropriate repair. | 2 | 1.2.2 Boiler leakage: procedure - Boiler tube end cracks or minor leakage. | Crack_tube.png | file://x:/photopub/docs/0000000469/2bb2b45e-2718-4b97-b899-a4de956ee77f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec63fbf3_6bed_4918_ac3a_c47c08fc5e2d
ELIN-612578-2016 | EL-384763-2016 | 7/20/2016 5:30:24 PM | ASSESS: EL: Final | png | #asFound | EL065 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | 1 | 1 | Overcurrent protection devices have not been identified as to what circuits they protect. This could lend to incorrectly de-energizing or energizing circuits that may be unsafe. | 1 | General Circuits have not been clearly marked or identified on panelboards, disconnecting means, switchboards, or similar equipment. | Panel_directory_incomplete.png | file://x:/photopub/docs/0000000459/e8ad98e7-6773-4f2d-b51e-aa704c095e89.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__72768285_3fac_4fe7_8879_6d4d98d0c759
ELIN-625696-2016 | EL-414251-2016 | 8/23/2016 11:51:14 AM | ASSESS: EL: Final | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | System ground plate was not buried prior energizing 240v single phase service to building. There exists a strong likelihood that the ground plate could be moved as a result of direct handling by a person and, should there exist a condition where electrical energy is being transmitted to ground, a person handling the plate could be fatally electrocuted if the person became part of the path to ground. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Exposed_system_ground_plate.png | file://x:/photopub/docs/0000000474/ba19fb7c-1ee1-470e-8001-98484f31309f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29d08948_7484_43e6_b471_cd20f89c4b6f
ELIN-622807-2016 | EL-280477-2015 | 8/4/2016 1:17:17 PM | ASSESS: EL: Final | png | #asFound | EL084 | Equipment Gas line, cast or water pipe has not been bonded | 3 | 3 | A residential well pump operating at 240 volts and 20 amps was found in a well casing that was not bonded to ground. The well casing could become energized and the overcurrent protection would not trip with the well casing isolated from ground. This could lead to injury to persons or damage to property. | 3 | Equipment Gas line, cast or water pipe has not been bonded | Well_casing__cable_armour_not_bonded.png | file://x:/photopub/docs/0000000466/27f41d90-1b53-4164-bdd1-507ff38ead2c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3b7c9819_1faf_4aab_9be6_15ab27671b48
GAHE-633792-2016 | HE-426121-2016 | 8/18/2016 4:05:04 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA108 | Venting system not connected or dislodged from energized appliance | 5 | 5 | Commercial convection oven was operating with its flue outside of the kitchen exhaust canopy. The flue products were being venting directly into the occupied work space. This could result in possible carbon monoxide poisoning. | 5 | Venting system not connected or dislodged from energized appliance | Convection_oven_outside_of_exhaust_canopy.png | file://x:/photopub/docs/0000000472/43b71a7f-54db-4fc2-a5fb-cc5649028e6b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c095493a_5523_4f11_aefd_d04cde436c60
GAIN-613398-2016 | GA-411140-2016 | 7/15/2016 9:34:22 AM | ASSESS: GA: Rough-In | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | A 1/2" branch gas line had a valve with a 5/8" outside diameter flare adaptor which was not capped or plugged. If the valve was leaking and no cap or plug in place, propane gas could have accumulated in the room and if a source of ignition was present, caused a fire and/or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Open_gas_line.png | file://x:/photopub/docs/0000000457/b76be63e-62b0-4a3f-b997-533d94ef241a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec4d768e_ae2f_4f90_82d7_887c2bab4540
ELIN-633127-2016 | EL-417262-2016 | 8/18/2016 1:51:59 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Type one panel exposed to damage from weather. This is a hazard as these types of panels are not built to be place in wet locations. This will severely affect the life span and the operation of the panel should it get wet. It is also a shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | B.png | file://x:/photopub/docs/0000000472/593605c0-e4c1-4db8-99d1-a48f002cb578.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc431cd1_0b55_4242_b6cc_7611fd5d78f4
ELIN-632868-2016 | EL-423514-2016 | 8/17/2016 1:31:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation of a tenant improvement for an office space, the new conductors for branch circuits where terminated onto the breakers of an existing energized panel. The breakers in the panel where not installed with lock out devices and the receptacles where not installed on the conductors in the office. If the breakers in the panel where turned on, there is a potential for a shock hazard if a persons came in contact with the energized conductors or a fire hazard if the energized conductors came in contact with the metal box and produced an arc. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Conductors_on_breakers.png | file://x:/photopub/docs/0000000472/66669871-c0ae-4386-aadf-c1b26ca07323.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f25dc6b_4f90_43af_bf4b_d87d6f07ef59
ELIN-632868-2016 | EL-423514-2016 | 8/17/2016 1:31:28 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | Electrical equipment is to be installed and guarded so that adequate provisions are made for the safety of persons and property. In this installation of a tenant improvement for an office space, the new conductors for branch circuits where terminated onto the breakers of an existing energized panel. The breakers in the panel where not installed with lock out devices and the receptacles where not installed on the conductors in the office. If the breakers in the panel where turned on, there is a potential for a shock hazard if a persons came in contact with the energized conductors or a fire hazard if the energized conductors came in contact with the metal box and produced an arc. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Devices_not_installed.png | file://x:/photopub/docs/0000000472/9b99f16e-3e30-4e22-8114-f5f1a9d4a98e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f25dc6b_4f90_43af_bf4b_d87d6f07ef59
GAHE-636474-2016 | HE-427808-2016 | 8/23/2016 3:17:40 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA063 | Open gas line connected to fuel supply (no cap/plug) | 5 | 5 | The as found hazard was a gas line which had not been sealed with a plug or cap. This is a hazard because if the valve were to be bumped open or begin to leak natural gas would enter the building uncontrolled. Risk of fire or explosion. | 5 | Open gas line connected to fuel supply (no cap/plug) | Gas_line.png | file://x:/photopub/docs/0000000474/a9d96c6c-6f05-40b4-b5e1-cb39d712233d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__3c8db875_c8f2_471b_b1f9_92ff2913cceb
GAIN-616916-2016 | GA-407491-2016 | 8/23/2016 10:10:44 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The C vent connector could over heat the combustible pipe and create a fire hazard. | 3 | Non compliant Type C Vent clearance | WH_C_vent_to_close_to_combustibles.png | file://x:/photopub/docs/0000000474/0b724ab4-a60e-40bd-b57b-c3a961a4faeb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b009ecdc_0ea4_46df_b46c_8adc6d3f1fd5
GAIN-616916-2016 | GA-407491-2016 | 8/23/2016 10:10:44 AM | ASSESS: GA: Final | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The C vent connector could over heat the combustible pipe and create a fire hazard. | 3 | Non compliant Type C Vent clearance | WH_C_vent_to_close_to_combustibles_.png | file://x:/photopub/docs/0000000474/8527edc1-84c8-4bd8-85ff-c59858867aef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b009ecdc_0ea4_46df_b46c_8adc6d3f1fd5
ELIN-620852-2016 | EL-276063-2015 | 8/8/2016 10:17:13 AM | ASSESS: EL: Final | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 3 | A 120V 15A washer outlet has been added to a general branch circuit already containing lighting and receptacles, this could result in damage to the equipment or wiring, also a possible fire hazard from overloading the existing branch circuit. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Washer_outlet.png | file://x:/photopub/docs/0000000467/71eafffc-4c5d-4283-b900-6bc11de5c06b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ae67a8b6_9304_47cc_a579_13b9d772b6dd
ELHE-607439-2016 | HE-408494-2016 | 7/12/2016 1:12:54 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords miss used overhead | 4 | Conductors, Misuse of flexible cords. | To_garage.png | file://x:/photopub/docs/0000000455/5511635b-e42e-4314-89ec-d45eed314cca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ae9eafa_257c_412f_99af_0b930a291359
ELHE-607439-2016 | HE-408494-2016 | 7/12/2016 1:12:54 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Flexible cords miss used overhead | 4 | Conductors, Misuse of flexible cords. | From_house.png | file://x:/photopub/docs/0000000455/7b50ee5a-ed44-4b15-a87e-2b748d819fe1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0ae9eafa_257c_412f_99af_0b930a291359
BPVOP-620292-2016 | 2275728 | 7/28/2016 9:30:26 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP028 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | 3 | 3 | Equipment room wood floor is rotting through | 3 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | Boiler_room_very_week_Floor.png | file://x:/photopub/docs/0000000463/7dc7db40-2352-447b-8436-b26377584a8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4b24db_0701_4dd1_9df8_66645353678f
BPVOP-620292-2016 | 2275728 | 7/28/2016 9:30:26 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP028 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | 3 | 3 | Equipment room wood floor is rotting through | 3 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | Gauge_glass_water_shutoff_Valve.png | file://x:/photopub/docs/0000000463/bb746278-5967-44d6-8b3d-d328fd87df6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4b24db_0701_4dd1_9df8_66645353678f
BPVOP-620292-2016 | 2275728 | 7/28/2016 9:30:26 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP028 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | 3 | 3 | Equipment room wood floor is rotting through | 3 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | Water_level_control_float_chamber.png | file://x:/photopub/docs/0000000463/eadced13-63fa-4072-9181-d27ad7ad3dd0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4b24db_0701_4dd1_9df8_66645353678f
BPVOP-620292-2016 | 2275728 | 7/28/2016 9:30:26 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP028 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | 3 | 3 | Equipment room wood floor is rotting through | 3 | 1.0.2 Clearances/Maintenance - Corrosion of reinforcing steel, freeze damage, spalling and cracking of foundations and supports is causing settling or heaving. | Blowdown_valve_leakage_taped.png | file://x:/photopub/docs/0000000463/328c28db-a167-4841-acda-344eaa9dc2ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba4b24db_0701_4dd1_9df8_66645353678f
ELIN-619528-2016 | EL-413304-2016 | 7/28/2016 12:04:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit cables run across the lower faces of ceiling rafters, where the vertical distance is greater than 1 meter, have to protected from mechanical damage which could result from persons stepping on cables when in the attic. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_run_across_lower_faces_of_rafters.png | file://x:/photopub/docs/0000000463/7677e705-cb41-4166-a949-04ecfd6100d9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afa5537b_b8e2_4492_9f04_5edc55987c5f
ELIN-619528-2016 | EL-413304-2016 | 7/28/2016 12:04:58 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Branch circuit cables run across the lower faces of ceiling rafters, where the vertical distance is greater than 1 meter, have to protected from mechanical damage which could result from persons stepping on cables when in the attic. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Cables_in_rafters.png | file://x:/photopub/docs/0000000463/3753163a-4582-4a0a-ac1e-394386da6400.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__afa5537b_b8e2_4492_9f04_5edc55987c5f
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Power_bar_cord_through_wall.png | file://x:/photopub/docs/0000000462/9df7538f-4eaa-40fa-83e4-45f9b5641739.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Water_damaged_electrical_.png | file://x:/photopub/docs/0000000462/e1c5aee7-cc2b-4579-a157-122e07240a90.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors.png | file://x:/photopub/docs/0000000462/f6a97269-d1e3-47b6-ae64-f52d94f798eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-567144-2016 | UW-380781-2016 | 7/27/2016 11:56:40 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL002 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | Exposed energized electrical. Possibility for shock or fire | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Exposed_conductors_at_range_area.png | file://x:/photopub/docs/0000000462/dfedc0a4-6841-4204-b37b-0394aeade2ca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__430fba7e_6ef1_49f8_823c_11088526d2be
ELIN-625194-2016 | EL-411856-2016 | 8/8/2016 2:53:24 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Wire damaged by improper termination. This is a fire hazard as a poor connection can cause excessive heat. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | B.png | file://x:/photopub/docs/0000000467/7408ab71-13c1-441a-b2b8-dbd6ffdde7ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6649dd8_37c4_4d5c_8f67_4b69056c0c5a
ELIN-625194-2016 | EL-411856-2016 | 8/8/2016 2:53:24 PM | ASSESS: EL: Final | png | #asFound | EL121 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Wire damaged by improper termination. This is a fire hazard as a poor connection can cause excessive heat. | 4 | Conductors • Cables, Raceways or conductors are damaged and need to be either replaced or repaired; and • Not suitable for continued use. | A.png | file://x:/photopub/docs/0000000467/b546e0d8-2336-4a00-b42e-00b4c0021a2d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6649dd8_37c4_4d5c_8f67_4b69056c0c5a
ELIN-610638-2016 | EL-389885-2016 | 7/18/2016 11:15:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | PVC conduits are required to terminate into threaded metal enclosures using female threaded PVC adapters together with metal conduit nipples. This is required because PVC expands and contracts at a different rate compared to metal. Movement between PVC and metal fittings can cause PVC fittings to crack, break, or pull out of metal fittings causing damage to the conduit and allowing water to enter electrical equipment. This installation of a new service on a residential property has a PVC service conduit terminated at the top of a meter base on a service pole. The PVC conduit is terminated using a PVC male adapter threaded into a female metal hub. Left uncorrected the male PVC adapter on the service conduit may crack, break, or pull apart allowing water to enter the meter base. Over time this may rust and corrode the conductor terminations inside the meter base posing a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Service_conduit_termination_on_top_of_meter_base.png | file://x:/photopub/docs/0000000457/9779bb2f-7ada-4460-9424-282a6d85acb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9e5b2dd_1d6f_48fb_b891_a3567e7a10a4
ELIN-613672-2016 | EL-411516-2016 | 8/3/2016 12:04:56 PM | ASSESS: EL: Final | png | #asFound | EL042 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | 2 | 2 | No photovoltaic system rapid shutdown device has been provided to de-energize DC conductors located greater than within 3 meters of arrays, in the event of an emergency, to minimize the likelihood of accidental shock to persons. Required for protection of fire suppression personnel. | 2 | Other categories may be referenced depending upon the as found hazard. Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons. | Photovoltaic_array_on_roof.png | file://x:/photopub/docs/0000000465/1d20741f-940c-4fea-ac75-7615a9941d33.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8978394a_ce78_4197_9a29_22be5f621309
ELIN-614240-2016 | EL-412503-2016 | 7/26/2016 9:17:51 AM | ASSESS: EL: Service Connection | png | #asFound | EL078 | Installation Grounding; conductor is not continuous. | 4 | 4 | In a new agricultural 200amp service upgrade, the 120/240volt 200amp panel has the system ground terminating to the panel tub and not the identified conductor as required. This could lead to a thermal effect. Picture attached. | 4 | Installation Grounding; conductor is not continuous. | Ground_connection_.png | file://x:/photopub/docs/0000000462/129d16b1-a5e1-4cbd-9bac-09403f20c3bf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__def5561b_e1b6_4ce9_8388_048cce0295ba
EDOP-625681-2016 | 2038083 | 8/4/2016 3:59:16 PM | ASSESS: ED OP: Call | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | Outstanding BCSA Safety Order SO-ED 2013-01. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | GriffinDataPlate.png | file://x:/photopub/docs/0000000467/d46aea98-43de-4317-b5c6-70722dec9ec1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b8806c3_4ec9_474c_a109_d87e68c7d03a
EDOP-625681-2016 | 2038083 | 8/4/2016 3:59:16 PM | ASSESS: ED OP: Call | png | #asFound | ED037 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | 3 | 3 | Outstanding BCSA Safety Order SO-ED 2013-01. | 3 | Safety critical monitoring incorrectly installed, bypassed or failed Unit is not in operation Risk Reg ED-02 | GriffinController.png | file://x:/photopub/docs/0000000467/55ed8bc3-4057-443a-a557-e7eb28dc3a6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b8806c3_4ec9_474c_a109_d87e68c7d03a
ELIN-629285-2016 | EL-352213-2016 | 8/22/2016 3:47:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120/240 volt 125 amp service has no service grounding conductor terminated onto service system neutral bar for grounding the consumer's service equipment. When service equipment is not grounded with grounding conductor and grounding electrode the service electrical equipment could have potential differences within electrical system and could become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4.png | file://x:/photopub/docs/0000000474/052e4806-f3a5-4c28-832f-213f74d5a597.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa329fa0_5bd2_476d_b2e6_ad9f0dcb08a2
ELIN-629285-2016 | EL-352213-2016 | 8/22/2016 3:47:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120/240 volt 125 amp service has no service grounding conductor terminated onto service system neutral bar for grounding the consumer's service equipment. When service equipment is not grounded with grounding conductor and grounding electrode the service electrical equipment could have potential differences within electrical system and could become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 1.png | file://x:/photopub/docs/0000000474/0c5895f7-4b83-4606-8059-3bd8f20922a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa329fa0_5bd2_476d_b2e6_ad9f0dcb08a2
ELIN-629285-2016 | EL-352213-2016 | 8/22/2016 3:47:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120/240 volt 125 amp service has no service grounding conductor terminated onto service system neutral bar for grounding the consumer's service equipment. When service equipment is not grounded with grounding conductor and grounding electrode the service electrical equipment could have potential differences within electrical system and could become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 6.png | file://x:/photopub/docs/0000000474/bb9a20c6-4605-4670-a29b-8eab5557742a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa329fa0_5bd2_476d_b2e6_ad9f0dcb08a2
ELIN-629285-2016 | EL-352213-2016 | 8/22/2016 3:47:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120/240 volt 125 amp service has no service grounding conductor terminated onto service system neutral bar for grounding the consumer's service equipment. When service equipment is not grounded with grounding conductor and grounding electrode the service electrical equipment could have potential differences within electrical system and could become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 3.png | file://x:/photopub/docs/0000000474/7bdeb31b-9fc0-4e8c-9c24-3dda8b869542.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa329fa0_5bd2_476d_b2e6_ad9f0dcb08a2
ELIN-629285-2016 | EL-352213-2016 | 8/22/2016 3:47:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120/240 volt 125 amp service has no service grounding conductor terminated onto service system neutral bar for grounding the consumer's service equipment. When service equipment is not grounded with grounding conductor and grounding electrode the service electrical equipment could have potential differences within electrical system and could become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 5.png | file://x:/photopub/docs/0000000474/3442f5bb-0a00-472a-840a-c556d2841af5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa329fa0_5bd2_476d_b2e6_ad9f0dcb08a2
ELIN-629285-2016 | EL-352213-2016 | 8/22/2016 3:47:07 PM | ASSESS: EL: Service Connection | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120/240 volt 125 amp service has no service grounding conductor terminated onto service system neutral bar for grounding the consumer's service equipment. When service equipment is not grounded with grounding conductor and grounding electrode the service electrical equipment could have potential differences within electrical system and could become an electrical shock hazard. | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 2.png | file://x:/photopub/docs/0000000474/59c95a93-92c8-439c-9973-d15115030e8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa329fa0_5bd2_476d_b2e6_ad9f0dcb08a2
ELIN-610638-2016 | EL-389885-2016 | 7/18/2016 11:15:11 AM | ASSESS: EL: Service Connection | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | PVC conduits are required to terminate into threaded metal enclosures using female threaded PVC adapters together with metal conduit nipples. This is required because PVC expands and contracts at a different rate compared to metal. Movement between PVC and metal fittings can cause PVC fittings to crack, break, or pull out of metal fittings causing damage to the conduit and allowing water to enter electrical equipment. This installation of a new service on a residential property has a PVC service conduit terminated at the top of a meter base on a service pole. The PVC conduit is terminated using a PVC male adapter threaded into a female metal hub. Left uncorrected the male PVC adapter on the service conduit may crack, break, or pull apart allowing water to enter the meter base. Over time this may rust and corrode the conductor terminations inside the meter base posing a fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Meter_base_on_pole.png | file://x:/photopub/docs/0000000457/ad083351-319a-41d0-9287-8878a9c2d13e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e9e5b2dd_1d6f_48fb_b891_a3567e7a10a4
ELIN-626845-2016 | EL-161617-2014 | 8/8/2016 2:19:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | No evidence of approval on LED drivers, A distance greater than 6 mm extends from the back wall to the cabinet. A high likelihood of arcs and sparks been created which will combust the wooden material. Box extenders have not been installed by the electrical contractor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Coto_to.png | file://x:/photopub/docs/0000000467/a170d6c6-3ac7-476e-a7f6-df7856281fe3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01e79f22_bdb9_4de5_aae2_155c1bac89d7
ELIN-597943-2016 | EL-383941-2016 | 6/28/2016 9:05:07 AM | ASSESS: EL: Final | png | #asFound | EL234 | Class II, all locations Area classification required | 2 | 2 | The Grain cleaner room separates grains products and delivers them to respective bins through electric augers. The area has concerns of being a hazardous location and no documentation | 2 | Class II, all locations Area classification required | Cleaner_building.png | file://x:/photopub/docs/0000000449/016054f4-25e9-4b8b-ae82-75c98e77162c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a9457257_d136_4217_a28c_4528254bc29e
BPVOP-603108-2016 | 2271384 | 6/29/2016 11:07:40 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP140 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | 1 | 1 |  | 1 | 4.0.1 Incorrect readings/alarms - Provided device range not correct | Pressure_gauge_range_not_to_code.png | file://x:/photopub/docs/0000000450/f8aea65d-62cd-44a4-b9c4-4830768a4acc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0940ca29_442d_4a02_9fae_edcd7bffd89b
ELIN-613715-2016 | EL-410040-2016 | 7/25/2016 1:53:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | The 100 amp 120/240 volt panel is missing a panel filler for an open breaker space to an energized panel, this is a shock hazard | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Missing_breaker_filler.png | file://x:/photopub/docs/0000000461/d9658cd3-2dad-4d68-b448-bcc4246da198.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8bd58ab2_ab15_4493_936c_5735617aaba1
ELIN-602675-2016 | UW-403799-2016 | 6/29/2016 2:27:53 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | Modification of Approved Equipment. Power block and wiring installed to facilitate connection of an electric furnace instead of an approved lug kit. This is a hazard as bare lugs are exposed. The approved lug kit comes with a plastic cover. 30A fused tap added in the furnace enclosure to feed a separate piece of equipment (heat pump). This is a hazard as the fuses are not readily accessible, and are located in the furnace in the crawl space. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | B.png | file://x:/photopub/docs/0000000450/16ba9224-93fc-4575-802c-4def820b5be3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26b855c6_5c79_47eb_ab7b_b71d6d639f21
ELIN-602675-2016 | UW-403799-2016 | 6/29/2016 2:27:53 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | Modification of Approved Equipment. Power block and wiring installed to facilitate connection of an electric furnace instead of an approved lug kit. This is a hazard as bare lugs are exposed. The approved lug kit comes with a plastic cover. 30A fused tap added in the furnace enclosure to feed a separate piece of equipment (heat pump). This is a hazard as the fuses are not readily accessible, and are located in the furnace in the crawl space. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | C.png | file://x:/photopub/docs/0000000450/37f2f70d-a855-4275-8c31-d8d2ff2200d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26b855c6_5c79_47eb_ab7b_b71d6d639f21
ELIN-602675-2016 | UW-403799-2016 | 6/29/2016 2:27:53 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL160 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 4 | Modification of Approved Equipment. Power block and wiring installed to facilitate connection of an electric furnace instead of an approved lug kit. This is a hazard as bare lugs are exposed. The approved lug kit comes with a plastic cover. 30A fused tap added in the furnace enclosure to feed a separate piece of equipment (heat pump). This is a hazard as the fuses are not readily accessible, and are located in the furnace in the crawl space. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | A.png | file://x:/photopub/docs/0000000450/00309ca3-efb3-4ee6-8452-91f0ef7833b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__26b855c6_5c79_47eb_ab7b_b71d6d639f21
GAIN-618104-2016 | GA-367548-2016 | 7/29/2016 11:59:16 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Contractor used the wrong material to reduce the exhaust vent size. | 3 | Unapproved venting material | HTPboilers4.png | file://x:/photopub/docs/0000000464/bff6119f-c4b4-49d9-bae8-f6bec143b7fe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0904c33d_67c0_4fd2_ace6_edbb43cf8ebe
GAIN-618104-2016 | GA-367548-2016 | 7/29/2016 11:59:16 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Contractor used the wrong material to reduce the exhaust vent size. | 3 | Unapproved venting material | HTPboilers.png | file://x:/photopub/docs/0000000464/f351ae54-bdb6-4728-8e6b-5bc975b4da3a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0904c33d_67c0_4fd2_ace6_edbb43cf8ebe
GAIN-618104-2016 | GA-367548-2016 | 7/29/2016 11:59:16 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Contractor used the wrong material to reduce the exhaust vent size. | 3 | Unapproved venting material | HTPboilers2.png | file://x:/photopub/docs/0000000464/626aa957-cc07-4c1d-b635-8733c7304ce5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0904c33d_67c0_4fd2_ace6_edbb43cf8ebe
GAIN-618104-2016 | GA-367548-2016 | 7/29/2016 11:59:16 AM | ASSESS: GA: Final | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Contractor used the wrong material to reduce the exhaust vent size. | 3 | Unapproved venting material | HTPboilers3.png | file://x:/photopub/docs/0000000464/5632e570-9b63-42db-985c-697579deb67e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0904c33d_67c0_4fd2_ace6_edbb43cf8ebe
ELIN-626845-2016 | EL-161617-2014 | 8/8/2016 2:19:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | No evidence of approval on LED drivers, A distance greater than 6 mm extends from the back wall to the cabinet. A high likelihood of arcs and sparks been created which will combust the wooden material. Box extenders have not been installed by the electrical contractor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Box_extender.png | file://x:/photopub/docs/0000000467/3806958f-3bf3-45fe-8c71-fe853dfe16c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01e79f22_bdb9_4de5_aae2_155c1bac89d7
ELIN-626845-2016 | EL-161617-2014 | 8/8/2016 2:19:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | No evidence of approval on LED drivers, A distance greater than 6 mm extends from the back wall to the cabinet. A high likelihood of arcs and sparks been created which will combust the wooden material. Box extenders have not been installed by the electrical contractor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | Front_view__Front_view_box_extender_not_installed.png | file://x:/photopub/docs/0000000467/1bff9a1a-7047-4dd5-a6ef-6e01719b840c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01e79f22_bdb9_4de5_aae2_155c1bac89d7
ELIN-626845-2016 | EL-161617-2014 | 8/8/2016 2:19:22 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL124 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | 4 | 4 | No evidence of approval on LED drivers, A distance greater than 6 mm extends from the back wall to the cabinet. A high likelihood of arcs and sparks been created which will combust the wooden material. Box extenders have not been installed by the electrical contractor. | 4 | Installation of electrical equipment Equipment is intended to be energized and not adequately locked out; Covers or canopies have not been installed. • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to persons. | No_evidence.png | file://x:/photopub/docs/0000000467/f1088765-3f32-42e3-a01a-d78a3fcf3315.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__01e79f22_bdb9_4de5_aae2_155c1bac89d7
ELIN-620740-2016 | EL-415923-2016 | 8/2/2016 7:31:56 AM | ASSESS: EL: Final | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | Ungrounded Flexible extension cord wiring was found operating on 15 amp 120 volt circuits feeding power to a permanent deep freeze, attached to carport structure, and in lieu of fixed wiring in a garden shed. Flexible cord can deteriorate over time and presents a risk for fire and potential injury for persons. | 4 | Conductors, Misuse of flexible cords. | Flexible_cord_wiring_under_and_through_stairs__gazebo_and_shed.png | file://x:/photopub/docs/0000000465/5e403ca1-e560-47a4-8a86-c481b34912f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e4ee283d_510a_4435_bdae_3a8db914a09b
ELIN-610216-2016 | EL-243595-2015 | 8/1/2016 7:35:53 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15 amp 120 volt receptacles in sleeping rooms of a dwelling are not protected by arc fault breakers as required. Cord connected equipment can fault in close confines around furniture in bedrooms and lead to fires and injury to persons. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Receptacles_in_4_bedrooms_no_afci.png | file://x:/photopub/docs/0000000465/73be46c4-b3e7-4504-a0f8-347849451224.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e58beb4d_f329_4fca_983d_0b93de75321e
ELIN-616605-2016 | EL-220840-2015 | 8/2/2016 1:21:01 PM | ASSESS: EL: Final | png | #asFound | EL151 | Installation of electrical equipment Entrance to dwelling does not have light. | 3 | 3 | No light has been installed at the rear entrance to a dwelling. A light fixture operating at 120 volts on a branch circuit has not been installed. Persons can be hurt when entering or leaving a dwelling when adequate illumination is not provided at entrances. | 1 | Installation of electrical equipment Entrance to dwelling does not have light. | No_light_switch_or_light_at_den_entrance_to_dwelling.png | file://x:/photopub/docs/0000000465/f3f05425-a224-4233-896d-308d03d33398.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__92e09d13_35fc_49d8_a654_2120018107f8
ELIN-639402-2016 | EL-394254-2016 | 8/30/2016 1:06:13 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 3 | DB 2 is not to be used above grade | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | ACWU_NOT_PROTECTED.png | file://x:/photopub/docs/0000000479/0c8b2c38-aa07-4073-b4ce-b89aaf2b23c6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f6cbb359_5664_429e_9791_dbd40d0ca2b5
ELIN-643484-2016 | EL-071319-2013 | 9/13/2016 9:59:04 AM | ASSESS: EL: Final | png | #asFound | EL149 | Installation of electrical equipment Boxes for lighting equipment are not suitable | 3 | 3 | 120 volt low voltage LED lighting box cover not approved for wet location. This could cause equipment damage. | 3 | Installation of electrical equipment Boxes for lighting equipment are not suitable | Cover_for_low_voltage_lighting_box_not_approved_for_wet_location.png | file://x:/photopub/docs/0000000484/80109e9a-a937-462f-9fcf-05009a800dd7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__191ba020_c7d9_4810_b10f_e80991479f86
BPVOP-626473-2016 | 2253255 | 8/8/2016 9:37:34 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale_on_vertical_tube.png | file://x:/photopub/docs/0000000468/e26cb932-ab4f-4ffc-8548-36dc6b0f0933.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc63788_7991_4bf0_b25b_533d3ba56e73
BPVOP-626473-2016 | 2253255 | 8/8/2016 9:37:34 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Hand_hole_scale.png | file://x:/photopub/docs/0000000468/273082a7-b7b1-4101-b98e-f8263307c812.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bc63788_7991_4bf0_b25b_533d3ba56e73
ELOP-424752-2015 | 4662 | 7/7/2016 10:10:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | Flexible cable and power bars used for permanent installations. Potential for fire and mechanical damage | 4 | Conductors, Misuse of flexible cords. | Flexible_cable_used_for_permanent_installation.png | file://x:/photopub/docs/0000000453/1205a9e6-0cc8-495b-9dfd-3eec5db34976.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54f47e9f_19f2_44c7_9ae2_201c0c11a605
ELOP-424752-2015 | 4662 | 7/7/2016 10:10:11 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 3 | Flexible cable and power bars used for permanent installations. Potential for fire and mechanical damage | 4 | Conductors, Misuse of flexible cords. | Flexible_cables_and_power_bars.png | file://x:/photopub/docs/0000000453/225a380f-ae1f-4744-abf0-68d2e490ff2e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__54f47e9f_19f2_44c7_9ae2_201c0c11a605
ELIN-627915-2016 | UW-422347-2016 | 8/12/2016 12:47:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 4 | The new signage on the Mall parking lot required removal of old signage, new concrete pedestals, disconnection of existing wiring and someone re-connected new sign without Permit or Sign Certification in place, the use of the 15 amp 120 volt non certified sign could lead to a shock hazard | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Sign.png | file://x:/photopub/docs/0000000470/ba703562-76be-4008-8eb3-a1351b678e02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f56916a_27b3_4c11_974e_33e9ea0cfed9
ELIN-627915-2016 | UW-422347-2016 | 8/12/2016 12:47:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 4 | The new signage on the Mall parking lot required removal of old signage, new concrete pedestals, disconnection of existing wiring and someone re-connected new sign without Permit or Sign Certification in place, the use of the 15 amp 120 volt non certified sign could lead to a shock hazard | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Not_energized_prior_to_disconnection.png | file://x:/photopub/docs/0000000470/c23dc370-6d25-4973-a353-5d61a2862fd5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f56916a_27b3_4c11_974e_33e9ea0cfed9
ELIN-627915-2016 | UW-422347-2016 | 8/12/2016 12:47:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 4 | The new signage on the Mall parking lot required removal of old signage, new concrete pedestals, disconnection of existing wiring and someone re-connected new sign without Permit or Sign Certification in place, the use of the 15 amp 120 volt non certified sign could lead to a shock hazard | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Red_tag_1.png | file://x:/photopub/docs/0000000470/8b171500-0799-4b92-9243-f36acefda79e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f56916a_27b3_4c11_974e_33e9ea0cfed9
ELIN-627915-2016 | UW-422347-2016 | 8/12/2016 12:47:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 4 | The new signage on the Mall parking lot required removal of old signage, new concrete pedestals, disconnection of existing wiring and someone re-connected new sign without Permit or Sign Certification in place, the use of the 15 amp 120 volt non certified sign could lead to a shock hazard | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Power_connections_made.png | file://x:/photopub/docs/0000000470/6f39570f-5d62-4605-845f-fa6d20390eb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f56916a_27b3_4c11_974e_33e9ea0cfed9
ELIN-627915-2016 | UW-422347-2016 | 8/12/2016 12:47:44 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL153 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | 3 | 4 | The new signage on the Mall parking lot required removal of old signage, new concrete pedestals, disconnection of existing wiring and someone re-connected new sign without Permit or Sign Certification in place, the use of the 15 amp 120 volt non certified sign could lead to a shock hazard | 3 | Installation of electrical equipment, Equipment is not approved for the specific use or location. | Red_tag_2.png | file://x:/photopub/docs/0000000470/89159ad7-c831-48db-a22e-64fa3b4692bb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f56916a_27b3_4c11_974e_33e9ea0cfed9
ELIN-640600-2016 | UW-429955-2016 | 8/29/2016 2:34:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 100amp cable altered by trimming conductors off so it would fit under the secondary side of the main 200amp main breaker. This is a fire hazard, the main breaker is not designed to be double tapped, the over current protection on the conductor is twice its allowable size. The rating of the conductor has been further reduced by the trimming of strands from it. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | A.png | file://x:/photopub/docs/0000000478/1b97f8c9-014a-47de-aa3b-cc7e5bb27f16.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__189fdfeb_2ad4_4167_aec8_e36496971ed1
ELIN-640600-2016 | UW-429955-2016 | 8/29/2016 2:34:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 100amp cable altered by trimming conductors off so it would fit under the secondary side of the main 200amp main breaker. This is a fire hazard, the main breaker is not designed to be double tapped, the over current protection on the conductor is twice its allowable size. The rating of the conductor has been further reduced by the trimming of strands from it. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | D.png | file://x:/photopub/docs/0000000478/c9d8017d-aee5-4aaa-b99c-7f5d35e285d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__189fdfeb_2ad4_4167_aec8_e36496971ed1
ELIN-640600-2016 | UW-429955-2016 | 8/29/2016 2:34:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 100amp cable altered by trimming conductors off so it would fit under the secondary side of the main 200amp main breaker. This is a fire hazard, the main breaker is not designed to be double tapped, the over current protection on the conductor is twice its allowable size. The rating of the conductor has been further reduced by the trimming of strands from it. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | C.png | file://x:/photopub/docs/0000000478/b63cfd13-ba19-4c81-ab25-f15f881b60f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__189fdfeb_2ad4_4167_aec8_e36496971ed1
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | N.png | file://x:/photopub/docs/0000000478/fe808d49-78e6-4cd6-889e-e4d814ad0061.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | I.png | file://x:/photopub/docs/0000000478/088061e9-7204-4cd6-a96c-3e41eb9f7f01.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640600-2016 | UW-429955-2016 | 8/29/2016 2:34:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 100amp cable altered by trimming conductors off so it would fit under the secondary side of the main 200amp main breaker. This is a fire hazard, the main breaker is not designed to be double tapped, the over current protection on the conductor is twice its allowable size. The rating of the conductor has been further reduced by the trimming of strands from it. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | G.png | file://x:/photopub/docs/0000000478/6e4e0969-4ba2-48a3-8ca1-b46cea223b35.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__189fdfeb_2ad4_4167_aec8_e36496971ed1
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | L.png | file://x:/photopub/docs/0000000478/45f14472-06c2-4d7b-b699-7db9e8e3fe66.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | M.png | file://x:/photopub/docs/0000000478/952f7ea4-9fa0-4490-95a6-278e962cb167.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | H.png | file://x:/photopub/docs/0000000478/37be1a09-f0c8-46af-af86-702341ec23d7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | O.png | file://x:/photopub/docs/0000000478/ebe114f3-ad2f-4a7c-9940-2654cecacb5c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640600-2016 | UW-429955-2016 | 8/29/2016 2:34:49 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL022 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | 4 | 4 | 100amp cable altered by trimming conductors off so it would fit under the secondary side of the main 200amp main breaker. This is a fire hazard, the main breaker is not designed to be double tapped, the over current protection on the conductor is twice its allowable size. The rating of the conductor has been further reduced by the trimming of strands from it. | 4 | Improper terminations or splices may result in overheating of conductors Cables or raceways have been mechanically damaged | F.png | file://x:/photopub/docs/0000000478/357cb634-2f43-41ca-89f0-feabf7d7b781.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__189fdfeb_2ad4_4167_aec8_e36496971ed1
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | J.png | file://x:/photopub/docs/0000000478/d355068e-a913-47d7-8fc7-4651212807e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | K.png | file://x:/photopub/docs/0000000478/c722f207-4b10-46be-b124-d5632ca13b07.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | P.png | file://x:/photopub/docs/0000000478/18ed9704-106d-47af-a8b6-f897a264d637.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELIN-640553-2016 | UW-429922-2016 | 8/29/2016 2:52:15 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL099 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | 3 | 4 | 4c #6 teck 90 on a 100A Eaton breaker installed in a Siemens panel. 4c, #6 copper conductors are permitted a maximum amperage of 65amps. This is a fire hazard as the cable is overloaded. Electrical equipment must be approved for its specific use. This is a fire hazard as the Eaton breaker does not properly connect to the bus of the Siemens panel. | 3 | Conductors, Cables, Raceways or conductors are not suitably sized, or of a type for their intended use. | Q.png | file://x:/photopub/docs/0000000478/c9792fe0-4226-4c2a-bf1f-70754fac7eb7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43f0c70b_ddf8_4aa0_a554_0e04b9d3b1f8
ELHE-602935-2016 | HE-403937-2016 | 6/29/2016 5:06:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | The 100 amp 120/240 volt branch feeder for the mobile home is fed with an underground cable to the pole and overhead to the main service. The pole has failed and is leaning, braced up by construction lumber and has no guy wire. The pole is susceptible to falling over with energized electrical attached, this is a shock hazard | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Mobile_home_pole_service_.png | file://x:/photopub/docs/0000000450/77f76885-abc2-4b7c-a3e5-3bffbefcfd4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51dd73cb_856e_4e3f_be3b_1be0af344aba
ELHE-602935-2016 | HE-403937-2016 | 6/29/2016 5:06:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | The 100 amp 120/240 volt branch feeder for the mobile home is fed with an underground cable to the pole and overhead to the main service. The pole has failed and is leaning, braced up by construction lumber and has no guy wire. The pole is susceptible to falling over with energized electrical attached, this is a shock hazard | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Pole_installation.png | file://x:/photopub/docs/0000000450/7fad34fb-30b1-4ab2-b5fe-9d1bcaf5f2cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51dd73cb_856e_4e3f_be3b_1be0af344aba
ELHE-602935-2016 | HE-403937-2016 | 6/29/2016 5:06:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | The 100 amp 120/240 volt branch feeder for the mobile home is fed with an underground cable to the pole and overhead to the main service. The pole has failed and is leaning, braced up by construction lumber and has no guy wire. The pole is susceptible to falling over with energized electrical attached, this is a shock hazard | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Trailer_connection_box.png | file://x:/photopub/docs/0000000450/be829d0e-2f01-40ce-9f18-b4aab40c4827.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51dd73cb_856e_4e3f_be3b_1be0af344aba
ELHE-602935-2016 | HE-403937-2016 | 6/29/2016 5:06:16 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | The 100 amp 120/240 volt branch feeder for the mobile home is fed with an underground cable to the pole and overhead to the main service. The pole has failed and is leaning, braced up by construction lumber and has no guy wire. The pole is susceptible to falling over with energized electrical attached, this is a shock hazard | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | Trailer_box_ground_connection.png | file://x:/photopub/docs/0000000450/701fd94b-fb9a-4681-946a-12f8f9871065.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__51dd73cb_856e_4e3f_be3b_1be0af344aba
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 1.png | file://x:/photopub/docs/0000000467/777a3dbd-80d3-4882-8a35-0c569cc78c69.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 5.png | file://x:/photopub/docs/0000000467/46d84a4f-1e40-4643-a2cb-965ee722dafa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 6.png | file://x:/photopub/docs/0000000467/130c0661-3a85-4753-aa00-81ef3db83ce8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
GAOP-200991-2014 | 2170379 | 6/27/2016 11:53:27 AM | ASSESS: GA OP: Periodic | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 |  | 2 | Appliance installed in a proposed hazardous location | Canfor_Mackenzie.png | file://x:/photopub/docs/0000000449/7785cede-2b3e-415a-85fd-5da49726272c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa4f712a_c275_431a_ada8_2ca6e58068e2
GAOP-200991-2014 | 2170379 | 6/27/2016 11:53:27 AM | ASSESS: GA OP: Periodic | png | #asFound | GA133 | Appliance installed in a proposed hazardous location | 2 | 2 |  | 2 | Appliance installed in a proposed hazardous location | Canfor_Mackenzie_2.png | file://x:/photopub/docs/0000000449/b20cc10a-1c7f-4af4-9d52-44be1627d46f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fa4f712a_c275_431a_ada8_2ca6e58068e2
ELIN-603917-2016 | UW-406318-2016 | 6/30/2016 2:26:14 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL091 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | 3 | 3 | In a new tenant improvement commercial retail unit, a 200amp 120/208volt feeder cable is not terminated correctly on its connector. This can lead to a shock hazard. | 3 | Continuity Electrical or mechanical continuity for metal raceways or enclosures is not continuous | Flex_connector.png | file://x:/photopub/docs/0000000451/e8f2d7f1-28cd-4cc1-b804-2a8ca69dac98.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__84d21dea_f637_48ad_a9ba_cdf83413deca
ELIN-626970-2016 | UW-421748-2016 | 8/9/2016 11:51:45 AM | ASSESS: EL IN: Unsafe Condition | jpg | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Branch circuit does not have an identified conductor. Potential for mis-wiring a junction and exposure to shock. | 3 | Conductors Equipment is not approved for the specific use. | buried JB.jpg | file://x:/photopub/docs/0000000468/1fabd28d-d3c2-4d40-a19d-127175e3bc28.jpg | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98dd2ec9_4456_4d90_a2ef_279e8941069b
ELOP-384904-2015 | 4143770 | 7/25/2016 4:37:16 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL159 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | 3 | 3 | Power disconnects must be provided on generator circuits. In this large resort installation a new control panel and system was installed using electronic disconnects instead of manual disconnects. The installing contractor was not allowed back on the resort so the owner bears the responsibility to make this code compliant and safe. | 3 | Protection and control Safety controls required for the safe operation of equipment are not provided or damaged. | No_local_disconnect_from_howie.png | file://x:/photopub/docs/0000000461/206de577-bbbc-4ea1-a5da-5902b8e999ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__90e56479_7e13_4c7c_a798_2214e0b6edc1
ELIN-628102-2016 | EL-422462-2016 | 8/15/2016 | ASSESS: EL: Service Connection | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found and confirmed service grounding plate electrode and its grounding conductor will not be buried deep enough in earth as required by code for effective service grounding system. When grounding electrode and its service grounding conductor is not buried to minimum earth covering requirements, the grounding system could be subject to possible mechanical damage and may not provide adequate and effective grounding of consumer's service power supply system for prevention of electrical fire or shock hazards to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | Plate_depth_confirmed_not_deep_enough.png | file://x:/photopub/docs/0000000471/aeb16638-25c9-42b8-9e18-db00962f485e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ee06eff_4d8d_48fe_b138_3af074bb6c70
GAIN-547203-2016 | GA-359365-2016 | 7/19/2016 3:29:27 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Without proper dirt pocket upstream of the regulator contamination could enter the regulator causing regulator failure. Regulator failure could cause damage to the connected equipment. | 2 | Not installed according to certified installation instructions | Gas_hose_kinked_.png | file://x:/photopub/docs/0000000468/ffcdbd4a-18be-4316-a154-ecdb35f9fd78.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1aad3b7b_8423_4d4e_87b8_6423d35b7f1e
GAIN-547203-2016 | GA-359365-2016 | 7/19/2016 3:29:27 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Without proper dirt pocket upstream of the regulator contamination could enter the regulator causing regulator failure. Regulator failure could cause damage to the connected equipment. | 2 | Not installed according to certified installation instructions | Regulators_without_proper_dirt_pocket_.png | file://x:/photopub/docs/0000000468/25fe4040-7b34-492f-8f79-0f58acff9b5e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1aad3b7b_8423_4d4e_87b8_6423d35b7f1e
ELIN-628538-2016 | EL-327765-2015 | 8/17/2016 10:30:16 AM | ASSESS: EL: Final | png | #asFound | EL128 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 3 | 3 | 2 20'amp 120 volt receptacles for kitchen counter were found connected to a 15 amp circuit breaker in a new dwelling. This receptacle is subject to overload of the breaker which could cause damage to property or unreliable service of the circuit for occupants. | 3 | Installation of electrical equipment Residential: branch circuit for kitchen counter receptacles is not split 15 A, or 20 A. | 15_amp_breaker_for_20_amp_outlets.png | file://x:/photopub/docs/0000000472/722a1028-8c78-4fdb-834f-4aa1b5dd033c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec4c1873_5fb7_49f8_98be_6e898786304a
ELIN-626385-2016 | EL-370541-2016 | 8/12/2016 10:51:59 AM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | A new residence under the latest code was found to have old stock arc fault breakers that were not combination rated. Wiring in the walls of the house and all cord connected equipment can fail leading to property damage or injury to persons where the correct breakers are not employed | 3 | Installation of electrical equipment Equipment is not approved for the specific use | Afci_breakers_not_combination_type.png | file://x:/photopub/docs/0000000472/eb765db6-0fe7-4bb1-85c6-0935c0201c20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6c8b52b7_e798_4299_8050_809a426ce73e
ELIN-639224-2016 | EL-424075-2016 | 8/31/2016 3:28:43 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found electrical equipment 120 volt 15 amp is not all bonded together. When electrical equipment is not all bonded together properly and if there is a fault condition on the system there is a possibility of an electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 101.png | file://x:/photopub/docs/0000000478/f73225fe-e45b-4a03-88ab-6493f9c217fa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8e4fca_74aa_4dd9_8349_3360831a8bd9
ELIN-639224-2016 | EL-424075-2016 | 8/31/2016 3:28:43 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found electrical equipment 120 volt 15 amp is not all bonded together. When electrical equipment is not all bonded together properly and if there is a fault condition on the system there is a possibility of an electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 102.png | file://x:/photopub/docs/0000000478/bfcee076-a591-42e1-8a0d-790deec5fed9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8e4fca_74aa_4dd9_8349_3360831a8bd9
ELIN-639224-2016 | EL-424075-2016 | 8/31/2016 3:28:43 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found electrical equipment 120 volt 15 amp is not all bonded together. When electrical equipment is not all bonded together properly and if there is a fault condition on the system there is a possibility of an electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 103.png | file://x:/photopub/docs/0000000478/9507d61a-7061-478d-997d-e5e6c1452748.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8e4fca_74aa_4dd9_8349_3360831a8bd9
ELIN-639224-2016 | EL-424075-2016 | 8/31/2016 3:28:43 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found electrical equipment 120 volt 15 amp is not all bonded together. When electrical equipment is not all bonded together properly and if there is a fault condition on the system there is a possibility of an electrical fire or shock hazard to people or property. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 100.png | file://x:/photopub/docs/0000000478/19cc0c22-b162-4c65-9e11-1118abba8858.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2f8e4fca_74aa_4dd9_8349_3360831a8bd9
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 2.png | file://x:/photopub/docs/0000000467/09ce2e4e-8cbe-41b8-9cf0-3b53184ecadc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4.png | file://x:/photopub/docs/0000000467/90a5da20-b5ce-4c9b-b1fa-d0bf4b06c9f4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 7.png | file://x:/photopub/docs/0000000467/87a8799e-cdcb-4095-ba6e-82b1d920773e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
ELIN-618114-2016 | EL-351625-2016 | 7/25/2016 4:49:21 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL012 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 4 | 4 | Found energized 120/240 volt 1 phase combination service panel with energized exposed conductors and bus bars in area of panelboard service compartment and distribution compartment. When an energized panelboard has missing covers on exposed energized conductors, the electrical equipment and system is an electrical fire or shock hazard to people and property. | 4 | Conductors are exposed to accidental contact by persons Secondary Poles and their associated hardware (line) are not adequate for the purpose; Clearances are not adequate. | 3.png | file://x:/photopub/docs/0000000467/2d7b1298-5bf1-49b7-a6d0-a3a7ef9b0860.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ce97ae3b_647f_4434_8990_e78abe04603f
ELIN-597899-2016 | EL-385055-2016 | 7/6/2016 8:17:17 PM | ASSESS: EL: Final | png | #asFound | EL119 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | 2 | 2 | Existing cables have pulled out of their connectors.This creates tension and strain on the terminations creating potential loose connections and exposed wiring. | 2 | Conductors Cables, Raceways or conductors are showing signs of wear or may be exposed to mechanical damage; and will need to be either replaced or repaired. | Cables_pulled_out.png | file://x:/photopub/docs/0000000452/eed49f45-dc3e-4434-9cdd-533ddfcfd29b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d5b8baa1_c834_4b31_8315_9ff7d1d53f8d
EDIN-614540-2016 | ED-389258-2016 | 7/28/2016 12:29:09 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | Loading ramp at lower landing is only as wide as the elevator door, creating a tripping hazard from the side of the ramp. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Ramp.png | file://x:/photopub/docs/0000000463/5f20cbed-8b8b-48e4-bc08-ff60316fdd95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2788f1c3_84ba_4423_b365_9b2af673ab05
ELIN-635030-2016 | EL-425697-2016 | 8/24/2016 11:47:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Roof_not_installed_on_house__.png | file://x:/photopub/docs/0000000475/865fcbf4-017d-4e1c-b6e4-929ebc18fb88.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94ac5ef0_22a2_4e25_917e_a703c53cc660
ELIN-635030-2016 | EL-425697-2016 | 8/24/2016 11:47:25 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Broken_hasp_on_temporary_panel_cover.png | file://x:/photopub/docs/0000000475/ec5cbccb-14c5-4864-a964-84b4619bf0f0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94ac5ef0_22a2_4e25_917e_a703c53cc660
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 111.png | file://x:/photopub/docs/0000000472/09f0432e-a424-41e2-a8bf-54df70011a1e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 113.png | file://x:/photopub/docs/0000000472/7bedda90-8854-495f-8228-129d70730d56.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 109.png | file://x:/photopub/docs/0000000472/1c821c13-c775-475b-acad-6e4a3da12c04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 103.png | file://x:/photopub/docs/0000000472/912e8ba3-07bc-4e5f-8a1a-afa6ab4be6c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 110.png | file://x:/photopub/docs/0000000472/f2d53180-fab2-40ca-b4d6-a9d9788ab5d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 102.png | file://x:/photopub/docs/0000000472/039a8be6-7125-4866-a27a-de9dcd1158e6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 105.png | file://x:/photopub/docs/0000000472/4667ad9f-b667-4721-9cb4-731cce7bbfe4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 108.png | file://x:/photopub/docs/0000000472/6f0eabb7-1d47-4393-b00f-771c7bdcac5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 106.png | file://x:/photopub/docs/0000000472/e680b414-22b6-44f9-a76b-91fccdef857a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 107.png | file://x:/photopub/docs/0000000472/cf0aa8ec-c56c-4589-b954-696dc8f45314.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 101.png | file://x:/photopub/docs/0000000472/8a7dcc78-4af9-4172-b12c-a1eaf7258606.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 100.png | file://x:/photopub/docs/0000000472/58fc56a7-21bf-4ae7-8eca-2e0a3c109ea9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 112.png | file://x:/photopub/docs/0000000472/0bfa4ba8-5041-403f-a011-47ac9eec917b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELIN-632252-2016 | UW-425099-2016 | 8/17/2016 8:00:51 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Found damaged, hazardous, non-compliant and unapproved 120 volt 15 amp connected temporary construction portable flexible cords. The flexible cords above had energized conductors exposed out of cord end receptacle boxes. When electrical equipment is damaged, non-compliant and unapproved electrical equipment with exposed energized conductors, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 104.png | file://x:/photopub/docs/0000000472/286e125f-5359-4182-930c-4bed7f5b783e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__47c97a7b_c1ac_4001_92b8_b628909de986
ELOP-559983-2016 | EL-376609-2016 | 8/3/2016 11:56:33 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Thermal, arc flash and shock hazard from possible mechanical damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Conduit2.png | file://x:/photopub/docs/0000000465/486bd81c-a786-4751-a459-4de9d81f50ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75346e3a_b294_4be6_be2d_26311f58aba9
ELOP-559983-2016 | EL-376609-2016 | 8/3/2016 11:56:33 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Thermal, arc flash and shock hazard from possible mechanical damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Breaker.png | file://x:/photopub/docs/0000000465/84994185-c764-49e1-bb49-58fbecf85614.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75346e3a_b294_4be6_be2d_26311f58aba9
ELOP-559983-2016 | EL-376609-2016 | 8/3/2016 11:56:33 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Thermal, arc flash and shock hazard from possible mechanical damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Service1.png | file://x:/photopub/docs/0000000465/dd296088-b738-4aed-a3c6-14d1b911dfcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75346e3a_b294_4be6_be2d_26311f58aba9
ELOP-559983-2016 | EL-376609-2016 | 8/3/2016 11:56:33 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Thermal, arc flash and shock hazard from possible mechanical damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Conduit1.png | file://x:/photopub/docs/0000000465/c2f08c8e-810e-496f-a4c8-c0f3a3ca39bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75346e3a_b294_4be6_be2d_26311f58aba9
ELOP-559983-2016 | EL-376609-2016 | 8/3/2016 11:56:33 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL107 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | 3 | 3 | Thermal, arc flash and shock hazard from possible mechanical damage. | 3 | Conductors Cables, Raceways or conductors are damaged and need to be either replaced or repaired, No expansion joint or not installed correctly. | Meter_jumper.png | file://x:/photopub/docs/0000000465/bff109c4-8a03-4431-bff7-5c59e0f6781c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__75346e3a_b294_4be6_be2d_26311f58aba9
GAIN-608665-2016 | GA-292388-2015 | 7/11/2016 10:35:57 AM | ASSESS: GA: Final | png | #asFound | GA084 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | 3 | 3 | Clearance between regulator vent and mechanical air intake to an appliance not maintained. Gas could be drawn into appliance if the regulator were to fail causing fire or explosion. | 3 | Relief style regulator/device terminating too close to a mechanical air inlet (Risk Registry Item GA-02) | Mechanical_air_intake_clearance_not_maintained.png | file://x:/photopub/docs/0000000454/dfefee87-c2e9-44a4-8b3f-e524254cd36b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e4a629b_5495_47ba_aff7_d8269e45ab99
GAUP-629130-2016 | UW-423091-2016 | 8/10/2016 8:02:11 AM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | Must use connector that is approved for moveable appliances. If not using the proper connector, after repeated movement the connector could crack and leak causing a fire and or injury. | 3 | Non-certified appliance connector | Unapproved_connector.png | file://x:/photopub/docs/0000000469/1469cc66-2c99-4d77-aea3-82435290fc9c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40d4c8ee_1c71_46dc_a1af_d5fb1c00abac
ELHE-643347-2016 | HE-433096-2016 | 9/1/2016 10:07:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | -extensive use of extension cords. Multiple high consumption electrical appliances connected. Extension cords have been used as a permanent wiring method due to insufficient receptacles and dedicated circuits. | 4 | Conductors, Misuse of flexible cords. | Pic_2.png | file://x:/photopub/docs/0000000479/251c525b-9669-4b1f-be7f-19bbb2727deb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2b0e14f_f6da_432d_a1e9_f3f9590b744a
ELHE-643347-2016 | HE-433096-2016 | 9/1/2016 10:07:14 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL116 | Conductors, Misuse of flexible cords. | 4 | 4 | -extensive use of extension cords. Multiple high consumption electrical appliances connected. Extension cords have been used as a permanent wiring method due to insufficient receptacles and dedicated circuits. | 4 | Conductors, Misuse of flexible cords. | Pic_1.png | file://x:/photopub/docs/0000000479/5fefd227-eaa1-4ab3-a69c-d90c99d850dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c2b0e14f_f6da_432d_a1e9_f3f9590b744a
ELIN-603125-2016 | 5443868 | 7/5/2016 9:24:49 AM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Junction box not properly supported and missing cover. This is a shock and fire hazard, as there is potential to contact live conductors and unintended movement of the box could weaken the splices creating hot spots. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | A.png | file://x:/photopub/docs/0000000452/3fe82e34-b51c-41b1-9696-4df71deba7b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b6a9019_5abb_48fe_884e_f7e2fe7a9cb9
ELOP-192710-2014 | 168 | 7/5/2016 8:30:45 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL229 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | 2 | 2 |  | 2 | Class II, wood dust, Minor cleanup required, and or Record management is incomplete. Wood dust mitigation and fire plans are in place and being followed. | Edge_saw_floor.png | file://x:/photopub/docs/0000000452/0e8c4d6c-8a6a-4b8b-a735-c569a6683357.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fa14adc_1358_454e_8d87_d312cff75cf5
ELIN-602296-2016 | EL-402493-2016 | 6/28/2016 11:13:10 AM | ASSESS: EL: Service Connection | png | #asFound | EL202 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | 3 | 3 | Service is energized prior to inspection. Contractor stated he has terminated the existing overhead line to the new mast, energized conductors are required to be disconnected prior to being worked on, accidental contact with energized conductors may cause shock, fire or damage to persons and property. | 3 | Energized work by qualified persons High or Low Voltage: • no procedures; • PPE in place; and • qualified workers performing work. | New_Service_and_Old_Service.png | file://x:/photopub/docs/0000000449/a2b690cf-4ea2-4aa2-a41a-337c4deeff86.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d75957c4_cc4f_4e0a_bfb0_cc94724ecd67
ELIN-601466-2016 | EL-391286-2016 | 6/28/2016 2:59:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | A fused disconnect switch has 100 amp fuses installed and is feeding a 100 amp panel. The wire installed from the meter base to the the fused disconnect is #6 copper and is rated for 60 amps. The 100 amp fuses are not protecting the #6 copper conductors. In the event of high circuit loading excess current could cause the wiring to fail before overcurrent reacts, a risk of shock or fire is present to persons or property as well as equipment damage | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Interior_of_200_amp_switch_fused_at_100_amps.png | file://x:/photopub/docs/0000000449/1b07f927-fb26-4f51-9aab-0d7aec3039d1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29896ca7_c1da_494a_a323_10a285271577
ELIN-601466-2016 | EL-391286-2016 | 6/28/2016 2:59:51 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL024 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | 4 | 4 | A fused disconnect switch has 100 amp fuses installed and is feeding a 100 amp panel. The wire installed from the meter base to the the fused disconnect is #6 copper and is rated for 60 amps. The 100 amp fuses are not protecting the #6 copper conductors. In the event of high circuit loading excess current could cause the wiring to fail before overcurrent reacts, a risk of shock or fire is present to persons or property as well as equipment damage | 3 | Conductor ampacity is not adequate for the calculated load Overcurrent device does not adequately protect conductors | Exterior_of_200_amp_disconnect_and_100_amp_panel.png | file://x:/photopub/docs/0000000449/c499267c-efd5-48fe-9d11-f7c512a69d60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__29896ca7_c1da_494a_a323_10a285271577
ELHE-620572-2016 | HE-417523-2016 | 7/28/2016 1:20:51 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Vacant meter openings are covered with wood covers. This material can easily be damaged and expose the meter connections creating a shock hazard. | 3 | General Equipment is not approved for the specific use | Meterstack.png | file://x:/photopub/docs/0000000463/74e05099-7cd9-4557-b3bd-7365a2638a6e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b657347_d7d0_414e_8799_4d9f1d5effe3
ELIN-637571-2016 | EL-402721-2016 | 8/26/2016 11:36:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Conduit is tight to exterior wall. Screw is close to conduit and demonstrates its vulnerability . If conductor was damaged from nail it would create a thermal and shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Inside_wall_conduit_.png | file://x:/photopub/docs/0000000476/9c4e0a0b-123a-456d-b371-858c921ef7e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94a5d0e5_d6b3_467c_9a48_b65bf6a03d92
ELIN-637571-2016 | EL-402721-2016 | 8/26/2016 11:36:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Conduit is tight to exterior wall. Screw is close to conduit and demonstrates its vulnerability . If conductor was damaged from nail it would create a thermal and shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Exterior_wall_with_no_protection_plate_.png | file://x:/photopub/docs/0000000476/e1cbe360-744e-406f-b477-f0669d46b041.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94a5d0e5_d6b3_467c_9a48_b65bf6a03d92
ELIN-637571-2016 | EL-402721-2016 | 8/26/2016 11:36:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Conduit is tight to exterior wall. Screw is close to conduit and demonstrates its vulnerability . If conductor was damaged from nail it would create a thermal and shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Exterior_wall.png | file://x:/photopub/docs/0000000476/c1bc0efc-8e4c-4794-b6b8-d94e970f07eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94a5d0e5_d6b3_467c_9a48_b65bf6a03d92
ELIN-637571-2016 | EL-402721-2016 | 8/26/2016 11:36:14 AM | ASSESS: EL: Service Connection | png | #asFound | EL026 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | 4 | 4 | Conduit is tight to exterior wall. Screw is close to conduit and demonstrates its vulnerability . If conductor was damaged from nail it would create a thermal and shock hazard. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is subject to mechanical damage, and adequate mechanical protection has not been provided. | Inside_wall.png | file://x:/photopub/docs/0000000476/990997f4-54d8-48d0-88d3-193549305881.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__94a5d0e5_d6b3_467c_9a48_b65bf6a03d92
GAIN-616278-2016 | GA-404637-2016 | 8/10/2016 10:52:44 AM | ASSESS: GA: Final | png | #asFound | GA134 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | 2 | 2 | Electrical connection safe, because not energized, but non compliant. If non compliant electrical connections were energized, live energy source could be exposed to public. | 2 | Electrical supply/switch safe but non-compliant to Canadian Electrical Code (example: location) | Non_compliant_electrical_connection.png | file://x:/photopub/docs/0000000468/70409fb7-efc8-445b-9b51-5664771c49ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__df4af2d6_ccdc_4953_adc0_4d8e80ec61f8
ELIN-610277-2016 | UW-410393-2016 | 7/12/2016 2:26:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Regulated electrical work performed by unqualified person | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Added_lights.png | file://x:/photopub/docs/0000000455/bf68f6cd-26b3-4d5e-8f4c-078e979618ef.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dac8fc14_a259_418d_865d_d688e6aa3837
ELIN-610277-2016 | UW-410393-2016 | 7/12/2016 2:26:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Regulated electrical work performed by unqualified person | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Kitchen_in_unit.png | file://x:/photopub/docs/0000000455/7576f1d1-58ef-48f1-997c-58227c6bbc4e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dac8fc14_a259_418d_865d_d688e6aa3837
ELIN-610277-2016 | UW-410393-2016 | 7/12/2016 2:26:28 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL003 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | 5 | 5 | Regulated electrical work performed by unqualified person | 5 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • bare energized parts such as busbars, terminals, conductors are exposed to accidental contact; and • in an area that is normally accessible to the general public. | Dishwasher_circuit_added.png | file://x:/photopub/docs/0000000455/f5f81d57-2716-41d4-a17c-82c0555db418.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__dac8fc14_a259_418d_865d_d688e6aa3837
GAWP-629482-2016 | GA-150931-2014 | 8/11/2016 1:26:18 PM | ASSESS: GA Work In Progress | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | The venting not being supported could lead to vent system coming disconnected from the furnace leaking products of combustion into the occupied space of the building. | 2 | Side wall vent termination not compliant with installation instructions | Venting_not_supported_.png | file://x:/photopub/docs/0000000469/91d4681d-2130-4914-bac9-c2b3b707ef46.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9975b490_4d86_4497_9f85_2dab6d2706f4
GAWP-629482-2016 | GA-150931-2014 | 8/11/2016 1:26:18 PM | ASSESS: GA Work In Progress | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 | The venting not being supported could lead to vent system coming disconnected from the furnace leaking products of combustion into the occupied space of the building. | 2 | Side wall vent termination not compliant with installation instructions | Venting_not_supprted.png | file://x:/photopub/docs/0000000469/b59d8d3e-000a-432d-b7e0-fe0dddbd818c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9975b490_4d86_4497_9f85_2dab6d2706f4
ELIN-631440-2016 | EL-422371-2016 | 8/25/2016 1:21:56 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | A new service for residential use rated 100 amps and 240 volts single phase has been installed. The main system ground has not been connected correctly. Damage to property or injury to persons can occur when grounding is not effectively connected. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Main_system_ground_improperly_connected_to_equipment_bond.png | file://x:/photopub/docs/0000000476/1b410c57-dc75-492e-9b55-8e8cf55f306f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__11d4946c_62f2_419f_afa0_c7debee67518
ELIN-638413-2016 | EL-401289-2016 | 8/25/2016 9:46:30 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 2 | A temporary connection of a permanent new residential 200 amp 240 V single phase service was authorized for connection to the utility. The temporary enclosure that was intended to provide a weatherproof and lockable environment was not constructed correctly to exclude rain from the equipment. Electrical equipment inside panel boards can be damaged by moisture and fail unpredictably. This could lead to property damage or injury to persons. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Roof_overhang_does_not_stop_rain_in_wind.png | file://x:/photopub/docs/0000000476/cbadf8fa-5917-48cb-a840-2e4d4f20d9e4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__43e4db1d_f8dd_4265_8d9d_f1814aaad49b
EDRI-645635-2016 | ED-388259-2016 | 9/7/2016 1:00:28 PM | ASSESS: ED RI: Extension | png | #asFound | ED052 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | 2 | 2 | Hoarding above lift was being built while we were operating lift with no request to shut down lift. | 2 | Switches / circuits controlling access point working correctly Some Oily Surface Fall prevention means in place Adequate lighting | Hoarding_level_17.png | file://x:/photopub/docs/0000000481/030eca58-11ae-41ab-ad0d-b150b7b7735b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73bd2912_415a_4570_8a7a_4f7b8155c2a8
ELIN-621892-2016 | EL-406717-2016 | 8/3/2016 1:26:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 | Thermoplastic wiring that is in contact with a heat source will overtime break down. The thermal plastic insulation and could potentially cause a fire due to overheating. | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | Wiring_in_contact_with_heat_source.png | file://x:/photopub/docs/0000000465/3ade24c5-8ca1-444d-b5d7-a5b159ca6c0e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7ccf0ec_6d31_4e0b_8c71_f2a8f8ded3ab
ELIN-621892-2016 | EL-406717-2016 | 8/3/2016 1:26:55 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL111 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | 2 | 2 | Thermoplastic wiring that is in contact with a heat source will overtime break down. The thermal plastic insulation and could potentially cause a fire due to overheating. | 2 | Conductors Temperature ratings for conductors are not appropriate for conditions of use | Item_2.png | file://x:/photopub/docs/0000000465/7bfc0ee1-18eb-4d44-a43f-968d12d895c5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d7ccf0ec_6d31_4e0b_8c71_f2a8f8ded3ab
ELIN-610168-2016 | EL-332030-2016 | 8/10/2016 4:07:52 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The point of attachment for over head service supply conductors is required to be located 150 - 300mm below the service weather head where the consumer service conductors exit the service conduit for connection to the supply conductors. This is required to prevent water from entering the service conduit and meter base where it can cause the internal components and conductor terminations in the meter base to rust and corrode. This installation of a service repair to 125A, 120/240V over head service to a house has a service conduit with a weather head located approximately 18" below the point of attachment. The service conductors exit the weather head in an upward direction towards the point of attachment. The service is energized. Left uncorrected water will run down the service conductors and enter the weather head and service conduit. The water will then enter the top of the meter base and over time will rust and corrode the internal components inside the meter base including the conductor terminations. This | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Point_of_attachment_apprx_18_inches_above_service_head_where_conductors_exit_conduit_in_an_upward_direction.png | file://x:/photopub/docs/0000000469/da6de14f-709d-4fb3-abf1-b265985dda11.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b6debe8_adeb_4469_bdb7_ebdd4b23391d
ELIN-625131-2016 | EL-390421-2016 | 8/10/2016 2:19:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors for cables installed outdoors need to be sized properly and installed properly to seal around the jacket of the cable. This is required so that water does not enter the equipment between the cable jacket and the cable connector seal. This installation of a new 200A 120/240V service for a house has a service cable installed on a pole that terminates into the top of a meter base mounted to the pole. There is a gap between the cable jacket and the cable connector seal. Left uncorrected this is a potential fire hazard if over time water enters the meter base and rusts/corrodes the internal meter base components and lugs that the service conductors terminate into. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_pole_.png | file://x:/photopub/docs/0000000469/432621c4-15c9-4b4f-9ed2-2ce4fdc63faa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3eaabf_c1ec_4902_a7f8_328b8f30ddd8
ELIN-610168-2016 | EL-332030-2016 | 8/10/2016 4:07:52 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The point of attachment for over head service supply conductors is required to be located 150 - 300mm below the service weather head where the consumer service conductors exit the service conduit for connection to the supply conductors. This is required to prevent water from entering the service conduit and meter base where it can cause the internal components and conductor terminations in the meter base to rust and corrode. This installation of a service repair to 125A, 120/240V over head service to a house has a service conduit with a weather head located approximately 18" below the point of attachment. The service conductors exit the weather head in an upward direction towards the point of attachment. The service is energized. Left uncorrected water will run down the service conductors and enter the weather head and service conduit. The water will then enter the top of the meter base and over time will rust and corrode the internal components inside the meter base including the conductor terminations. This | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_base_and_service_conduit_on_exterior_of_house_.png | file://x:/photopub/docs/0000000469/84688929-0281-4b10-8a3a-201f72045d52.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b6debe8_adeb_4469_bdb7_ebdd4b23391d
ELIN-625131-2016 | EL-390421-2016 | 8/10/2016 2:19:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors for cables installed outdoors need to be sized properly and installed properly to seal around the jacket of the cable. This is required so that water does not enter the equipment between the cable jacket and the cable connector seal. This installation of a new 200A 120/240V service for a house has a service cable installed on a pole that terminates into the top of a meter base mounted to the pole. There is a gap between the cable jacket and the cable connector seal. Left uncorrected this is a potential fire hazard if over time water enters the meter base and rusts/corrodes the internal meter base components and lugs that the service conductors terminate into. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_cable_not_sealed_around_service_cable_at_top_of_meter_base_.png | file://x:/photopub/docs/0000000469/78cac5ea-34b4-4105-92ed-d2b945942d34.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3eaabf_c1ec_4902_a7f8_328b8f30ddd8
ELIN-610168-2016 | EL-332030-2016 | 8/10/2016 4:07:52 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The point of attachment for over head service supply conductors is required to be located 150 - 300mm below the service weather head where the consumer service conductors exit the service conduit for connection to the supply conductors. This is required to prevent water from entering the service conduit and meter base where it can cause the internal components and conductor terminations in the meter base to rust and corrode. This installation of a service repair to 125A, 120/240V over head service to a house has a service conduit with a weather head located approximately 18" below the point of attachment. The service conductors exit the weather head in an upward direction towards the point of attachment. The service is energized. Left uncorrected water will run down the service conductors and enter the weather head and service conduit. The water will then enter the top of the meter base and over time will rust and corrode the internal components inside the meter base including the conductor terminations. This | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Side_of_house_where_service_is_located_.png | file://x:/photopub/docs/0000000469/4c4e2ec5-4403-448b-bd57-1c0e51948aae.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b6debe8_adeb_4469_bdb7_ebdd4b23391d
ELIN-625131-2016 | EL-390421-2016 | 8/10/2016 2:19:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors for cables installed outdoors need to be sized properly and installed properly to seal around the jacket of the cable. This is required so that water does not enter the equipment between the cable jacket and the cable connector seal. This installation of a new 200A 120/240V service for a house has a service cable installed on a pole that terminates into the top of a meter base mounted to the pole. There is a gap between the cable jacket and the cable connector seal. Left uncorrected this is a potential fire hazard if over time water enters the meter base and rusts/corrodes the internal meter base components and lugs that the service conductors terminate into. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | New_house_under_construction.png | file://x:/photopub/docs/0000000469/5eadd622-f6ea-4f57-8a9a-63c98bc9d2f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3eaabf_c1ec_4902_a7f8_328b8f30ddd8
GAHE-639488-2016 | HE-429257-2016 | 8/26/2016 1:17:19 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was a custom approved bakery oven which had been modified by removing a power venter, this created a condition where the oven was spilling products of combustion into the building. This is a hazard because carbon monoxide is entering the building where employees are working and the public is coming in to purchase goods. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | CO_measured.png | file://x:/photopub/docs/0000000476/9b5b6215-eb72-4dc7-b97c-8bb0cc5ff8c7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40744281_0d38_4516_9382_db0d24c2d754
GAHE-639488-2016 | HE-429257-2016 | 8/26/2016 1:17:19 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA110 | Atmospheric venting system installed where back drafting or spillage is occurring | 5 | 5 | The as found hazard was a custom approved bakery oven which had been modified by removing a power venter, this created a condition where the oven was spilling products of combustion into the building. This is a hazard because carbon monoxide is entering the building where employees are working and the public is coming in to purchase goods. | 5 | Atmospheric venting system installed where back drafting or spillage is occurring | Oven_hood.png | file://x:/photopub/docs/0000000476/f549567a-2610-46dc-963d-f2140219a4d0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__40744281_0d38_4516_9382_db0d24c2d754
ELHE-637678-2016 | HE-428070-2016 | 8/24/2016 4:14:12 PM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL090 | Continuity Bonding; method for equipment is not adequate. | 3 | 3 | The gradient control mat for a high voltage switch is not properly bonded to the switch handle. This could result in a shock hazard to the operator of the switch. | 3 | Continuity Bonding; method for equipment is not adequate. | Mat.png | file://x:/photopub/docs/0000000475/03d6ccba-4e00-488a-834b-37346d2db632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__af648abb_32c8_4367_a54d_0ac092ba9b93
BPVOP-616203-2016 | BPV-0000131264-2014 | 7/21/2016 2:24:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Scale.png | file://x:/photopub/docs/0000000459/0e741747-cef6-4788-9b03-8bfa0a5e3f2a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__750d2f7e_1d86_49ad_a8a9_70e2a441bd15
ELIN-625131-2016 | EL-390421-2016 | 8/10/2016 2:19:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors for cables installed outdoors need to be sized properly and installed properly to seal around the jacket of the cable. This is required so that water does not enter the equipment between the cable jacket and the cable connector seal. This installation of a new 200A 120/240V service for a house has a service cable installed on a pole that terminates into the top of a meter base mounted to the pole. There is a gap between the cable jacket and the cable connector seal. Left uncorrected this is a potential fire hazard if over time water enters the meter base and rusts/corrodes the internal meter base components and lugs that the service conductors terminate into. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_cable_connector_on_top_of_meter_base_is_not_sealed_around_the_service_cable.png | file://x:/photopub/docs/0000000469/1df85f9b-9933-4e2b-9903-ac2349f79bcf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3eaabf_c1ec_4902_a7f8_328b8f30ddd8
ELIN-610168-2016 | EL-332030-2016 | 8/10/2016 4:07:52 PM | ASSESS: EL: Final | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | The point of attachment for over head service supply conductors is required to be located 150 - 300mm below the service weather head where the consumer service conductors exit the service conduit for connection to the supply conductors. This is required to prevent water from entering the service conduit and meter base where it can cause the internal components and conductor terminations in the meter base to rust and corrode. This installation of a service repair to 125A, 120/240V over head service to a house has a service conduit with a weather head located approximately 18" below the point of attachment. The service conductors exit the weather head in an upward direction towards the point of attachment. The service is energized. Left uncorrected water will run down the service conductors and enter the weather head and service conduit. The water will then enter the top of the meter base and over time will rust and corrode the internal components inside the meter base including the conductor terminations. This | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Service_conductors_exit_service_weather_head_in_an_upward_direction.png | file://x:/photopub/docs/0000000469/fe5130ed-4f39-42d3-878f-6b0eb1a3bfce.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b6debe8_adeb_4469_bdb7_ebdd4b23391d
ELIN-625131-2016 | EL-390421-2016 | 8/10/2016 2:19:44 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Cable connectors for cables installed outdoors need to be sized properly and installed properly to seal around the jacket of the cable. This is required so that water does not enter the equipment between the cable jacket and the cable connector seal. This installation of a new 200A 120/240V service for a house has a service cable installed on a pole that terminates into the top of a meter base mounted to the pole. There is a gap between the cable jacket and the cable connector seal. Left uncorrected this is a potential fire hazard if over time water enters the meter base and rusts/corrodes the internal meter base components and lugs that the service conductors terminate into. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Meter_base_on_pole.png | file://x:/photopub/docs/0000000469/bb8d231d-1a00-48c0-8186-78930917f2a0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4b3eaabf_c1ec_4902_a7f8_328b8f30ddd8
ELIN-640968-2016 | EL-430173-2016 | 8/31/2016 2:56:23 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized open panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Energized_unprotected_panel.png | file://x:/photopub/docs/0000000478/38327163-e62a-452b-8e52-4e70c3c9ae7d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a0e5252_5881_4e6d_8311_7187b2ff4b4e
ELIN-640968-2016 | EL-430173-2016 | 8/31/2016 2:56:23 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized open panel. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Open_panel_208V.png | file://x:/photopub/docs/0000000478/ffc7a161-c838-4dd6-b78b-577d9717c68f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a0e5252_5881_4e6d_8311_7187b2ff4b4e
BPVOP-630162-2016 | 2270723 | 8/12/2016 11:48:31 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of low pressure steam heating boiler with 132 square meters heating surface it is determined that safety valve has exceeded the required 5year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary and can lead to an incident due rapid uncontrolled release of steam/hot water. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_VALVES.png | file://x:/photopub/docs/0000000470/0fb11d90-2b5a-4fc2-9652-9938699e60ad.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2e2f1906_7939_430f_89fd_ed9324c2cb8e
BPVOP-630163-2016 | 2270725 | 8/12/2016 1:14:35 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP132 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | 3 | 3 | Upon assessment of low pressure steam heating boiler with 132 square meters heating surface it is determined that safety valve is leaking. Leaky safety may result in complete failure of safety valve with likelihood of severe incident. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device indicates signs of leakage | Leaky_safety_valve.png | file://x:/photopub/docs/0000000470/23cd4d59-2cbb-423d-8941-a5e9eca4f55e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1d716e7e_06ab_449f_80e8_d0011dc06a41
GAIN-602885-2016 | GA-323393-2015 | 7/5/2016 11:08:37 AM | ASSESS: GA: Final | png | #asFound | GA038 | Pipe supports not compliant but in place | 1 | 1 | Incorrect piping supports in place. Piping and tubing supports must be metallic to prevent damage to gas system in the event of a fire. | 1 | Pipe supports not compliant but in place | Incorrect_piping_supports_.png | file://x:/photopub/docs/0000000452/0995f237-6dbe-4630-adec-42fd74b71296.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__acd63fab_2388_4764_ab3a_550c497df7c2
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_cover_plate.png | file://x:/photopub/docs/0000000453/39985f16-e4cf-4bc4-b3fc-73425ced8035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Not_secured_to_wall.png | file://x:/photopub/docs/0000000453/ca88418b-9cb2-4faf-9cca-355b6db05bca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_support.png | file://x:/photopub/docs/0000000453/3b0f68a3-febf-4f0c-9f56-ac05e01a0773.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_disconnect_switch.png | file://x:/photopub/docs/0000000453/e48e7cb3-accc-48d4-b0ca-821ee053fcaa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | C-Can_with_panel_and_no_bond.png | file://x:/photopub/docs/0000000453/3ff2f05f-0e1b-41c4-8e7d-6ffeda17ad8f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Drum_switch.png | file://x:/photopub/docs/0000000453/500c4c62-d758-4286-8171-4ae3eb0b4d4d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
GAHE-608122-2016 | HE-408875-2016 | 7/11/2016 12:09:55 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA116 | Supports/termination present, but not in compliance with mfg instructions | 1 | 1 | Found water heater exhaust vent installed too close to an opening window. This could cause the products of combustion to circulate into the open window. | 1 | Supports/termination present, but not in compliance with mfg instructions | 3377_164a_street.png | file://x:/photopub/docs/0000000454/c272f304-952f-46d4-bc1c-412d49d60703.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ef809ac3_7e00_4cde_afbd_ce85edccf4a3
GAUP-641983-2016 | UW-430906-2016 | 9/2/2016 2:38:08 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA131 | Equipment service clearance non compliant | 1 | 1 | Appliance service clearance not met. | 1 | Equipment service clearance non compliant | Appliance_service_clearance_not_met_.png | file://x:/photopub/docs/0000000479/375fc714-4c50-42c9-8629-21e07ad0ef10.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ece054cd_fc83_4cef_ac34_130bf9e7fe09
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | No_in-use_covers.png | file://x:/photopub/docs/0000000453/487871b6-51c0-4a33-ab7b-dc954cf1a6df.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-603027-2016 | UW-403992-2016 | 6/29/2016 1:33:08 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL073 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | 4 | 4 | In a new equestrian center, the owner installed a 100amp 120/240volt 1phase electrical panel complete with branch circuit wiring into a 40' steel C-can structure without bonding the enclosure. This can lead to a shock hazard. (Pictures attached) | 4 | Effective grounding Bonding; service raceway, equipment, or enclosure has not been properly bonded. | Incorrect_bond_and_no_cover.png | file://x:/photopub/docs/0000000453/f077204c-cbce-4673-8175-b1e059325627.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6b7101a9_1ff6_4f9e_9579_158c258c16f6
ELIN-607828-2016 | EL-394796-2016 | 7/11/2016 4:53:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | ACWU.png | file://x:/photopub/docs/0000000454/58474d5b-42a3-4ad0-a719-829d5dae931c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c6fdf3_00e8_4fac_82b2_c2a9dc2a3f77
ELIN-607828-2016 | EL-394796-2016 | 7/11/2016 4:53:39 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Meter_base_entry.png | file://x:/photopub/docs/0000000454/81799ccb-bb4f-45d0-a923-6f13d8a8e8aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__07c6fdf3_00e8_4fac_82b2_c2a9dc2a3f77
ELIN-621468-2016 | EL-401228-2016 | 8/3/2016 10:06:47 AM | ASSESS: EL: Service Connection | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | A new 200 amp 240 volt residential consumers electrical service has been authorized for connection to the utility. The electrical equipment is accessible to unauthorized operation or tampering. This can create a risk to persons or property. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Main_service_panel_authorized_for_cconnection_not_lockable.png | file://x:/photopub/docs/0000000465/b33d5d8e-44ef-4386-a3a3-6beae1ffe190.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7be64e75_e814_4149_bb5d_d8da432f8ff9
GAUP-613987-2016 | UW-413025-2016 | 7/19/2016 10:14:38 AM | ASSESS: GA UP: Hazard Elimination | png | #asFound | GA105 | Unapproved venting material | 3 | 3 | Unapproved venting system. Using an unapproved venting system for a positive pressure venting appliance may cause flue products to enter an occupied space causing exposure to occupants. | 3 | Unapproved venting material | Unapproved_venting_system.png | file://x:/photopub/docs/0000000458/4cb2cad5-3494-4bec-9f07-e24e775a7b3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d6439f67_5e20_4237_b734_6a55bcd3bf22
ELHE-612218-2016 | HE-411770-2016 | 8/9/2016 10:43:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables approved for direct burial installed in underground locations must be buried to the correct depth to prevent it from getting damaged by future excavation in areas where the cable is buried. This is required to prevent the cable sheath, conductor insulation, and conductors from getting damaged. This installation has an energized 15A 120/240V under ground cable installed from one unit of a duplex to a detached garage that is installed only a couple inches below grade in one location adjacent to the detached garage. The cable is for lighting and receptacles in the garage. Left uncorrected this is a potential shock and fire hazard if the cable sheath, conductor insulation, or conductors get damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_cable.png | file://x:/photopub/docs/0000000468/77b90c44-55c3-4e08-a502-f906fc79a9cf.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3864689_74c9_4e05_913d_1ac740bdcb2f
ELHE-612218-2016 | HE-411770-2016 | 8/9/2016 10:43:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables approved for direct burial installed in underground locations must be buried to the correct depth to prevent it from getting damaged by future excavation in areas where the cable is buried. This is required to prevent the cable sheath, conductor insulation, and conductors from getting damaged. This installation has an energized 15A 120/240V under ground cable installed from one unit of a duplex to a detached garage that is installed only a couple inches below grade in one location adjacent to the detached garage. The cable is for lighting and receptacles in the garage. Left uncorrected this is a potential shock and fire hazard if the cable sheath, conductor insulation, or conductors get damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Detached_garage_.png | file://x:/photopub/docs/0000000468/74155db1-8efd-4b81-842f-e3071ed5aa9e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3864689_74c9_4e05_913d_1ac740bdcb2f
ELHE-612218-2016 | HE-411770-2016 | 8/9/2016 10:43:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables approved for direct burial installed in underground locations must be buried to the correct depth to prevent it from getting damaged by future excavation in areas where the cable is buried. This is required to prevent the cable sheath, conductor insulation, and conductors from getting damaged. This installation has an energized 15A 120/240V under ground cable installed from one unit of a duplex to a detached garage that is installed only a couple inches below grade in one location adjacent to the detached garage. The cable is for lighting and receptacles in the garage. Left uncorrected this is a potential shock and fire hazard if the cable sheath, conductor insulation, or conductors get damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Exposed_cable_entering_garage.png | file://x:/photopub/docs/0000000468/1bad2a06-3afb-4b03-b05c-b8af8bec27d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3864689_74c9_4e05_913d_1ac740bdcb2f
ELHE-612218-2016 | HE-411770-2016 | 8/9/2016 10:43:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables approved for direct burial installed in underground locations must be buried to the correct depth to prevent it from getting damaged by future excavation in areas where the cable is buried. This is required to prevent the cable sheath, conductor insulation, and conductors from getting damaged. This installation has an energized 15A 120/240V under ground cable installed from one unit of a duplex to a detached garage that is installed only a couple inches below grade in one location adjacent to the detached garage. The cable is for lighting and receptacles in the garage. Left uncorrected this is a potential shock and fire hazard if the cable sheath, conductor insulation, or conductors get damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Location_where_cable_is_exposed_at_grade_level.png | file://x:/photopub/docs/0000000468/94a30433-4b03-4c98-b95a-2039f42f422e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3864689_74c9_4e05_913d_1ac740bdcb2f
ELHE-612218-2016 | HE-411770-2016 | 8/9/2016 10:43:31 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL114 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | 3 | 3 | Non-metallic sheathed cables approved for direct burial installed in underground locations must be buried to the correct depth to prevent it from getting damaged by future excavation in areas where the cable is buried. This is required to prevent the cable sheath, conductor insulation, and conductors from getting damaged. This installation has an energized 15A 120/240V under ground cable installed from one unit of a duplex to a detached garage that is installed only a couple inches below grade in one location adjacent to the detached garage. The cable is for lighting and receptacles in the garage. Left uncorrected this is a potential shock and fire hazard if the cable sheath, conductor insulation, or conductors get damaged. | 3 | Conductors The location of cables, raceways, or conductors are not located in an acceptable location. | Front_on_the_duplex_on_the_corner_of_Callaghan_and_Shadbolt.png | file://x:/photopub/docs/0000000468/8ec70d20-46cf-4418-a131-9cd52422683f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3864689_74c9_4e05_913d_1ac740bdcb2f
BPVOP-662234-2016 | 2253144 | 9/13/2016 11:33:22 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Expansions_tank.png | file://x:/photopub/docs/0000000484/88cbd49f-e871-4581-90ca-efade1ee0baa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c9fdacb8_f18e_42d1_bf08_0e72d3df948d
GAIN-626647-2016 | GA-382067-2016 | 8/11/2016 11:27:08 AM | ASSESS: GA: Final | png | #asFound | GA055 | Bonding for Corrugated Stainless Steel Tubing missing | 3 | 3 | Bonding not installed on corrugated stainless steel tubing(CSST)system. CSST must be bonded as per installation instructions as it could be damaged due to an electrical fault causing uncontrolled release of gas. | 3 | Bonding for Corrugated Stainless Steel Tubing missing | no_bonding_on_CSST_tubing_system.png | file://x:/photopub/docs/0000000469/238411cf-1a73-4215-bd8e-82f0543fb6a1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4d560bad_0e2d_4ded_b27c_d34965f05b5d
GAIN-615146-2016 | GA-409751-2016 | 8/3/2016 1:46:50 PM | ASSESS: GA: Final | png | #asFound | GA085 | Regulator vent not terminated as per manufacturers instruction | 3 | 3 | Line regulator installed indoors without proper external leak limiting device. A failed regulator would let an unapproved volume of gas into to indoor space potentially causing a fire of explosion. | 3 | Regulator vent not terminated as per manufacturers instruction | Line_regulator.png | file://x:/photopub/docs/0000000465/2d613955-b14a-44de-8eba-76815cbf9450.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70a5c6b2_caf1_4bf5_8017_aa50fda27255
BPVOP-623564-2016 | BPV-283420-2015 | 7/28/2016 12:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Rear_door_refractory_overview.png | file://x:/photopub/docs/0000000465/13114c4e-a11f-41c6-8a46-4a37abd2fb6d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85e7c5e8_573a_4830_93dd_e25dc92e4fbc
BPVOP-623564-2016 | BPV-283420-2015 | 7/28/2016 12:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Rear_door_refractory_crack_.png | file://x:/photopub/docs/0000000465/173e2492-1e23-483e-8afd-38a4408366dd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85e7c5e8_573a_4830_93dd_e25dc92e4fbc
BPVOP-623564-2016 | BPV-283420-2015 | 7/28/2016 12:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Front_door_refractory_heat_resistant_material_repairs.png | file://x:/photopub/docs/0000000465/9514eacb-ba8b-45d0-b7f5-1d1beff41ad6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85e7c5e8_573a_4830_93dd_e25dc92e4fbc
BPVOP-623564-2016 | BPV-283420-2015 | 7/28/2016 12:00:00 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP202 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | 2 | 2 |  | 2 | 5.1.0 In service proc/process - Fallen or cracked refractory in boiler furnace | Rear_door_refractory_overview2.png | file://x:/photopub/docs/0000000465/3ac07318-3452-4acc-9bd1-95a5d40ee260.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__85e7c5e8_573a_4830_93dd_e25dc92e4fbc
ELIN-644360-2016 | EL-423552-2016 | 9/6/2016 12:29:26 PM | ASSESS: EL: Service Connection | png | #asFound | EL030 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Condensation may become present in service equipment. | Panel_Enclosure.png | file://x:/photopub/docs/0000000480/cbe59bcb-bd25-468d-9b4c-92563ea31ed6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab721d83_bf8f_4821_9c06_c92f34373268
ELIN-640362-2016 | EL-339134-2016 | 9/6/2016 1:02:56 PM | ASSESS: EL: Final | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Electrical_Room.png | file://x:/photopub/docs/0000000480/b118705e-51c6-423c-9489-56a0706bfa53.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1ec15021_5f98_47d0_8763_893111f129c1
BPVOP-611130-2016 | 2270480 | 7/13/2016 12:41:57 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP136 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | 4 | 3 | Upon review of safety relief valve testing log of Hot Water Boiler with Heating surface area of 37square meters, Maximum Allowable Working Pressure (MAWP) of 125psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve lifted at 73psig which is above tolerance limit for deviation in safety relief valve set pressure and an indication of malfunction (Possible sticking or jamming of parts). If safety relief valve fails due to malfunction (sticking or jamming of parts) boiler will be subjected pressure above MAWP and this could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 4 | 3.1.1 Safeties will not function - Pressure Relief Device Failed relief or pop test | LOG_BOOK.png | file://x:/photopub/docs/0000000455/c37ef9ad-3c25-4d0c-9d67-2081ef571753.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2b6eddc4_339f_458b_b2b7_f66b2ca73e5f
ELOP-432171-2015 | EL-148643-2014 | 8/12/2016 1:55:23 PM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL017 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | 3 | 3 | Electrical distribution equipment is blocked with junk items stored at the front of breaker panels, thus creating inaccessibility hazard and infringing on the minimum working space required for maintenance and repairs on the electrical equipment. | 3 | Placement of equipment does not allow for adequate access or egress. • Working space or clearances around equipment are inadequate; • Doors or exits are not acceptable. | Electrical_room.png | file://x:/photopub/docs/0000000470/a0ee8f88-09ef-498d-ba2b-425a39321ff0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__87939c6e_758a_4197_b856_1c59b4952d39
ELIN-634867-2016 | EL-189823-2014 | 9/16/2016 11:05:17 AM | ASSESS: EL: Final | png | #asFound | EL010 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 3 | 2 | Point of attachment for overhead conductors is not as high as code minimum requires.The wires as installed are too low to the ground. A person carrying a ladder or similar product could touch the wires and possibly be shocked. | 3 | Conductors are exposed to accidental contact by persons Overhead power conductors, are not attached or supported adequately. | 11avehazelton.png | file://x:/photopub/docs/0000000486/9e9a750e-d858-45cd-b2f3-d3bb2c0913e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a2c4ec95_d090_41d1_b722_2e02fbd5bbd8
ELIN-640633-2016 | EL-401235-2016 | 9/16/2016 1:02:31 PM | ASSESS: EL: Final | png | #asFound | EL098 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | 3 | 3 | Sub feeder cables are entered through the main section of the main distribution panel.Conductors passing through this section of raceway are subject to contact with the main conductors that have no over current protection.A short circuit condition could occur relying on the supply authorities fuse protection to open the circuit. | 3 | Conductors Equipment is not approved for the specific use. The location of cables, raceways, or overhead conductors are not located in an acceptable location. | Ft_Babine.png | file://x:/photopub/docs/0000000486/3c4184c6-c01c-4f52-9ff4-635ed9bf8e3f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf1eec15_8c99_4c36_a24b_63acf0a1e739
ELIN-640105-2016 | EL-406723-2016 | 9/14/2016 2:20:00 PM | ASSESS: EL: Service Connection | png | #asFound | EL033 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | 3 | 3 | Cables from meter base exceed the allowable length for not having over current protection. | 3 | Improper installation or location of equipment, conductors, cables or raceways Conductors are located inside building beyond 1.5m | Tachet.png | file://x:/photopub/docs/0000000486/9b5a2844-8de9-45a2-aa15-d2c35a6e8eea.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5e86cf96_54b2_46ed_b1c4_be85857d144e
ELIN-640896-2016 | EL-359769-2016 | 9/16/2016 1:38:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation has new receptacle circuits that were added as part of a renovation to the kitchen area of an existing house. AFCI protection was not provided for two 15A 120V receptacle branch circuits. This is a potential fire hazard if arcing faults occur on these receptacle branch circuits or from the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Exterior_receptacle_that_was_not_AFCI_protected_.png | file://x:/photopub/docs/0000000486/c6f9650d-f936-4256-a4b6-f4437e2879a8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd195c6b_8fba_476e_aecc_de1064320a96
ELIN-640896-2016 | EL-359769-2016 | 9/16/2016 1:38:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation has new receptacle circuits that were added as part of a renovation to the kitchen area of an existing house. AFCI protection was not provided for two 15A 120V receptacle branch circuits. This is a potential fire hazard if arcing faults occur on these receptacle branch circuits or from the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Microwave_receptacle_that_was_not_AFCI_protected.png | file://x:/photopub/docs/0000000486/ef35f07e-b291-41a6-9963-e3d4b877af63.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd195c6b_8fba_476e_aecc_de1064320a96
ELIN-640896-2016 | EL-359769-2016 | 9/16/2016 1:38:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation has new receptacle circuits that were added as part of a renovation to the kitchen area of an existing house. AFCI protection was not provided for two 15A 120V receptacle branch circuits. This is a potential fire hazard if arcing faults occur on these receptacle branch circuits or from the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Front_of_house_where_renovation_occurred_.png | file://x:/photopub/docs/0000000486/907e4329-747f-41ab-a409-767b7b6e545b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd195c6b_8fba_476e_aecc_de1064320a96
ELIN-633545-2016 | EL-382541-2016 | 8/25/2016 1:22:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | The neutral system in the main distribution is not properly grounded. 100 amp, 120/240 volt. This is a thermal effect condition. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Neutral_system_not_properly_grounded.png | file://x:/photopub/docs/0000000475/ecf54166-65b6-47ff-9214-c70d0f4eb817.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fe0c37e4_4e6b_4d66_b982_26e2d18144c6
AMOP-637932-2016 | AM-304424-2015 | 8/25/2016 2:10:50 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | Structural tethers were not attached, could weaken the structures integrity | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Structure_tether.png | file://x:/photopub/docs/0000000475/36268008-0188-4107-a817-8f4e8852e497.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdad8ad7_df71_4db9_b88f_512b27150752
BPVOP-640254-2016 | 3493717 | 8/29/2016 9:20:54 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Mud_drum_with_scale.png | file://x:/photopub/docs/0000000479/108f0562-b094-4f4e-bb60-921763a9bcca.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e0c081a_b191_4f94_85ba_6915f184162c
BPVOP-640254-2016 | 3493717 | 8/29/2016 9:20:54 AM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP069 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | 2 | 2 |  | 2 | 1.2.3 Boiler construction - Heavy scale or deposits on boiler heat exchange surfaces requiring removal or improved water treatment. | Mud_drum_scale.png | file://x:/photopub/docs/0000000479/9cf4a6de-6cec-4b34-9c7a-63d4ee264e65.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6e0c081a_b191_4f94_85ba_6915f184162c
ELHE-618563-2016 | HE-416078-2016 | 7/29/2016 11:39:45 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | Residential multi- unit tenant space has 120 volt reverse polarity receptacle that has sparked and create fire hazard and potential shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Lo.png | file://x:/photopub/docs/0000000463/a7bb1340-3d85-4277-8c43-edffbe913e32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f53ff547_d00a_4618_8d47_cde7f0b6e651
ELHE-618563-2016 | HE-416078-2016 | 7/29/2016 11:39:45 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | Residential multi- unit tenant space has 120 volt reverse polarity receptacle that has sparked and create fire hazard and potential shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Rverse.png | file://x:/photopub/docs/0000000463/ec07e498-ebd3-4395-9a5e-66c7b3711302.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f53ff547_d00a_4618_8d47_cde7f0b6e651
ELHE-618563-2016 | HE-416078-2016 | 7/29/2016 11:39:45 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | Residential multi- unit tenant space has 120 volt reverse polarity receptacle that has sparked and create fire hazard and potential shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Garage.png | file://x:/photopub/docs/0000000463/efe3e1b9-421d-4694-bb53-7ed490d6b921.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f53ff547_d00a_4618_8d47_cde7f0b6e651
ELIN-604999-2016 | EL-351622-2016 | 7/5/2016 1:52:43 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding conductor has not been terminated correctly at the neutral bus any fault currents that may occur may not travel to the ground plate and provide equal potential protection two individuals whom may be working on the electrical system. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_conductor__grounding_conductor_not_terminated_on_the_neutral_bus.png | file://x:/photopub/docs/0000000452/3c2d4bfa-34da-4293-a04a-adfcfc0c4938.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__693807f7_6482_4c2c_a788_37b6e5a837b4
ELIN-645423-2016 | EL-344301-2016 | 9/9/2016 7:31:42 AM | ASSESS: EL: Final | png | #asFound | EL127 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | 3 | 3 | Receptacles for use in a kitchen rated 20 amps and 120 volts are not provided as required on kitchen island and on counter. Occupants may resort to using extension cords that may run past sinks. Cooking appliances or other heating equipment and this can lead to property damage or injury to persons | 3 | Installation of electrical equipment Residential: kitchen counter receptacles are not properly spaced. | Kitchen_and_bedroom_walls_receptacle_spacing_not_to_minimum_requirements.png | file://x:/photopub/docs/0000000482/ef969c2f-0044-44a2-8945-643fda3c2b20.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bc08898_5080_498e_ae49_f95fab80f299
BPVIN-643608-2016 | BPV-433209-2016 | 9/2/2016 12:52:23 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP181 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | 3 | 3 | Safety devices protect equipment from dangerous conditions and damage. During the inspection of 5 machined mounted air receivers(MAWP 175-200 psig), I found that the Pressure Relief Devices not replaced within the last 3 years as per Safety Order SO-B60505303. Potential exists for an incident to occur due to a safety device not providing intended level of control. | 3 | 5.1.0 In service proc/process - Safety orders not followed or adhered to. | PRD.png | file://x:/photopub/docs/0000000479/e9a6ec8e-4312-4955-8b03-acddc86b637c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ba8ed07d_87f4_4834_9615_bcba87845f9a
ELIN-640451-2016 | EL-308514-2015 | 8/30/2016 9:44:55 AM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | Electrical panel installed in an outer wall of open shop is subject to moisture .The code requires panels installed outdoors be rain tight or installed in rain tight enclosures. Moisture in electrical equipment can cause corrosion and over current devices to fail. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Telkwa_high_rd.png | file://x:/photopub/docs/0000000477/2ac1adc4-310c-4a91-b22c-91fc685cff21.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1900351c_298e_4544_8a25_8ddf4c6a2481
ELIN-640454-2016 | EL-308514-2015 | 8/30/2016 9:28:22 AM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The CEC requires ARC fault protection on circuits supplying bed room receptacles. This bed room circuit is connected to a regular breaker.Arc fault breakers add extra protection for faulty electrical cords from appliances such as lamps,TVs and clock radios. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Arcfault.png | file://x:/photopub/docs/0000000477/5a042b34-efa6-4666-9df2-a86bf94029ed.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__66ad8beb_476e_4b20_9b28_6d4ec5219f5a
BPVOP-583711-2016 | 2297061 | 6/29/2016 11:02:18 AM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP149 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | 3 | 3 | During the inspection of a Freon Refrigeration System was found that the leak detector was calibrated in 2012, not annually as per CSA B52. | 3 | 4.1.1 Incorrect readings/alarms - Refrigerant vapour detector out of calibration | Leak_monitor.png | file://x:/photopub/docs/0000000450/1a5ea90d-7143-4865-b473-966d39c87439.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ed406cd0_012a_4aa3_a7ce_b67ba8de32d0
ELIN-602383-2016 | EL-247900-2015 | 6/30/2016 9:53:41 AM | ASSESS: EL: Final | png | #asFound | EL001 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | 3 | 3 | 15A 120V 14/2 NMD wire has been left hanging out of the wall without being terminated to a box or a light fixture, the wiring can be energized by use of the switch, this presents a shock hazard to persons using the washroom or persons installing the light fixture. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is de-energized; • Equipment is intended to be energized and not adequately locked out; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to general public. | Light_wire.png | file://x:/photopub/docs/0000000451/83e80c8b-4eba-45ea-aa87-89115629086e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b3c25171_e793_400b_8c09_77e0fb5640a5
EDRI-665403-2016 | ED-411008-2016 | 9/16/2016 1:00:21 PM | ASSESS: ED RI: Extension | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | Crane brace is installed in front of landing 8 creating a significant trip hazard. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Crane_brace.png | file://x:/photopub/docs/0000000486/d8319e54-1864-4178-bc3f-935d0a946825.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c57fcfd_747b_4512_8641_b7c97d281606
EDRI-665402-2016 | ED-411012-2016 | 9/16/2016 12:49:36 PM | ASSESS: ED RI: Extension | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | A large crane brace is installed on the floor of landing 8, in front of the gates. The brace creates a significant tripping hazard. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Crane_brace1.png | file://x:/photopub/docs/0000000486/7fc678ba-bb9f-4273-91de-9b983c9c4bc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8a9bf8d1_09ad_4b0b_9643_3669f696cee5
GAIN-630831-2016 | GA-424087-2016 | 8/18/2016 8:14:03 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | Plastic venting for an operating boiler was installed but none of the joints were glued. The venting could easily become dislodged and allow the flue products to enter the occupied space. Flue products entering the occupied space could result in potential carbon monoxide poisoning. | 5 | Special venting system not glued or connected as per certified instructions | Unglued_venting.png | file://x:/photopub/docs/0000000472/2830bbf7-7302-410e-a781-bd702bd5e4aa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a2510e6_33ec_4fa0_8e6f_5c7735a5cb9d
GAIN-630831-2016 | GA-424087-2016 | 8/18/2016 8:14:03 AM | ASSESS: GA: Final | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | Plastic venting for an operating boiler was installed but none of the joints were glued. The venting could easily become dislodged and allow the flue products to enter the occupied space. Flue products entering the occupied space could result in potential carbon monoxide poisoning. | 5 | Special venting system not glued or connected as per certified instructions | Unglued_venting_2.png | file://x:/photopub/docs/0000000472/d6ce1b8c-b8ee-4021-b774-1ce762a45fc6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a2510e6_33ec_4fa0_8e6f_5c7735a5cb9d
GAUP-662078-2016 | UW-436738-2016 | 9/14/2016 9:44:48 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | 500 USWG propane tank is installed against dwelling building. Minimum 10 feet clearance not met, in the event of propane release or servicing access may not available | 2 | Installation clearances or set backs to propane containers not met | 5.png | file://x:/photopub/docs/0000000485/907f9c9d-834e-4f19-b302-ff6a20e30037.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd2faed_b7d8_49ec_952e_70d332d96136
GAUP-662081-2016 | UW-436740-2016 | 9/14/2016 10:00:19 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | Propane regulators installed that liquid could enter. Vapour regulators not designed for liquid and could damage regulator. | 4 | 1st stage regulator installed below container liquid level | Unit_4-3.png | file://x:/photopub/docs/0000000485/b245eae2-c8de-441b-b6e5-d45649506fd8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d99c2e5_0809_416f_9f46_bb44777071b0
GAUP-662077-2016 | UW-436737-2016 | 9/14/2016 8:59:01 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | First stage regulator installed below liquid level of tank. Liquid could enter the vapour design regulator and cause it to fail or liquid propane percent to enter the supply piping | 4 | 1st stage regulator installed below container liquid level | 2.png | file://x:/photopub/docs/0000000485/a34b4851-5694-4039-bdfe-5ed67355bdde.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b121d7f_24d4_47dc_9cee_6c91cc5ed7c2
GAUP-662081-2016 | UW-436740-2016 | 9/14/2016 10:00:19 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | Propane regulators installed that liquid could enter. Vapour regulators not designed for liquid and could damage regulator. | 4 | 1st stage regulator installed below container liquid level | Unit_4_2.png | file://x:/photopub/docs/0000000485/1c2c78e6-c60d-4dc9-8028-498231f2a667.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d99c2e5_0809_416f_9f46_bb44777071b0
GAUP-662077-2016 | UW-436737-2016 | 9/14/2016 8:59:01 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | First stage regulator installed below liquid level of tank. Liquid could enter the vapour design regulator and cause it to fail or liquid propane percent to enter the supply piping | 4 | 1st stage regulator installed below container liquid level | 1.png | file://x:/photopub/docs/0000000485/8f64d443-074e-483f-b5fa-71ef905d95db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b121d7f_24d4_47dc_9cee_6c91cc5ed7c2
GAUP-662081-2016 | UW-436740-2016 | 9/14/2016 10:00:19 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | Propane regulators installed that liquid could enter. Vapour regulators not designed for liquid and could damage regulator. | 4 | 1st stage regulator installed below container liquid level | Unit_4-1.png | file://x:/photopub/docs/0000000485/24ba3ffa-6b16-4397-b1b6-8be85688eb5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d99c2e5_0809_416f_9f46_bb44777071b0
GAUP-662078-2016 | UW-436738-2016 | 9/14/2016 9:44:48 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 | 500 USWG propane tank is installed against dwelling building. Minimum 10 feet clearance not met, in the event of propane release or servicing access may not available | 2 | Installation clearances or set backs to propane containers not met | 4.png | file://x:/photopub/docs/0000000485/a6315bb8-3397-4942-8cef-626f0283cdf3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bcd2faed_b7d8_49ec_952e_70d332d96136
GAUP-662066-2016 | UW-436732-2016 | 9/14/2016 8:30:32 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA010 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | 3 | 3 | Regulator vent installed by unit heater exhaust termination | 3 | Air supply/vent terminations with-in minimum required meter/relief clearance zone | Heat.png | file://x:/photopub/docs/0000000485/2082fabe-4004-4407-b875-17aeea2d5183.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ab6aa163_8459_42d3_aa2f_c3d9093c9fb7
GAUP-662077-2016 | UW-436737-2016 | 9/14/2016 8:59:01 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | First stage regulator installed below liquid level of tank. Liquid could enter the vapour design regulator and cause it to fail or liquid propane percent to enter the supply piping | 4 | 1st stage regulator installed below container liquid level | 3.png | file://x:/photopub/docs/0000000485/b3a6a153-30ad-46db-91c3-2b97f89ba774.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5b121d7f_24d4_47dc_9cee_6c91cc5ed7c2
GAIN-613384-2016 | GA-368244-2016 | 8/8/2016 3:39:21 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 |  | 2 | Not installed according to certified installation instructions | Valleyview.png | file://x:/photopub/docs/0000000467/4d6c7b98-429c-4fb5-a915-eb99bc06d81e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__956e3ca4_b774_4dc1_9903_dd77eb449bff
ELIN-618286-2016 | EL-298636-2015 | 8/4/2016 8:22:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120 volt approved portable cord connected fluorescent luminaire with three prong plug male cord cap end has bonding conductor blade broken off and completely removed intentionally for plugging into two prong female screw shell adapter for luminaire. When electrical equipment is not bonded as required for use of approved electrical equipment, the luminaire is a possible electrical fire or shock hazard to people or property if there is a fault condition within luminaire wiring system. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 41.png | file://x:/photopub/docs/0000000466/4458bdd9-f701-4dd2-b08b-5cfabbbff035.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__690f0bc1_6161_4376_9888_9e7a6253481d
ELIN-618286-2016 | EL-298636-2015 | 8/4/2016 8:22:40 PM | ASSESS: EL: Rough Wiring-Partial | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found 120 volt approved portable cord connected fluorescent luminaire with three prong plug male cord cap end has bonding conductor blade broken off and completely removed intentionally for plugging into two prong female screw shell adapter for luminaire. When electrical equipment is not bonded as required for use of approved electrical equipment, the luminaire is a possible electrical fire or shock hazard to people or property if there is a fault condition within luminaire wiring system. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 40.png | file://x:/photopub/docs/0000000466/392427cb-81bc-4a2d-b0ee-1e516ab1057d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__690f0bc1_6161_4376_9888_9e7a6253481d
ELIN-605772-2016 | EL-394431-2016 | 7/27/2016 12:52:49 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | In a new homeowner shop and outbuilding, the 120/240volt 200amp supply service feeder enters the main panel and is strapped back into the tub using all-round which is biting into the jacket of the conductor. This can lead to substantial equipment damage | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | All-round_used_to_strap_conductors.png | file://x:/photopub/docs/0000000462/fdee931b-e42f-44b0-a356-3d696715fd04.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__6cd56d53_0653_4e64_8524_eb18aea250cb
GAOP-660412-2016 | 2170901 | 9/13/2016 1:14:22 PM | ASSESS: GA OP: Periodic | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 |  | 2 | Installation clearances or set backs to propane containers not met | Tank_with_encroaching_tree.png | file://x:/photopub/docs/0000000484/51811546-ba20-4ff8-9b33-5785ab56c253.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33539389_7B66_4F7D_9E3C_6D6343953F39
GAOP-660412-2016 | 2170901 | 9/13/2016 1:14:22 PM | ASSESS: GA OP: Periodic | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 |  | 2 | Installation clearances or set backs to propane containers not met | Cylinder_storage.png | file://x:/photopub/docs/0000000484/3d29bfde-91c6-490f-82a0-eae363a18d67.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33539389_7B66_4F7D_9E3C_6D6343953F39
GAOP-660412-2016 | 2170901 | 9/13/2016 1:14:22 PM | ASSESS: GA OP: Periodic | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 |  | 2 | Installation clearances or set backs to propane containers not met | Fuel_tank_separation.png | file://x:/photopub/docs/0000000484/b99fd358-c267-4a1c-b101-f9bab9916b37.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__33539389_7B66_4F7D_9E3C_6D6343953F39
ELIN-635648-2016 | EL-381434-2016 | 8/23/2016 5:07:23 PM | ASSESS: EL: Final | png | #asFound | EL072 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | 4 | 4 | Found EMT raceway had no bonding bushing for bonding all electrical equipment together to its power supply system. When bonding is not continuous for bonding all electrical equipment together there is a possibility of an electrical shock in the event there is a short or fault condition in the electrical equipment. | 3 | Effective grounding/bonding Service equipment, or enclosure has not been properly bonded. | EMT_NO_BONDING_BUSHING_TO_BOND_IN_PLASTIC_BOX.png | file://x:/photopub/docs/0000000475/06f0bf79-0a0b-4124-8c1f-5654516999ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1b6022e3_2448_4815_9daa_5d8f9b2c8d3e
ELIN-610527-2016 | EL-410693-2016 | 7/20/2016 10:43:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pic2.png | file://x:/photopub/docs/0000000459/392cc465-39a4-4cba-9479-00d24115b41b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3b4213c_3e99_4c86_85bc_cd26965f1a4f
ELIN-610527-2016 | EL-410693-2016 | 7/20/2016 10:43:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pic4.png | file://x:/photopub/docs/0000000459/3248b562-00d6-401b-9fc3-bac36678723b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3b4213c_3e99_4c86_85bc_cd26965f1a4f
ELIN-610527-2016 | EL-410693-2016 | 7/20/2016 10:43:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pic3.png | file://x:/photopub/docs/0000000459/51197d78-a607-43e2-8400-8bbe75bc73a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3b4213c_3e99_4c86_85bc_cd26965f1a4f
ELIN-610527-2016 | EL-410693-2016 | 7/20/2016 10:43:29 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 |  | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Pic1.png | file://x:/photopub/docs/0000000459/e9b412de-86ed-4926-a56d-badc0376fbdd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e3b4213c_3e99_4c86_85bc_cd26965f1a4f
ELOP-384905-2015 | EL-014113-2013 | 7/20/2016 9:52:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL158 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | 3 | 3 | Care must be taken to provide ventilation for battery banks as they can produce corrosive and explosive gas when charged. In this guest residence an inverter charger backup system was installed in a basement sealed in a wooden enclosure in the electrical room. | 3 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | Inverter.png | file://x:/photopub/docs/0000000459/8aff99d2-9e16-4539-bdb4-87857a0537f7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cb146e6_6836_4053_bc0c_dba1466b3446
ELIN-621119-2016 | EL-381866-2016 | 7/29/2016 1:13:08 PM | ASSESS: EL: Service Connection | png | #asFound | EL080 | Installation Grounding; Electrode or grounding conductor are not present. | 4 | 4 | Grounding conductor in main panel is terminated on a lug on the enclosure. Grounded neutral systems as in this case, require grounding to terminate on the neutral bussing. Terminating to the neutral will allow overcurrent devices to clear faults as intended. Overcurrent devices not reacting or performing as required may result in high conductor temperature during a fault which may result in shock or fire to persons or property. | 3 | Installation Grounding; Electrode or grounding conductor are not present. | Grounding_conductor_not_terminated_on_neutral_bussing.png | file://x:/photopub/docs/0000000463/e6c5bd39-6e06-457e-aaf5-0f408db33d29.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f7b4bfe_9cc1_43a5_81eb_5604419c6b97
BPVIN-627568-2016 | BPV-422086-2016 | 8/9/2016 1:18:14 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon the assessment of two CO2 Tanks with MAWP of 300 psig, was found that the Pressure Relief Devices were overdue as per CSA B51. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | PRD_S.png | file://x:/photopub/docs/0000000468/50191067-0770-4d2d-a78e-bff98a416b45.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__345ad80e_6f0f_4f2d_95d6_c09c9e269884
ELOP-384905-2015 | EL-014113-2013 | 7/20/2016 9:52:16 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL158 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | 3 | 3 | Care must be taken to provide ventilation for battery banks as they can produce corrosive and explosive gas when charged. In this guest residence an inverter charger backup system was installed in a basement sealed in a wooden enclosure in the electrical room. | 3 | Installation of electrical equipment Inadequate ventilation is provided for equipment. | Inverter_battery_pack.png | file://x:/photopub/docs/0000000459/43da05db-9835-4dfd-8334-501ba82e99ff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9cb146e6_6836_4053_bc0c_dba1466b3446
ELOP-278799-2014 | EL-185182-2014 | 7/20/2016 10:22:10 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL277 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | 3 | 3 | Elecrical equipment must be maintained in safe working order. In this private lodge a fire alarm system component had been removed for service or testing and had not been reinstalled when complete. | 3 | Life Safety System, Fire Alarm, Emergency systems, Life safety system is incomplete or showing signs of failure. | EOL_relay_not_reinstalled.png | file://x:/photopub/docs/0000000459/9b959f81-c9b6-4c89-8977-6d91969ff120.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e34d7d2_3149_426c_ab27_4b2a8200a746
ELIN-613424-2016 | UW-412488-2016 | 7/18/2016 11:56:17 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Primary_line_built_no_permit.png | file://x:/photopub/docs/0000000458/a4ee4eee-778d-4197-8ba9-6de1a2d2ff13.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__76ee1f55_e5cb_4350_917f_699c447e0d6c
ELIN-627413-2016 | EL-421489-2016 | 8/11/2016 8:07:55 AM | ASSESS: EL: Final | png | #asFound | EL138 | Installation of electrical equipment General: boxes are not accessible. | 3 | 3 | Outlet junction box is not accessible. This could be a hazard if the junction was to fail. Trouble shooting and maintenance would be impossible with no access to the outlet box junction. | 3 | Installation of electrical equipment General: boxes are not accessible. | No_access.png | file://x:/photopub/docs/0000000470/f158e39c-6be8-4968-b928-0900443ec138.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__39cea3fb_1057_4d1b_9fd0_d6ce0df3ef09
GAIN-634668-2016 | GA-416982-2016 | 8/19/2016 10:50:20 AM | ASSESS: GA: Rough-In | png | #asFound | GA051 | Non-compliant material/fittings installed | 3 | 3 | Type "gas" copper is not approved for underground unless factory coated. Lighter wall copper is more easily subject to damage and corrosion which may lead to leaks. | 3 | Non-compliant material/fittings installed | Type_g_copper.png | file://x:/photopub/docs/0000000474/3dd8c4f2-4c93-4645-923d-f4f03b9bd941.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fc132a4_21c1_439c_8ca6_9334453989f3
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4.png | file://x:/photopub/docs/0000000468/e7dd2266-ccd2-468c-9721-6086597dc74c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 3.png | file://x:/photopub/docs/0000000468/b5213b00-c654-48a3-a3c1-d8dd145803cb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 7.png | file://x:/photopub/docs/0000000468/f4fb759b-4927-4e37-b3bc-9e2f2d6c4865.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 8.png | file://x:/photopub/docs/0000000468/2ea4e39c-3b5e-4f38-954b-2ee5d55b0f7f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 6.png | file://x:/photopub/docs/0000000468/991b8d76-5f0a-45fc-9fb4-6ab38dfa908a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 01.png | file://x:/photopub/docs/0000000468/2a3937ab-56ea-499e-b875-18f4d4d2a5a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
ELIN-558990-2016 | EL-371935-2016 | 8/8/2016 5:15:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL108 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 4 | 4 | Found energized armoured feeder cable 120/240 volt connected to power supply system while this cable was laying on earth in driveway where there is vehicular traffic and heavy construction machinery driving over the cable and causing damages to cable. When armoured cable is driven over by equipment and machinery which causes bending or cutting of cable armour covering, the insulated conductors inside armoured cable could short out to metal armour and could cause a possible electrical fire or shock hazard to people or property. | 4 | Conductors Cables, Raceways or conductors are damaged and needs to be either replaced or repaired. Not suitable for continued use. | 5.png | file://x:/photopub/docs/0000000468/74572eca-8dc4-45b0-b6ce-bcfa7607997c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac11add1_e415_48da_a8c7_75dc312ce688
AMOP-630517-2016 | 2044502 | 8/15/2016 2:33:28 PM | ASSESS: AM OP: Operational | png | #asFound | AM000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | Pic1.png | file://x:/photopub/docs/0000000470/5ed622bf-c1c9-4556-a83b-be4a16d9994c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a3e2abd5_a74a_4b41_a370_c0d2a4685cd3
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 106.png | file://x:/photopub/docs/0000000471/776c79fa-3994-4f46-af45-790b5fa71798.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-607296-2016 | UW-408182-2016 | 7/7/2016 3:02:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found electrical equipment rated 120 volt did not have electrical equipment bonded at all or not bonded properly as required for safety. When electrical equipment is not bonded and if there is a fault condition or short circuit on supply system, the over-current devices might not trip as quickly and as effectively as required and could result in electrical fire or shock hazards to people and property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Incorrect_or_no_bonding_continuity1.png | file://x:/photopub/docs/0000000453/a74418ef-8c17-4346-b679-7cc7563ab570.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eb4f9c6_b35a_404a_9030_c4373f68c2e3
ELIN-607296-2016 | UW-408182-2016 | 7/7/2016 3:02:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found electrical equipment rated 120 volt did not have electrical equipment bonded at all or not bonded properly as required for safety. When electrical equipment is not bonded and if there is a fault condition or short circuit on supply system, the over-current devices might not trip as quickly and as effectively as required and could result in electrical fire or shock hazards to people and property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Incorrect_or_no_bonding_continuity3.png | file://x:/photopub/docs/0000000453/4843c01d-d35b-477e-93b3-9c5e2fc9fff9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eb4f9c6_b35a_404a_9030_c4373f68c2e3
ELIN-607296-2016 | UW-408182-2016 | 7/7/2016 3:02:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found electrical equipment rated 120 volt did not have electrical equipment bonded at all or not bonded properly as required for safety. When electrical equipment is not bonded and if there is a fault condition or short circuit on supply system, the over-current devices might not trip as quickly and as effectively as required and could result in electrical fire or shock hazards to people and property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Incorrect_or_no_bonding_continuity4.png | file://x:/photopub/docs/0000000453/39946dc3-c255-4863-a033-3619f14e3847.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eb4f9c6_b35a_404a_9030_c4373f68c2e3
ELIN-607296-2016 | UW-408182-2016 | 7/7/2016 3:02:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found electrical equipment rated 120 volt did not have electrical equipment bonded at all or not bonded properly as required for safety. When electrical equipment is not bonded and if there is a fault condition or short circuit on supply system, the over-current devices might not trip as quickly and as effectively as required and could result in electrical fire or shock hazards to people and property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Incorrect_polarity_and_no_bonding_of_receptacle.png | file://x:/photopub/docs/0000000453/f8e70f83-bb47-4b37-a788-bca370f37668.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eb4f9c6_b35a_404a_9030_c4373f68c2e3
ELIN-607296-2016 | UW-408182-2016 | 7/7/2016 3:02:48 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL085 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | 4 | 4 | Found electrical equipment rated 120 volt did not have electrical equipment bonded at all or not bonded properly as required for safety. When electrical equipment is not bonded and if there is a fault condition or short circuit on supply system, the over-current devices might not trip as quickly and as effectively as required and could result in electrical fire or shock hazards to people and property. | 4 | Equipment Receptacles, outlet boxes, and junction boxes are not properly bonded | Incorrect_or_no_bonding_continuity2.png | file://x:/photopub/docs/0000000453/7fdfff5e-a124-4246-98a3-ffec734de7d3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0eb4f9c6_b35a_404a_9030_c4373f68c2e3
GAIN-619588-2016 | GA-416889-2016 | 8/4/2016 9:00:12 AM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Regulator not installed as per manufacturers installation instructions. Regulator may not perform as designed when not installed as per installation instructions. | 2 | Not installed according to certified installation instructions | Regulator_not_installed_as_per_manufacturers_installation_instructions.png | file://x:/photopub/docs/0000000465/bdcf2f5f-4507-4ec4-b94c-05c53339e832.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a16ce31b_3346_42ca_b934_b66d40808c91
ELIN-642970-2016 | EL-431266-2016 | 9/8/2016 11:03:13 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL028 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | 4 | 4 | An existing residential service rated 100 amps and 240 volts was found to be fed from the utility by NSF cable that was in direct contact with the metal roof sheathing of the residence. This condition will result in property damage or injury to persons if not rectified. | 4 | Improper installation or location of equipment, conductors, cables or raceways Mechanical protection for conductors is not adequate | NSF_in_contact_with_metal_roof__incomplete_circuits_energized.png | file://x:/photopub/docs/0000000482/59eeaa7a-8a37-4061-b138-0e752832bfcc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ec1509fd_fa18_4f83_bec8_5e4918d7c54b
BPVOP-632006-2016 | 2269463 | 8/16/2016 12:35:44 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of low pressure steam heating boiler with 38 square meters heating surface it is determined that there is no record of testing safety valve as per CSA B51. Lack of or delinquency in testing as required may subject boiler to pressure above MAWP (due to failure of safety valve to operate) if control and safety devices fail to shut down boiler. This could result in failure of pressure-boundary of boiler with likelihood of incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.) | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Safety_valve.png | file://x:/photopub/docs/0000000471/62b4ec1a-7393-4d7a-bf10-b5eb29a54175.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d585c38d_6926_4f6d_91a2_72ea2c5ae638
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 100.png | file://x:/photopub/docs/0000000471/ccd67053-dc90-440b-aba3-88084c699d91.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 102.png | file://x:/photopub/docs/0000000471/ac9e01f2-d4df-4ac8-a525-eb322c785661.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 104.png | file://x:/photopub/docs/0000000471/28f0d3c6-f686-4693-84a5-fcfc12ba13f2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 103.png | file://x:/photopub/docs/0000000471/98474f20-8b1e-4051-8ec7-529bfa3beec0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 105.png | file://x:/photopub/docs/0000000471/d23a3eeb-f2d0-4359-8ae2-38077523d54e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-628101-2016 | EL-422460-2016 | 8/16/2016 11:44:13 AM | ASSESS: EL: Service Connection | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Found unapproved, damaged and non-compliant electrical equipment for energized 120volt flexible extension cord with conductors exposed and hanging outdoors on earth grade. When non-compliant, damaged, unsafe and unapproved electrical equipment above is laying energized and exposed on earth grade, the electrical equipment is an electrical fire or shock hazard to people or property. | 3 | Conductors Equipment is not approved for the specific use. | 101.png | file://x:/photopub/docs/0000000471/76cae948-29c6-4e8d-aa5b-b82028c91364.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__73caf31d_d4ca_4036_8e1a_76314f928bf2
ELIN-645623-2016 | EL-433784-2016 | 9/12/2016 2:42:54 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found outdoor receptacle located less than one meter above grade has a dry location cover installed on outlet box. When outdoor receptacle boxes don't have wet location cover installed, the electrical equipment may be a possible electrical shock or fire hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | outdoor_receptacle_has_dry_cover_only_2.png | file://x:/photopub/docs/0000000484/a1735055-45f9-432c-85cc-8b1aac819647.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8df97fcd_6d99_4bf8_8a84_eab0f5571d35
ELIN-645623-2016 | EL-433784-2016 | 9/12/2016 2:42:54 PM | ASSESS: EL: Final | png | #asFound | EL123 | Installation of electrical equipment Equipment is not approved for the specific use | 3 | 3 | Found outdoor receptacle located less than one meter above grade has a dry location cover installed on outlet box. When outdoor receptacle boxes don't have wet location cover installed, the electrical equipment may be a possible electrical shock or fire hazard to people or property. | 3 | Installation of electrical equipment Equipment is not approved for the specific use | outdoor_receptacle_has_dry_cover_only.png | file://x:/photopub/docs/0000000484/b86c9917-14e8-401b-b9f8-56ce2339a397.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8df97fcd_6d99_4bf8_8a84_eab0f5571d35
EDMA-602763-2016 | ED-209209-2015 | 6/27/2016 7:02:09 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED047 | Wear or defects that are : Likely to progress Contractor is not aware of condition | 3 | 3 | Hoisting ropes are used to move the elevator up and down under normal operation. For this elevator the hoisting ropes are arranged in a manner that they have to run through a deflector sheave on top of the elevator counterweight. During an inspection the counterweight buffer test was performed and one of the hoisting ropes came off from the counterweight defector sheave. Although, the rope retainers of the defector sheaves were properly adjusted, the probably of the ropes skipping from the sheave is unlikely but not impossible for higher speed cars such as this one running at 500 feet per minute. Further movement of the elevator was not possible as the rope that skipped off was jamming the sheave. This was a modernized 36 stop traction elevator located in a hotel. | 3 | Wear or defects that are : Likely to progress Contractor is not aware of condition | Hoisting_rope_skipped_from_counterweight_sheave.png | file://x:/photopub/docs/0000000453/1266cfda-b76d-4e87-91e1-3ff5c34d2a8b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da932fe0_2050_4ee0_b5ca_63c4a78412c4
EDMA-602777-2016 | ED-284335-2015 | 6/23/2016 8:02:47 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | A barrier used for fall protection into the elevator hoistway is used to protect the elevator mechanic when he is doing work around the hoistway. During a modernization inspection, it was found if the mechanic was servicing the governor he would be putting himself into danger because there is not a fall protection barrier installed around the governor. It was found the elevator contractor failed to recognize the need for the barrier. This 6 stop traction elevator is located in a renovated hotel building. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Top_of_hoistway_governor.png | file://x:/photopub/docs/0000000453/fd587bec-76fa-49af-9221-b15a20a6d98e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6c094ac_aea6_4fa5_9282_728ab2696e32
EDMA-602777-2016 | ED-284335-2015 | 6/23/2016 8:02:47 PM | ASSESS: ED MA: Acceptance | png | #asFound | ED053 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | 3 | 3 | A barrier used for fall protection into the elevator hoistway is used to protect the elevator mechanic when he is doing work around the hoistway. During a modernization inspection, it was found if the mechanic was servicing the governor he would be putting himself into danger because there is not a fall protection barrier installed around the governor. It was found the elevator contractor failed to recognize the need for the barrier. This 6 stop traction elevator is located in a renovated hotel building. | 3 | Switches / circuits controlling access point working correctly Some Oily Surface Loose Fall prevention means in place Dim lighting | Access_point_of_governor.png | file://x:/photopub/docs/0000000453/e092cec9-f1be-4282-9e24-f9516c44f4b5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e6c094ac_aea6_4fa5_9282_728ab2696e32
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | H.png | file://x:/photopub/docs/0000000483/3ef47e62-8f08-45c8-bcee-99e125e68ef0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | B.png | file://x:/photopub/docs/0000000483/2f734cc3-e5db-4c6c-8f4d-b6f8553d8bba.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | C.png | file://x:/photopub/docs/0000000483/f9d9e228-4104-4f64-984e-216aac4b8851.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | O.png | file://x:/photopub/docs/0000000483/59dde8bd-408a-4d73-8c6c-32126634412f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | G.png | file://x:/photopub/docs/0000000483/e82cc5fe-52ac-4d1f-96cb-f6c98d741737.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | F.png | file://x:/photopub/docs/0000000483/dee53be5-b45a-4190-a499-921d71754bb9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | N.png | file://x:/photopub/docs/0000000483/1f779922-dbcd-4332-befd-24514b1b2095.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | I.png | file://x:/photopub/docs/0000000483/ea11775f-e0e9-4d9a-8478-baaca2b0f853.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | J.png | file://x:/photopub/docs/0000000483/819156de-deee-444f-84df-8d4695936d15.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | L.png | file://x:/photopub/docs/0000000483/41e218a6-7afd-4f14-9bc5-6c60d9bccdf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | K.png | file://x:/photopub/docs/0000000483/add57e5e-fda4-4241-8fa5-5152712b527c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | M.png | file://x:/photopub/docs/0000000483/e0dc794e-eeea-49e4-8966-979c8d1bd03a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-658068-2016 | UW-435445-2016 | 9/8/2016 9:51:23 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Unpermited electrical work. This installation has several non compliances. Exposed live conductors, non metallic sheathed cable used for outdoor wiring, ground fault protection missing, db2 conduit used above ground. These are all fire and shock hazards. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | A.png | file://x:/photopub/docs/0000000483/cde1485e-b38a-48c1-b5f5-46f70871140b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2ef683f3_8d52_4293_a42d_8ce521fa9d8d
ELIN-608052-2016 | EL-347650-2016 | 7/12/2016 8:36:59 AM | ASSESS: EL: Final | png | #asFound | EL132 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | 4 | 4 | The electrical Code requires all cables to be terminated in an approved box or device with a cover plate. This is to ensure that person do not come in contact with energized parts and that a fault in the energized conductors do not come in contact with combustible material which could lead to a shock or fire hazard. During a final electrical inspection for a single family home with a suite, a #10 awg non-metallic sheathed cable was entered into a 100 amp sub panel. The cable was not terminated on to a breaker. The cable was for a future dryer receptacle in the suite closet and the cable was installed behind the drywall with a box and cover plate. If the cable was terminated to a breaker or came in contact with the electrical panel bus, the cable could become energized which poses a fire and shock hazard. | 4 | Installation of electrical equipment Box or cabinet has not been provided at junction, splice, outlet, switch, or pull box. | Dryer_cable_entered_into_panel_and_installed_open_inside_of_wall_in_laundry_closet_of_suite_.png | file://x:/photopub/docs/0000000455/9ffb0690-552c-4117-ac5d-43f308f3b752.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ad1405bc_01a3_4f54_aa3d_c45fb0d8ea14
AMOP-608085-2016 | 2047389 | 7/7/2016 4:40:37 PM | ASSESS: AM OP: Periodic | png | #asFound | AM046 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | 3 | 3 | A cut-wire is used to detect a deropement condition of a sheave assembly of a ropeway. It was observed that a deropement cut wire switch was installed not through the terminal block (terminal block had been subjected to previous damage) that was located on the sheave assembly but instead was connected with a pair of wire nuts terminals. There is a high probability that in the event of a deropement, because of the extra slack in the cut-wire loop that was created by using wire nut connectors, that the the cut-wire would become displaced and would not sever and would not shutdown the device in the event of a deropement. This condition could cause excessive damage to the wire rope and the sheave assembly. | 3 | Safety critical monitoring bypassed or failed in manner reasonably detectable by maintenance operation program | Tower_2_cut-wire.png | file://x:/photopub/docs/0000000454/b46446e9-3726-448b-aec5-572ccef0aeb8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2c8c7da7_d0d3_4b35_9542_33011005316e
AMOP-610610-2016 | AM-142447-2014 | 7/13/2016 4:35:34 PM | ASSESS: AM OP: Periodic | png | #asFound | AM027 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | 2 | 2 | During the inspection it was observed that over-height motor vehicle traffic (e.g. telescopic handler moving under the rope with boom extended)was moving under the zipline rope along an established roadway. Moving motor vehicle making contact with the overhead zipline rope could result in catastrophic equipment damage. | 2 | Improper operational practice Unmaintained loading/unloading area Anticipated obstacles to safe loading/unloading not managed | Road_to_zipline_rope_clearance_510_cm.png | file://x:/photopub/docs/0000000459/d2e3d5a0-5107-45d5-bbd5-fa7c68a0b632.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__e936a7e7_265c_40ba_a9d5_0b85e9296e42
BPVIN-628573-2016 | BPV-422806-2016 | 8/10/2016 1:23:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | Pressure relief devices protect equipment from over pressure conditions and damage. Devices must be installed according to all applicable standards. I found a plug installed in lieu of a pressure relief device on a 200psi air receiver mounted with machine. Potential exists for an over pressure incident to occur due to a safety device not providing intended control. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | Unit_in_service.png | file://x:/photopub/docs/0000000472/9810b51f-f58e-4139-b017-a27cb63b6c25.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ab04f5_97e6_4d63_a3e3_5da58afd5615
BPVIN-628573-2016 | BPV-422806-2016 | 8/10/2016 1:23:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | Pressure relief devices protect equipment from over pressure conditions and damage. Devices must be installed according to all applicable standards. I found a plug installed in lieu of a pressure relief device on a 200psi air receiver mounted with machine. Potential exists for an over pressure incident to occur due to a safety device not providing intended control. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | Unit_disconnected_and_taken_out_of_service_.png | file://x:/photopub/docs/0000000472/07162a5e-b63c-43ba-9601-4394818507bd.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ab04f5_97e6_4d63_a3e3_5da58afd5615
BPVIN-628573-2016 | BPV-422806-2016 | 8/10/2016 1:23:59 PM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP123 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | 5 | 5 | Pressure relief devices protect equipment from over pressure conditions and damage. Devices must be installed according to all applicable standards. I found a plug installed in lieu of a pressure relief device on a 200psi air receiver mounted with machine. Potential exists for an over pressure incident to occur due to a safety device not providing intended control. | 5 | 3.1.1 Safeties will not function - Pressure Relief Device Safety relief valve removed or bypassed | Name_plate.png | file://x:/photopub/docs/0000000472/cb681eda-27cf-4991-82cd-59f6363cc814.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__67ab04f5_97e6_4d63_a3e3_5da58afd5615
ELIN-602132-2016 | EL-327133-2015 | 7/20/2016 1:52:19 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | The existing 200 amp 120/240 volt panel from original cabin (on original wall section) is used as the temporary panel. A roof is built over the structure however there is no lockable door in place and the panel is subject to harsh weather conditions. This can lead to both a shock and equipment damage issue. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | Temp_panel.png | file://x:/photopub/docs/0000000459/00b75dca-04d3-4cc6-9cbc-9f74ec69dfc1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ebd1a61f_4a57_41eb_a37a_3fd0164ca887
ELIN-617976-2016 | EL-380309-2016 | 8/26/2016 2:46:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Unfused conductors concealed in wall present fire hazard. Lag screw point of attachment with 200A conductors crossing public road is not adequate to support weight of unfused triplex. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Totem2.png | file://x:/photopub/docs/0000000476/82a45cab-4f08-4eb5-a854-b03f0ec29b3e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc7f33f_817f_4717_b795_fb1646dab697
ELIN-617976-2016 | EL-380309-2016 | 8/26/2016 2:46:37 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 4 | Unfused conductors concealed in wall present fire hazard. Lag screw point of attachment with 200A conductors crossing public road is not adequate to support weight of unfused triplex. | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Totem.png | file://x:/photopub/docs/0000000476/c47633ff-6de9-4666-86b5-16342685a0a2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fdc7f33f_817f_4717_b795_fb1646dab697
AMOP-664193-2016 | 3553511 | 9/16/2016 4:28:39 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | Locking nuts on anchoring were loose, turnbuckles could back off, causing loss of tension on system | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Ziptrek_loose_hardware_6.png | file://x:/photopub/docs/0000000486/7f355a1f-89cf-4ea8-8f20-bba5b1e69be6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2aaa44e4_12b3_448e_9381_08cf44ed0184
AMOP-664189-2016 | 3553510 | 9/16/2016 4:15:41 PM | ASSESS: AM OP: Periodic | png | #asFound | AM001 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | 2 | 2 | Locking nuts on anchoring were loose, turnbuckles could back off, causing loss of tension on system | 2 | Suspected defects that are: Reasonably detectable by maintenance program Unlikely to propagate | Ziptrek_loose_hardware.png | file://x:/photopub/docs/0000000486/fa91744f-9c7e-48d9-a66f-93efd0a9913e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d19f8ffc_326e_4d75_a2e3_de51117dd2ef
ELIN-612715-2016 | EL-352822-2016 | 7/18/2016 2:20:52 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Dissimilar brands of breakers found in main panel. Specific brand breakers are designed to fit and provide overcurrent protection for same brand panels. Different brand breakers operate at different specifications and parameters, if a fault were to occur, clearing of the fault may not occur and damage to persons or property may occur. | 3 | General Equipment is not approved for the specific use | Dissimilar_breaker_brands_in_same_panel__.png | file://x:/photopub/docs/0000000457/67e24ac6-2a25-48cb-84f1-c9725aee7d5a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44c300c5_b158_4ccf_83f6_dde2c4efbe8d
ELIN-612715-2016 | EL-352822-2016 | 7/18/2016 2:20:52 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Dissimilar brands of breakers found in main panel. Specific brand breakers are designed to fit and provide overcurrent protection for same brand panels. Different brand breakers operate at different specifications and parameters, if a fault were to occur, clearing of the fault may not occur and damage to persons or property may occur. | 3 | General Equipment is not approved for the specific use | Dissimilar_breaker_brand_in_same_panel__.png | file://x:/photopub/docs/0000000457/631a1ba5-9c2b-4dc2-92e7-da2a6d692a00.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__44c300c5_b158_4ccf_83f6_dde2c4efbe8d
GAIN-649758-2016 | GA-404476-2016 | 9/14/2016 8:51:09 AM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Dryer.png | file://x:/photopub/docs/0000000485/de1356c9-90ee-4406-92cc-d3268b7ca1c8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0a8abef1_d242_4c9e_a86e_eb87962c7e91
ELIN-617959-2016 | EL-414874-2016 | 8/5/2016 7:27:40 AM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 | In the 30A 240V subpanel a filler has not been installed for a unused branch breaker location, the interior energized components could be contacted creating a shock hazard or damage to the panel. | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Panel_filler.png | file://x:/photopub/docs/0000000466/3cb727a9-caa9-41ef-81c0-5790be590648.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd5e06d8_0f26_4bd8_b9a8_6868e06852f6
ELIN-614598-2016 | EL-345779-2016 | 7/18/2016 1:44:29 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Energized, underground consumer service raceway bedded in angular material, accessible to general public, not adequately guarded from mechanical damage and limits of approach to gas supply piping not maintained. This poses a serious risk of personal injury (shock) or catastrophic property damage (thermal event/explosion) due to occurrence to mechanical damage or impact. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_service_raceways_02.png | file://x:/photopub/docs/0000000459/78881b6a-eab4-4f2a-b0a8-717cef451f2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8239665b_02c7_4172_bd3b_f33693df4a91
GAIN-629114-2016 | GA-423074-2016 | 8/19/2016 8:31:04 AM | ASSESS: GA: Final | png | #asFound | GA121 | insufficient mechanical air intake clearance to gas regulator relief | 3 | 3 | Mechanical appliance intake installed with less than the required minimum to meter relief opening. A failure of the regulator of the meter would allow high pressure gas to be released.If this was to occur while the appliance was in operation,fuel would be drawn into the combustion chamber of the appliance. Possible over fire condition leading to fire and or equipment damage. | 3 | insufficient mechanical air intake clearance to gas regulator relief | Cedric.png | file://x:/photopub/docs/0000000473/99b7067e-46bb-495a-99f8-edfb02157f79.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__ac7ee20a_f732_4b70_a032_e2a0a1f22002
GAIN-633033-2016 | GA-388104-2016 | 8/19/2016 9:27:26 AM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Oak_street.png | file://x:/photopub/docs/0000000473/20038ead-2423-43c0-b708-a64aee3f909f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf10c559_f190_4c9e_a595_4fe533ea520b
GAOP-222813-2014 | GA-144771-2014 | 9/12/2016 1:39:00 PM | ASSESS: GA OP: Periodic | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 |  | 2 | Inadequate protection Low traffic | Inadequate_vehicle_protection__.png | file://x:/photopub/docs/0000000484/7b570039-c6f4-4be9-a777-d25175c9b574.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4767b4bf_dc7c_4dd7_a5b1_a43223673ce3
GAOP-222813-2014 | GA-144771-2014 | 9/12/2016 1:39:00 PM | ASSESS: GA OP: Periodic | png | #asFound | GA023 | Inadequate protection Low traffic | 2 | 2 |  | 2 | Inadequate protection Low traffic | Jersey_no_post_barrier_below_vehicle_travel_surface.png | file://x:/photopub/docs/0000000484/2c75be73-cdc2-4b6e-8178-430f514f99f1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4767b4bf_dc7c_4dd7_a5b1_a43223673ce3
GAIN-661633-2016 | GA-425911-2016 | 9/13/2016 1:59:24 PM | ASSESS: GA: Final | png | #asFound | GA043 | Certified appliance connector installed but not approved for application | 2 | 2 |  | 2 | Certified appliance connector installed but not approved for application | Riverside.png | file://x:/photopub/docs/0000000485/60899001-b20a-49a9-a40f-1cb70d2553d5.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0f5b845b_b6ce_47be_bb7c_fcd2a5c3e6c2
ELOP-415770-2015 | EL-134253-2014 | 7/14/2016 10:47:28 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | Energized conductors present in junction box, in the workshop area. Junction boxes require covers when conductors pass through or terminate at the junction. Accidental contact with exposed conductors may cause shock or fire to persons or property. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Live_conductor_in_junction_in_workshop_area.png | file://x:/photopub/docs/0000000456/6a05b87a-5f0a-4fb9-8f60-4cb605c8ff75.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__320c4182_c109_428d_add2_86dab57906da
GAUP-662313-2016 | UW-436871-2016 | 9/13/2016 1:20:47 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA060 | 1st stage regulator installed below container liquid level | 4 | 4 | High pressure regulator installed below liquid level, liquid propane could enter the vapour service regulator and cause failure. | 4 | 1st stage regulator installed below container liquid level | Reg.png | file://x:/photopub/docs/0000000484/a2c9b9a3-2b2e-4e87-9999-62339912f8de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9ddfbc6b_caa0_4b94_8c6b_7595e590bac1
BPVOP-666896-2016 | 5033810 | 9/19/2016 3:27:38 PM | ASSESS: BPV OP: Re-Certification REF/PV | png | #asFound | BP014 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | 1 | 1 |  | 1 | 1.0.2 Clearances/Maintenance - Clearances are less than 24 inches but are sufficient for operation, maintenance and inspection | Air_compressor_clearance.png | file://x:/photopub/docs/0000000487/af5c2dbc-5ba0-4a48-843c-4f41f3254923.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__565b6fd7_1d0f_433e_b17d_64d8d3f4bab6
ELIN-614597-2016 | EL-345778-2016 | 7/18/2016 12:05:23 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Energized, underground consumer service raceway bedded in angular material, accessible to general public, not adequately guarded from mechanical damage and limits of approach to gas supply piping not maintained. This poses a serious risk of personal injury (shock) or catastrophic property damage (thermal event/explosion) due to occurrence to mechanical damage or impact. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_service_raceway.png | file://x:/photopub/docs/0000000459/bcf90973-e132-42bb-8da2-147e6a3855b2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__edba6c06_72fb_4cee_8d89_f2adb022308b
ELIN-614598-2016 | EL-345779-2016 | 7/18/2016 1:44:29 PM | ASSESS: EL IN: Work-in-Progress | png | #asFound | EL029 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | 3 | 3 | Energized, underground consumer service raceway bedded in angular material, accessible to general public, not adequately guarded from mechanical damage and limits of approach to gas supply piping not maintained. This poses a serious risk of personal injury (shock) or catastrophic property damage (thermal event/explosion) due to occurrence to mechanical damage or impact. | 3 | Improper installation or location of equipment, conductors, cables or raceways Inadequate Distances; burial depth and protection for underground cables or raceways | View01_service_raceways02.png | file://x:/photopub/docs/0000000459/2de79525-34f6-4ac2-a638-fef636398310.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8239665b_02c7_4172_bd3b_f33693df4a91
ELIN-612513-2016 | EL-403653-2016 | 7/20/2016 9:51:27 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Dry location, energized consumer service equipment installed in an area that is not adequately protected from the effects of weather. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to the deterioration of the consumer service equipment and failure of the safety systems as a result of the exposure to the effects of weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View02_structure.png | file://x:/photopub/docs/0000000459/a9a7d56f-b6ff-424e-9b7f-799131963820.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c389a88a_5db1_4c4b_bb07_f1b31be4153a
ELIN-612513-2016 | EL-403653-2016 | 7/20/2016 9:51:27 AM | ASSESS: EL: Final | png | #asFound | EL057 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | 3 | 3 | Dry location, energized consumer service equipment installed in an area that is not adequately protected from the effects of weather. This poses a serious risk of personal injury (shock) or property damage (thermal event) due to the deterioration of the consumer service equipment and failure of the safety systems as a result of the exposure to the effects of weather. | 3 | Improper installation or location of equipment, conductors, cables or raceways Enclosure is not rated for the environment or conditions of use | View01_main_distribution.png | file://x:/photopub/docs/0000000459/9df8ee1c-d292-4db3-8475-8e1db00a1370.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__c389a88a_5db1_4c4b_bb07_f1b31be4153a
GAIN-630843-2016 | GA-402701-2016 | 8/19/2016 1:50:40 PM | ASSESS: GA: Final | png | #asFound | GA097 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | 2 | 2 | Supply air from DFMAU unit venting into drop ceiling where products of combustion could accumulate and build up. Combustible products and carbon monoxide could accumulate in the drop ceiling space of the restaurant. | 2 | Non compliant venting system ex: improper grading, incorrect glue/ fasteners | Supply_air_from_DFMAU_pressurizing_drop_ceiling_space_.png | file://x:/photopub/docs/0000000473/48e11a13-fba6-4086-a855-ab0d31e5e0ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__110b6549_a6c9_43ea_9b68_8a857c43688b
GAIN-611719-2016 | GA-395982-2016 | 7/15/2016 2:31:05 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 |  | 2 | Physical protection of piping and tubing absent. | Willow.png | file://x:/photopub/docs/0000000464/fa817ba6-a507-4edd-96ea-7fa6aa7768cc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd750bad_e95d_4f77_a3ba_cb8f43abb566
ELIN-627817-2016 | EL-351037-2016 | 8/22/2016 11:25:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | -Open access to bare live parts in Main combination panel board. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_fillers.png | file://x:/photopub/docs/0000000474/49ed76ab-7bc3-4647-b981-a38731824980.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3d9962_5e00_4b19_bd19_15c2dd30c7ad
ELIN-627817-2016 | EL-351037-2016 | 8/22/2016 11:25:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | -Open access to bare live parts in Main combination panel board. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Panel_filler.png | file://x:/photopub/docs/0000000474/63560c29-6305-4690-8c3e-2acf72822b3d.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3d9962_5e00_4b19_bd19_15c2dd30c7ad
ELIN-627817-2016 | EL-351037-2016 | 8/22/2016 11:25:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | -Open access to bare live parts in Main combination panel board. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Bcm2.png | file://x:/photopub/docs/0000000474/6046e669-ff89-4d19-8e56-776e2c2fe557.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3d9962_5e00_4b19_bd19_15c2dd30c7ad
ELIN-627817-2016 | EL-351037-2016 | 8/22/2016 11:25:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | -Open access to bare live parts in Main combination panel board. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Bcm3.png | file://x:/photopub/docs/0000000474/6c1f65aa-47eb-4a9f-a28f-8895807534e1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3d9962_5e00_4b19_bd19_15c2dd30c7ad
BPVOP-662572-2016 | 2954047 | 9/13/2016 12:29:50 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP184 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | 3 | 3 | All flammables and combustibles materials should be properly stored. During the inspection of a Hot Water Boiler with MAWP of 87 psig combustibles blocking the air intake were found. | 3 | 5.1.0 In service proc/process - Combustibles stored in boiler or machinery room. | Combustibles_blocking_air_intake.png | file://x:/photopub/docs/0000000484/c1d86707-df73-4485-a625-f0b64a752bc9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fc250381_8a05_4e23_8037_bebcdf6f088d
ELIN-626959-2016 | UW-421734-2016 | 8/9/2016 1:22:51 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Branch circuit does not have identified conductor. Possibility for energizing incorrect voltage resulting in shock. | 3 | Conductors Equipment is not approved for the specific use. | Potlighting.png | file://x:/photopub/docs/0000000468/b9f83ee6-616d-4f85-a28a-5498e65df0e2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4ce624c_522a_4208_b273_e0ceabf6da90
ELIN-626959-2016 | UW-421734-2016 | 8/9/2016 1:22:51 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Branch circuit does not have identified conductor. Possibility for energizing incorrect voltage resulting in shock. | 3 | Conductors Equipment is not approved for the specific use. | Receptacles_and_wiring.png | file://x:/photopub/docs/0000000468/261c0ae1-3e29-4f1c-9982-6a3f1ff9840e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a4ce624c_522a_4208_b273_e0ceabf6da90
ELIN-626970-2016 | UW-421748-2016 | 8/9/2016 11:51:45 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL112 | Conductors Equipment is not approved for the specific use. | 3 | 3 | Branch circuit does not have an identified conductor. Potential for mis-wiring a junction and exposure to shock. | 3 | Conductors Equipment is not approved for the specific use. | Potlighting_wired_with_Heatex_240v_.png | file://x:/photopub/docs/0000000468/74cea7ec-cff4-4b0c-b469-453d6b32d5ac.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__98dd2ec9_4456_4d90_a2ef_279e8941069b
ELIN-627817-2016 | EL-351037-2016 | 8/22/2016 11:25:56 AM | ASSESS: EL: Final | png | #asFound | EL004 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | 4 | 4 | -Open access to bare live parts in Main combination panel board. | 4 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is normally accessible to authorized persons only. | Box_covers_missing.png | file://x:/photopub/docs/0000000474/1a887d37-e983-45f1-825c-15f24bdfa3a7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2d3d9962_5e00_4b19_bd19_15c2dd30c7ad
EDRI-665105-2016 | ED-330094-2015 | 9/16/2016 8:22:00 AM | ASSESS: ED RI: Final | png | #asFound | ED057 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | 2 | 2 | A Hole in the bottom landing creates a tripping hazard to anyone using the hoist. | 2 | • Uneven Landing Surface • Temp Slipping /Tripping Hazard | Rogers_arena_deck.png | file://x:/photopub/docs/0000000486/5507b391-01e3-4c61-b41b-b63aa0842baa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4bebbd9b_38bc_4ca7_8e1b_4775eef82bb8
GAUP-616205-2016 | UW-414741-2016 | 7/25/2016 1:21:50 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The single wall vent from the water heater is to close to combustibles in multiple locations. | 3 | Non compliant Type C Vent clearance | Single_wall_vent_connector_to_close_to_wood_door_.png | file://x:/photopub/docs/0000000461/357d0500-e3da-4e72-b47e-44a3bdbcb0de.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c10c607_a102_4346_a8a4_fb21adfb764c
GAUP-616205-2016 | UW-414741-2016 | 7/25/2016 1:21:50 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The single wall vent from the water heater is to close to combustibles in multiple locations. | 3 | Non compliant Type C Vent clearance | Water_heater_in_contact_with_cabinet_.png | file://x:/photopub/docs/0000000461/e3f6d155-ec46-4cfc-95cd-753556999efa.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c10c607_a102_4346_a8a4_fb21adfb764c
GAUP-616209-2016 | UW-414748-2016 | 7/25/2016 2:12:26 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | The special vent system was not sealed to the furnace outlet. The lack of sealant could leak products of combustion into the occupied living area creating a hazard. The special vent termination location next to the meter regulator could draw in gas from the regulator in the event of the regulator relief venting gas. This could cause a fire or explosion. | 5 | Special venting system not glued or connected as per certified instructions | Special_vent_system_terminated_to_close_to_meter_.png | file://x:/photopub/docs/0000000461/d59f849e-9b0c-4286-8371-c39b8c392bff.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b656145_f1bd_4382_9c6d_80dd3ae3bfa4
GAUP-616209-2016 | UW-414748-2016 | 7/25/2016 2:12:26 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | The special vent system was not sealed to the furnace outlet. The lack of sealant could leak products of combustion into the occupied living area creating a hazard. The special vent termination location next to the meter regulator could draw in gas from the regulator in the event of the regulator relief venting gas. This could cause a fire or explosion. | 5 | Special venting system not glued or connected as per certified instructions | Special_vent_system_not_supported_.png | file://x:/photopub/docs/0000000461/e2b3f4ad-f984-4702-9862-66d609994818.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b656145_f1bd_4382_9c6d_80dd3ae3bfa4
GAUP-616205-2016 | UW-414741-2016 | 7/25/2016 1:21:50 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The single wall vent from the water heater is to close to combustibles in multiple locations. | 3 | Non compliant Type C Vent clearance | Vent_connector_in_contact_with_gas_pipe_.png | file://x:/photopub/docs/0000000461/ce4a56cb-e58b-4a7b-b95b-50516347fc14.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c10c607_a102_4346_a8a4_fb21adfb764c
GAUP-616205-2016 | UW-414741-2016 | 7/25/2016 1:21:50 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The single wall vent from the water heater is to close to combustibles in multiple locations. | 3 | Non compliant Type C Vent clearance | Single_wall_vent_connector_to_close_to_furnace_vent_material_.png | file://x:/photopub/docs/0000000461/abc59bc2-950a-4732-a61a-474e4f4dd201.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c10c607_a102_4346_a8a4_fb21adfb764c
GAUP-616209-2016 | UW-414748-2016 | 7/25/2016 2:12:26 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA109 | Special venting system not glued or connected as per certified instructions | 5 | 5 | The special vent system was not sealed to the furnace outlet. The lack of sealant could leak products of combustion into the occupied living area creating a hazard. The special vent termination location next to the meter regulator could draw in gas from the regulator in the event of the regulator relief venting gas. This could cause a fire or explosion. | 5 | Special venting system not glued or connected as per certified instructions | Special_vent_not_sealed_.png | file://x:/photopub/docs/0000000461/f641ad83-3925-4381-8120-89f8aae53ea6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__0b656145_f1bd_4382_9c6d_80dd3ae3bfa4
GAUP-616205-2016 | UW-414741-2016 | 7/25/2016 1:21:50 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA101 | Non compliant Type C Vent clearance | 3 | 3 | The single wall vent from the water heater is to close to combustibles in multiple locations. | 3 | Non compliant Type C Vent clearance | C_vent_to_close_to_combustible_furnace_vent_.png | file://x:/photopub/docs/0000000461/4a106da3-c0bc-4e4c-b517-6c4889b4824a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__8c10c607_a102_4346_a8a4_fb21adfb764c
ELIN-611394-2016 | UW-411302-2016 | 7/15/2016 4:22:31 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL129 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | 3 | 2 | Exterior 120v receptacle requires a dedicated branch circuit to minimize the likelihood of overloading the branch circuit. Not considered a hazard. | 3 | Installation of electrical equipment Residential: Circuit has not been provided for appliances that require unique, separate or dedicated circuit. | Exterior_receptacle_in_attached_garage.png | file://x:/photopub/docs/0000000455/36a97df3-abc0-455d-948d-8ecff02fd4a9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f4ebffbb_c2d2_4cba_90b0_ca04761814b4
BPVOP-612013-2016 | 2270321 | 7/14/2016 12:34:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment it is determined that pressure and temperature rating of valves and fittings on blow off line is not rated to code. Valves and fittings may fail early in service due to type of stress valves and fittings sustain in service. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | Blowoff_line.png | file://x:/photopub/docs/0000000456/02396aed-8f97-45aa-b319-0e1434713266.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22b6618b_9250_4435_991c_fb2c8dee4e22
BPVOP-612013-2016 | 2270321 | 7/14/2016 12:34:32 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP003 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | 1 | 1 | Upon assessment it is determined that pressure and temperature rating of valves and fittings on blow off line is not rated to code. Valves and fittings may fail early in service due to type of stress valves and fittings sustain in service. | 1 | 1.0.1 Temp/Pressure ratings not met - Pressure or temperature rating of vessel/piping system component less than design pressure or temperature but suitable for operating conditions | FEED_WATER_BYPASS_LINE.png | file://x:/photopub/docs/0000000456/125be1c6-bdd1-45ab-aee3-f2be4eac8c60.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__22b6618b_9250_4435_991c_fb2c8dee4e22
ELIN-662936-2016 | EL-388761-2016 | 9/15/2016 1:42:02 PM | ASSESS: EL: Service Connection | png | #asFound | EL156 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | 3 | 3 | Site made wood bracket to mount service meter to pole. Approved mounting brackets or other means are acceptable for mounting meter to pole. Over time site made wood bracket may rot and meter attachement may become compromised and come loose. Unattached meter may provide risk of shock and fire to persons and property. | 3 | Installation of electrical equipment Boxes or cabinets are not securely mounted. | Site_made_wood_bracket_for_meter_base.png | file://x:/photopub/docs/0000000485/cdb5f7cf-4428-439c-afb8-5a77f2280153.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9c115324_7fe0_4af7_af1b_2072c812536e
GAIN-522425-2016 | GA-342972-2016 | 7/19/2016 1:55:01 PM | ASSESS: GA: Final | png | #asFound | GA077 | Not installed according to certified installation instructions | 2 | 2 | Regulator not installed as per manufacturers installation instructions. Regulator may not operate properly when not installed according to instructions. | 2 | Not installed according to certified installation instructions | Regulator_not_installed_as_per_manufacturers_installation_instructions.png | file://x:/photopub/docs/0000000458/6f4682fd-0261-4aa6-bd11-7641d0dac08e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__70d5888e_8b4a_4c65_9a31_09b531f2c732
GAIN-610956-2016 | GA-411013-2016 | 7/19/2016 12:02:12 PM | ASSESS: GA: Final | png | #asFound | GA042 | Physical protection of piping and tubing absent. | 2 | 2 | Physical protection of gas connector not in place. When an appliance is connected using a certified connector and is subject to movement, the connector may be damaged by stress from movement. | 2 | Physical protection of piping and tubing absent. | No_physical_protection_of_gas_connector_.png | file://x:/photopub/docs/0000000458/009db8c4-8b87-4960-a2bb-da29f1428c73.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e3cab7e_2eec_4dd4_81f8_e73c94dccb88
ELIN-662417-2016 | EL-410027-2016 | 9/14/2016 3:32:21 PM | ASSESS: EL: Final | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Dry type transformer is mounted on combustible material. This condition could lead to a potential fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Transformer_mounting_.png | file://x:/photopub/docs/0000000485/e29bcdde-70f5-4e8d-9025-7407697ec40c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32aef139_312a_4c26_9683_599e19b43f68
ELIN-662417-2016 | EL-410027-2016 | 9/14/2016 3:32:21 PM | ASSESS: EL: Final | png | #asFound | EL181 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | 4 | 4 | Dry type transformer is mounted on combustible material. This condition could lead to a potential fire hazard. | 4 | General Construction Indoor: Indoor dry-type, not properly separated from combustibles. | Transformer_decal.png | file://x:/photopub/docs/0000000485/8967854a-5ac1-4473-aac6-79138d6e6a7e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__32aef139_312a_4c26_9683_599e19b43f68
ELIN-662682-2016 | EL-437179-2016 | 9/15/2016 11:30:55 AM | ASSESS: EL: Final | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Trailer is energized through the use of a male cord cap being plugged into the female receptacle mounted on the trailer. This presents a possible shock hazard | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | power_connection.png | file://x:/photopub/docs/0000000485/3826c849-5e58-4572-82d7-102145c63280.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1e84a59f_c875_4b2d_81fc_ae0d9598816c
ELIN-640526-2016 | EL-260324-2015 | 9/15/2016 1:45:18 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | 600 V cable has been installed without connectors at either end. This is a possible shock and/or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | Shelving_in_front_of_panel.png | file://x:/photopub/docs/0000000485/73aac596-3f67-42d9-882f-21b1611bca0a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5bed5d5_3a7c_4e15_b026_cca4bcd00fa5
ELIN-640526-2016 | EL-260324-2015 | 9/15/2016 1:45:18 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | 600 V cable has been installed without connectors at either end. This is a possible shock and/or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | transformer.png | file://x:/photopub/docs/0000000485/5d8c67a4-a3db-4f3b-ba4c-1df44542bb6f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5bed5d5_3a7c_4e15_b026_cca4bcd00fa5
ELIN-640526-2016 | EL-260324-2015 | 9/15/2016 1:45:18 PM | ASSESS: EL: Final | png | #asFound | EL025 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 3 | 3 | 600 V cable has been installed without connectors at either end. This is a possible shock and/or fire hazard. | 3 | Improper installation or location of equipment, conductors, cables or raceways Raceways are not suitably drained, No expansion joint or not installed correctly. | 50A_fuses__no_connector.png | file://x:/photopub/docs/0000000485/0a7c95d4-ef4d-45e8-9b35-73fff831e7ec.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__b5bed5d5_3a7c_4e15_b026_cca4bcd00fa5
GAIN-558387-2016 | GA-366889-2016 | 7/28/2016 10:36:55 AM | ASSESS: GA: Final | png | #asFound | GA098 | Side wall vent termination not compliant with installation instructions | 2 | 2 |  | 2 | Side wall vent termination not compliant with installation instructions | Vent_term1.png | file://x:/photopub/docs/0000000464/b20c734c-7d4c-47bc-a6e5-6bf8ade58a2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5af67b64_9c70_49b7_9a68_1b58bb59171a
GAIN-616018-2016 | GA-414567-2016 | 7/28/2016 9:09:40 AM | ASSESS: GA: Final | png | #asFound | GA053 | Non-certified appliance connector | 3 | 3 | Un-approved appliance connector for appliance on casters. With repeated movement for cleaning, un-approved connectors are known to fail and leak, possibly causing fire and injury | 3 | Non-certified appliance connector | Range_Connector.png | file://x:/photopub/docs/0000000464/c0831503-e765-4ae2-b4b1-b4dfd08c7cf6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__5bdd14eb_0719_42eb_bc94_d50e6636e56a
GAIN-618926-2016 | GA-411659-2016 | 7/29/2016 11:34:47 AM | ASSESS: GA: Rough-In | png | #asFound | GA102 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | 3 | 3 | Venting products could enter building opening causing illness | 3 | Vent termination non-compliant over public sidewalk, grade, building opening or air supply inlet | Vent_term.png | file://x:/photopub/docs/0000000464/c666c68a-74b4-48ca-86de-a51580b971e0.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9b354350_d97b_489d_9bbd_ecb236669744
ELIN-641070-2016 | EL-429907-2016 | 8/31/2016 2:55:32 PM | ASSESS: EL: Service Connection | png | #asFound | EL031 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | 4 | 3 | This assessment found a residential service panel installed without the required weather protection. If the main breaker becomes wet it could fail to operate properly presenting a shock and fire hazard | 4 | Improper installation or location of equipment, conductors, cables or raceways Equipment is not suitable for the location | Panel_exposed_to_weather.png | file://x:/photopub/docs/0000000478/23fa0599-b994-48b0-aca8-a5cc450d51b1.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4ef30b47_7c1d_48d9_a1ca_0b14ae182150
GAIN-664912-2016 | GA-026075-2013 | 9/15/2016 5:37:33 PM | ASSESS: GA: Final | png | #asFound | GA139 | Incorrect appliance type installed for application | 3 | 3 | Incorrect appliance for application. Clearance to combustible material requirements are not met when solid fuel fireplace has been extensively modified. Fire could result from clearance to combustibles not being met. | 3 | Incorrect appliance type installed for application | Modified_firebox.png | file://x:/photopub/docs/0000000485/a93aa542-adb9-470b-a262-efc1074ed06c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__836168cd_208c_4dde_9071_33120abdbe34
ELIN-615955-2016 | UW-414528-2016 | 7/22/2016 11:18:55 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | The teck cable is not terminated with a proper connector. The cable could be pulled out of the terminals and create a shock hazard. |  |  | Cable_run_to_distribution_.png | file://x:/photopub/docs/0000000460/e525ded9-a5c2-4ff7-a468-5b04b19195e7.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2951f57d_fafe_415d_b3d6_a20b6f2e3415
ELIN-615955-2016 | UW-414528-2016 | 7/22/2016 11:18:55 AM | ASSESS: EL IN: Unsafe Condition | png | #asFound |  |  |  |  | The teck cable is not terminated with a proper connector. The cable could be pulled out of the terminals and create a shock hazard. |  |  | Cable_termination.png | file://x:/photopub/docs/0000000460/642546e2-40b3-40ae-bd87-8bb34bcc4715.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__2951f57d_fafe_415d_b3d6_a20b6f2e3415
AMIN-612080-2016 | AM-411599-2016 | 7/14/2016 5:04:32 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | It was observed that 6 of 16 lower attachment points were not anchored. Design submission documentation indicates that all 16 lower and 6 upper attachment points are to be anchored to the ground. The operators did not appear to be aware of the need that all attachment points are to be anchored. A hazard exists in which the device could become unstable in the even of excessive high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Example_of_1_of_6_attachment_points_not_anchored.png | file://x:/photopub/docs/0000000458/14d23abb-fda0-41f6-8781-2e1a8a319528.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89cafe83_0864_4b43_8943_792241f15132
ELIN-616497-2016 | EL-414891-2016 | 7/22/2016 10:32:34 AM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL036 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | 2 | 2 | The communication supply cables attached to the power supply mast and a 300 mm clearance has not been maintained.This could potentially lead to an induced voltage being implied onto the communication wiring. | 2 | Improper installation or location of equipment, conductors, cables or raceways Raceways or cables are not adequately supported. | Communication_support_attachment_is_unapproved.png | file://x:/photopub/docs/0000000460/3c5733b1-0f18-4bbd-9b15-b9f8416328d2.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20099f08_31d5_4e63_826b_7ae3a3981d4f
GAWP-616506-2016 | GA-386470-2016 | 7/21/2016 8:01:03 AM | ASSESS: GA Work In Progress | png | #asFound | GA061 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | 4 | 4 | An uncapped live gas line was protested only by a ball type shut off valve. The opening or failure of the valve would allow gas to flow into the occupied space possibly resulting in a fire or explosion. | 4 | Open gas line connected to fuel supply with valve in off position (no cap/plug) | Uncapped_gas_line.png | file://x:/photopub/docs/0000000460/9d029246-23bb-4796-88a9-c07e6f5ca7eb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__da068205_0fcd_4619_8db9_9285fa498cb1
ELIN-640097-2016 | EL-429614-2016 | 9/1/2016 10:19:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 400_amp_3_position_meter_installation.png | file://x:/photopub/docs/0000000479/007ddc40-5d8d-4d6f-b66a-7d0c3d4134f6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bddabcb_bc4e_4762_96b1_632ffa32431e
ELIN-640097-2016 | EL-429614-2016 | 9/1/2016 10:19:17 AM | ASSESS: EL: Service Connection | png | #asFound | EL000 | No Created Hazard Identified | 0 | 0 |  | 0 | No Created Hazard Identified | 4_0_al_rw90.png | file://x:/photopub/docs/0000000479/591bec0f-fa9e-4eae-881c-480a07fd6837.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7bddabcb_bc4e_4762_96b1_632ffa32431e
AMIN-612080-2016 | AM-411599-2016 | 7/14/2016 5:04:32 PM | ASSESS: AM IN: Acceptance | png | #asFound | AM052 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | 3 | 3 | It was observed that 6 of 16 lower attachment points were not anchored. Design submission documentation indicates that all 16 lower and 6 upper attachment points are to be anchored to the ground. The operators did not appear to be aware of the need that all attachment points are to be anchored. A hazard exists in which the device could become unstable in the even of excessive high winds. | 3 | Anchoring is not installed as per manufacturers requirements Baffling is not present and unit is not in operation | Example_of_one_of_the_attachment_point_that_was_not_anchored.png | file://x:/photopub/docs/0000000458/b919b7e1-2a21-42a4-bc7f-f4ab5f093dbe.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__89cafe83_0864_4b43_8943_792241f15132
GAIN-627346-2016 | GA-388104-2016 | 8/12/2016 8:54:34 AM | ASSESS: GA: Final | png | #asFound | GA099 | Non compliant Type B Vent Clearance | 2 | 2 |  | 2 | Non compliant Type B Vent Clearance | Oak_street.png | file://x:/photopub/docs/0000000470/c2fe8389-22ce-4fb0-9b78-455e3f871433.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__37b238e3_6924_4cc3_b1d8_08f0f78d0ae4
ELIN-631874-2016 | EL-377921-2016 | 8/18/2016 2:59:13 PM | ASSESS: EL: Final | png | #asFound | EL006 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | 2 | 2 |  | 2 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are not exposed to accidental contact; and • in an area that is not normally accessible to persons, | Overhead_door_receptacle.png | file://x:/photopub/docs/0000000472/2c52106d-01ce-4299-ae19-b49879b10da3.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a31c3795_1dcf_439c_93b4_3c8ff3314a96
ELIN-606879-2016 | EL-279775-2015 | 7/11/2016 9:09:11 AM | ASSESS: EL: Final | png | #asFound | EL140 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | 15A 120V receptacles have been installed within 1.5m of the laundry counter sink without GFCI protection, this could result in equipment damage or a shock hazard to persons. | 3 | Installation of electrical equipment Residential: receptacle within 1.5 m of a sink is not GFCI protected. | Sink_Receptacle.png | file://x:/photopub/docs/0000000454/03993733-e06a-4c9d-9253-2a8465261d5b.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__1bd98785_f9ce_454f_885d_51bfb9cabe15
GAHE-665415-2016 | HE-438906-2016 | 9/16/2016 12:48:25 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | The as found hazard was a pool boiler which had been incorrectly reassembled after a service. The unit was assembled without reinstalling a flue collector plate responsible for directing the flue gases into the venting system. This is a hazard because it was allow the flue gases to enter the mechanical room. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | CO_measurement_.png | file://x:/photopub/docs/0000000486/985448dc-ae37-4d73-b550-ffc5502d9c77.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74a74e17_dd43_4295_a592_82773ea274c3
GAHE-665415-2016 | HE-438906-2016 | 9/16/2016 12:48:25 PM | ASSESS: GA HE: Hazard Elimination | png | #asFound | GA154 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | 5 | 5 | The as found hazard was a pool boiler which had been incorrectly reassembled after a service. The unit was assembled without reinstalling a flue collector plate responsible for directing the flue gases into the venting system. This is a hazard because it was allow the flue gases to enter the mechanical room. | 5 | Appliance placed into service unsafely (example: flame impingement produces excessive Carbon Monoxide and appliance spills) | Missing_flue_plate.png | file://x:/photopub/docs/0000000486/c92ac2e8-64bf-4b3b-a961-0221bd401c4c.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__74a74e17_dd43_4295_a592_82773ea274c3
ELIN-640896-2016 | EL-359769-2016 | 9/16/2016 1:38:34 PM | ASSESS: EL: Final | png | #asFound | EL141 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | 3 | 3 | The code requires most receptacle branch circuits in dwelling units to be Arc Fault Circuit Interrupter (AFCI) protected. This is required to provide protection from series and parallel arcing faults that can occur on branch circuit wiring and within cords and portable equipment plugged into receptacles. This installation has new receptacle circuits that were added as part of a renovation to the kitchen area of an existing house. AFCI protection was not provided for two 15A 120V receptacle branch circuits. This is a potential fire hazard if arcing faults occur on these receptacle branch circuits or from the equipment that is plugged into them. | 3 | Installation of electrical equipment Residential: Receptacle within 1.5 m of a sink is not GFCI protected. | Outside_receptacle_circuit_that_requires_AFCI_protection.png | file://x:/photopub/docs/0000000486/d7467ae8-3203-4a0d-84f2-6631080d09db.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bd195c6b_8fba_476e_aecc_de1064320a96
GAUP-659089-2016 | UW-435768-2016 | 9/9/2016 12:54:00 PM | ASSESS: GA UP: Regulated Work WO Permit | png | #asFound | GA002 | Installation clearances or set backs to propane containers not met | 2 | 2 |  | 2 | Installation clearances or set backs to propane containers not met | Electrical_deficiency1.png | file://x:/photopub/docs/0000000487/e538c095-b967-46de-bb3f-b6d6203e34f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9a4464ab_9a8d_4989_8250_52d0282d7316
ELIN-666687-2016 | UW-265372-2015 | 9/19/2016 1:32:10 PM | ASSESS: EL IN: Unsafe Condition | png | #asFound | EL249 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | 4 | 4 | Electrical service and distribution has been exposed to weather and not maintained. This is a equipment damage condition. 120/240 Volt, 400 Amp. | 4 | Category 1 • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. | Weathered_old_electrical_service_and_distribution_.png | file://x:/photopub/docs/0000000487/74812e6a-dd53-4295-a0a4-888c4685be2f.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d325d109_49e2_45cf_ae92_968544b2f53a
ELHE-618563-2016 | HE-416078-2016 | 7/29/2016 11:39:45 AM | ASSESS: EL HE: Hazard Elimination | png | #asFound | EL133 | Installation of electrical equipment General: improper polarity at receptacle. | 3 | 3 | Residential multi- unit tenant space has 120 volt reverse polarity receptacle that has sparked and create fire hazard and potential shock hazard. | 3 | Installation of electrical equipment General: improper polarity at receptacle. | Review.png | file://x:/photopub/docs/0000000463/0ddcb7a8-4a0a-40a9-998c-613301c8c65e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__f53ff547_d00a_4618_8d47_cde7f0b6e651
GAIN-618099-2016 | GA-410877-2016 | 7/26/2016 8:09:49 AM | ASSESS: GA: Final | png | #asFound | GA119 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | 3 | 3 | An insufficient air supply opening was provided for a laundry room at a motel with two commercial dryers and three commercial hot water tanks installed. If either or both of the dryers were to operate with the laundry room door closed it could create a negative environment allowing the flue products of the water heaters to spill into the space. The laundry room is occasionally occupied by staff and spilled flue products could result in potential carbon monoxide poisoning. | 3 | Combustion/Ventilation air requirements non-compliant (In consideration of size, screens, grills, support). | Insufficient_air_supply_opening.png | file://x:/photopub/docs/0000000461/22449036-e81f-4201-b419-ad08b047557a.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__20ffb920_c826_4375_a45f_f7ec7d1f68bc
EDIN-620730-2016 | ED-367356-2016 | 8/11/2016 1:17:59 PM | ASSESS: ED IN: Acceptance | png | #asFound | ED056 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | 3 | 3 | Edge of access ramp at lower landing exposed/not protected with a railing. Users could trip/fall from the side of ramp. | 3 | Uneven Landing Surface Slipping /Tripping Hazard Well Lit | Lower_landing_ramp.png | file://x:/photopub/docs/0000000469/a5f35324-a2ac-4138-950c-be2ea647e704.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__9fcc4c95_cb65_4ea8_a4b4_2cf7e75ee72e
ELIN-629445-2016 | EL-352233-2016 | 8/12/2016 1:32:50 PM | ASSESS: EL: Service Connection | png | #asFound | EL005 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | 3 | 3 | Panel is open and scheduled to be energized. Potential for shock. | 3 | Equipment / Conductors are exposed to accidental contact by persons Equipment is energized; • covers or other protective barriers are not present or damaged; • energized parts are exposed to accidental contact; and • in an area that is not normally accessible to persons. | Panel_exposed_and_neutral_grounded.png | file://x:/photopub/docs/0000000470/39d1b00f-ba64-484b-914a-07f1e76425d4.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__fd644f95_10db_4f03_b84d_1394b100a260
BPVOP-611131-2016 | 2270479 | 7/13/2016 2:24:47 PM | ASSESS: BPV OP: Re-Certification Boiler | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | Upon assessment of Hot Water Boiler with Heating surface area of 37square meters, Maximum Allowable Working Pressure (MAWP) of 125psig and Maximum Allowable Water Temperature (MAWT) of 250*Fahrenheit, it was determined that safety relief valve has exceeded the required 6year interval for servicing/replacement. Failure to have safety valve serviced or replaced as required may subject boiler to pressure above MAWP if operating control fails to shut down boiler. This could result in failure of pressure-boundary with rapid uncontrolled release of hot water and may cause a severe incident (severe scalding of personnel in the vicinity, damage to nearby equipment etc.). | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | SAFETY_RELIEF_VALVE.png | file://x:/photopub/docs/0000000455/3f2e57c3-42b7-450b-88c3-2a3bb0c604f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7f13c898_d399_4909_8fc2_90b54d268955
AMOP-632000-2016 | 3277054 | 8/16/2016 1:05:53 PM | ASSESS: AM OP: Periodic | png | #asFound | AM028 | Procedures/Signs not posted Improper training or procedure | 1 | 1 | Inadequate signage to keep area clear at splashdown. | 1 | Procedures/Signs not posted Improper training or procedure | Splashdown_pic.png | file://x:/photopub/docs/0000000471/34655df4-e5f5-482c-a97f-34341271fb95.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__290e121a_3fd1_4ce4_a03c_67e304fc9e3c
ELIN-661600-2016 | EL-436420-2016 | 9/14/2016 11:15:35 AM | ASSESS: EL: Final | png | #asFound | EL137 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | 3 | 3 | Standard receptacles and cover installed for exterior receptacles. Receptacles exposed to weather may cause stray voltages to be present when in use. These stray voltages may cause shock or fire to persons or property if adequate covers and GFCI protection is not available. | 3 | Installation of electrical equipment General: covers or canopies on boxes have not been installed. | Wet_location_cover_not_installed_.png | file://x:/photopub/docs/0000000485/f915035e-2fe5-401e-80d9-0db043056ddc.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__bf3df74b_b2e5_4858_a468_1b2fbb66da56
ELIN-602352-2016 | EL-401741-2016 | 7/12/2016 9:24:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 3 | Connection configurations on the secondary of transformers are required to be completed according to the wiring diagrams supplied by the manufacturer. This is required to ensure that the proper terminations are made to provide the intended voltage ratings for the system being connected. This installation of a 600V to 120/240V, 25 KVA transformer in a shipping container at a fish farm has the secondary windings connected incorrectly. There is bus bars connecting both leads of the transformer windings together creating a short circuit condition on the secondary of the transformer. This is a fire hazard if the over current devices on the primary of the transformer do not open the circuit and the transformer windings over heat and start on fire. The system is currently not energized but connection to the utility was requested and the connection was pending prior to the inspection. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Connections_on_secondary_of_transformer_-_windings_are_shorted_out_from_factory.png | file://x:/photopub/docs/0000000455/e9fc9074-5087-4136-bb5f-fa076cc42779.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1c22fa_5f05_4afe_bfad_0854ea526986
ELIN-602352-2016 | EL-401741-2016 | 7/12/2016 9:24:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 3 | Connection configurations on the secondary of transformers are required to be completed according to the wiring diagrams supplied by the manufacturer. This is required to ensure that the proper terminations are made to provide the intended voltage ratings for the system being connected. This installation of a 600V to 120/240V, 25 KVA transformer in a shipping container at a fish farm has the secondary windings connected incorrectly. There is bus bars connecting both leads of the transformer windings together creating a short circuit condition on the secondary of the transformer. This is a fire hazard if the over current devices on the primary of the transformer do not open the circuit and the transformer windings over heat and start on fire. The system is currently not energized but connection to the utility was requested and the connection was pending prior to the inspection. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Name_plate_data_and_wiring_diagrams_for_transformer_.png | file://x:/photopub/docs/0000000455/151a3274-d5b7-489d-bf18-2098095667f9.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1c22fa_5f05_4afe_bfad_0854ea526986
ELIN-602352-2016 | EL-401741-2016 | 7/12/2016 9:24:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 3 | Connection configurations on the secondary of transformers are required to be completed according to the wiring diagrams supplied by the manufacturer. This is required to ensure that the proper terminations are made to provide the intended voltage ratings for the system being connected. This installation of a 600V to 120/240V, 25 KVA transformer in a shipping container at a fish farm has the secondary windings connected incorrectly. There is bus bars connecting both leads of the transformer windings together creating a short circuit condition on the secondary of the transformer. This is a fire hazard if the over current devices on the primary of the transformer do not open the circuit and the transformer windings over heat and start on fire. The system is currently not energized but connection to the utility was requested and the connection was pending prior to the inspection. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 25_KVA_transformer_where_connections_are_incorrect.png | file://x:/photopub/docs/0000000455/56ba4cb0-0250-4686-9562-751d9ebf4114.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1c22fa_5f05_4afe_bfad_0854ea526986
ELIN-602352-2016 | EL-401741-2016 | 7/12/2016 9:24:11 PM | ASSESS: EL: Service Connection | png | #asFound | EL157 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | 4 | 3 | Connection configurations on the secondary of transformers are required to be completed according to the wiring diagrams supplied by the manufacturer. This is required to ensure that the proper terminations are made to provide the intended voltage ratings for the system being connected. This installation of a 600V to 120/240V, 25 KVA transformer in a shipping container at a fish farm has the secondary windings connected incorrectly. There is bus bars connecting both leads of the transformer windings together creating a short circuit condition on the secondary of the transformer. This is a fire hazard if the over current devices on the primary of the transformer do not open the circuit and the transformer windings over heat and start on fire. The system is currently not energized but connection to the utility was requested and the connection was pending prior to the inspection. | 4 | Installation of electrical equipment • Equipment is damaged and needs to be either replaced or repaired; and • Not suitable for continued use. Examples may be enviromental, mounting means, ventilation, etc. | Container_where_equipment_is_installed_inside.png | file://x:/photopub/docs/0000000455/c44e6b2b-0a6b-4796-a07b-ca49b26b0ecb.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__7e1c22fa_5f05_4afe_bfad_0854ea526986
ELIN-625498-2016 | EL-351160-2016 | 8/8/2016 4:46:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Conductor termination lugs in breaker panels are required to be approved for the equipment that they are connected to. This is required to ensure a solid conductor connection to the equipment is maintained. This installation for wiring of a new house has a solderless termination lug installed onto the neutral bus in the main panel that is not approved for use with this panel. The lug is fastened to the bus with one of the wire termination screws on the bus which does not provide a solid connection between the lug and the bus. The neutral conductor of the sub-panel feeder cable is terminated into this lug. Left uncorrected this is a potential fire hazard if the connection becomes loose and over heats. | 3 | General Equipment is not approved for the specific use | Main_panel_in_garage.png | file://x:/photopub/docs/0000000467/767985ee-f83d-4ea8-a9c2-ab10e9a3eb32.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__128a1dbe_1454_4f07_825b_ae76a2d2d0f5
ELIN-625498-2016 | EL-351160-2016 | 8/8/2016 4:46:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Conductor termination lugs in breaker panels are required to be approved for the equipment that they are connected to. This is required to ensure a solid conductor connection to the equipment is maintained. This installation for wiring of a new house has a solderless termination lug installed onto the neutral bus in the main panel that is not approved for use with this panel. The lug is fastened to the bus with one of the wire termination screws on the bus which does not provide a solid connection between the lug and the bus. The neutral conductor of the sub-panel feeder cable is terminated into this lug. Left uncorrected this is a potential fire hazard if the connection becomes loose and over heats. | 3 | General Equipment is not approved for the specific use | Front_of_house_under_construction.png | file://x:/photopub/docs/0000000467/aa7abe46-9dd9-4fa0-9741-9c173cbe78a6.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__128a1dbe_1454_4f07_825b_ae76a2d2d0f5
ELIN-625498-2016 | EL-351160-2016 | 8/8/2016 4:46:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Conductor termination lugs in breaker panels are required to be approved for the equipment that they are connected to. This is required to ensure a solid conductor connection to the equipment is maintained. This installation for wiring of a new house has a solderless termination lug installed onto the neutral bus in the main panel that is not approved for use with this panel. The lug is fastened to the bus with one of the wire termination screws on the bus which does not provide a solid connection between the lug and the bus. The neutral conductor of the sub-panel feeder cable is terminated into this lug. Left uncorrected this is a potential fire hazard if the connection becomes loose and over heats. | 3 | General Equipment is not approved for the specific use | a_lug_that_is_not_approved_for_this_panel_is_fastened_to_the_neutral_bus.png | file://x:/photopub/docs/0000000467/e15ca3fb-7686-4223-918e-d8ac6519508e.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__128a1dbe_1454_4f07_825b_ae76a2d2d0f5
ELIN-625498-2016 | EL-351160-2016 | 8/8/2016 4:46:08 PM | ASSESS: EL: Rough Wiring-Complete | png | #asFound | EL069 | General Equipment is not approved for the specific use | 3 | 3 | Conductor termination lugs in breaker panels are required to be approved for the equipment that they are connected to. This is required to ensure a solid conductor connection to the equipment is maintained. This installation for wiring of a new house has a solderless termination lug installed onto the neutral bus in the main panel that is not approved for use with this panel. The lug is fastened to the bus with one of the wire termination screws on the bus which does not provide a solid connection between the lug and the bus. The neutral conductor of the sub-panel feeder cable is terminated into this lug. Left uncorrected this is a potential fire hazard if the connection becomes loose and over heats. | 3 | General Equipment is not approved for the specific use | Inside_main_panel_and_neutral_termination_lug_for_suite_feeder_neutral_conductor.png | file://x:/photopub/docs/0000000467/587c17d1-8333-477d-9ff7-0588808cf1da.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__128a1dbe_1454_4f07_825b_ae76a2d2d0f5
ELIN-639292-2016 | EL-349575-2016 | 8/29/2016 11:39:36 AM | ASSESS: EL: Final | png | #asFound | EL142 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | 3 | 3 | Receptacle not installed on finished wall. If receptacles are not installed where required, and the circuit is turned on at the over current device, there is a potential for energized conductors to be present. If these energized conductors accidentally come in contact with persons or property there is a potential for shock and fire. | 3 | Installation of electrical equipment Residential: tamper-resistant receptacles have not been installed where required. | Receptacle_not_installed__.png | file://x:/photopub/docs/0000000477/376b6a7a-35fc-4ed1-8b74-4e1f36c1d224.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__4108e437_a26a_4016_b77e_4e9fa45a34b0
ELOP-585450-2016 | 5235 | 9/2/2016 10:24:50 AM | ASSESS: EL OP: Regular Scheduled | png | #asFound | EL064 | General Working space or dedicated space is being used for storage | 1 | 1 |  | 1 | General Working space or dedicated space is being used for storage | Main_Distribution.png | file://x:/photopub/docs/0000000479/c1fd259b-a33c-493c-ac0d-7d6c2f084b02.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__d33b1f03_b39c_46ff_affe_a7d41d6404b8
BPVIN-661498-2016 | BPV-436204-2016 | 9/8/2016 9:07:25 AM | ASSESS: BPV IN: Final (First Certification) REF/PV | png | #asFound | BP131 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | 3 | 3 | There is no records of when the safety valve was last replaced or serviced on a air receiver machine mount with a maximum working pressure of 200 psig. If left in this condition, the safety valve could malfunction resulting in a critical situation. | 3 | 3.1.1 Safeties will not function - Pressure Relief Device valve service or test intervals beyond the required interval outlined in CSA B-51 | Air_receiver.png | file://x:/photopub/docs/0000000485/6e46cc57-15f1-4eeb-bbda-5f3f6a9f94f8.png | http://app02/energovprod/Default.aspx?Link=EnerGovSilverlight_Inspections_ManageInspection__a6328355_28d6_467b_a8a7_7f4e4dcfd30b